## Info
This Excel file provides a summary of the experimental data that has been acquired by Verschaffel-Drefke et al. (2021) and is presentend in "Heat Dissipation in variable Underground Power Cable Beddings: Experiences from a Real Scale Field Experiment". Further information can be found in the corresponding Energies publication.
Basic Bedding Properties:
The main properties of the bedding materials used in the study are summarized.
TH Bedding Characteristics:
The measured water retention characteristics (WRC), unsaturated hydraulic conductivity characteristics (UHCC) and thermal conductivity dryout curves (TCDC) of the four bedding materials of the main field are provided.
Load Profils:
The load profiles used for the dynamic loading experiments are presented.
Experiment - Data - MF_IV_CL:
The measured data of the constant loading experiment of the single MV-trefoil (IV) is provided.
Experiment - Data - MF_IV_EVU:
The measured data of the dynamic loading experiment with the EVU-profile of the single MV-trefoil (IV) is provided.
Experiment - Data - MF_IV_PV:
The measured data of the dynamic loading experiment with the PV-profile of the single MV-trefoil (IV) is provided.
Experiment - Data - SF_V+VI:
The measured data of the constand and dynamic loading experiments of the protection pipe systems (V) and (VI) are provided.
Experiment - Data - MF_III_CL:
The measured data of the constand loading experiments during the long-term experiment of the two MV-Trefoils (II) is provided.
Weather - Data - Temp:
The measured air and undisturbed soil temperatures at the location of the weather station over one calendar year are provided.

## Basic Bedding Properties
[5 empty] | Main Field |  |  |  | Side Field
| Parameter |  |  | Unit | Silt | Sand | Fluidized Backfill | Loam | Grouting Material (cable duct)
Solid Phase Properties | Grain Size Distribution | d10 |  | mm | 0.007 | 0.09 | 0.18* | < 0.001 | not available
|  | d30 |  | mm | 0.02 | 0.14 | 0.34* | 0.006
|  | d50 |  | mm | 0.03 | 0.19 | 0.51* | 0.04
|  | d60 |  | mm | 0.04 | 0.21 | 0.63* | 0.06
|  | Uniformity coefficient CU |  | - | 5.7 | 2.3 | 3.5* | > 15
| Grain Density |  |  | g cm-3 | 2.67 | 2.66 | 2.75 | 2.75 | 2.56
| Organic Content |  |  | M.-% | 1.9 | 1.1 | 0.8 | 1.4 | not available
| Heat Capacity | Specific | at 20 °C | J g-1 K-1 | 0.77 | 0.74 | 0.75 | 0.8 | 0.74
|  |  | at 70 °C |  | 0.87 | 0.86 | 0.89 | 0.89 | 0.9
|  | Volumetric | at 20 °C | J m-3 K-1 | 2055900 | 1968400 | 2062500 | 2200000 | 1894400
|  |  | at 70 °C |  | 2322900 | 2287600 | 2447500 | 2447500 | 2304000
Bulk Properties | Packing | Dry Density |  | g cm-3 | 1.72 | 1.62 | 1.64 | 1.75 | 1
|  | Porosity |  | % | 35.6 | 39.1 | 40.4 | 36.4 | 60.9
| Thermal Conductivity | Dry |  | W m-1 K-1 | see data in "TH Bedding Characteristic" |  |  |  | 0.59
|  | Wet (near saturation) |  | W m-1 K-1 |  |  |  |  | 3.01
*Dry raw materials prior to hardening

## TH Bedding Characteristic
| Silt | [5 empty] | Sand | [5 empty] | Fluidized Backfill | [5 empty] | Loam
| Water Retention Characteristics |  | Unsaturated Hydraulic Conductivity Characteristics |  | Thermal Conductivity Dryout Curve |  | Water Retention Characteristics |  | Unsaturated Hydraulic Conductivity Characteristics |  | Thermal Conductivity Dryout Curve |  | Water Retention Characteristics |  | Unsaturated Hydraulic Conductivity Characteristics |  | Thermal Conductivity Dryout Curve |  | Water Retention Characteristics |  | Unsaturated Hydraulic Conductivity Characteristics |  | Thermal Conductivity Dryout Curve
Parameter | Volumetric Water Content | pF | Volumetric Water Content | Hydraulic Conductivity | Volumetric Water Content | Thermal Conductivity | Volumetric Water Content | pF | Volumetric Water Content | Hydraulic Conductivity | Volumetric Water Content | Thermal Conductivity | Volumetric Water Content | pF | Volumetric Water Content | Hydraulic Conductivity | Volumetric Water Content | Thermal Conductivity | Volumetric Water Content | pF | Volumetric Water Content | Hydraulic Conductivity | Volumetric Water Content | Thermal Conductivity
Unit | % |  | % | m s-1 | % | W m-1 K-1 | % |  | % | m s-1 | % | W m-1 K-1 | % |  | % | m s-1 | % | W m-1 K-1 | % |  | % | m s-1 | % | W m-1 K-1
| 38.37 | 1.056 | 35.91 | 1.1844e-08 | 38.34 | 1.985 | 35.46 | 0.616 | 13.25 | 1.8344e-08 | 35.25 | 2.185 | 40.07 | 0.502 | 31.42 | 1.1053e-08 | 40.58 | 2.195 | 36.87 | 0.68 | 33.92 | 5.4136e-09 | 36.98 | 1.53
| 38.37 | 1.059 | 35.87 | 1.1053e-08 | 38.05 | 1.985 | 35.46 | 0.614 | 12.95 | 1.5977e-08 | 34.94 | 2.185 | 40.07 | 0.502 | 31.37 | 1.0315e-08 | 40.5 | 2.192 | 36.87 | 0.68 | 33.86 | 4.9373e-09 | 36.94 | 1.543
| 38.37 | 1.063 | 35.83 | 1.0556e-08 | 37.77 | 1.974 | 35.46 | 0.612 | 12.66 | 1.2986e-08 | 34.73 | 2.184 | 40.07 | 0.503 | 31.33 | 1.0081e-08 | 40.41 | 2.192 | 36.87 | 0.68 | 33.8 | 4.6077e-09 | 36.89 | 1.541
| 38.37 | 1.066 | 35.79 | 1.0081e-08 | 37.57 | 1.968 | 35.46 | 0.611 | 12.35 | 1.1311e-08 | 34.51 | 2.181 | 40.07 | 0.503 | 31.29 | 9.8511e-09 | 40.33 | 2.194 | 36.86 | 0.681 | 33.75 | 4.4003e-09 | 36.84 | 1.542
| 38.36 | 1.063 | 35.75 | 9.4078e-09 | 37.41 | 1.967 | 35.46 | 0.613 | 12.04 | 9.4078e-09 | 34.3 | 2.182 | 40.07 | 0.504 | 31.25 | 1.0081e-08 | 40.24 | 2.193 | 36.86 | 0.681 | 33.69 | 4.3002e-09 | 36.79 | 1.528
| 38.36 | 1.054 | 35.71 | 9.1936e-09 | 37.23 | 1.954 | 35.46 | 0.62 | 11.75 | 7.1365e-09 | 34.09 | 2.18 | 40.06 | 0.506 | 31.2 | 9.4078e-09 | 40.17 | 2.191 | 36.86 | 0.682 | 33.63 | 3.338e-09 | 36.73 | 1.541
| 38.35 | 1.045 | 35.67 | 8.58e-09 | 37.1 | 1.956 | 35.45 | 0.628 | 11.47 | 6.0742e-09 | 33.88 | 2.178 | 40.06 | 0.507 | 31.16 | 8.58e-09 | 40.08 | 2.193 | 36.86 | 0.682 | 33.57 | 2.6515e-09 | 36.67 | 1.541
| 38.34 | 1.041 | 35.63 | 8.1938e-09 | 36.93 | 1.962 | 35.43 | 0.638 | 11.18 | 5.0523e-09 | 33.68 | 2.178 | 40.05 | 0.509 | 31.12 | 7.1365e-09 | 39.99 | 2.192 | 36.86 | 0.683 | 33.52 | 2.3631e-09 | 36.62 | 1.536
| 38.34 | 1.042 | 35.59 | 8.0073e-09 | 36.78 | 1.959 | 35.42 | 0.652 | 10.89 | 4.2023e-09 | 33.47 | 2.179 | 40.05 | 0.51 | 31.08 | 7.3027e-09 | 39.9 | 2.19 | 36.85 | 0.683 | 33.46 | 2.1061e-09 | 36.56 | 1.538
| 38.33 | 1.039 | 35.55 | 8.1938e-09 | 36.66 | 1.959 | 35.39 | 0.669 | 10.61 | 3.338e-09 | 33.26 | 2.18 | 40.04 | 0.512 | 17.66 | 1.0802e-11 | 39.83 | 2.191 | 36.85 | 0.684 | 33.4 | 2.1061e-09 | 36.49 | 1.536
| 38.32 | 1.038 | 35.51 | 7.825e-09 | 35.38 | 1.948 | 35.37 | 0.688 | 10.34 | 2.5911e-09 | 33.05 | 2.178 | 40.04 | 0.514 |  |  | 39.75 | 2.189 | 36.85 | 0.684 | 33.34 | 2.2054e-09 | 36.42 | 1.533
| 38.3 | 1.044 | 35.47 | 7.6469e-09 | 35.28 | 1.95 | 35.34 | 0.716 | 10.1 | 1.8771e-09 | 32.85 | 2.178 | 40.03 | 0.515 |  |  | 39.64 | 2.194 | 36.84 | 0.683 | 33.28 | 2.0113e-09 | 36.35 | 1.531
| 38.29 | 1.048 | 35.43 | 7.3027e-09 | 35.18 | 1.947 | 35.31 | 0.749 | 9.87 | 1.491e-09 | 32.65 | 2.178 | 40.02 | 0.516 |  |  | 39.56 | 2.191 | 36.84 | 0.683 | 33.21 | 2.0113e-09 | 36.29 | 1.531
| 38.28 | 1.053 | 35.38 | 7.1365e-09 | 35.08 | 1.946 | 35.27 | 0.758 | 9.66 | 1.2402e-09 | 32.45 | 2.179 | 40.01 | 0.517 |  |  | 39.48 | 2.192 | 36.83 | 0.684 | 33.15 | 2.1061e-09 | 36.22 | 1.532
| 38.26 | 1.057 | 35.34 | 6.8153e-09 | 34.98 | 1.944 | 35.23 | 0.754 | 9.45 | 9.4078e-10 | 32.26 | 2.173 | 40 | 0.518 |  |  | 39.39 | 2.19 | 36.82 | 0.686 | 33.09 | 2.0113e-09 | 36.14 | 1.532
| 38.24 | 1.06 | 35.3 | 6.6602e-09 | 34.88 | 1.95 | 35.19 | 0.756 | 9.27 | 7.1365e-10 | 32.06 | 2.174 | 39.99 | 0.518 |  |  | 39.3 | 2.191 | 36.82 | 0.689 | 33.03 | 1.9208e-09 | 36.08 | 1.535
| 38.23 | 1.063 | 35.26 | 6.5086e-09 | 34.78 | 1.945 | 35.15 | 0.765 | 9.13 | 3.5767e-10 | 31.88 | 2.176 | 39.98 | 0.517 |  |  | 39.2 | 2.187 | 36.81 | 0.692 | 32.97 | 1.8344e-09 | 36 | 1.535
| 38.21 | 1.066 | 35.22 | 6.5086e-09 | 34.71 | 1.95 | 35.11 | 0.776 | 9 | 4.1066e-10 | 31.69 | 2.174 | 39.97 | 0.516 |  |  | 39.16 | 2.184 | 36.8 | 0.695 | 32.9 | 1.8344e-09 | 35.94 | 1.535
| 38.19 | 1.068 | 35.18 | 6.8153e-09 | 34.61 | 1.947 | 35.06 | 0.781 | 8.86 | 3.5767e-10 | 31.49 | 2.172 | 39.96 | 0.513 |  |  | 39.06 | 2.194 | 36.8 | 0.697 | 32.84 | 1.673e-09 | 35.87 | 1.531
| 38.16 | 1.07 | 35.14 | 6.8153e-09 | 34.51 | 1.949 | 35.01 | 0.783 | 8.71 | 3.1878e-10 | 31.31 | 2.17 | 39.95 | 0.504 |  |  | 38.96 | 2.173 | 36.79 | 0.698 | 32.77 | 1.5977e-09 | 35.78 | 1.533
| 38.14 | 1.074 | 35.1 | 6.2156e-09 | 34.44 | 1.948 | 34.96 | 0.789 | 8.57 | 2.1061e-10 | 31.12 | 2.174 | 39.93 | 0.486 |  |  | 38.85 | 2.161 | 36.78 | 0.708 | 32.71 | 1.673e-09 | 35.71 | 1.535
| 38.12 | 1.078 | 35.06 | 6.5086e-09 | 34.34 | 1.949 | 34.91 | 0.803 | 8.44 | 1.9208e-10 | 30.94 | 2.171 | 39.92 | 0.467 |  |  | 38.8 | 2.169 | 36.77 | 0.746 | 32.64 | 1.5977e-09 | 35.63 | 1.533
| 38.09 | 1.082 | 35.02 | 7.4728e-09 | 34.28 | 1.952 | 34.86 | 0.821 | 8.3 | 1.5258e-10 | 30.75 | 2.172 | 39.9 | 0.456 |  |  | 38.69 | 2.164 | 36.76 | 0.791 | 32.58 | 1.3915e-09 | 35.56 | 1.532
| 38.06 | 1.086 | 34.98 | 7.6469e-09 | 34.21 | 1.954 | 34.81 | 0.846 | 8.17 | 1.2691e-10 | 30.57 | 2.172 | 39.89 | 0.46 |  |  | 38.64 | 2.166 | 36.75 | 0.824 | 32.51 | 1.3598e-09 | 35.48 | 1.531
| 38.04 | 1.087 | 34.94 | 7.825e-09 | 34.11 | 1.952 | 34.76 | 0.897 | 8.04 | 9.4078e-11 | 30.38 | 2.172 | 39.87 | 0.476 |  |  | 38.53 | 2.163 | 36.74 | 0.855 | 32.44 | 1.4571e-09 | 35.4 | 1.527
| 38.01 | 1.091 | 34.89 | 8.1938e-09 | 34.04 | 1.956 | 34.71 | 0.968 | 7.91 | 8.0073e-11 | 30.2 | 2.173 | 39.86 | 0.496 |  |  | 38.47 | 2.155 | 36.73 | 0.89 | 32.38 | 1.3915e-09 | 35.32 | 1.528
| 37.98 | 1.098 | 34.85 | 8.0073e-09 | 33.93 | 1.96 | 34.66 | 1.043 | 7.79 | 6.3604e-11 | 30.02 | 2.173 | 39.84 | 0.515 |  |  | 38.36 | 2.15 | 36.71 | 0.929 | 32.31 | 1.2986e-09 | 35.26 | 1.532
| 37.95 | 1.108 | 34.81 | 8.1938e-09 | 33.86 | 1.961 | 34.6 | 1.118 | 7.67 | 4.9373e-11 | 29.84 | 2.172 | 39.82 | 0.533 |  |  | 38.31 | 2.148 | 36.7 | 0.979 | 32.24 | 1.212e-09 | 35.18 | 1.53
| 37.92 | 1.118 | 34.77 | 8.1938e-09 | 33.79 | 1.962 | 34.56 | 1.189 | 7.56 | 4.0132e-11 | 29.67 | 2.173 | 39.8 | 0.551 |  |  | 38.19 | 2.139 | 36.69 | 1.02 | 32.17 | 1.1574e-09 | 35.09 | 1.53
| 37.88 | 1.128 | 34.73 | 8.0073e-09 | 33.72 | 1.964 | 34.51 | 1.255 | 7.45 | 3.338e-11 | 29.49 | 2.172 | 39.78 | 0.569 |  |  | 38.13 | 2.138 | 36.67 | 1.012 | 32.1 | 1.1311e-09 | 35.04 | 1.531
| 37.85 | 1.138 | 34.69 | 7.825e-09 | 33.65 | 1.964 | 34.45 | 1.316 | 7.34 | 2.2568e-11 | 29.32 | 2.164 | 39.76 | 0.587 |  |  | 38.02 | 2.135 | 36.66 | 0.993 | 32.03 | 1.1053e-09 | 34.95 | 1.531
| 37.82 | 1.148 | 34.65 | 7.4728e-09 | 33.54 | 1.961 | 34.4 | 1.373 | 7.25 | 1.7926e-11 | 29.14 | 2.169 | 39.74 | 0.607 |  |  | 37.96 | 2.131 | 36.64 | 1.009 | 31.96 | 1.1053e-09 | 34.89 | 1.531
| 37.78 | 1.157 | 34.61 | 7.1365e-09 | 33.46 | 1.96 | 34.34 | 1.425 | 7.16 | 1.673e-11 | 28.97 | 2.163 | 39.72 | 0.635 |  |  | 37.9 | 2.128 | 36.63 | 1.046 | 31.89 | 1.0802e-09 | 34.8 | 1.531
| 37.75 | 1.167 | 34.57 | 7.1365e-09 | 33.39 | 1.96 | 34.29 | 1.471 | 7.06 | 1.6349e-11 | 28.8 | 2.162 | 39.7 | 0.67 |  |  | 37.79 | 2.124 | 36.61 | 1.094 | 31.82 | 1.0556e-09 | 34.74 | 1.532
| 37.72 | 1.176 | 34.53 | 7.1365e-09 | 33.23 | 1.962 | 34.23 | 1.511 | 5.84 | 1.5258e-12 | 28.62 | 2.16 | 39.67 | 0.704 |  |  | 37.73 | 2.12 | 36.6 | 1.092 | 31.75 | 1.0556e-09 | 34.65 | 1.532
| 37.69 | 1.184 | 34.49 | 6.8153e-09 | 33.15 | 1.957 | 34.16 | 1.546 |  |  | 28.45 | 2.153 | 39.65 | 0.732 |  |  | 37.67 | 2.118 | 36.58 | 1.044 | 31.68 | 9.8511e-10 | 34.59 | 1.532
| 37.66 | 1.194 | 34.45 | 6.5086e-09 | 33.07 | 1.953 | 34.1 | 1.577 |  |  | 28.27 | 2.155 | 39.63 | 0.757 |  |  | 37.61 | 2.118 | 36.56 | 1.03 | 31.6 | 8.9843e-10 | 34.53 | 1.531
| 37.63 | 1.204 | 34.41 | 6.3604e-09 | 32.98 | 1.959 | 34.04 | 1.603 |  |  | 28.1 | 2.149 | 39.6 | 0.785 |  |  | 37.49 | 2.113 | 36.54 | 1.057 | 31.53 | 8.7798e-10 | 34.44 | 1.531
| 37.6 | 1.216 | 34.37 | 6.3604e-09 | 32.89 | 1.96 | 33.97 | 1.626 |  |  | 27.92 | 2.151 | 39.57 | 0.816 |  |  | 37.42 | 2.11 | 36.52 | 1.07 | 31.46 | 8.58e-10 | 34.38 | 1.531
| 37.57 | 1.233 | 34.33 | 6.2156e-09 | 32.8 | 1.963 | 33.9 | 1.641 |  |  | 27.75 | 2.142 | 39.55 | 0.848 |  |  | 37.36 | 2.108 | 36.5 | 1.044 | 31.38 | 8.3847e-10 | 34.32 | 1.532
| 37.55 | 1.251 | 34.28 | 6.2156e-09 | 32.71 | 1.966 | 33.83 | 1.634 |  |  | 27.57 | 2.139 | 39.52 | 0.878 |  |  | 37.3 | 2.108 | 36.48 | 1.032 | 31.31 | 8.3847e-10 | 34.26 | 1.528
| 37.52 | 1.259 | 34.24 | 6.5086e-09 | 32.61 | 1.962 | 33.76 | 1.637 |  |  | 27.41 | 2.134 | 39.49 | 0.89 |  |  | 37.24 | 2.104 | 36.46 | 1.052 | 31.23 | 8.0073e-10 | 34.2 | 1.532
| 37.49 | 1.257 | 34.2 | 6.3604e-09 | 32.52 | 1.966 | 33.69 | 1.653 |  |  | 27.23 | 2.13 | 39.46 | 0.883 |  |  | 37.11 | 2.104 | 36.44 | 1.076 | 31.16 | 7.825e-10 | 34.1 | 1.528
| 37.46 | 1.262 | 34.16 | 6.0742e-09 | 32.43 | 1.968 | 33.61 | 1.657 |  |  | 27.06 | 2.125 | 39.43 | 0.892 |  |  | 37.05 | 2.1 | 36.41 | 1.098 | 31.08 | 7.825e-10 | 34.04 | 1.531
| 37.43 | 1.286 | 34.12 | 5.9359e-09 | 32.33 | 1.971 | 33.54 | 1.66 |  |  | 26.89 | 2.121 | 39.4 | 0.949 |  |  | 36.98 | 2.1 | 36.39 | 1.113 | 31.01 | 7.6469e-10 | 33.98 | 1.53
| 37.41 | 1.312 | 34.08 | 5.9359e-09 | 32.29 | 1.963 | 33.46 | 1.667 |  |  | 26.71 | 2.115 | 39.37 | 0.995 |  |  | 36.92 | 2.094 | 36.37 | 1.129 | 30.93 | 7.6469e-10 | 33.91 | 1.53
| 37.38 | 1.33 | 34.04 | 6.0742e-09 | 32.2 | 1.969 | 33.37 | 1.678 |  |  | 26.53 | 2.108 | 39.34 | 1.009 |  |  | 36.85 | 2.093 | 36.34 | 1.143 | 30.86 | 6.3604e-10 | 33.85 | 1.527
| 37.35 | 1.346 | 33.99 | 6.9741e-09 | 32.1 | 1.972 | 33.29 | 1.683 |  |  | 26.35 | 2.103 | 39.31 | 1.029 |  |  | 36.79 | 2.093 | 36.32 | 1.158 | 30.78 | 6.0742e-10 | 33.78 | 1.526
| 37.32 | 1.361 | 33.95 | 7.3027e-09 | 32 | 1.971 | 33.21 | 1.686 |  |  | 26.18 | 2.093 | 39.28 | 1.066 |  |  | 36.72 | 2.092 | 36.29 | 1.172 | 30.7 | 6.8153e-10 | 33.71 | 1.523
| 37.28 | 1.374 | 33.91 | 6.9741e-09 | 31.89 | 1.965 | 33.12 | 1.69 |  |  | 26 | 2.086 | 39.24 | 1.109 |  |  | 36.65 | 2.09 | 36.26 | 1.102 | 30.62 | 6.5086e-10 | 33.65 | 1.523
| 37.25 | 1.386 | 33.87 | 6.2156e-09 | 31.84 | 1.971 | 33.03 | 1.693 |  |  | 25.82 | 2.081 | 39.21 | 1.153 |  |  | 36.59 | 2.09 | 36.23 | 1.011 | 30.54 | 5.8008e-10 | 33.58 | 1.526
| 37.22 | 1.397 | 33.82 | 5.9359e-09 | 31.73 | 1.968 | 32.95 | 1.695 |  |  | 25.64 | 2.074 | 39.17 | 1.197 |  |  | 36.45 | 2.09 | 36.21 | 1.018 | 30.47 | 5.8008e-10 | 33.51 | 1.523
| 37.19 | 1.407 | 33.78 | 5.4136e-09 | 31.62 | 1.972 | 32.86 | 1.694 |  |  | 25.45 | 2.065 | 39.14 | 1.241 |  |  | 36.38 | 2.082 | 36.18 | 1.03 | 30.39 | 5.4136e-10 | 33.44 | 1.522
| 37.16 | 1.416 | 33.74 | 4.4003e-09 | 31.5 | 1.975 | 32.77 | 1.696 |  |  | 25.27 | 2.053 | 39.1 | 1.282 |  |  | 36.32 | 2.085 | 36.15 | 1.043 | 30.31 | 4.715e-10 | 33.37 | 1.522
| 37.12 | 1.424 | 33.69 | 3.8325e-09 | 31.44 | 1.978 | 32.68 | 1.7 |  |  | 25.09 | 2.041 | 39.06 | 1.312 |  |  | 36.25 | 2.081 | 36.11 | 1.053 | 30.23 | 4.5028e-10 | 33.3 | 1.521
| 37.09 | 1.431 | 33.65 | 3.66e-09 | 31.32 | 1.968 | 32.58 | 1.702 |  |  | 24.9 | 2.032 | 39.03 | 1.35 |  |  | 36.18 | 2.08 | 36.08 | 1.062 | 30.15 | 4.4003e-10 | 33.23 | 1.522
| 37.06 | 1.437 | 33.61 | 3.5767e-09 | 31.2 | 1.968 | 32.49 | 1.703 |  |  | 24.72 | 2.019 | 38.99 | 1.411 |  |  | 36.11 | 2.075 | 36.05 | 1.072 | 30.07 | 4.4003e-10 | 33.19 | 1.521
| 37.02 | 1.445 | 33.56 | 3.262e-09 | 31.14 | 1.969 | 32.4 | 1.705 |  |  | 24.53 | 2.004 | 38.95 | 1.449 |  |  | 36.04 | 2.075 | 36.02 | 1.079 | 29.98 | 4.3002e-10 | 33.12 | 1.519
| 36.99 | 1.454 | 33.52 | 2.7132e-09 | 31.02 | 1.971 | 32.3 | 1.706 |  |  | 24.35 | 1.993 | 38.91 | 1.481 |  |  | 35.97 | 2.072 | 35.98 | 1.091 | 29.9 | 4.2023e-10 | 33.04 | 1.517
| 36.95 | 1.462 | 33.47 | 2.2054e-09 | 30.89 | 1.965 | 32.21 | 1.707 |  |  | 24.17 | 1.982 | 38.87 | 1.554 |  |  | 35.9 | 2.071 | 35.95 | 1.111 | 29.82 | 4.0132e-10 | 32.97 | 1.516
| 36.92 | 1.469 | 33.42 | 2.0113e-09 | 30.82 | 1.953 | 32.11 | 1.709 |  |  | 23.99 | 1.966 | 38.83 | 1.613 |  |  | 35.83 | 2.066 | 35.91 | 1.127 | 29.74 | 3.9218e-10 | 32.89 | 1.516
| 36.88 | 1.476 | 33.38 | 2.1061e-09 | 30.69 | 1.954 | 32.01 | 1.71 |  |  | 23.81 | 1.952 | 38.79 | 1.654 |  |  | 35.76 | 2.065 | 35.88 | 1.138 | 29.66 | 3.7453e-10 | 32.82 | 1.514
| 36.84 | 1.484 | 33.33 | 2.1061e-09 | 30.56 | 1.951 | 31.91 | 1.711 |  |  | 23.63 | 1.942 | 38.75 | 1.71 |  |  | 35.69 | 2.063 | 35.84 | 1.146 | 29.57 | 3.5767e-10 | 32.78 | 1.511
| 36.81 | 1.492 | 33.28 | 1.6349e-09 | 30.49 | 1.948 | 31.81 | 1.712 |  |  | 23.46 | 1.929 | 38.7 | 1.773 |  |  | 35.69 | 2.063 | 35.8 | 1.159 | 29.49 | 3.4953e-10 | 32.7 | 1.512
| 36.77 | 1.499 | 33.23 | 1.3598e-09 | 30.36 | 1.947 | 31.71 | 1.713 |  |  | 23.29 | 1.915 | 38.66 | 1.836 |  |  | 35.61 | 2.06 | 35.76 | 1.175 | 29.41 | 3.338e-10 | 32.63 | 1.511
| 36.74 | 1.505 | 33.18 | 1.4239e-09 | 30.29 | 1.953 | 31.61 | 1.714 |  |  | 23.11 | 1.901 | 38.62 | 1.894 |  |  | 35.54 | 2.055 | 35.72 | 1.19 | 29.32 | 3.1878e-10 | 32.55 | 1.511
| 36.7 | 1.511 | 33.13 | 1.5613e-09 | 30.15 | 1.948 | 31.5 | 1.715 |  |  | 22.93 | 1.888 | 38.57 | 1.948 |  |  | 35.47 | 2.053 | 35.68 | 1.203 | 29.24 | 2.9073e-10 | 32.51 | 1.509
| 36.66 | 1.518 | 33.08 | 1.5977e-09 | 30.01 | 1.945 | 31.39 | 1.716 |  |  | 22.76 | 1.881 | 38.53 | 1.994 |  |  | 35.4 | 2.052 | 35.64 | 1.219 | 29.15 | 2.7764e-10 | 32.43 | 1.508
| 36.62 | 1.524 | 33.03 | 1.4571e-09 | 29.94 | 1.942 | 31.29 | 1.717 |  |  | 22.58 | 1.869 | 38.48 | 2.031 |  |  | 35.32 | 2.051 | 35.6 | 1.228 | 29.07 | 2.7764e-10 | 32.35 | 1.507
| 36.59 | 1.53 | 32.98 | 1.4239e-09 | 29.8 | 1.944 | 31.18 | 1.717 |  |  | 22.4 | 1.862 | 38.44 | 2.076 |  |  | 35.25 | 2.047 | 35.56 | 1.234 | 28.98 | 2.5911e-10 | 32.31 | 1.507
| 36.55 | 1.542 | 32.93 | 1.491e-09 | 29.73 | 1.941 | 31.07 | 1.718 |  |  | 22.22 | 1.853 | 38.39 | 2.121 |  |  | 35.18 | 2.049 | 35.52 | 1.241 | 28.9 | 2.4745e-10 | 32.23 | 1.504
| 36.51 | 1.558 | 32.87 | 1.6349e-09 | 29.59 | 1.938 | 30.96 | 1.72 |  |  | 22.04 | 1.846 | 38.35 | 2.154 |  |  | 35.1 | 2.043 | 35.47 | 1.245 | 28.81 | 2.4182e-10 | 32.15 | 1.504
| 36.47 | 1.572 | 32.82 | 1.7926e-09 | 29.52 | 1.945 | 30.85 | 1.721 |  |  | 21.86 | 1.838 | 38.3 | 2.189 |  |  | 35.03 | 2.037 | 35.43 | 1.256 | 28.72 | 2.3093e-10 | 32.11 | 1.502
| 36.43 | 1.586 | 32.76 | 1.7119e-09 | 29.38 | 1.941 | 30.73 | 1.721 |  |  | 21.68 | 1.835 | 38.25 | 2.232 |  |  | 34.95 | 2.041 | 35.38 | 1.266 | 28.64 | 2.1552e-10 | 32.03 | 1.501
| 36.39 | 1.601 | 32.7 | 1.5258e-09 | 29.3 | 1.941 | 30.62 | 1.721 |  |  | 21.5 | 1.83 | 38.21 | 2.274 |  |  | 34.95 | 2.034 | 35.34 | 1.276 | 28.55 | 2.1061e-10 | 31.95 | 1.499
| 36.35 | 1.615 | 32.64 | 1.8771e-09 | 29.16 | 1.938 | 30.5 | 1.723 |  |  | 21.32 | 1.826 | 38.16 | 2.311 |  |  | 34.88 | 2.034 | 35.29 | 1.292 | 28.46 | 2.0582e-10 | 31.9 | 1.498
| 36.31 | 1.627 | 32.59 | 2.1552e-09 | 29.09 | 1.936 | 30.38 | 1.724 |  |  | 21.15 | 1.821 | 38.11 | 2.344 |  |  | 34.8 | 2.027 | 35.24 | 1.305 | 28.38 | 2.0113e-10 | 31.82 | 1.497
| 36.27 | 1.64 | 32.53 | 1.673e-09 | 28.94 | 1.945 | 30.27 | 1.725 |  |  | 20.97 | 1.821 | 38.06 | 2.376 |  |  | 34.73 | 2.025 | 35.2 | 1.32 | 28.29 | 1.9208e-10 | 31.78 | 1.497
| 36.24 | 1.653 | 32.47 | 1.4239e-09 | 28.87 | 1.941 | 30.15 | 1.726 |  |  | 20.79 | 1.815 | 38.01 | 2.404 |  |  | 34.65 | 2.021 | 35.15 | 1.334 | 28.2 | 1.8344e-10 | 31.69 | 1.494
| 36.2 | 1.667 | 32.42 | 1.3598e-09 | 28.73 | 1.939 | 30.03 | 1.726 |  |  | 20.61 | 1.814 | 37.97 | 2.428 |  |  | 34.58 | 2.022 | 35.1 | 1.342 | 28.11 | 1.7926e-10 | 31.65 | 1.493
| 36.16 | 1.68 | 32.36 | 1.4239e-09 | 28.66 | 1.933 | 29.9 | 1.726 |  |  | 20.44 | 1.814 | 37.92 | 2.452 |  |  | 34.5 | 2.018 | 35.05 | 1.352 | 28.02 | 1.7119e-10 | 31.57 | 1.492
| 36.12 | 1.693 | 32.3 | 1.3915e-09 | 28.59 | 1.932 | 29.78 | 1.728 |  |  | 20.27 | 1.813 | 37.87 | 2.474 |  |  | 34.5 | 2.018 | 35 | 1.365 | 27.93 | 1.5613e-10 | 31.48 | 1.492
| 36.08 | 1.706 | 32.25 | 1.5258e-09 | 28.45 | 1.927 | 29.66 | 1.728 |  |  | 20.09 | 1.812 | 37.82 | 2.493 |  |  | 34.42 | 2.014 | 34.95 | 1.381 | 27.84 | 1.4239e-10 | 31.44 | 1.492
| 36.04 | 1.719 | 32.19 | 2.3093e-09 | 28.38 | 1.925 | 29.54 | 1.728 |  |  | 19.92 | 1.802 | 37.77 | 2.511 |  |  | 34.35 | 2.015 | 34.9 | 1.391 | 27.75 | 1.3289e-10 | 31.35 | 1.493
| 36 | 1.731 | 32.13 | 3.4158e-09 | 28.24 | 1.928 | 29.41 | 1.729 |  |  | 19.75 | 1.806 | 37.72 | 2.527 |  |  | 34.27 | 2.013 | 34.85 | 1.404 | 27.66 | 1.2986e-10 | 31.31 | 1.492
| 35.95 | 1.744 | 32.07 | 4.3002e-09 | 28.17 | 1.922 | 29.29 | 1.731 |  |  | 19.58 | 1.804 | 37.67 | 2.543 |  |  | 34.19 | 2.013 | 34.8 | 1.415 | 27.57 | 1.2691e-10 | 31.22 | 1.489
| 35.91 | 1.756 | 32.01 | 2.8411e-09 | 28.03 | 1.927 | 29.16 | 1.731 |  |  | 19.41 | 1.809 | 37.62 | 2.557 |  |  | 34.11 | 2.009 | 34.75 | 1.416 | 27.48 | 1.1844e-10 | 31.17 | 1.492
| 35.87 | 1.769 | 31.95 | 2.3631e-09 | 27.96 | 1.924 | 29.03 | 1.732 |  |  | 19.25 | 1.799 | 37.56 | 2.571 |  |  | 34.11 | 2.01 | 34.7 | 1.421 | 27.39 | 1.1311e-10 | 31.09 | 1.492
| 35.83 | 1.781 | 31.88 | 2.5321e-09 | 27.89 | 1.922 | 28.9 | 1.733 |  |  | 19.08 | 1.801 | 37.51 | 2.584 |  |  | 34.03 | 2.003 | 34.65 | 1.431 | 27.3 | 1.0556e-10 | 31.04 | 1.489
| 35.79 | 1.793 | 31.82 | 2.2054e-09 | 27.76 | 1.924 | 28.77 | 1.733 |  |  | 18.91 | 1.792 | 37.46 | 2.597 |  |  | 33.95 | 2 | 34.6 | 1.442 | 27.21 | 1.0081e-10 | 30.95 | 1.488
| 35.75 | 1.805 | 31.75 | 1.9208e-09 | 27.69 | 1.919 | 28.64 | 1.734 |  |  | 18.74 | 1.794 | 37.41 | 2.608 |  |  | 33.88 | 2.001 | 34.55 | 1.452 | 27.12 | 9.8511e-11 | 30.91 | 1.492
| 35.71 | 1.818 | 31.69 | 2.0113e-09 | 27.62 | 1.918 | 28.51 | 1.735 |  |  | 18.57 | 1.79 | 37.35 | 2.618 |  |  | 33.8 | 2 | 34.5 | 1.46 | 27.03 | 9.6269e-11 | 30.82 | 1.493
| 35.67 | 1.83 | 31.62 | 2.0582e-09 | 27.48 | 1.915 | 28.37 | 1.736 |  |  | 18.41 | 1.788 | 37.3 | 2.627 |  |  | 33.8 | 1.998 | 34.44 | 1.472 | 26.94 | 9.4078e-11 | 30.77 | 1.492
| 35.63 | 1.841 | 31.56 | 1.9208e-09 | 27.41 | 1.913 | 28.24 | 1.737 |  |  | 18.23 | 1.779 | 37.25 | 2.635 |  |  | 33.72 | 1.995 | 34.39 | 1.49 | 26.85 | 9.4078e-11 | 30.73 | 1.491
| 35.59 | 1.853 | 31.49 | 1.7926e-09 | 27.27 | 1.91 | 28.1 | 1.738 |  |  | 18.06 | 1.775 | 37.19 | 2.643 |  |  | 33.65 | 1.995 | 34.34 | 1.503 | 26.75 | 8.9843e-11 | 30.63 | 1.492
| 35.55 | 1.866 | 31.42 | 1.7119e-09 | 27.2 | 1.91 | 27.96 | 1.739 |  |  | 17.82 | 1.769 | 37.14 | 2.65 |  |  | 33.57 | 1.989 | 34.29 | 1.51 | 26.66 | 8.58e-11 | 30.59 | 1.489
| 35.51 | 1.878 | 31.35 | 1.7119e-09 | 27.13 | 1.916 | 27.82 | 1.74 |  |  | 17.6 | 1.767 | 37.08 | 2.656 |  |  | 33.49 | 1.99 | 34.24 | 1.517 | 26.57 | 8.3847e-11 | 30.5 | 1.491
| 35.47 | 1.891 | 31.28 | 1.673e-09 | 26.99 | 1.921 | 27.67 | 1.74 |  |  | 17.37 | 1.764 | 37.02 | 2.661 |  |  | 33.49 | 1.989 | 34.19 | 1.526 | 21.37 | 9.6269e-12 | 30.45 | 1.493
| 35.43 | 1.906 | 31.21 | 1.7518e-09 | 26.92 | 1.909 | 27.53 | 1.741 |  |  | 17.13 | 1.758 | 36.97 | 2.667 |  |  | 33.42 | 1.985 | 34.13 | 1.529 |  |  | 30.36 | 1.491
| 35.38 | 1.92 | 31.14 | 1.7119e-09 | 26.85 | 1.907 | 27.39 | 1.742 |  |  | 16.88 | 1.749 | 36.91 | 2.673 |  |  | 33.34 | 1.983 | 34.08 | 1.53 |  |  | 30.31 | 1.489
| 35.34 | 1.934 | 31.07 | 1.5977e-09 | 26.78 | 1.91 | 27.25 | 1.742 |  |  | 16.64 | 1.742 | 36.85 | 2.678 |  |  | 33.26 | 1.98 | 34.03 | 1.541 |  |  | 30.26 | 1.491
| 35.3 | 1.949 | 31 | 1.5613e-09 | 26.64 | 1.9 | 27.1 | 1.743 |  |  | 16.4 | 1.739 | 36.8 | 2.683 |  |  | 33.26 | 1.978 | 33.97 | 1.562 |  |  | 30.17 | 1.488
| 35.26 | 1.964 | 30.92 | 1.5613e-09 | 26.57 | 1.918 | 26.95 | 1.744 |  |  | 16.16 | 1.732 | 36.74 | 2.688 |  |  | 33.18 | 1.977 | 33.92 | 1.586 |  |  | 30.12 | 1.488
| 35.22 | 1.979 | 30.85 | 1.6349e-09 | 26.5 | 1.922 | 26.8 | 1.746 |  |  | 15.92 | 1.729 | 36.68 | 2.693 |  |  | 33.1 | 1.973 | 33.86 | 1.609 |  |  | 30.07 | 1.489
| 35.18 | 1.994 | 30.78 | 1.5258e-09 | 26.35 | 1.912 | 26.64 | 1.747 |  |  | 15.69 | 1.717 | 36.62 | 2.698 |  |  | 33.02 | 1.97 | 33.8 | 1.63 |  |  | 29.98 | 1.489
| 35.14 | 2.009 | 30.7 | 1.2986e-09 | 26.28 | 1.912 | 26.48 | 1.747 |  |  | 15.46 | 1.716 | 36.56 | 2.702 |  |  | 33.02 | 1.98 | 33.75 | 1.65 |  |  | 29.93 | 1.487
| 35.1 | 2.024 | 30.63 | 1.2402e-09 | 26.21 | 1.909 | 26.32 | 1.748 |  |  | 15.23 | 1.712 | 36.5 | 2.707 |  |  | 32.93 | 1.968 | 33.69 | 1.671 |  |  | 29.84 | 1.489
| 35.06 | 2.038 | 30.55 | 1.2402e-09 | 26.14 | 1.892 | 26.16 | 1.748 |  |  | 15 | 1.7 | 36.45 | 2.711 |  |  | 32.84 | 1.965 | 33.63 | 1.686 |  |  | 29.79 | 1.488
| 35.02 | 2.053 | 30.47 | 1.212e-09 | 26 | 1.921 | 26 | 1.749 |  |  | 14.77 | 1.7 | 36.39 | 2.716 |  |  | 32.84 | 1.968 | 33.57 | 1.691 |  |  | 29.74 | 1.486
| 34.98 | 2.067 | 30.4 | 1.1844e-09 | 25.93 | 1.904 | 25.84 | 1.749 |  |  | 14.55 | 1.692 | 36.32 | 2.72 |  |  | 32.77 | 1.964 | 33.52 | 1.693 |  |  | 29.64 | 1.487
| 34.94 | 2.08 | 30.32 | 1.1574e-09 | 25.86 | 1.933 | 25.67 | 1.75 |  |  | 14.32 | 1.685 | 36.26 | 2.725 |  |  | 32.7 | 1.962 | 33.46 | 1.707 |  |  | 29.6 | 1.487
| 34.89 | 2.094 | 30.24 | 1.212e-09 | 25.79 | 1.894 | 25.5 | 1.751 |  |  | 14.08 | 1.679 | 36.2 | 2.729 |  |  | 32.63 | 1.963 | 33.4 | 1.736 |  |  | 29.55 | 1.487
| 34.85 | 2.107 | 30.16 | 1.3289e-09 | 25.65 | 1.892 | 25.33 | 1.753 |  |  | 13.87 | 1.677 | 36.14 | 2.734 |  |  | 32.63 | 1.962 | 33.34 | 1.764 |  |  | 29.45 | 1.486
| 34.81 | 2.12 | 15.68 | 1.673e-11 | 25.58 | 1.93 | 25.15 | 1.754 |  |  | 13.65 | 1.671 | 36.08 | 2.738 |  |  | 32.57 | 1.963 | 33.28 | 1.786 |  |  | 29.4 | 1.486
| 34.77 | 2.133 |  |  | 25.51 | 1.922 | 24.97 | 1.755 |  |  | 13.43 | 1.664 | 36.02 | 2.743 |  |  | 32.52 | 1.962 | 33.21 | 1.811 |  |  | 29.35 | 1.484
| 34.73 | 2.145 |  |  | 25.43 | 1.909 | 24.79 | 1.756 |  |  | 13.23 | 1.657 | 35.96 | 2.747 |  |  | 32.52 | 1.958 | 33.15 | 1.837 |  |  | 29.3 | 1.481
| 34.69 | 2.157 |  |  | 25.29 | 1.891 | 24.61 | 1.757 |  |  | 13 | 1.651 | 35.89 | 2.752 |  |  | 32.46 | 1.961 | 33.09 | 1.859 |  |  | 29.21 | 1.481
| 34.65 | 2.169 |  |  | 25.23 | 1.851 | 24.43 | 1.758 |  |  | 12.79 | 1.645 | 35.83 | 2.756 |  |  | 32.41 | 1.956 | 33.03 | 1.883 |  |  | 29.16 | 1.478
| 34.61 | 2.18 |  |  | 25.16 | 1.953 | 24.25 | 1.76 |  |  | 12.59 | 1.637 | 35.77 | 2.76 |  |  | 32.36 | 1.957 | 32.97 | 1.906 |  |  | 29.11 | 1.476
| 34.57 | 2.191 |  |  | 25.09 | 1.888 | 24.07 | 1.761 |  |  | 12.36 | 1.634 | 35.7 | 2.765 |  |  | 32.36 | 1.954 | 32.9 | 1.93 |  |  | 29.01 | 1.477
| 34.53 | 2.202 |  |  | 25.02 | 1.875 | 23.89 | 1.762 |  |  | 12.15 | 1.632 | 35.64 | 2.769 |  |  | 32.31 | 1.954 | 32.84 | 1.95 |  |  | 28.96 | 1.474
| 34.49 | 2.213 |  |  | 24.88 | 1.889 | 23.71 | 1.764 |  |  | 11.92 | 1.623 | 35.57 | 2.773 |  |  | 32.26 | 1.954 | 32.77 | 1.974 |  |  | 28.91 | 1.474
| 34.45 | 2.224 |  |  | 24.81 | 1.864 | 23.53 | 1.765 |  |  | 11.73 | 1.62 | 35.51 | 2.778 |  |  | 32.21 | 1.95 | 32.71 | 2 |  |  | 28.86 | 1.471
| 34.41 | 2.234 |  |  | 24.67 | 1.852 | 23.35 | 1.766 |  |  | 11.54 | 1.611 | 35.44 | 2.782 |  |  | 32.16 | 1.948 | 32.64 | 2.024 |  |  | 28.76 | 1.469
| 34.37 | 2.244 |  |  | 24.61 | 1.855 | 23.16 | 1.768 |  |  | 11.34 | 1.614 | 35.38 | 2.787 |  |  | 32.16 | 1.947 | 32.58 | 2.045 |  |  | 28.71 | 1.469
| 34.33 | 2.252 |  |  | 24.47 | 1.845 | 22.97 | 1.769 |  |  | 11.14 | 1.609 | 35.31 | 2.791 |  |  | 32.11 | 1.945 | 32.51 | 2.068 |  |  | 28.66 | 1.469
| 34.28 | 2.257 |  |  | 24.4 | 1.806 | 22.79 | 1.771 |  |  | 10.93 | 1.604 | 35.25 | 2.796 |  |  | 32.06 | 1.945 | 32.44 | 2.094 |  |  | 28.61 | 1.469
| 34.24 | 2.26 |  |  | 24.34 | 1.855 | 22.59 | 1.773 |  |  | 10.75 | 1.601 | 35.18 | 2.8 |  |  | 32.06 | 1.944 | 32.38 | 2.117 |  |  | 28.51 | 1.468
| 34.2 | 2.263 |  |  | 24.27 | 1.818 | 22.4 | 1.775 |  |  | 10.57 | 1.597 | 35.11 | 2.805 |  |  | 32.01 | 1.944 | 32.31 | 2.138 |  |  | 28.46 | 1.469
| 34.16 | 2.265 |  |  | 24.21 | 1.817 | 22.2 | 1.777 |  |  | 10.37 | 1.591 | 35.05 | 2.809 |  |  | 31.96 | 1.942 | 32.24 | 2.159 |  |  | 28.41 | 1.469
| 34.12 | 2.271 |  |  | 24.14 | 1.827 | 22.01 | 1.779 |  |  | 10.2 | 1.591 | 34.98 | 2.814 |  |  | 31.96 | 1.942 | 32.17 | 2.18 |  |  | 28.36 | 1.467
| 34.08 | 2.278 |  |  | 24.01 | 1.873 | 21.81 | 1.781 |  |  | 10.05 | 1.586 | 34.91 | 2.818 |  |  | 31.91 | 1.937 | 32.1 | 2.201 |  |  | 28.31 | 1.469
| 34.04 | 2.287 |  |  | 23.88 | 1.869 | 21.61 | 1.783 |  |  | 9.9 | 1.584 | 34.85 | 2.823 |  |  | 31.87 | 1.938 | 32.03 | 2.222 |  |  | 28.21 | 1.464
| 33.99 | 2.296 |  |  | 23.82 | 1.842 | 21.41 | 1.786 |  |  | 9.76 | 1.583 | 34.78 | 2.827 |  |  | 31.87 | 1.937 | 31.96 | 2.243 |  |  | 28.16 | 1.467
| 33.95 | 2.304 |  |  | 23.76 | 1.845 | 21.21 | 1.788 |  |  | 9.62 | 1.577 | 34.71 | 2.832 |  |  | 31.82 | 1.934 | 31.89 | 2.262 |  |  | 28.11 | 1.468
| 33.91 | 2.315 |  |  | 23.7 | 1.845 | 21.01 | 1.79 |  |  | 9.49 | 1.573 | 34.64 | 2.836 |  |  | 31.77 | 1.934 | 31.82 | 2.281 |  |  | 28.06 | 1.464
| 33.87 | 2.326 |  |  | 23.63 | 1.829 | 20.81 | 1.793 |  |  | 9.35 | 1.574 | 34.57 | 2.841 |  |  | 31.77 | 1.935 | 31.75 | 2.299 |  |  | 27.96 | 1.464
| 33.82 | 2.334 |  |  | 23.51 | 1.843 | 20.61 | 1.795 |  |  | 9.23 | 1.573 | 34.5 | 2.845 |  |  | 31.72 | 1.934 | 31.68 | 2.316 |  |  | 27.9 | 1.465
| 33.78 | 2.342 |  |  | 23.45 | 1.832 | 20.4 | 1.798 |  |  | 9.15 | 1.575 | 34.43 | 2.85 |  |  | 31.68 | 1.932 | 31.6 | 2.332 |  |  | 27.85 | 1.463
| 33.74 | 2.346 |  |  | 23.39 | 1.861 | 20.2 | 1.8 |  |  | 9.08 | 1.572 | 34.36 | 2.854 |  |  | 31.68 | 1.93 | 31.53 | 2.349 |  |  | 27.8 | 1.464
| 33.69 | 2.348 |  |  | 23.33 | 1.866 | 19.99 | 1.803 |  |  | 8.98 | 1.573 | 34.29 | 2.858 |  |  | 31.63 | 1.93 | 31.46 | 2.366 |  |  | 27.75 | 1.463
| 33.65 | 2.353 |  |  | 23.27 | 1.836 | 19.79 | 1.806 |  |  | 8.89 | 1.572 | 34.22 | 2.862 |  |  | 31.63 | 1.93 | 31.38 | 2.382 |  |  | 27.7 | 1.465
| 33.61 | 2.362 |  |  | 23.21 | 1.84 | 19.59 | 1.808 |  |  | 8.8 | 1.572 | 34.15 | 2.867 |  |  | 31.58 | 1.929 | 31.31 | 2.398 |  |  | 27.6 | 1.463
| 33.56 | 2.37 |  |  | 23.16 | 1.833 | 19.38 | 1.811 |  |  | 8.69 | 1.568 | 34.08 | 2.871 |  |  | 31.54 | 1.929 | 31.23 | 2.412 |  |  | 27.55 | 1.459
| 33.52 | 2.37 |  |  | 23.1 | 1.846 | 19.18 | 1.813 |  |  | 8.6 | 1.567 | 34.01 | 2.876 |  |  | 31.54 | 1.927 | 31.16 | 2.429 |  |  | 27.5 | 1.456
| 33.47 | 2.368 |  |  | 23.04 | 1.852 | 18.97 | 1.815 |  |  | 8.52 | 1.564 | 33.94 | 2.88 |  |  | 31.49 | 1.924 | 31.08 | 2.444 |  |  | 27.45 | 1.459
| 33.42 | 2.372 |  |  | 22.98 | 1.837 | 18.77 | 1.818 |  |  | 8.42 | 1.564 | 33.87 | 2.884 |  |  | 31.45 | 1.925 | 31.01 | 2.459 |  |  | 27.4 | 1.46
| 33.38 | 2.383 |  |  | 22.87 | 1.836 | 18.56 | 1.821 |  |  | 8.35 | 1.56 | 33.8 | 2.888 |  |  | 31.45 | 1.92 | 30.93 | 2.473 |  |  | 27.34 | 1.46
| 33.33 | 2.395 |  |  | 22.81 | 1.834 | 18.35 | 1.824 |  |  | 8.26 | 1.559 | 33.73 | 2.892 |  |  | 31.4 | 1.92 | 30.86 | 2.482 |  |  | 27.29 | 1.457
| 33.28 | 2.406 |  |  | 22.76 | 1.826 | 18.12 | 1.829 |  |  | 8.16 | 1.554 | 33.66 | 2.896 |  |  | 31.4 | 1.918 | 30.78 | 2.494 |  |  | 27.19 | 1.458
| 33.23 | 2.424 |  |  | 22.7 | 1.836 | 17.86 | 1.834 |  |  | 8.1 | 1.553 | 33.59 | 2.9 |  |  | 31.35 | 1.919 | 30.7 | 2.512 |  |  | 27.14 | 1.457
| 33.18 | 2.448 |  |  | 22.64 | 1.836 | 17.56 | 1.839 |  |  | 8.01 | 1.55 | 33.52 | 2.904 |  |  | 31.31 | 1.919 | 30.62 | 2.528 |  |  | 27.09 | 1.453
| 33.13 | 2.469 |  |  | 22.59 | 1.836 | 17.27 | 1.844 |  |  | 7.94 | 1.546 | 33.45 | 2.908 |  |  | 31.31 | 1.918 | 30.54 | 2.546 |  |  | 27.04 | 1.453
| 33.08 | 2.49 |  |  | 22.53 | 1.84 | 16.96 | 1.85 |  |  | 7.86 | 1.543 | 33.38 | 2.912 |  |  | 31.26 | 1.916 | 30.47 | 2.562 |  |  | 26.99 | 1.452
| 33.03 | 2.509 |  |  | 22.48 | 1.832 | 16.64 | 1.855 |  |  | 7.78 | 1.542 | 33.31 | 2.916 |  |  | 31.22 | 1.916 | 30.39 | 2.578 |  |  | 26.94 | 1.449
| 32.98 | 2.526 |  |  | 22.42 | 1.833 | 16.33 | 1.862 |  |  | 7.72 | 1.537 | 33.24 | 2.92 |  |  | 31.22 | 1.913 | 30.31 | 2.596 |  |  | 26.89 | 1.448
| 32.93 | 2.536 |  |  | 22.36 | 1.834 | 16.01 | 1.868 |  |  | 7.64 | 1.535 | 33.16 | 2.924 |  |  | 31.17 | 1.911 | 30.23 | 2.612 |  |  | 26.78 | 1.451
| 32.87 | 2.542 |  |  | 22.31 | 1.826 | 15.71 | 1.874 |  |  | 7.57 | 1.533 | 33.09 | 2.929 |  |  | 31.17 | 1.915 | 30.15 | 2.627 |  |  | 26.73 | 1.449
| 32.82 | 2.548 |  |  | 22.25 | 1.83 | 15.4 | 1.88 |  |  | 7.51 | 1.53 | 33.01 | 2.933 |  |  | 31.12 | 1.912 | 30.07 | 2.641 |  |  | 26.68 | 1.449
| 32.76 | 2.56 |  |  | 22.2 | 1.829 | 15.09 | 1.887 |  |  | 7.45 | 1.526 | 32.93 | 2.938 |  |  | 31.08 | 1.912 | 29.98 | 2.655 |  |  | 26.63 | 1.456
| 32.7 | 2.58 |  |  | 22.14 | 1.826 | 14.78 | 1.893 |  |  | 7.39 | 1.521 | 32.85 | 2.942 |  |  | 31.08 | 1.915 | 29.9 | 2.669 |  |  | 26.58 | 1.451
| 32.64 | 2.596 |  |  | 22.08 | 1.826 | 14.47 | 1.901 |  |  | 7.31 | 1.517 | 32.78 | 2.946 |  |  | 31.03 | 1.91 | 29.82 | 2.684 |  |  | 26.53 | 1.446
| 32.59 | 2.609 |  |  | 21.97 | 1.829 | 14.16 | 1.908 |  |  | 7.26 | 1.517 | 32.71 | 2.95 |  |  | 31.03 | 1.91 | 29.74 | 2.699 |  |  | 26.48 | 1.444
| 32.53 | 2.627 |  |  | 21.91 | 1.824 | 13.85 | 1.916 |  |  | 7.21 | 1.51 | 32.65 | 2.953 |  |  | 30.98 | 1.909 | 29.66 | 2.713 |  |  | 26.43 | 1.447
| 32.47 | 2.646 |  |  | 21.86 | 1.824 | 13.55 | 1.924 |  |  | 7.14 | 1.508 | 32.6 | 2.955 |  |  | 30.98 | 1.911 | 29.57 | 2.728 |  |  | 26.38 | 1.442
| 32.42 | 2.663 |  |  | 21.8 | 1.821 | 13.25 | 1.932 |  |  | 7.09 | 1.503 | 32.54 | 2.958 |  |  | 30.94 | 1.909 | 29.49 | 2.742 |  |  | 26.33 | 1.437
| 32.36 | 2.677 |  |  | 21.74 | 1.826 | 12.95 | 1.941 |  |  | 7.02 | 1.501 | 32.49 | 2.961 |  |  | 30.89 | 1.909 | 29.41 | 2.757 |  |  | 26.28 | 1.446
| 32.3 | 2.692 |  |  | 21.68 | 1.821 | 12.66 | 1.95 |  |  | 6.97 | 1.497 | 32.44 | 2.963 |  |  | 30.89 | 1.909 | 29.32 | 2.771 |  |  | 26.17 | 1.443
| 32.25 | 2.706 |  |  | 21.63 | 1.82 | 12.35 | 1.959 |  |  | 6.91 | 1.495 | 32.39 | 2.966 |  |  | 30.84 | 1.909 | 29.24 | 2.785 |  |  | 26.12 | 1.444
| 32.19 | 2.713 |  |  | 21.57 | 1.808 | 12.04 | 1.969 |  |  | 6.86 | 1.488 | 32.34 | 2.968 |  |  | 30.84 | 1.905 | 29.15 | 2.799 |  |  | 26.07 | 1.443
| 32.13 | 2.715 |  |  | 21.51 | 1.808 | 11.75 | 1.979 |  |  | 6.81 | 1.484 | 32.3 | 2.971 |  |  | 30.79 | 1.906 | 29.07 | 2.814 |  |  | 26.02 | 1.444
| 32.07 | 2.719 |  |  | 21.45 | 1.808 | 11.47 | 1.99 |  |  | 6.74 | 1.483 | 32.25 | 2.974 |  |  | 30.74 | 1.906 | 28.98 | 2.829 |  |  | 25.97 | 1.454
| 32.01 | 2.727 |  |  | 21.39 | 1.809 | 11.18 | 2.001 |  |  | 6.69 | 1.481 | 32.21 | 2.977 |  |  | 30.74 | 1.909 | 28.9 | 2.843 |  |  | 25.92 | 1.438
| 31.95 | 2.74 |  |  | 21.33 | 1.811 | 10.89 | 2.013 |  |  | 6.64 | 1.477 | 32.16 | 2.979 |  |  | 30.69 | 1.905 | 28.81 | 2.858 |  |  | 25.87 | 1.443
| 31.88 | 2.753 |  |  | 21.27 | 1.809 | 10.61 | 2.025 |  |  | 6.6 | 1.47 | 32.12 | 2.982 |  |  | 30.69 | 1.905 | 28.72 | 2.872 |  |  | 25.82 | 1.443
| 31.82 | 2.768 |  |  | 21.2 | 1.805 | 10.34 | 2.038 |  |  | 6.55 | 1.468 | 32.07 | 2.985 |  |  | 30.64 | 1.902 | 28.64 | 2.887 |  |  | 25.77 | 1.434
| 31.75 | 2.782 |  |  | 21.14 | 1.814 | 10.1 | 2.052 |  |  | 6.5 | 1.463 | 32.03 | 2.987 |  |  | 30.64 | 1.916 | 28.55 | 2.902 |  |  | 25.72 | 1.437
| 31.69 | 2.793 |  |  | 21.08 | 1.802 | 9.87 | 2.066 |  |  | 6.45 | 1.458 | 31.98 | 2.99 |  |  | 30.59 | 1.903 | 28.46 | 2.917 |  |  | 25.67 | 1.433
| 31.62 | 2.803 |  |  | 21.01 | 1.812 | 9.66 | 2.081 |  |  | 6.4 | 1.458 | 31.94 | 2.992 |  |  | 30.54 | 1.907 | 28.38 | 2.932 |  |  | 25.62 | 1.434
| 31.56 | 2.812 |  |  | 20.82 | 1.758 | 9.45 | 2.097 |  |  | 6.35 | 1.452 | 31.89 | 2.995 |  |  | 30.54 | 1.905 | 28.29 | 2.946 |  |  | 25.57 | 1.439
| 31.49 | 2.82 |  |  | 20.75 | 1.774 | 9.27 | 2.115 |  |  | 6.31 | 1.45 | 31.85 | 2.997 |  |  | 30.48 | 1.913 | 28.2 | 2.961 |  |  | 25.53 | 1.438
| 31.42 | 2.827 |  |  | 20.69 | 1.777 | 9.13 | 2.132 |  |  | 6.25 | 1.444 | 31.8 | 3 |  |  | 30.48 | 1.921 | 28.11 | 2.974 |  |  | 25.48 | 1.431
| 31.35 | 2.836 |  |  | 20.62 | 1.78 | 9 | 2.15 |  |  | 6.2 | 1.444 | 31.76 | 3.002 |  |  | 30.43 | 1.902 | 28.02 | 2.988 |  |  | 25.43 | 1.421
| 31.28 | 2.844 |  |  | 20.56 | 1.777 | 8.86 | 2.169 |  |  | 6.15 | 1.439 | 31.72 | 3.005 |  |  | 30.43 | 1.905 | 27.93 | 3.003 |  |  | 25.38 | 1.422
| 31.21 | 2.85 |  |  | 20.49 | 1.776 | 8.71 | 2.191 |  |  | 6.1 | 1.432 | 31.67 | 3.007 |  |  | 30.37 | 1.906 | 27.84 | 3.018 |  |  | 25.33 | 1.423
| 31.14 | 2.857 |  |  | 20.42 | 1.773 | 8.57 | 2.216 |  |  | 6.06 | 1.427 | 31.63 | 3.009 |  |  | 30.37 | 1.905 | 27.75 | 3.033 |  |  | 25.28 | 1.432
| 31.07 | 2.865 |  |  | 20.36 | 1.773 | 8.44 | 2.243 |  |  | 6.01 | 1.427 | 31.59 | 3.012 |  |  | 30.31 | 1.897 | 27.66 | 3.048 |  |  | 25.23 | 1.418
| 31 | 2.871 |  |  | 20.29 | 1.774 | 8.3 | 2.272 |  |  | 5.97 | 1.422 | 31.54 | 3.014 |  |  | 30.25 | 1.921 | 27.57 | 3.063 |  |  | 25.18 | 1.423
| 30.92 | 2.878 |  |  | 20.22 | 1.773 | 8.17 | 2.303 |  |  | 5.94 | 1.417 | 31.5 | 3.016 |  |  | 30.25 | 1.882 | 27.48 | 3.079 |  |  | 25.14 | 1.416
| 30.85 | 2.883 |  |  | 20.16 | 1.78 | 8.04 | 2.335 |  |  | 5.88 | 1.412 | 31.46 | 3.018 |  |  | 30.19 | 1.893 | 27.39 | 3.095 |  |  | 25.09 | 1.412
| 30.78 | 2.888 |  |  | 20.16 | 1.768 | 7.91 | 2.369 |  |  | 5.85 | 1.413 | 31.42 | 3.021 |  |  | 30.19 | 1.89 | 27.3 | 3.11 |  |  | 25.04 | 1.419
| 30.7 | 2.893 |  |  | 19.96 | 1.767 | 7.79 | 2.404 |  |  | 5.81 | 1.403 | 31.37 | 3.023 |  |  | 30.13 | 1.895 | 27.21 | 3.126 |  |  | 25 | 1.413
| 30.63 | 2.898 |  |  | 19.89 | 1.782 | 7.67 | 2.44 |  |  | 5.76 | 1.394 | 31.33 | 3.025 |  |  | 30.13 | 1.897 | 27.12 | 3.14 |  |  | 24.95 | 1.416
| 30.55 | 2.903 |  |  | 19.75 | 1.731 | 7.56 | 2.476 |  |  | 5.73 | 1.397 | 31.29 | 3.028 |  |  | 30.08 | 1.899 | 27.03 | 3.155 |  |  | 24.91 | 1.412
| 30.47 | 2.908 |  |  | 19.68 | 1.753 | 7.45 | 2.514 |  |  | 5.68 | 1.39 | 31.25 | 3.03 |  |  | 30.08 | 1.894 | 26.94 | 3.169 |  |  | 24.86 | 1.409
| 30.4 | 2.912 |  |  | 19.61 | 1.76 | 7.34 | 2.551 |  |  | 5.65 | 1.389 | 31.2 | 3.033 |  |  | 30.04 | 1.893 | 26.85 | 3.184 |  |  | 24.82 | 1.414
| 30.32 | 2.917 |  |  | 19.55 | 1.738 | 7.25 | 2.589 |  |  | 5.62 | 1.379 | 31.16 | 3.035 |  |  | 30.04 | 1.897 | 26.75 | 3.198 |  |  | 24.77 | 1.406
| 30.24 | 2.921 |  |  | 19.48 | 1.747 | 7.16 | 2.627 |  |  | 5.57 | 1.37 | 31.12 | 3.037 |  |  | 30 | 1.892 | 26.66 | 3.212 |  |  | 24.73 | 1.412
| 30.16 | 2.925 |  |  | 19.41 | 1.742 | 7.06 | 2.664 |  |  | 5.53 | 1.369 | 31.08 | 3.039 |  |  | 29.96 | 1.898 | 26.57 | 3.226 |  |  | 24.69 | 1.416
| 15.68 | 3.911 |  |  | 19.34 | 1.739 | 5.84 | 3.114 |  |  | 5.5 | 1.364 | 17.66 | 3.904 |  |  | 29.96 | 1.901 | 21.37 | 3.903 |  |  | 24.65 | 1.403
| 10.53 | 4.21 |  |  | 19.27 | 1.751 | 4.83 | 3.85 |  |  | 5.46 | 1.356 | 2.46 | 5.57 |  |  | 29.93 | 1.898 | 17.12 | 4.41 |  |  | 24.6 | 1.398
| 8.1 | 4.47 |  |  | 19.2 | 1.731 | 4.02 | 4.1 |  |  | 5.43 | 1.359 | 1.98 | 5.64 |  |  | 29.93 | 1.897 | 14.27 | 4.73 |  |  | 24.56 | 1.4
| 6.1 | 4.85 |  |  | 19.13 | 1.734 | 2.81 | 4.46 |  |  | 5.39 | 1.352 | 1.25 | 6.13 |  |  | 29.89 | 1.897 | 13.47 | 4.79 |  |  | 24.52 | 1.401
| 2.02 | 6.13 |  |  | 19.06 | 1.726 | 1.71 | 4.78 |  |  | 5.35 | 1.35 | 0.88 | 6.2 |  |  | 29.89 | 1.893 | 2.44 | 6.19 |  |  | 24.48 | 1.401
| 0.92 | 6.52 |  |  | 19.06 | 1.725 | 0.24 | 5.64 |  |  | 5.32 | 1.342 |  |  |  |  | 29.86 | 1.898 |  |  |  |  | 24.43 | 1.401
[5 empty] | 18.99 | 1.725 | 0.13 | 6.35 |  |  | 5.28 | 1.339 |  |  |  |  | 29.86 | 1.906 |  |  |  |  | 24.39 | 1.397
[5 empty] | 18.92 | 1.728 |  |  |  |  | 5.24 | 1.338 |  |  |  |  | 29.82 | 1.892 |  |  |  |  | 24.35 | 1.387
[5 empty] | 18.84 | 1.735 |  |  |  |  | 5.21 | 1.338 |  |  |  |  | 29.82 | 1.896 |  |  |  |  | 24.31 | 1.393
[5 empty] | 18.77 | 1.721 |  |  |  |  | 5.18 | 1.327 |  |  |  |  | 29.79 | 1.897 |  |  |  |  | 24.27 | 1.387
[5 empty] | 18.7 | 1.726 |  |  |  |  | 5.15 | 1.324 |  |  |  |  | 29.79 | 1.894 |  |  |  |  | 24.23 | 1.391
[5 empty] | 18.63 | 1.732 |  |  |  |  | 5.12 | 1.316 |  |  |  |  | 29.76 | 1.897 |  |  |  |  | 24.18 | 1.387
[5 empty] | 18.56 | 1.724 |  |  |  |  | 5.09 | 1.312 |  |  |  |  | 29.76 | 1.897 |  |  |  |  | 24.14 | 1.386
[5 empty] | 18.49 | 1.732 |  |  |  |  | 5.05 | 1.309 |  |  |  |  | 29.73 | 1.899 |  |  |  |  | 24.1 | 1.395
[5 empty] | 18.41 | 1.724 |  |  |  |  | 5.03 | 1.306 |  |  |  |  | 29.73 | 1.901 |  |  |  |  | 24.06 | 1.382
[5 empty] | 18.34 | 1.683 |  |  |  |  | 4.98 | 1.303 |  |  |  |  | 29.7 | 1.902 |  |  |  |  | 24.02 | 1.387
[5 empty] | 18.27 | 1.716 |  |  |  |  | 4.98 | 1.299 |  |  |  |  | 29.7 | 1.896 |  |  |  |  | 23.97 | 1.384
[5 empty] | 18.19 | 1.782 |  |  |  |  | 4.92 | 1.295 |  |  |  |  | 29.67 | 1.905 |  |  |  |  | 23.93 | 1.381
[5 empty] | 18.12 | 1.747 |  |  |  |  | 4.9 | 1.287 |  |  |  |  | 29.67 | 1.898 |  |  |  |  | 23.89 | 1.38
[5 empty] | 18.05 | 1.738 |  |  |  |  | 4.87 | 1.285 |  |  |  |  | 29.64 | 1.899 |  |  |  |  | 23.84 | 1.387
[5 empty] | 17.83 | 1.618 |  |  |  |  | 4.84 | 1.281 |  |  |  |  | 29.61 | 1.901 |  |  |  |  | 23.8 | 1.377
[5 empty] | 17.68 | 1.627 |  |  |  |  | 4.81 | 1.275 |  |  |  |  | 29.61 | 1.901 |  |  |  |  | 23.75 | 1.377
[5 empty] | 17.6 | 1.706 |  |  |  |  | 4.78 | 1.274 |  |  |  |  | 29.58 | 1.897 |  |  |  |  | 23.71 | 1.375
[5 empty] | 17.53 | 1.785 |  |  |  |  | 4.75 | 1.269 |  |  |  |  | 29.58 | 1.896 |  |  |  |  | 23.71 | 1.372
[5 empty] | 17.45 | 1.724 |  |  |  |  | 4.71 | 1.263 |  |  |  |  | 29.55 | 1.894 |  |  |  |  | 23.66 | 1.371
[5 empty] | 17.38 | 1.683 |  |  |  |  | 4.67 | 1.259 |  |  |  |  | 29.55 | 1.893 |  |  |  |  | 23.62 | 1.372
[5 empty] | 17.3 | 1.706 |  |  |  |  | 4.66 | 1.257 |  |  |  |  | 29.53 | 1.896 |  |  |  |  | 23.57 | 1.368
[5 empty] | 17.22 | 1.681 |  |  |  |  | 4.62 | 1.252 |  |  |  |  | 29.53 | 1.893 |  |  |  |  | 23.52 | 1.37
[5 empty] | 17.15 | 1.666 |  |  |  |  | 4.6 | 1.248 |  |  |  |  | 29.5 | 1.893 |  |  |  |  | 23.47 | 1.37
[5 empty] | 17.15 | 1.676 |  |  |  |  | 4.57 | 1.245 |  |  |  |  | 29.5 | 1.887 |  |  |  |  | 23.42 | 1.361
[5 empty] | 17.07 | 1.671 |  |  |  |  | 4.54 | 1.24 |  |  |  |  | 29.47 | 1.883 |  |  |  |  | 23.37 | 1.366
[5 empty] | 17 | 1.676 |  |  |  |  | 4.51 | 1.235 |  |  |  |  | 29.47 | 1.889 |  |  |  |  | 23.32 | 1.365
[5 empty] | 16.92 | 1.665 |  |  |  |  | 4.49 | 1.231 |  |  |  |  | 29.44 | 1.886 |  |  |  |  | 23.27 | 1.36
[5 empty] | 16.84 | 1.688 |  |  |  |  | 4.44 | 1.223 |  |  |  |  | 29.44 | 1.884 |  |  |  |  | 23.21 | 1.361
[5 empty] | 16.76 | 1.649 |  |  |  |  | 4.43 | 1.221 |  |  |  |  | 29.42 | 1.88 |  |  |  |  | 23.16 | 1.36
[5 empty] | 16.69 | 1.627 |  |  |  |  | 4.39 | 1.214 |  |  |  |  | 29.42 | 1.882 |  |  |  |  | 23.16 | 1.359
[5 empty] | 16.61 | 1.659 |  |  |  |  | 4.38 | 1.211 |  |  |  |  | 29.39 | 1.88 |  |  |  |  | 23.1 | 1.359
[5 empty] | 16.53 | 1.652 |  |  |  |  | 4.37 | 1.204 |  |  |  |  | 29.39 | 1.878 |  |  |  |  | 23.05 | 1.355
[5 empty] | 16.45 | 1.658 |  |  |  |  | 4.34 | 1.199 |  |  |  |  | 29.36 | 1.873 |  |  |  |  | 22.99 | 1.355
[5 empty] | 16.37 | 1.638 |  |  |  |  | 4.32 | 1.194 |  |  |  |  | 29.36 | 1.877 |  |  |  |  | 22.92 | 1.353
[5 empty] | 16.29 | 1.639 |  |  |  |  | 4.29 | 1.189 |  |  |  |  | 29.36 | 1.876 |  |  |  |  | 22.86 | 1.353
[5 empty] | 16.22 | 1.644 |  |  |  |  | 4.27 | 1.183 |  |  |  |  | 29.33 | 1.878 |  |  |  |  | 22.79 | 1.353
[5 empty] | 16.22 | 1.571 |  |  |  |  | 4.24 | 1.179 |  |  |  |  | 29.33 | 1.874 |  |  |  |  | 22.72 | 1.35
[5 empty] | 16.14 | 1.685 |  |  |  |  | 4.2 | 1.174 |  |  |  |  | 29.3 | 1.874 |  |  |  |  | 22.65 | 1.347
[5 empty] | 15.9 | 1.661 |  |  |  |  | 4.19 | 1.168 |  |  |  |  | 29.3 | 1.872 |  |  |  |  | 22.59 | 1.332
[5 empty] | 15.82 | 1.581 |  |  |  |  | 4.17 | 1.162 |  |  |  |  | 29.27 | 1.87 |  |  |  |  | 22.59 | 1.342
[5 empty] | 15.57 | 1.699 |  |  |  |  | 4.14 | 1.155 |  |  |  |  | 29.27 | 1.87 |  |  |  |  | 22.53 | 1.345
[5 empty] | 15.49 | 1.592 |  |  |  |  | 4.12 | 1.148 |  |  |  |  | 29.24 | 1.874 |  |  |  |  | 22.48 | 1.339
[5 empty] | 15.41 | 1.62 |  |  |  |  | 4.1 | 1.141 |  |  |  |  | 29.24 | 1.87 |  |  |  |  | 22.42 | 1.339
[5 empty] | 15.33 | 1.558 |  |  |  |  | 4.06 | 1.135 |  |  |  |  | 29.21 | 1.872 |  |  |  |  | 22.36 | 1.338
[5 empty] | 15.17 | 1.582 |  |  |  |  | 4.05 | 1.129 |  |  |  |  | 29.21 | 1.87 |  |  |  |  | 22.31 | 1.338
[5 empty] | 15.08 | 1.607 |  |  |  |  | 4.04 | 1.122 |  |  |  |  | 29.18 | 1.868 |  |  |  |  | 22.25 | 1.337
[5 empty] | 15 | 1.617 |  |  |  |  | 4 | 1.117 |  |  |  |  | 29.18 | 1.87 |  |  |  |  | 22.2 | 1.333
[5 empty] | 15 | 1.599 |  |  |  |  | 3.96 | 1.112 |  |  |  |  | 29.15 | 1.87 |  |  |  |  | 22.15 | 1.331
[5 empty] | 14.92 | 1.603 |  |  |  |  | 3.96 | 1.107 |  |  |  |  | 29.15 | 1.868 |  |  |  |  | 22.15 | 1.331
[5 empty] | 14.83 | 1.597 |  |  |  |  | 3.93 | 1.102 |  |  |  |  | 29.12 | 1.866 |  |  |  |  | 22.1 | 1.328
[5 empty] | 14.75 | 1.595 |  |  |  |  | 3.91 | 1.095 |  |  |  |  | 29.12 | 1.866 |  |  |  |  | 22.05 | 1.327
[5 empty] | 14.67 | 1.596 |  |  |  |  | 3.9 | 1.091 |  |  |  |  | 29.09 | 1.866 |  |  |  |  | 22 | 1.326
[5 empty] | 14.67 | 1.595 |  |  |  |  | 3.88 | 1.085 |  |  |  |  | 29.09 | 1.87 |  |  |  |  | 21.94 | 1.323
[5 empty] | 14.58 | 1.596 |  |  |  |  | 3.86 | 1.08 |  |  |  |  | 29.06 | 1.865 |  |  |  |  | 21.89 | 1.321
[5 empty] | 14.5 | 1.596 |  |  |  |  | 3.83 | 1.074 |  |  |  |  | 29.06 | 1.868 |  |  |  |  | 21.85 | 1.319
[5 empty] | 14.41 | 1.596 |  |  |  |  | 3.82 | 1.067 |  |  |  |  | 29.03 | 1.862 |  |  |  |  | 21.85 | 1.319
[5 empty] | 14.33 | 1.597 |  |  |  |  | 3.81 | 1.062 |  |  |  |  | 29.03 | 1.862 |  |  |  |  | 21.8 | 1.316
[5 empty] | 14.33 | 1.599 |  |  |  |  | 3.78 | 1.056 |  |  |  |  | 29.03 | 1.862 |  |  |  |  | 21.75 | 1.312
[5 empty] | 14.24 | 1.578 |  |  |  |  | 3.77 | 1.051 |  |  |  |  | 29 | 1.86 |  |  |  |  | 21.7 | 1.315
[5 empty] | 14.16 | 1.607 |  |  |  |  | 3.76 | 1.045 |  |  |  |  | 29 | 1.86 |  |  |  |  | 21.65 | 1.312
[5 empty] | 14.07 | 1.604 |  |  |  |  | 3.73 | 1.038 |  |  |  |  | 28.97 | 1.861 |  |  |  |  | 21.6 | 1.311
[5 empty] | 13.99 | 1.637 |  |  |  |  | 3.72 | 1.032 |  |  |  |  | 28.97 | 1.858 |  |  |  |  | 21.55 | 1.309
[5 empty] | 13.99 | 1.549 |  |  |  |  | 3.71 | 1.026 |  |  |  |  | 28.94 | 1.858 |  |  |  |  | 21.55 | 1.308
[5 empty] | 13.9 | 1.563 |  |  |  |  | 3.69 | 1.02 |  |  |  |  | 28.94 | 1.86 |  |  |  |  | 21.5 | 1.305
[5 empty] | 13.82 | 1.558 |  |  |  |  | 3.67 | 1.015 |  |  |  |  | 28.91 | 1.859 |  |  |  |  | 21.45 | 1.306
[5 empty] | 13.73 | 1.561 |  |  |  |  | 3.66 | 1.009 |  |  |  |  | 28.91 | 1.859 |  |  |  |  | 21.4 | 1.304
[5 empty] | 13.64 | 1.575 |  |  |  |  | 3.63 | 1.003 |  |  |  |  | 28.88 | 1.858 |  |  |  |  | 21.34 | 1.303
[5 empty] | 13.64 | 1.56 |  |  |  |  | 3.62 | 0.995 |  |  |  |  | 28.88 | 1.857 |  |  |  |  | 21.29 | 1.301
[5 empty] | 13.55 | 1.563 |  |  |  |  | 3.6 | 0.99 |  |  |  |  | 28.85 | 1.858 |  |  |  |  | 21.24 | 1.299
[5 empty] | 13.47 | 1.56 |  |  |  |  | 3.57 | 0.984 |  |  |  |  | 28.85 | 1.858 |  |  |  |  | 21.24 | 1.3
[5 empty] | 13.38 | 1.561 |  |  |  |  | 3.57 | 0.979 |  |  |  |  | 28.85 | 1.859 |  |  |  |  | 21.19 | 1.295
[5 empty] | 13.29 | 1.563 |  |  |  |  | 3.55 | 0.973 |  |  |  |  | 28.83 | 1.857 |  |  |  |  | 21.13 | 1.297
[5 empty] | 13.29 | 1.556 |  |  |  |  | 3.53 | 0.968 |  |  |  |  | 28.83 | 1.855 |  |  |  |  | 21.08 | 1.295
[5 empty] | 13.2 | 1.558 |  |  |  |  | 3.5 | 0.962 |  |  |  |  | 28.8 | 1.854 |  |  |  |  | 21.02 | 1.294
[5 empty] | 13.11 | 1.553 |  |  |  |  | 3.5 | 0.957 |  |  |  |  | 28.8 | 1.854 |  |  |  |  | 20.96 | 1.294
[5 empty] | 13.03 | 1.556 |  |  |  |  | 3.47 | 0.951 |  |  |  |  | 28.77 | 1.853 |  |  |  |  | 20.96 | 1.294
[5 empty] | 13.03 | 1.546 |  |  |  |  | 3.47 | 0.945 |  |  |  |  | 28.77 | 1.855 |  |  |  |  | 20.9 | 1.292
[5 empty] | 12.94 | 1.549 |  |  |  |  | 3.47 | 0.94 |  |  |  |  | 28.74 | 1.852 |  |  |  |  | 20.84 | 1.291
[5 empty] | 12.85 | 1.54 |  |  |  |  | 3.45 | 0.933 |  |  |  |  | 28.74 | 1.853 |  |  |  |  | 20.78 | 1.289
[5 empty] | 12.76 | 1.54 |  |  |  |  | 3.43 | 0.927 |  |  |  |  | 28.71 | 1.854 |  |  |  |  | 20.72 | 1.287
[5 empty] | 12.67 | 1.54 |  |  |  |  | 3.41 | 0.922 |  |  |  |  | 28.71 | 1.853 |  |  |  |  | 20.65 | 1.286
[5 empty] | 12.67 | 1.545 |  |  |  |  | 3.39 | 0.917 |  |  |  |  | 28.71 | 1.851 |  |  |  |  | 20.65 | 1.284
[5 empty] | 12.58 | 1.546 |  |  |  |  | 3.38 | 0.911 |  |  |  |  | 28.68 | 1.854 |  |  |  |  | 20.58 | 1.283
[5 empty] | 12.49 | 1.54 |  |  |  |  | 3.37 | 0.906 |  |  |  |  | 28.68 | 1.853 |  |  |  |  | 20.51 | 1.283
[5 empty] | 12.4 | 1.534 |  |  |  |  | 3.36 | 0.9 |  |  |  |  | 28.65 | 1.852 |  |  |  |  | 20.44 | 1.28
[5 empty] | 12.4 | 1.531 |  |  |  |  | 3.35 | 0.895 |  |  |  |  | 28.65 | 1.852 |  |  |  |  | 20.36 | 1.275
[5 empty] | 12.31 | 1.528 |  |  |  |  | 3.32 | 0.889 |  |  |  |  | 28.62 | 1.852 |  |  |  |  | 20.36 | 1.276
[5 empty] | 12.21 | 1.532 |  |  |  |  | 3.31 | 0.884 |  |  |  |  | 28.62 | 1.851 |  |  |  |  | 20.29 | 1.272
[5 empty] | 12.12 | 1.528 |  |  |  |  | 3.27 | 0.877 |  |  |  |  | 28.59 | 1.852 |  |  |  |  | 20.21 | 1.271
[5 empty] | 12.12 | 1.518 |  |  |  |  | 3.27 | 0.872 |  |  |  |  | 28.59 | 1.848 |  |  |  |  | 20.14 | 1.271
[5 empty] | 12.03 | 1.492 |  |  |  |  | 3.26 | 0.867 |  |  |  |  | 28.59 | 1.848 |  |  |  |  | 20.06 | 1.269
[5 empty] | 11.94 | 1.517 |  |  |  |  | 3.24 | 0.862 |  |  |  |  | 28.56 | 1.848 |  |  |  |  | 20.06 | 1.265
[5 empty] | 11.85 | 1.518 |  |  |  |  | 3.23 | 0.859 |  |  |  |  | 28.56 | 1.845 |  |  |  |  | 19.99 | 1.264
[5 empty] | 11.85 | 1.516 |  |  |  |  | 3.22 | 0.852 |  |  |  |  | 28.53 | 1.846 |  |  |  |  | 19.91 | 1.26
[5 empty] | 11.75 | 1.516 |  |  |  |  | 3.22 | 0.849 |  |  |  |  | 28.53 | 1.845 |  |  |  |  | 19.83 | 1.258
[5 empty] | 11.66 | 1.512 |  |  |  |  | 3.2 | 0.844 |  |  |  |  | 28.5 | 1.847 |  |  |  |  | 19.75 | 1.257
[5 empty] | 11.66 | 1.512 |  |  |  |  | 3.18 | 0.84 |  |  |  |  | 28.5 | 1.845 |  |  |  |  | 19.75 | 1.255
[5 empty] | 11.66 | 1.509 |  |  |  |  | 3.16 | 0.835 |  |  |  |  | 28.5 | 1.846 |  |  |  |  | 19.68 | 1.253
[5 empty] | 11.66 | 1.509 |  |  |  |  | 3.16 | 0.83 |  |  |  |  | 28.46 | 1.846 |  |  |  |  | 19.6 | 1.252
[5 empty] | 11.66 | 1.517 |  |  |  |  | 3.15 | 0.825 |  |  |  |  | 28.46 | 1.844 |  |  |  |  | 19.52 | 1.249
[5 empty] | 0.04 | 0.674 |  |  |  |  | 3.12 | 0.821 |  |  |  |  | 28.43 | 1.843 |  |  |  |  | 19.44 | 1.248
[11 empty] | 3.12 | 0.816 |  |  |  |  | 28.43 | 1.844 |  |  |  |  | 19.44 | 1.246
[11 empty] | 3.1 | 0.812 |  |  |  |  | 28.4 | 1.844 |  |  |  |  | 19.36 | 1.243
[11 empty] | 3.1 | 0.807 |  |  |  |  | 28.4 | 1.843 |  |  |  |  | 19.27 | 1.242
[11 empty] | 3.09 | 0.803 |  |  |  |  | 28.4 | 1.842 |  |  |  |  | 19.19 | 1.239
[11 empty] | 3.07 | 0.8 |  |  |  |  | 28.37 | 1.84 |  |  |  |  | 19.11 | 1.237
[11 empty] | 3.05 | 0.796 |  |  |  |  | 28.37 | 1.843 |  |  |  |  | 19.11 | 1.235
[11 empty] | 3.05 | 0.791 |  |  |  |  | 28.33 | 1.84 |  |  |  |  | 19.02 | 1.234
[11 empty] | 3.05 | 0.787 |  |  |  |  | 28.33 | 1.841 |  |  |  |  | 18.94 | 1.231
[11 empty] | 3.03 | 0.783 |  |  |  |  | 28.3 | 1.84 |  |  |  |  | 18.85 | 1.231
[11 empty] | 3.02 | 0.78 |  |  |  |  | 28.3 | 1.839 |  |  |  |  | 18.77 | 1.226
[11 empty] | 3 | 0.776 |  |  |  |  | 28.3 | 1.84 |  |  |  |  | 18.77 | 1.225
[11 empty] | 2.98 | 0.772 |  |  |  |  | 28.26 | 1.837 |  |  |  |  | 18.68 | 1.224
[11 empty] | 2.98 | 0.768 |  |  |  |  | 28.26 | 1.837 |  |  |  |  | 18.59 | 1.223
[11 empty] | 2.96 | 0.764 |  |  |  |  | 28.23 | 1.837 |  |  |  |  | 18.5 | 1.22
[11 empty] | 2.95 | 0.762 |  |  |  |  | 28.23 | 1.837 |  |  |  |  | 18.5 | 1.22
[11 empty] | 2.94 | 0.757 |  |  |  |  | 28.19 | 1.834 |  |  |  |  | 18.41 | 1.216
[11 empty] | 2.93 | 0.754 |  |  |  |  | 28.19 | 1.834 |  |  |  |  | 18.32 | 1.217
[11 empty] | 2.92 | 0.751 |  |  |  |  | 28.19 | 1.834 |  |  |  |  | 18.23 | 1.214
[11 empty] | 2.9 | 0.747 |  |  |  |  | 28.15 | 1.831 |  |  |  |  | 0.04 | 0.428
[11 empty] | 2.9 | 0.744 |  |  |  |  | 28.15 | 1.831
[11 empty] | 2.92 | 0.741 |  |  |  |  | 28.11 | 1.833
[11 empty] | 2.92 | 0.739 |  |  |  |  | 28.11 | 1.832
[11 empty] | 2.91 | 0.735 |  |  |  |  | 28.07 | 1.825
[11 empty] | 2.9 | 0.733 |  |  |  |  | 28.07 | 1.827
[11 empty] | 2.89 | 0.73 |  |  |  |  | 28.07 | 1.826
[11 empty] | 2.88 | 0.728 |  |  |  |  | 28.03 | 1.823
[11 empty] | 2.87 | 0.725 |  |  |  |  | 28.03 | 1.821
[11 empty] | 2.86 | 0.723 |  |  |  |  | 27.99 | 1.822
[11 empty] | 2.85 | 0.719 |  |  |  |  | 27.99 | 1.822
[11 empty] | 2.84 | 0.717 |  |  |  |  | 27.99 | 1.822
[11 empty] | 2.82 | 0.714 |  |  |  |  | 27.95 | 1.82
[11 empty] | 2.82 | 0.713 |  |  |  |  | 27.95 | 1.817
[11 empty] | 2.81 | 0.71 |  |  |  |  | 27.91 | 1.818
[11 empty] | 2.8 | 0.708 |  |  |  |  | 27.91 | 1.815
[11 empty] | 2.8 | 0.706 |  |  |  |  | 27.91 | 1.814
[11 empty] | 2.79 | 0.704 |  |  |  |  | 27.87 | 1.812
[11 empty] | 2.78 | 0.703 |  |  |  |  | 27.87 | 1.814
[11 empty] | 2.77 | 0.7 |  |  |  |  | 27.82 | 1.813
[11 empty] | 2.76 | 0.698 |  |  |  |  | 27.82 | 1.812
[11 empty] | 2.75 | 0.696 |  |  |  |  | 27.78 | 1.812
[11 empty] | 2.73 | 0.694 |  |  |  |  | 27.78 | 1.81
[11 empty] | 2.72 | 0.692 |  |  |  |  | 27.78 | 1.813
[11 empty] | 2.71 | 0.691 |  |  |  |  | 27.73 | 1.809
[11 empty] | 2.7 | 0.689 |  |  |  |  | 27.73 | 1.809
[11 empty] | 2.69 | 0.687 |  |  |  |  | 27.69 | 1.807
[11 empty] | 2.69 | 0.686 |  |  |  |  | 27.69 | 1.807
[11 empty] | 2.68 | 0.685 |  |  |  |  | 27.69 | 1.808
[11 empty] | 2.67 | 0.682 |  |  |  |  | 27.64 | 1.804
[11 empty] | 2.67 | 0.681 |  |  |  |  | 27.64 | 1.805
[11 empty] | 2.66 | 0.68 |  |  |  |  | 27.6 | 1.804
[11 empty] | 2.65 | 0.679 |  |  |  |  | 27.6 | 1.803
[11 empty] | 2.64 | 0.677 |  |  |  |  | 27.6 | 1.803
[11 empty] | 2.63 | 0.675 |  |  |  |  | 27.55 | 1.802
[11 empty] | 2.63 | 0.673 |  |  |  |  | 27.55 | 1.801
[11 empty] | 2.62 | 0.672 |  |  |  |  | 27.5 | 1.802
[11 empty] | 2.61 | 0.671 |  |  |  |  | 27.5 | 1.801
[11 empty] | 2.6 | 0.67 |  |  |  |  | 27.5 | 1.801
[11 empty] | 2.59 | 0.668 |  |  |  |  | 27.46 | 1.799
[11 empty] | 2.58 | 0.667 |  |  |  |  | 27.46 | 1.798
[11 empty] | 2.57 | 0.666 |  |  |  |  | 27.41 | 1.797
[11 empty] | 2.56 | 0.665 |  |  |  |  | 27.41 | 1.798
[11 empty] | 2.55 | 0.663 |  |  |  |  | 27.41 | 1.795
[11 empty] | 2.54 | 0.662 |  |  |  |  | 27.36 | 1.795
[11 empty] | 2.53 | 0.662 |  |  |  |  | 27.36 | 1.796
[11 empty] | 2.52 | 0.661 |  |  |  |  | 27.36 | 1.796
[11 empty] | 2.51 | 0.659 |  |  |  |  | 27.31 | 1.794
[11 empty] | 2.5 | 0.658 |  |  |  |  | 27.31 | 1.793
[11 empty] | 2.49 | 0.657 |  |  |  |  | 27.26 | 1.795
[11 empty] | 2.48 | 0.656 |  |  |  |  | 27.26 | 1.79
[11 empty] | 2.47 | 0.654 |  |  |  |  | 27.26 | 1.791
[11 empty] | 2.47 | 0.653 |  |  |  |  | 27.21 | 1.79
[11 empty] | 2.46 | 0.653 |  |  |  |  | 27.21 | 1.791
[11 empty] | 2.45 | 0.652 |  |  |  |  | 27.16 | 1.793
[11 empty] | 2.45 | 0.651 |  |  |  |  | 27.16 | 1.789
[11 empty] | 2.44 | 0.649 |  |  |  |  | 27.16 | 1.789
[11 empty] | 2.43 | 0.649 |  |  |  |  | 27.11 | 1.788
[11 empty] | 2.42 | 0.648 |  |  |  |  | 27.11 | 1.791
[11 empty] | 2.41 | 0.647 |  |  |  |  | 27.05 | 1.789
[11 empty] | 2.41 | 0.645 |  |  |  |  | 27.05 | 1.786
[11 empty] | 2.4 | 0.645 |  |  |  |  | 27.05 | 1.788
[11 empty] | 0.05 | 0.495 |  |  |  |  | 27 | 1.786
[11 empty] | 0.05 | 0.473 |  |  |  |  | 27 | 1.784
[17 empty] | 27 | 1.788
[17 empty] | 26.95 | 1.787
[17 empty] | 26.95 | 1.785
[17 empty] | 26.89 | 1.783
[17 empty] | 26.89 | 1.783
[17 empty] | 26.89 | 1.781
[17 empty] | 26.84 | 1.782
[17 empty] | 26.84 | 1.779
[17 empty] | 26.78 | 1.781
[17 empty] | 26.78 | 1.778
[17 empty] | 26.78 | 1.779
[17 empty] | 26.73 | 1.778
[17 empty] | 26.73 | 1.777
[17 empty] | 26.73 | 1.776
[17 empty] | 26.67 | 1.778
[17 empty] | 26.67 | 1.776
[17 empty] | 26.61 | 1.773
[17 empty] | 26.61 | 1.772
[17 empty] | 26.61 | 1.773
[17 empty] | 26.56 | 1.767
[17 empty] | 26.56 | 1.767
[17 empty] | 26.56 | 1.767
[17 empty] | 26.5 | 1.767
[17 empty] | 26.5 | 1.764
[17 empty] | 26.44 | 1.766
[17 empty] | 26.44 | 1.762
[17 empty] | 26.44 | 1.761
[17 empty] | 26.38 | 1.76
[17 empty] | 26.38 | 1.76
[17 empty] | 26.38 | 1.76
[17 empty] | 26.32 | 1.76
[17 empty] | 26.32 | 1.757
[17 empty] | 26.32 | 1.758
[17 empty] | 26.26 | 1.754
[17 empty] | 26.26 | 1.756
[17 empty] | 26.2 | 1.753
[17 empty] | 26.2 | 1.752
[17 empty] | 26.2 | 1.752
[17 empty] | 26.13 | 1.753
[17 empty] | 26.13 | 1.752
[17 empty] | 26.13 | 1.751
[17 empty] | 26.07 | 1.75
[17 empty] | 26.07 | 1.749
[17 empty] | 26.01 | 1.746
[17 empty] | 26.01 | 1.745
[17 empty] | 26.01 | 1.744
[17 empty] | 25.95 | 1.746
[17 empty] | 25.95 | 1.745
[17 empty] | 25.95 | 1.745
[17 empty] | 25.88 | 1.741
[17 empty] | 25.88 | 1.742
[17 empty] | 25.88 | 1.742
[17 empty] | 25.82 | 1.74
[17 empty] | 25.82 | 1.741
[17 empty] | 25.75 | 1.739
[17 empty] | 25.75 | 1.739
[17 empty] | 25.75 | 1.739
[17 empty] | 25.68 | 1.737
[17 empty] | 25.68 | 1.738
[17 empty] | 25.68 | 1.736
[17 empty] | 25.62 | 1.735
[17 empty] | 25.62 | 1.736
[17 empty] | 25.62 | 1.737
[17 empty] | 25.55 | 1.733
[17 empty] | 25.55 | 1.734
[17 empty] | 25.55 | 1.735
[17 empty] | 25.48 | 1.733
[17 empty] | 25.48 | 1.734
[17 empty] | 25.48 | 1.736
[17 empty] | 25.41 | 1.733
[17 empty] | 25.41 | 1.732
[17 empty] | 25.34 | 1.729
[17 empty] | 25.34 | 1.733
[17 empty] | 25.34 | 1.731
[17 empty] | 25.27 | 1.728
[17 empty] | 25.27 | 1.728
[17 empty] | 25.27 | 1.729
[17 empty] | 25.2 | 1.728
[17 empty] | 25.2 | 1.728
[17 empty] | 25.2 | 1.727
[17 empty] | 25.13 | 1.728
[17 empty] | 25.13 | 1.727
[17 empty] | 25.13 | 1.727
[17 empty] | 25.06 | 1.724
[17 empty] | 25.06 | 1.727
[17 empty] | 25.06 | 1.723
[17 empty] | 24.99 | 1.724
[17 empty] | 24.99 | 1.722
[17 empty] | 24.99 | 1.722
[17 empty] | 24.91 | 1.722
[17 empty] | 24.91 | 1.722
[17 empty] | 24.84 | 1.721
[17 empty] | 24.84 | 1.72
[17 empty] | 24.84 | 1.718
[17 empty] | 24.76 | 1.72
[17 empty] | 24.76 | 1.718
[17 empty] | 24.76 | 1.718
[17 empty] | 24.69 | 1.716
[17 empty] | 24.69 | 1.719
[17 empty] | 24.69 | 1.716
[17 empty] | 24.61 | 1.715
[17 empty] | 24.61 | 1.713
[17 empty] | 24.61 | 1.715
[17 empty] | 24.54 | 1.715
[17 empty] | 24.54 | 1.711
[17 empty] | 24.54 | 1.711
[17 empty] | 24.46 | 1.715
[17 empty] | 24.46 | 1.714
[17 empty] | 24.46 | 1.711
[17 empty] | 24.38 | 1.713
[17 empty] | 24.38 | 1.714
[17 empty] | 24.38 | 1.715
[17 empty] | 24.3 | 1.715
[17 empty] | 24.3 | 1.716
[17 empty] | 24.3 | 1.72
[17 empty] | 24.22 | 1.722
[17 empty] | 24.22 | 1.719
[17 empty] | 24.22 | 1.716
[17 empty] | 24.14 | 1.721
[17 empty] | 24.14 | 1.718
[17 empty] | 24.14 | 1.718
[17 empty] | 24.06 | 1.716
[17 empty] | 24.06 | 1.715
[17 empty] | 24.06 | 1.715
[17 empty] | 23.98 | 1.71
[17 empty] | 23.98 | 1.712
[17 empty] | 23.98 | 1.709
[17 empty] | 23.9 | 1.706
[17 empty] | 23.9 | 1.704
[17 empty] | 23.9 | 1.702
[17 empty] | 23.82 | 1.702
[17 empty] | 23.82 | 1.699
[17 empty] | 23.82 | 1.697
[17 empty] | 23.73 | 1.696
[17 empty] | 23.73 | 1.698
[17 empty] | 23.73 | 1.696
[17 empty] | 23.65 | 1.694
[17 empty] | 23.65 | 1.692
[17 empty] | 23.65 | 1.692
[17 empty] | 23.57 | 1.69
[17 empty] | 23.57 | 1.689
[17 empty] | 23.57 | 1.689
[17 empty] | 23.48 | 1.687
[17 empty] | 23.48 | 1.689
[17 empty] | 23.48 | 1.685
[17 empty] | 23.39 | 1.685
[17 empty] | 23.39 | 1.684
[17 empty] | 23.39 | 1.684
[17 empty] | 23.31 | 1.682
[17 empty] | 23.31 | 1.683
[17 empty] | 23.31 | 1.682
[17 empty] | 23.22 | 1.682
[17 empty] | 23.22 | 1.682
[17 empty] | 23.22 | 1.681
[17 empty] | 23.13 | 1.679
[17 empty] | 23.13 | 1.678
[17 empty] | 23.13 | 1.678
[17 empty] | 23.04 | 1.675
[17 empty] | 23.04 | 1.676
[17 empty] | 23.04 | 1.676
[17 empty] | 22.95 | 1.674
[17 empty] | 22.95 | 1.675
[17 empty] | 22.95 | 1.675
[17 empty] | 22.86 | 1.675
[17 empty] | 22.86 | 1.672
[17 empty] | 22.86 | 1.67
[17 empty] | 22.86 | 1.672
[17 empty] | 22.77 | 1.671
[17 empty] | 22.77 | 1.67
[17 empty] | 22.77 | 1.669
[17 empty] | 22.68 | 1.671
[17 empty] | 22.68 | 1.67
[17 empty] | 22.68 | 1.67
[17 empty] | 22.59 | 1.668
[17 empty] | 22.59 | 1.668
[17 empty] | 22.59 | 1.666
[17 empty] | 22.5 | 1.665
[17 empty] | 22.5 | 1.645
[17 empty] | 22.5 | 1.66
[17 empty] | 22.4 | 1.666
[17 empty] | 22.4 | 1.666
[17 empty] | 22.4 | 1.664
[17 empty] | 22.3 | 1.662
[17 empty] | 22.3 | 1.656
[17 empty] | 22.3 | 1.66
[17 empty] | 22.2 | 1.653
[17 empty] | 22.2 | 1.66
[17 empty] | 22.2 | 1.657
[17 empty] | 22.11 | 1.651
[17 empty] | 22.11 | 1.648
[17 empty] | 22.11 | 1.653
[17 empty] | 22.02 | 1.671
[17 empty] | 22.02 | 1.648
[17 empty] | 21.92 | 1.646
[17 empty] | 21.82 | 1.638
[17 empty] | 21.82 | 1.639
[17 empty] | 21.82 | 1.641
[17 empty] | 21.72 | 1.641
[17 empty] | 21.72 | 1.644
[17 empty] | 21.72 | 1.642
[17 empty] | 21.72 | 1.644
[17 empty] | 21.61 | 1.646
[17 empty] | 21.61 | 1.645
[17 empty] | 21.61 | 1.647
[17 empty] | 21.51 | 1.648
[17 empty] | 21.51 | 1.649
[17 empty] | 21.51 | 1.651
[17 empty] | 21.4 | 1.653
[17 empty] | 21.4 | 1.653
[17 empty] | 21.4 | 1.65
[17 empty] | 21.3 | 1.653
[17 empty] | 21.3 | 1.649
[17 empty] | 21.3 | 1.647
[17 empty] | 21.2 | 1.645
[17 empty] | 21.2 | 1.642
[17 empty] | 21.2 | 1.64
[17 empty] | 21.2 | 1.641
[17 empty] | 21.1 | 1.64
[17 empty] | 21.1 | 1.638
[17 empty] | 21.1 | 1.637
[17 empty] | 21.01 | 1.635
[17 empty] | 21.01 | 1.631
[17 empty] | 21.01 | 1.633
[17 empty] | 20.91 | 1.628
[17 empty] | 20.91 | 1.628
[17 empty] | 20.91 | 1.627
[17 empty] | 20.91 | 1.626
[17 empty] | 20.82 | 1.624
[17 empty] | 20.82 | 1.624
[17 empty] | 20.82 | 1.62
[17 empty] | 20.72 | 1.62
[17 empty] | 20.72 | 1.621
[17 empty] | 20.72 | 1.618
[17 empty] | 20.63 | 1.618
[17 empty] | 20.63 | 1.614
[17 empty] | 20.63 | 1.613
[17 empty] | 20.53 | 1.612
[17 empty] | 20.53 | 1.611
[17 empty] | 20.53 | 1.612
[17 empty] | 20.53 | 1.611
[17 empty] | 20.44 | 1.61
[17 empty] | 20.44 | 1.606
[17 empty] | 20.44 | 1.607
[17 empty] | 20.35 | 1.604
[17 empty] | 20.35 | 1.606
[17 empty] | 20.35 | 1.604
[17 empty] | 20.26 | 1.603
[17 empty] | 20.26 | 1.602
[17 empty] | 20.26 | 1.601
[17 empty] | 20.26 | 1.601
[17 empty] | 20.17 | 1.599
[17 empty] | 20.17 | 1.596
[17 empty] | 20.17 | 1.596
[17 empty] | 20.08 | 1.597
[17 empty] | 20.08 | 1.592
[17 empty] | 20.08 | 1.594
[17 empty] | 19.99 | 1.593
[17 empty] | 19.99 | 1.596
[17 empty] | 19.99 | 1.594
[17 empty] | 19.99 | 1.593
[17 empty] | 19.9 | 1.589
[17 empty] | 19.9 | 1.593
[17 empty] | 19.9 | 1.589
[17 empty] | 19.81 | 1.591
[17 empty] | 19.81 | 1.591
[17 empty] | 19.81 | 1.587
[17 empty] | 19.81 | 1.589
[17 empty] | 19.72 | 1.581
[17 empty] | 19.72 | 1.589
[17 empty] | 19.64 | 1.592
[17 empty] | 19.64 | 1.592
[17 empty] | 19.64 | 1.596
[17 empty] | 19.55 | 1.611
[17 empty] | 19.55 | 1.589
[17 empty] | 19.55 | 1.583
[17 empty] | 19.47 | 1.586
[17 empty] | 19.47 | 1.587
[17 empty] | 19.47 | 1.584
[17 empty] | 19.38 | 1.585
[17 empty] | 19.38 | 1.586
[17 empty] | 19.38 | 1.581
[17 empty] | 19.38 | 1.586
[17 empty] | 19.3 | 1.583
[17 empty] | 19.3 | 1.581
[17 empty] | 19.3 | 1.584
[17 empty] | 19.22 | 1.586
[17 empty] | 19.22 | 1.585
[17 empty] | 19.22 | 1.585
[17 empty] | 19.22 | 1.584
[17 empty] | 19.14 | 1.584
[17 empty] | 19.14 | 1.583
[17 empty] | 19.14 | 1.585
[17 empty] | 19.06 | 1.582
[17 empty] | 19.06 | 1.582
[17 empty] | 19.06 | 1.581
[17 empty] | 19.06 | 1.582
[17 empty] | 18.99 | 1.578
[17 empty] | 18.99 | 1.58
[17 empty] | 18.99 | 1.579
[17 empty] | 18.91 | 1.578
[17 empty] | 18.91 | 1.581
[17 empty] | 18.91 | 1.581
[17 empty] | 18.84 | 1.581
[17 empty] | 18.84 | 1.581
[17 empty] | 18.84 | 1.58
[17 empty] | 18.84 | 1.579
[17 empty] | 18.77 | 1.577
[17 empty] | 18.77 | 1.58
[17 empty] | 18.77 | 1.577
[17 empty] | 18.7 | 1.574
[17 empty] | 18.7 | 1.572
[17 empty] | 18.7 | 1.572
[17 empty] | 18.7 | 1.573
[17 empty] | 18.64 | 1.571
[17 empty] | 18.64 | 1.571
[17 empty] | 18.64 | 1.568
[17 empty] | 18.64 | 1.566
[17 empty] | 18.57 | 1.566
[17 empty] | 18.57 | 1.565
[17 empty] | 18.57 | 1.564
[17 empty] | 18.51 | 1.561
[17 empty] | 18.51 | 1.56
[17 empty] | 18.51 | 1.56
[17 empty] | 18.51 | 1.56
[17 empty] | 18.45 | 1.558
[17 empty] | 18.45 | 1.558
[17 empty] | 18.45 | 1.557
[17 empty] | 18.39 | 1.553
[17 empty] | 18.39 | 1.553
[17 empty] | 18.39 | 1.553
[17 empty] | 18.39 | 1.551
[17 empty] | 18.33 | 1.551
[17 empty] | 18.33 | 1.549
[17 empty] | 18.33 | 1.549
[17 empty] | 18.28 | 1.548
[17 empty] | 18.28 | 1.548
[17 empty] | 18.28 | 1.547
[17 empty] | 18.28 | 1.547
[17 empty] | 18.22 | 1.546
[17 empty] | 18.22 | 1.547
[17 empty] | 18.22 | 1.544
[17 empty] | 18.16 | 1.544
[17 empty] | 18.16 | 1.544
[17 empty] | 18.16 | 1.542
[17 empty] | 18.16 | 1.541
[17 empty] | 18.1 | 1.54
[17 empty] | 18.1 | 1.54
[17 empty] | 18.1 | 1.539
[17 empty] | 18.1 | 1.538
[17 empty] | 18.03 | 1.537
[17 empty] | 18.03 | 1.536
[17 empty] | 18.03 | 1.536
[17 empty] | 17.97 | 1.535
[17 empty] | 17.97 | 1.534
[17 empty] | 17.97 | 1.535
[17 empty] | 17.97 | 1.533
[17 empty] | 17.9 | 1.534
[17 empty] | 17.9 | 1.533
[17 empty] | 17.9 | 1.531
[17 empty] | 17.84 | 1.532
[17 empty] | 17.84 | 1.53
[17 empty] | 17.84 | 1.528
[17 empty] | 17.84 | 1.528
[17 empty] | 17.76 | 1.528
[17 empty] | 17.76 | 1.526
[17 empty] | 17.76 | 1.527
[17 empty] | 17.76 | 1.525
[17 empty] | 17.69 | 1.523
[17 empty] | 17.69 | 1.523
[17 empty] | 17.69 | 1.522
[17 empty] | 17.61 | 1.523
[17 empty] | 17.61 | 1.522
[17 empty] | 17.61 | 1.52
[17 empty] | 17.61 | 1.52
[17 empty] | 17.52 | 1.518
[17 empty] | 17.52 | 1.52
[17 empty] | 17.52 | 1.519
[17 empty] | 17.52 | 1.516
[17 empty] | 17.42 | 1.517
[17 empty] | 17.42 | 1.514
[17 empty] | 17.42 | 1.518
[17 empty] | 17.33 | 1.517
[17 empty] | 17.33 | 1.512
[17 empty] | 17.33 | 1.51
[17 empty] | 17.33 | 1.511
[17 empty] | 17.24 | 1.512
[17 empty] | 17.24 | 1.51
[17 empty] | 17.24 | 1.508
[17 empty] | 17.24 | 1.509
[17 empty] | 17.15 | 1.509
[17 empty] | 17.15 | 1.506
[17 empty] | 17.15 | 1.517
[17 empty] | 17.07 | 1.516
[17 empty] | 17.07 | 1.515
[17 empty] | 17.07 | 1.512
[17 empty] | 17.07 | 1.514
[17 empty] | 17 | 1.516
[17 empty] | 17 | 1.513
[17 empty] | 17 | 1.517
[17 empty] | 17 | 1.513
[17 empty] | 16.93 | 1.514
[17 empty] | 16.93 | 1.513
[17 empty] | 16.93 | 1.512
[17 empty] | 16.93 | 1.512
[17 empty] | 16.87 | 1.514
[17 empty] | 16.87 | 1.512
[17 empty] | 16.87 | 1.51
[17 empty] | 16.81 | 1.508
[17 empty] | 16.81 | 1.507
[17 empty] | 16.81 | 1.508
[17 empty] | 16.81 | 1.508
[17 empty] | 16.75 | 1.507
[17 empty] | 16.75 | 1.504
[17 empty] | 16.75 | 1.503
[17 empty] | 16.75 | 1.503
[17 empty] | 16.7 | 1.503
[17 empty] | 16.7 | 1.5
[17 empty] | 16.7 | 1.499
[17 empty] | 16.7 | 1.497
[17 empty] | 16.65 | 1.5
[17 empty] | 16.65 | 1.498
[17 empty] | 16.65 | 1.497
[17 empty] | 16.6 | 1.494
[17 empty] | 16.6 | 1.495
[17 empty] | 16.6 | 1.494
[17 empty] | 16.6 | 1.492
[17 empty] | 16.55 | 1.49
[17 empty] | 16.55 | 1.49
[17 empty] | 16.55 | 1.487
[17 empty] | 16.55 | 1.488
[17 empty] | 16.5 | 1.486
[17 empty] | 16.5 | 1.485
[17 empty] | 16.5 | 1.485
[17 empty] | 16.5 | 1.481
[17 empty] | 16.45 | 1.482
[17 empty] | 16.45 | 1.483
[17 empty] | 16.45 | 1.48
[17 empty] | 16.45 | 1.477
[17 empty] | 16.4 | 1.478
[17 empty] | 16.4 | 1.481
[17 empty] | 16.4 | 1.475
[17 empty] | 16.35 | 1.476
[17 empty] | 16.35 | 1.475
[17 empty] | 16.35 | 1.475
[17 empty] | 16.35 | 1.475
[17 empty] | 16.3 | 1.475
[17 empty] | 16.3 | 1.472
[17 empty] | 16.3 | 1.473
[17 empty] | 16.3 | 1.473
[17 empty] | 16.24 | 1.471
[17 empty] | 16.24 | 1.47
[17 empty] | 16.24 | 1.475
[17 empty] | 16.24 | 1.473
[17 empty] | 16.19 | 1.47
[17 empty] | 16.19 | 1.469
[17 empty] | 16.19 | 1.464
[17 empty] | 16.13 | 1.464
[17 empty] | 16.13 | 1.462
[17 empty] | 16.13 | 1.46
[17 empty] | 16.13 | 1.46
[17 empty] | 16.07 | 1.46
[17 empty] | 16.07 | 1.458
[17 empty] | 16.07 | 1.464
[17 empty] | 15.94 | 1.46
[17 empty] | 15.94 | 1.457
[17 empty] | 15.94 | 1.416
[17 empty] | 15.87 | 1.462
[17 empty] | 15.87 | 1.439
[17 empty] | 15.87 | 1.452
[17 empty] | 15.8 | 1.44
[17 empty] | 15.8 | 1.455
[17 empty] | 15.8 | 1.447
[17 empty] | 15.8 | 1.452
[17 empty] | 15.73 | 1.447
[17 empty] | 15.73 | 1.442
[17 empty] | 15.73 | 1.453
[17 empty] | 15.73 | 1.452
[17 empty] | 15.65 | 1.445
[17 empty] | 15.65 | 1.45
[17 empty] | 15.65 | 1.454
[17 empty] | 15.65 | 1.449
[17 empty] | 15.58 | 1.452
[17 empty] | 15.58 | 1.468
[17 empty] | 15.58 | 1.41
[17 empty] | 15.58 | 1.475
[17 empty] | 15.5 | 1.478
[17 empty] | 15.43 | 1.436
[17 empty] | 15.43 | 1.455
[17 empty] | 15.43 | 1.475
[17 empty] | 15.35 | 1.457
[17 empty] | 15.35 | 1.4
[17 empty] | 15.35 | 1.361
[17 empty] | 15.35 | 1.34
[17 empty] | 15.27 | 1.445
[17 empty] | 15.27 | 1.439
[17 empty] | 15.27 | 1.489
[17 empty] | 15.27 | 1.399
[17 empty] | 15.19 | 1.406
[17 empty] | 15.19 | 1.436
[17 empty] | 15.19 | 1.436
[17 empty] | 15.19 | 1.44
[17 empty] | 15.11 | 1.43
[17 empty] | 15.11 | 1.469
[17 empty] | 15.11 | 1.37
[17 empty] | 15.11 | 1.422
[17 empty] | 15.03 | 1.424
[17 empty] | 15.03 | 1.43
[17 empty] | 15.03 | 1.43
[17 empty] | 14.95 | 1.419
[17 empty] | 14.95 | 1.392
[17 empty] | 14.95 | 1.412
[17 empty] | 14.87 | 1.41
[17 empty] | 14.87 | 1.409
[17 empty] | 14.79 | 1.41
[17 empty] | 14.71 | 1.39
[17 empty] | 14.71 | 1.398
[17 empty] | 14.71 | 1.396
[17 empty] | 14.71 | 1.392
[17 empty] | 14.63 | 1.396
[17 empty] | 14.63 | 1.392
[17 empty] | 14.63 | 1.4
[17 empty] | 14.63 | 1.386
[17 empty] | 14.55 | 1.398
[17 empty] | 14.55 | 1.392
[17 empty] | 14.55 | 1.395
[17 empty] | 14.55 | 1.356
[17 empty] | 14.47 | 1.39
[17 empty] | 14.47 | 1.393
[17 empty] | 14.47 | 1.393
[17 empty] | 14.47 | 1.389
[17 empty] | 14.4 | 1.394
[17 empty] | 14.4 | 1.383
[17 empty] | 14.4 | 1.389
[17 empty] | 14.4 | 1.383
[17 empty] | 14.32 | 1.381
[17 empty] | 14.32 | 1.398
[17 empty] | 14.32 | 1.376
[17 empty] | 14.32 | 1.384
[17 empty] | 14.25 | 1.398
[17 empty] | 14.25 | 1.379
[17 empty] | 14.25 | 1.387
[17 empty] | 14.25 | 1.398
[17 empty] | 14.17 | 1.412
[17 empty] | 14.17 | 1.341
[17 empty] | 14.17 | 1.379
[17 empty] | 14.17 | 1.36
[17 empty] | 14.1 | 1.376
[17 empty] | 14.1 | 1.379
[17 empty] | 14.1 | 1.38
[17 empty] | 14.1 | 1.382
[17 empty] | 14.02 | 1.378
[17 empty] | 14.02 | 1.379
[17 empty] | 14.02 | 1.377
[17 empty] | 14.02 | 1.377
[17 empty] | 13.95 | 1.375
[17 empty] | 13.95 | 1.375
[17 empty] | 13.95 | 1.376
[17 empty] | 13.95 | 1.375
[17 empty] | 13.87 | 1.374
[17 empty] | 13.87 | 1.373
[17 empty] | 13.87 | 1.371
[17 empty] | 13.87 | 1.373
[17 empty] | 13.8 | 1.372
[17 empty] | 13.8 | 1.37
[17 empty] | 13.8 | 1.369
[17 empty] | 13.8 | 1.37
[17 empty] | 13.8 | 1.37
[17 empty] | 13.73 | 1.371
[17 empty] | 13.73 | 1.371
[17 empty] | 13.73 | 1.371
[17 empty] | 13.73 | 1.373
[17 empty] | 13.65 | 1.376
[17 empty] | 13.65 | 1.375
[17 empty] | 13.65 | 1.379
[17 empty] | 13.65 | 1.378
[17 empty] | 13.58 | 1.373
[17 empty] | 13.58 | 1.371
[17 empty] | 13.58 | 1.371
[17 empty] | 13.58 | 1.368
[17 empty] | 13.5 | 1.367
[17 empty] | 13.5 | 1.366
[17 empty] | 13.5 | 1.364
[17 empty] | 13.5 | 1.362
[17 empty] | 13.43 | 1.36
[17 empty] | 13.43 | 1.355
[17 empty] | 13.43 | 1.355
[17 empty] | 13.43 | 1.354
[17 empty] | 13.36 | 1.352
[17 empty] | 13.36 | 1.351
[17 empty] | 13.36 | 1.348
[17 empty] | 13.36 | 1.348
[17 empty] | 13.36 | 1.346
[17 empty] | 13.28 | 1.347
[17 empty] | 13.28 | 1.343
[17 empty] | 13.28 | 1.342
[17 empty] | 13.28 | 1.34
[17 empty] | 13.21 | 1.34
[17 empty] | 13.21 | 1.339
[17 empty] | 13.21 | 1.337
[17 empty] | 13.21 | 1.334
[17 empty] | 13.14 | 1.336
[17 empty] | 13.14 | 1.335
[17 empty] | 13.14 | 1.333
[17 empty] | 13.14 | 1.332
[17 empty] | 13.07 | 1.33
[17 empty] | 13.07 | 1.329
[17 empty] | 13.07 | 1.328
[17 empty] | 13.07 | 1.327
[17 empty] | 13 | 1.326
[17 empty] | 13 | 1.325
[17 empty] | 13 | 1.323
[17 empty] | 13 | 1.323
[17 empty] | 13 | 1.322
[17 empty] | 12.92 | 1.32
[17 empty] | 12.92 | 1.318
[17 empty] | 12.92 | 1.317
[17 empty] | 12.92 | 1.317
[17 empty] | 12.85 | 1.314
[17 empty] | 12.85 | 1.313
[17 empty] | 12.85 | 1.313
[17 empty] | 12.85 | 1.312
[17 empty] | 12.79 | 1.311
[17 empty] | 12.79 | 1.309
[17 empty] | 12.79 | 1.309
[17 empty] | 12.79 | 1.307
[17 empty] | 12.72 | 1.307
[17 empty] | 12.72 | 1.305
[17 empty] | 12.72 | 1.304
[17 empty] | 12.72 | 1.303
[17 empty] | 12.72 | 1.302
[17 empty] | 12.65 | 1.302
[17 empty] | 12.65 | 1.3
[17 empty] | 12.65 | 1.298
[17 empty] | 12.65 | 1.299
[17 empty] | 12.58 | 1.299
[17 empty] | 12.58 | 1.298
[17 empty] | 12.58 | 1.298
[17 empty] | 12.58 | 1.295
[17 empty] | 12.51 | 1.295
[17 empty] | 12.51 | 1.295
[17 empty] | 12.51 | 1.293
[17 empty] | 12.51 | 1.292
[17 empty] | 12.45 | 1.293
[17 empty] | 12.45 | 1.291
[17 empty] | 12.45 | 1.291
[17 empty] | 12.45 | 1.29
[17 empty] | 12.45 | 1.289
[17 empty] | 12.38 | 1.289
[17 empty] | 12.38 | 1.289
[17 empty] | 12.38 | 1.287
[17 empty] | 12.38 | 1.286
[17 empty] | 12.32 | 1.287
[17 empty] | 12.32 | 1.285
[17 empty] | 12.32 | 1.284
[17 empty] | 12.32 | 1.284
[17 empty] | 12.26 | 1.284
[17 empty] | 12.26 | 1.283
[17 empty] | 12.26 | 1.283
[17 empty] | 12.26 | 1.282
[17 empty] | 12.26 | 1.281
[17 empty] | 12.2 | 1.278
[17 empty] | 12.2 | 1.28
[17 empty] | 12.2 | 1.279
[17 empty] | 12.2 | 1.279
[17 empty] | 12.14 | 1.281
[17 empty] | 12.14 | 1.282
[17 empty] | 12.14 | 1.283
[17 empty] | 12.14 | 1.285
[17 empty] | 12.08 | 1.287
[17 empty] | 12.08 | 1.287
[17 empty] | 12.08 | 1.283
[17 empty] | 0.09 | 0.404
[17 empty] | 0.08 | 0.385

## Load Profils
|  | EVU load profile | PV load profile
Parameter | Time of Day | Relative load | Relative load
Unit | h | - | -
| 0 | 0.5 | 0.197
| 0.5 | 0.48 | 0.191
| 1 | 0.46 | 0.195
| 1.5 | 0.44 | 0.194
| 2 | 0.42 | 0.191
| 2.5 | 0.415 | 0.185
| 3 | 0.41 | 0.187
| 3.5 | 0.405 | 0.183
| 4 | 0.4 | 0.203
| 4.5 | 0.42 | 0.202
| 5 | 0.44 | 0.207
| 5.5 | 0.53333 | 0.214
| 6 | 0.62667 | 0.199
| 6.5 | 0.72 | 0.164
| 7 | 0.81333 | 0.103
| 7.5 | 0.90667 | 0.026
| 8 | 1 | 0.123
| 8.5 | 0.99 | 0.28
| 9 | 0.98 | 0.445
| 9.5 | 0.97 | 0.568
| 10 | 0.96 | 0.685
| 10.5 | 0.93 | 0.767
| 11 | 0.9 | 0.815
| 11.5 | 0.87 | 0.884
| 12 | 0.84 | 0.912
| 12.5 | 0.83 | 0.931
| 13 | 0.82 | 0.994
| 13.5 | 0.81 | 0.979
| 14 | 0.8 | 1
| 14.5 | 0.81 | 0.96
| 15 | 0.82 | 0.877
| 15.5 | 0.83 | 0.82
| 16 | 0.84 | 0.757
| 16.5 | 0.8425 | 0.663
| 17 | 0.845 | 0.54
| 17.5 | 0.8475 | 0.404
| 18 | 0.85 | 0.139
| 18.5 | 0.8375 | 0.093
| 19 | 0.825 | 0.162
| 19.5 | 0.8125 | 0.131
| 20 | 0.8 | 0.237
| 20.5 | 0.7625 | 0.254
| 21 | 0.725 | 0.276
| 21.5 | 0.6875 | 0.278
| 22 | 0.65 | 0.302
| 22.5 | 0.6125 | 0.292
| 23 | 0.575 | 0.254
| 23.5 | 0.5375 | 0.236
| 24 | 0.5 | 0.197

## Experiment - Data - MF_IV_CL
Electric Load and Cable Temperatures | [6 empty] | Weather Station Data
|  |  | Silt | Sand | Fluidized Backfill | Loam
Parameter | Time | Electrical load (IV) | Conductor Temperature | Conductor Temperature | Conductor Temperature | Conductor Temperature | Parameter | Time | Air Temperature | Soil Temperature [-0.8 m] | Time | Precipitation
Unit | d | A | °C | °C | °C | °C | Unit | d | °C | °C | d | mm/h
| 0 | 310.605 | 51.432 | 66.837 | 45.234 | 82.62 |  | 0 | 5.8 | 13.3 | 0 | 0
| 0.0069444 | 310.534 | 51.441 | 66.837 | 45.243 | 82.618 |  | 0.020833 | 5.8 | 13.3 | 0.041667 | 0
| 0.013889 | 310.499 | 51.423 | 66.821 | 45.23 | 82.597 |  | 0.041667 | 5.8 | 13.3 | 0.083333 | 0
| 0.020833 | 311.446 | 51.444 | 66.827 | 45.244 | 82.606 |  | 0.0625 | 6 | 13.3 | 0.125 | 0
| 0.027778 | 310.664 | 51.445 | 66.826 | 45.241 | 82.608 |  | 0.083333 | 5.9 | 13.3 | 0.16667 | 0
| 0.034722 | 310.894 | 51.434 | 66.814 | 45.23 | 82.586 |  | 0.10417 | 5.8 | 13.3 | 0.20833 | 0
| 0.041667 | 311.03 | 51.453 | 66.82 | 45.244 | 82.603 |  | 0.125 | 5.8 | 13.3 | 0.25 | 0
| 0.048611 | 311.204 | 51.448 | 66.826 | 45.247 | 82.605 |  | 0.14583 | 5.8 | 13.3 | 0.29167 | 0
| 0.055556 | 311.185 | 51.455 | 66.83 | 45.252 | 82.608 |  | 0.16667 | 5.6 | 13.3 | 0.33333 | 0
| 0.0625 | 311.218 | 51.463 | 66.83 | 45.253 | 82.612 |  | 0.1875 | 5.4 | 13.3 | 0.375 | 0
| 0.069444 | 310.802 | 51.467 | 66.84 | 45.261 | 82.622 |  | 0.20833 | 5.4 | 13.3 | 0.41667 | 0
| 0.076389 | 311.427 | 51.457 | 66.826 | 45.245 | 82.604 |  | 0.22917 | 5.5 | 13.3 | 0.45833 | 0
| 0.083333 | 310.95 | 51.463 | 66.824 | 45.251 | 82.612 |  | 0.25 | 5.4 | 13.3 | 0.5 | 0
| 0.090278 | 311.895 | 51.459 | 66.831 | 45.253 | 82.613 |  | 0.27083 | 5.2 | 13.3 | 0.54167 | 0
| 0.097222 | 312.294 | 51.477 | 66.838 | 45.262 | 82.622 |  | 0.29167 | 5.2 | 13.3 | 0.58333 | 0
| 0.10417 | 311.407 | 51.491 | 66.849 | 45.277 | 82.647 |  | 0.3125 | 5.2 | 13.3 | 0.625 | 0
| 0.11111 | 311.734 | 51.499 | 66.863 | 45.282 | 82.66 |  | 0.33333 | 5.3 | 13.3 | 0.66667 | 0
| 0.11806 | 311.191 | 51.492 | 66.855 | 45.275 | 82.657 |  | 0.35417 | 5.4 | 13.3 | 0.70833 | 0
| 0.125 | 311.436 | 51.486 | 66.852 | 45.272 | 82.649 |  | 0.375 | 5.6 | 13.3 | 0.75 | 0
| 0.13194 | 312.088 | 51.497 | 66.867 | 45.281 | 82.659 |  | 0.39583 | 5.8 | 13.3 | 0.79167 | 0
| 0.13889 | 311.785 | 51.495 | 66.864 | 45.278 | 82.661 |  | 0.41667 | 5.9 | 12.8 | 0.83333 | 0
| 0.14583 | 312.548 | 51.517 | 66.88 | 45.295 | 82.686 |  | 0.4375 | 6.2 | 12.8 | 0.875 | 0
| 0.15278 | 311.162 | 51.515 | 66.881 | 45.293 | 82.69 |  | 0.45833 | 6.6 | 12.8 | 0.91667 | 0
| 0.15972 | 310.979 | 51.494 | 66.872 | 45.279 | 82.673 |  | 0.47917 | 7.2 | 12.8 | 0.95833 | 0
| 0.16667 | 311.57 | 51.5 | 66.875 | 45.28 | 82.674 |  | 0.5 | 7.7 | 12.8 | 1 | 0
| 0.17361 | 311.704 | 51.484 | 66.865 | 45.27 | 82.663 |  | 0.52083 | 9.1 | 12.8 | 1.0417 | 0
| 0.18056 | 311.48 | 51.492 | 66.869 | 45.271 | 82.666 |  | 0.54167 | 8.9 | 12.8 | 1.0833 | 0.2
| 0.1875 | 311.541 | 51.494 | 66.872 | 45.273 | 82.668 |  | 0.5625 | 8.7 | 12.8 | 1.125 | 0.2
| 0.19444 | 311.591 | 51.494 | 66.871 | 45.276 | 82.668 |  | 0.58333 | 9.9 | 12.8 | 1.1667 | 0.4
| 0.20139 | 311.221 | 51.479 | 66.856 | 45.257 | 82.651 |  | 0.60417 | 10.5 | 12.8 | 1.2083 | 0
| 0.20833 | 310.502 | 51.448 | 66.83 | 45.241 | 82.619 |  | 0.625 | 9.8 | 12.8 | 1.25 | 0.2
| 0.21528 | 310.744 | 51.432 | 66.818 | 45.221 | 82.598 |  | 0.64583 | 8.9 | 12.8 | 1.2917 | 0
| 0.22222 | 311.282 | 51.452 | 66.826 | 45.232 | 82.608 |  | 0.66667 | 8.8 | 12.8 | 1.3333 | 0
| 0.22917 | 311.61 | 51.454 | 66.826 | 45.24 | 82.612 |  | 0.6875 | 8.6 | 12.8 | 1.375 | 0
| 0.23611 | 309.405 | 51.427 | 66.811 | 45.224 | 82.584 |  | 0.70833 | 8.3 | 12.8 | 1.4167 | 0
| 0.24306 | 309.441 | 51.369 | 66.758 | 45.17 | 82.518 |  | 0.72917 | 7.9 | 12.8 | 1.4583 | 0
| 0.25 | 309.6 | 51.315 | 66.708 | 45.129 | 82.451 |  | 0.75 | 7.9 | 12.8 | 1.5 | 0
| 0.25694 | 308.915 | 51.266 | 66.664 | 45.089 | 82.382 |  | 0.77083 | 7.8 | 12.8 | 1.5417 | 0
| 0.26389 | 308.098 | 51.221 | 66.614 | 45.052 | 82.315 |  | 0.79167 | 7.5 | 12.8 | 1.5833 | 0
| 0.27083 | 307.511 | 51.164 | 66.555 | 45.006 | 82.229 |  | 0.8125 | 7.3 | 12.8 | 1.625 | 0
| 0.27778 | 311.132 | 51.291 | 66.625 | 45.103 | 82.339 |  | 0.83333 | 7.2 | 12.8 | 1.6667 | 0
| 0.28472 | 309.785 | 51.305 | 66.644 | 45.122 | 82.355 |  | 0.85417 | 7.1 | 12.8 | 1.7083 | 0
| 0.29167 | 310.158 | 51.287 | 66.63 | 45.105 | 82.333 |  | 0.875 | 6.9 | 12.8 | 1.75 | 0
| 0.29861 | 309.861 | 51.254 | 66.587 | 45.071 | 82.292 |  | 0.89583 | 6.8 | 12.8 | 1.7917 | 0
| 0.30556 | 311.405 | 51.319 | 66.631 | 45.125 | 82.354 |  | 0.91667 | 6.8 | 12.8 | 1.8333 | 0
| 0.3125 | 315.194 | 51.454 | 66.724 | 45.226 | 82.492 |  | 0.9375 | 6.8 | 12.8 | 1.875 | 0
| 0.31944 | 310.919 | 51.413 | 66.716 | 45.2 | 82.473 |  | 0.95833 | 6.8 | 12.8 | 1.9167 | 0
| 0.32639 | 310.556 | 51.36 | 66.682 | 45.154 | 82.427 |  | 0.97917 | 6.8 | 12.8 | 1.9583 | 0
| 0.33333 | 309.922 | 51.321 | 66.649 | 45.121 | 82.383 |  | 1 | 6.7 | 12.8 | 2 | 0
| 0.34028 | 309.987 | 51.303 | 66.629 | 45.105 | 82.365 |  | 1.0208 | 6.7 | 12.8 | 2.0417 | 0
| 0.34722 | 310.524 | 51.308 | 66.627 | 45.104 | 82.362 |  | 1.0417 | 6.7 | 12.8 | 2.0833 | 0
| 0.35417 | 310.51 | 51.312 | 66.626 | 45.115 | 82.364 |  | 1.0625 | 6.5 | 12.8 | 2.125 | 0
| 0.36111 | 309.933 | 51.309 | 66.625 | 45.11 | 82.356 |  | 1.0833 | 6.4 | 12.8 | 2.1667 | 0
| 0.36806 | 309.924 | 51.289 | 66.604 | 45.09 | 82.335 |  | 1.1042 | 6.2 | 12.8 | 2.2083 | 0
| 0.375 | 309.65 | 51.265 | 66.581 | 45.073 | 82.304 |  | 1.125 | 6.1 | 12.8 | 2.25 | 0
| 0.38194 | 309.418 | 51.224 | 66.543 | 45.036 | 82.252 |  | 1.1458 | 6.1 | 12.8 | 2.2917 | 0
| 0.38889 | 309.455 | 51.176 | 66.496 | 45 | 82.195 |  | 1.1667 | 6.1 | 12.8 | 2.3333 | 0
| 0.39583 | 308.909 | 51.147 | 66.461 | 44.972 | 82.145 |  | 1.1875 | 6.1 | 12.8 | 2.375 | 0
| 0.40278 | 308.039 | 51.102 | 66.418 | 44.941 | 82.082 |  | 1.2083 | 6.1 | 12.8 | 2.4167 | 0
| 0.40972 | 311.549 | 51.253 | 66.519 | 45.061 | 82.221 |  | 1.2292 | 6 | 12.8 | 2.4583 | 0
| 0.41667 | 311.147 | 51.313 | 66.568 | 45.108 | 82.296 |  | 1.25 | 6 | 12.8 | 2.5 | 0
| 0.42361 | 311.64 | 51.358 | 66.606 | 45.139 | 82.353 |  | 1.2708 | 6.1 | 12.8 | 2.5417 | 0
| 0.43056 | 311.926 | 51.374 | 66.631 | 45.152 | 82.385 |  | 1.2917 | 6.1 | 12.8 | 2.5833 | 0
| 0.4375 | 310.878 | 51.385 | 66.646 | 45.153 | 82.412 |  | 1.3125 | 6.1 | 12.8 | 2.625 | 0
| 0.44444 | 311.838 | 51.397 | 66.658 | 45.168 | 82.432 |  | 1.3333 | 6.1 | 12.8 | 2.6667 | 0
| 0.45139 | 312.522 | 51.411 | 66.676 | 45.178 | 82.464 |  | 1.3542 | 6.2 | 12.8 | 2.7083 | 0
| 0.45833 | 311.77 | 51.4 | 66.678 | 45.166 | 82.461 |  | 1.375 | 6.3 | 12.8 | 2.75 | 0
| 0.46528 | 311.128 | 51.382 | 66.67 | 45.15 | 82.453 |  | 1.3958 | 6.5 | 12.8 | 2.7917 | 0
| 0.47222 | 311.377 | 51.39 | 66.677 | 45.158 | 82.467 |  | 1.4167 | 6.7 | 12.8 | 2.8333 | 0
| 0.47917 | 311.83 | 51.389 | 66.676 | 45.157 | 82.475 |  | 1.4375 | 6.9 | 12.8 | 2.875 | 0
| 0.48611 | 311.079 | 51.371 | 66.667 | 45.145 | 82.455 |  | 1.4583 | 7.1 | 12.8 | 2.9167 | 0
| 0.49306 | 310.64 | 51.34 | 66.64 | 45.115 | 82.427 |  | 1.4792 | 7.2 | 12.8 | 2.9583 | 0
| 0.5 | 311.579 | 51.34 | 66.64 | 45.115 | 82.425 |  | 1.5 | 7.3 | 12.8 | 3 | 0
| 0.50694 | 310.805 | 51.359 | 66.651 | 45.126 | 82.442 |  | 1.5208 | 7.4 | 12.8 | 3.0417 | 0
| 0.51389 | 310.793 | 51.348 | 66.649 | 45.127 | 82.437 |  | 1.5417 | 7.5 | 12.8 | 3.0833 | 0
| 0.52083 | 311.09 | 51.346 | 66.641 | 45.113 | 82.436 |  | 1.5625 | 7.6 | 12.8 | 3.125 | 0
| 0.52778 | 311.903 | 51.36 | 66.647 | 45.125 | 82.445 |  | 1.5833 | 7.9 | 12.8 | 3.1667 | 0
| 0.53472 | 311.053 | 51.369 | 66.656 | 45.134 | 82.456 |  | 1.6042 | 8.2 | 12.8 | 3.2083 | 0
| 0.54167 | 311.796 | 51.385 | 66.671 | 45.145 | 82.476 |  | 1.625 | 8.2 | 12.8 | 3.25 | 0
| 0.54861 | 311.587 | 51.411 | 66.687 | 45.159 | 82.507 |  | 1.6458 | 8.4 | 12.8 | 3.2917 | 0
| 0.55556 | 312.425 | 51.429 | 66.714 | 45.181 | 82.534 |  | 1.6667 | 8.6 | 12.8 | 3.3333 | 0.2
| 0.5625 | 312.597 | 51.463 | 66.746 | 45.208 | 82.581 |  | 1.6875 | 8.4 | 12.8 | 3.375 | 0.6
| 0.56944 | 313.829 | 51.514 | 66.788 | 45.234 | 82.639 |  | 1.7083 | 8.4 | 12.8 | 3.4167 | 0
| 0.57639 | 312.002 | 51.529 | 66.811 | 45.253 | 82.679 |  | 1.7292 | 8.4 | 12.8 | 3.4583 | 0
| 0.58333 | 312.495 | 51.496 | 66.798 | 45.226 | 82.664 |  | 1.75 | 8.4 | 12.8 | 3.5 | 0
| 0.59028 | 312.725 | 51.478 | 66.787 | 45.209 | 82.649 |  | 1.7708 | 8.1 | 12.8 | 3.5417 | 0
| 0.59722 | 312.599 | 51.475 | 66.785 | 45.205 | 82.647 |  | 1.7917 | 7.8 | 12.8 | 3.5833 | 0
| 0.60417 | 312.246 | 51.479 | 66.789 | 45.202 | 82.655 |  | 1.8125 | 7.4 | 12.8 | 3.625 | 0
| 0.61111 | 312.459 | 51.467 | 66.787 | 45.201 | 82.647 |  | 1.8333 | 7.3 | 12.8 | 3.6667 | 0
| 0.61806 | 312.25 | 51.473 | 66.793 | 45.205 | 82.654 |  | 1.8542 | 7.2 | 12.8 | 3.7083 | 0
| 0.625 | 312.545 | 51.458 | 66.785 | 45.187 | 82.643 |  | 1.875 | 6.9 | 12.8 | 3.75 | 0
| 0.63194 | 312.807 | 51.477 | 66.798 | 45.207 | 82.672 |  | 1.8958 | 6.8 | 12.8 | 3.7917 | 0
| 0.63889 | 312.808 | 51.496 | 66.821 | 45.222 | 82.697 |  | 1.9167 | 6.7 | 12.8 | 3.8333 | 0
| 0.64583 | 313.155 | 51.507 | 66.83 | 45.226 | 82.707 |  | 1.9375 | 6.6 | 12.8 | 3.875 | 0
| 0.65278 | 313.09 | 51.509 | 66.831 | 45.225 | 82.719 |  | 1.9583 | 6.4 | 12.8 | 3.9167 | 0
| 0.65972 | 312.352 | 51.501 | 66.835 | 45.222 | 82.714 |  | 1.9792 | 6.3 | 12.8 | 3.9583 | 0
| 0.66667 | 312.712 | 51.507 | 66.837 | 45.218 | 82.735 |  | 2 | 6.2 | 12.8 | 4 | 0
| 0.67361 | 312.087 | 51.491 | 66.832 | 45.214 | 82.723 |  | 2.0208 | 6.1 | 12.8 | 4.0417 | 0
| 0.68056 | 312.343 | 51.472 | 66.819 | 45.195 | 82.703 |  | 2.0417 | 5.9 | 12.8 | 4.0833 | 0
| 0.6875 | 311.497 | 51.452 | 66.805 | 45.18 | 82.682 |  | 2.0625 | 5.6 | 12.8 | 4.125 | 0
| 0.69444 | 311.342 | 51.424 | 66.779 | 45.158 | 82.65 |  | 2.0833 | 5.1 | 12.8 | 4.1667 | 0
| 0.70139 | 311.552 | 51.388 | 66.752 | 45.129 | 82.615 |  | 2.1042 | 4.4 | 12.8 | 4.2083 | 0
| 0.70833 | 310.801 | 51.366 | 66.726 | 45.107 | 82.58 |  | 2.125 | 3.9 | 12.8 | 4.25 | 0
| 0.71528 | 310.511 | 51.332 | 66.697 | 45.084 | 82.537 |  | 2.1458 | 3.3 | 12.8 | 4.2917 | 0
| 0.72222 | 310.806 | 51.304 | 66.668 | 45.059 | 82.495 |  | 2.1667 | 2.9 | 12.8 | 4.3333 | 0
| 0.72917 | 310.429 | 51.257 | 66.624 | 45.024 | 82.441 |  | 2.1875 | 2.4 | 12.8 | 4.375 | 0
| 0.73611 | 310.283 | 51.205 | 66.569 | 44.982 | 82.364 |  | 2.2083 | 2.3 | 12.8 | 4.4167 | 0
| 0.74306 | 308.704 | 51.131 | 66.5 | 44.925 | 82.271 |  | 2.2292 | 2.3 | 12.8 | 4.4583 | 0
| 0.75 | 308.475 | 51.046 | 66.412 | 44.853 | 82.154 |  | 2.25 | 1.6 | 12.8 | 4.5 | 0
| 0.75694 | 308.252 | 50.96 | 66.322 | 44.788 | 82.028 |  | 2.2708 | 1.6 | 12.8 | 4.5417 | 0
| 0.76389 | 309.577 | 51.007 | 66.328 | 44.818 | 82.035 |  | 2.2917 | 1.4 | 12.8 | 4.5833 | 0
| 0.77083 | 309.098 | 50.992 | 66.301 | 44.81 | 82.006 |  | 2.3125 | 1.1 | 12.8 | 4.625 | 0
| 0.77778 | 310.299 | 51.008 | 66.289 | 44.814 | 81.997 |  | 2.3333 | 0.7 | 12.8 | 4.6667 | 0
| 0.78472 | 310.143 | 51.024 | 66.294 | 44.833 | 81.997 |  | 2.3542 | 0.6 | 12.8 | 4.7083 | 0
| 0.79167 | 310.622 | 51.042 | 66.296 | 44.845 | 82.01 |  | 2.375 | 0.8 | 12.8 | 4.75 | 0
| 0.79861 | 310.448 | 51.083 | 66.316 | 44.872 | 82.038 |  | 2.3958 | 2.1 | 12.8 | 4.7917 | 0
| 0.80556 | 311.59 | 51.113 | 66.338 | 44.898 | 82.071 |  | 2.4167 | 3.1 | 12.8 | 4.8333 | 0
| 0.8125 | 311.342 | 51.169 | 66.377 | 44.943 | 82.134 |  | 2.4375 | 4.3 | 12.8 | 4.875 | 0
| 0.81944 | 311.771 | 51.21 | 66.411 | 44.974 | 82.185 |  | 2.4583 | 5.1 | 12.8 | 4.9167 | 0
| 0.82639 | 312.571 | 51.28 | 66.474 | 45.023 | 82.266 |  | 2.4792 | 6.1 | 12.8 | 4.9583 | 0
| 0.83333 | 313.367 | 51.354 | 66.54 | 45.08 | 82.364 |  | 2.5 | 7.2 | 12.8 | 5 | 0
| 0.84028 | 314.447 | 51.434 | 66.612 | 45.148 | 82.47 |  | 2.5208 | 8.3 | 12.8 | 5.0417 | 0
| 0.84722 | 311.117 | 51.313 | 66.551 | 45.056 | 82.38 |  | 2.5417 | 9.4 | 12.8 | 5.0833 | 0
| 0.85417 | 311.837 | 51.273 | 66.52 | 45.021 | 82.337 |  | 2.5625 | 10.4 | 12.8 | 5.125 | 0
| 0.86111 | 312.139 | 51.279 | 66.53 | 45.033 | 82.35 |  | 2.5833 | 11.3 | 12.8 | 5.1667 | 0
| 0.86806 | 311.275 | 51.258 | 66.522 | 45.017 | 82.331 |  | 2.6042 | 11.7 | 12.8 | 5.2083 | 0
| 0.875 | 311.129 | 51.254 | 66.517 | 45.012 | 82.324 |  | 2.625 | 11.4 | 12.8 | 5.25 | 0
| 0.88194 | 311.91 | 51.255 | 66.523 | 45.02 | 82.333 |  | 2.6458 | 11.2 | 12.8 | 5.2917 | 0
| 0.88889 | 311.537 | 51.228 | 66.498 | 44.996 | 82.299 |  | 2.6667 | 11.1 | 12.8 | 5.3333 | 0
| 0.89583 | 311.022 | 51.234 | 66.508 | 45.003 | 82.309 |  | 2.6875 | 10.8 | 12.8 | 5.375 | 0
| 0.90278 | 311.473 | 51.226 | 66.499 | 44.997 | 82.29 |  | 2.7083 | 10.8 | 12.8 | 5.4167 | 0
| 0.90972 | 311.832 | 51.244 | 66.508 | 45.013 | 82.309 |  | 2.7292 | 10.6 | 12.8 | 5.4583 | 0
| 0.91667 | 312.184 | 51.268 | 66.532 | 45.035 | 82.336 |  | 2.75 | 10.2 | 12.8 | 5.5 | 0
| 0.92361 | 312.762 | 51.288 | 66.551 | 45.051 | 82.364 |  | 2.7708 | 9.8 | 12.8 | 5.5417 | 0
| 0.93056 | 312.975 | 51.344 | 66.603 | 45.101 | 82.43 |  | 2.7917 | 9.4 | 12.8 | 5.5833 | 0.2
| 0.9375 | 313.864 | 51.408 | 66.659 | 45.146 | 82.504 |  | 2.8125 | 8.9 | 12.8 | 5.625 | 0
| 0.94444 | 310.774 | 51.428 | 66.699 | 45.178 | 82.548 |  | 2.8333 | 8.6 | 12.8 | 5.6667 | 0
| 0.95139 | 308.769 | 51.312 | 66.617 | 45.079 | 82.443 |  | 2.8542 | 8.4 | 12.8 | 5.7083 | 0
| 0.95833 | 308.779 | 51.166 | 66.501 | 44.958 | 82.283 |  | 2.875 | 8.4 | 12.8 | 5.75 | 0
| 0.96528 | 308.128 | 51.087 | 66.428 | 44.901 | 82.178 |  | 2.8958 | 8.4 | 12.8 | 5.7917 | 0
| 0.97222 | 309.134 | 51.05 | 66.382 | 44.869 | 82.111 |  | 2.9167 | 8.5 | 12.8 | 5.8333 | 0
| 0.97917 | 309.947 | 51.038 | 66.36 | 44.865 | 82.074 |  | 2.9375 | 8.3 | 12.8 | 5.875 | 0
| 0.98611 | 310.048 | 51.05 | 66.353 | 44.873 | 82.061 |  | 2.9583 | 8.3 | 12.8 | 5.9167 | 0.2
| 0.99306 | 310.975 | 51.072 | 66.363 | 44.893 | 82.069 |  | 2.9792 | 8.2 | 12.8 | 5.9583 | 0
| 1 | 310.281 | 51.11 | 66.382 | 44.923 | 82.097 |  | 3 | 8.2 | 12.8 | 6 | 0
| 1.0069 | 310.419 | 51.138 | 66.401 | 44.943 | 82.12 |  | 3.0208 | 8.1 | 12.8 | 6.0417 | 0
| 1.0139 | 311.136 | 51.126 | 66.392 | 44.941 | 82.113 |  | 3.0417 | 8.1 | 12.8 | 6.0833 | 0.2
| 1.0208 | 311.5 | 51.153 | 66.407 | 44.956 | 82.132 |  | 3.0625 | 8.1 | 12.8 | 6.125 | 0
| 1.0278 | 311.943 | 51.174 | 66.421 | 44.968 | 82.152 |  | 3.0833 | 8.1 | 12.8 | 6.1667 | 0
| 1.0347 | 311.84 | 51.22 | 66.467 | 45.01 | 82.208 |  | 3.1042 | 8.1 | 12.8 | 6.2083 | 0
| 1.0417 | 311.633 | 51.237 | 66.481 | 45.025 | 82.232 |  | 3.125 | 8 | 12.8 | 6.25 | 0
| 1.0486 | 311.276 | 51.239 | 66.496 | 45.029 | 82.239 |  | 3.1458 | 7.9 | 12.8 | 6.2917 | 0
| 1.0556 | 311.05 | 51.233 | 66.496 | 45.026 | 82.246 |  | 3.1667 | 7.9 | 12.8 | 6.3333 | 0
| 1.0625 | 311.169 | 51.216 | 66.488 | 45.014 | 82.232 |  | 3.1875 | 7.9 | 12.8 | 6.375 | 0
| 1.0694 | 311.096 | 51.232 | 66.495 | 45.022 | 82.246 |  | 3.2083 | 7.9 | 12.2 | 6.4167 | 0
| 1.0764 | 311.933 | 51.245 | 66.513 | 45.036 | 82.264 |  | 3.2292 | 7.9 | 12.2 | 6.4583 | 0
| 1.0833 | 311.654 | 51.259 | 66.528 | 45.044 | 82.283 |  | 3.25 | 7.9 | 12.2 | 6.5 | 0
| 1.0903 | 311.287 | 51.267 | 66.54 | 45.058 | 82.295 |  | 3.2708 | 8 | 12.2 | 6.5417 | 0
| 1.0972 | 311.802 | 51.27 | 66.542 | 45.059 | 82.302 |  | 3.2917 | 8 | 12.2 | 6.5833 | 0
| 1.1042 | 311.493 | 51.264 | 66.545 | 45.055 | 82.302 |  | 3.3125 | 7.9 | 12.2 | 6.625 | 0
| 1.1111 | 312.037 | 51.266 | 66.554 | 45.059 | 82.313 |  | 3.3333 | 7.9 | 12.2 | 6.6667 | 0
| 1.1181 | 311.979 | 51.281 | 66.567 | 45.064 | 82.318 |  | 3.3542 | 7.9 | 12.2 | 6.7083 | 0
| 1.125 | 311.376 | 51.274 | 66.563 | 45.062 | 82.325 |  | 3.375 | 8.2 | 12.2 | 6.75 | 0
| 1.1319 | 311.531 | 51.285 | 66.573 | 45.074 | 82.336 |  | 3.3958 | 8.4 | 12.2 | 6.7917 | 0
| 1.1389 | 311.887 | 51.278 | 66.579 | 45.072 | 82.331 |  | 3.4167 | 8.7 | 12.2 | 6.8333 | 0
| 1.1458 | 311.618 | 51.306 | 66.596 | 45.092 | 82.362 |  | 3.4375 | 8.9 | 12.2 | 6.875 | 0
| 1.1528 | 312.085 | 51.325 | 66.617 | 45.11 | 82.384 |  | 3.4583 | 9.2 | 12.2 | 6.9167 | 0
| 1.1597 | 311.4 | 51.324 | 66.627 | 45.111 | 82.394 |  | 3.4792 | 9.4 | 12.2 | 6.9583 | 0
| 1.1667 | 312.2 | 51.336 | 66.638 | 45.116 | 82.411 |  | 3.5 | 10.4 | 12.2 | 7 | 0
| 1.1736 | 311.357 | 51.331 | 66.641 | 45.118 | 82.411 |  | 3.5208 | 11.2 | 12.2 | 7.0417 | 0
| 1.1806 | 311.553 | 51.316 | 66.633 | 45.105 | 82.402 |  | 3.5417 | 12 | 12.2 | 7.0833 | 0
| 1.1875 | 311.21 | 51.318 | 66.639 | 45.11 | 82.404 |  | 3.5625 | 12.3 | 12.2 | 7.125 | 0
| 1.1944 | 311.34 | 51.3 | 66.628 | 45.094 | 82.385 |  | 3.5833 | 12.3 | 12.2 | 7.1667 | 0
| 1.2014 | 310.786 | 51.286 | 66.614 | 45.084 | 82.373 |  | 3.6042 | 11.9 | 12.2 | 7.2083 | 0
| 1.2083 | 311.466 | 51.272 | 66.606 | 45.08 | 82.353 |  | 3.625 | 12.6 | 12.2 | 7.25 | 0
| 1.2153 | 310.699 | 51.26 | 66.594 | 45.066 | 82.335 |  | 3.6458 | 12.9 | 12.2 | 7.2917 | 0
| 1.2222 | 310.431 | 51.241 | 66.577 | 45.051 | 82.306 |  | 3.6667 | 13.1 | 12.2 | 7.3333 | 0
| 1.2292 | 310.889 | 51.229 | 66.566 | 45.04 | 82.29 |  | 3.6875 | 13.2 | 12.2 | 7.375 | 0
| 1.2361 | 310.321 | 51.197 | 66.534 | 45.019 | 82.25 |  | 3.7083 | 12.8 | 12.2 | 7.4167 | 0
| 1.2431 | 309.529 | 51.17 | 66.513 | 45 | 82.213 |  | 3.7292 | 11.7 | 12.2 | 7.4583 | 0
| 1.25 | 309.357 | 51.13 | 66.475 | 44.969 | 82.166 |  | 3.75 | 11.1 | 12.2 | 7.5 | 0
| 1.2569 | 309.343 | 51.097 | 66.435 | 44.937 | 82.108 |  | 3.7708 | 11.1 | 12.2 | 7.5417 | 0
| 1.2639 | 308.456 | 51.042 | 66.38 | 44.895 | 82.036 |  | 3.7917 | 10.5 | 12.2 | 7.5833 | 0
| 1.2708 | 308.424 | 50.994 | 66.335 | 44.86 | 81.966 |  | 3.8125 | 10.2 | 12.2 | 7.625 | 0
| 1.2778 | 308.433 | 50.942 | 66.274 | 44.821 | 81.89 |  | 3.8333 | 10.2 | 12.2 | 7.6667 | 0
| 1.2847 | 307.989 | 50.906 | 66.233 | 44.789 | 81.816 |  | 3.8542 | 10.1 | 12.2 | 7.7083 | 0
| 1.2917 | 314.928 | 51.082 | 66.325 | 44.912 | 81.968 |  | 3.875 | 9.7 | 12.2 | 7.75 | 0
| 1.2986 | 311.156 | 51.108 | 66.368 | 44.955 | 82.008 |  | 3.8958 | 9.4 | 12.2 | 7.7917 | 0
| 1.3056 | 313.012 | 51.192 | 66.427 | 45.013 | 82.095 |  | 3.9167 | 9.3 | 12.2 | 7.8333 | 0
| 1.3125 | 313.636 | 51.3 | 66.519 | 45.102 | 82.234 |  | 3.9375 | 9.1 | 12.2 | 7.875 | 0
| 1.3194 | 312.454 | 51.332 | 66.565 | 45.126 | 82.287 |  | 3.9583 | 9 | 12.2 | 7.9167 | 0
| 1.3264 | 312.795 | 51.338 | 66.575 | 45.13 | 82.321 |  | 3.9792 | 8.9 | 12.2 | 7.9583 | 0
| 1.3333 | 312.711 | 51.352 | 66.607 | 45.141 | 82.356 |  | 4 | 8.8 | 12.2 | 8 | 0
| 1.3403 | 311.546 | 51.34 | 66.607 | 45.132 | 82.36 |  | 4.0208 | 8.7 | 12.2 | 8.0417 | 0
| 1.3472 | 311.306 | 51.333 | 66.611 | 45.126 | 82.363 |  | 4.0417 | 8.4 | 12.2 | 8.0833 | 0
| 1.3542 | 311.224 | 51.298 | 66.588 | 45.102 | 82.335 |  | 4.0625 | 8.2 | 12.2 | 8.125 | 0.4
| 1.3611 | 310.693 | 51.273 | 66.576 | 45.081 | 82.314 |  | 4.0833 | 7.8 | 12.2 | 8.1667 | 0
| 1.3681 | 310.21 | 51.233 | 66.549 | 45.051 | 82.273 |  | 4.1042 | 7.6 | 12.2 | 8.2083 | 0
| 1.375 | 310.159 | 51.186 | 66.511 | 45.007 | 82.218 |  | 4.125 | 7.7 | 12.2 | 8.25 | 0
| 1.3819 | 309.559 | 51.147 | 66.475 | 44.984 | 82.168 |  | 4.1458 | 7.9 | 12.2 | 8.2917 | 0
| 1.3889 | 309.316 | 51.105 | 66.433 | 44.952 | 82.108 |  | 4.1667 | 7.9 | 12.2 | 8.3333 | 0
| 1.3958 | 309.445 | 51.066 | 66.387 | 44.918 | 82.048 |  | 4.1875 | 7.8 | 12.2 | 8.375 | 0
| 1.4028 | 308.982 | 51.01 | 66.338 | 44.871 | 81.974 |  | 4.2083 | 7.9 | 12.2 | 8.4167 | 0
| 1.4097 | 309.152 | 50.981 | 66.298 | 44.847 | 81.917 |  | 4.2292 | 7.9 | 12.2 | 8.4583 | 0
| 1.4167 | 308.476 | 50.945 | 66.249 | 44.823 | 81.859 |  | 4.25 | 7.9 | 12.2 | 8.5 | 0
| 1.4236 | 307.919 | 50.896 | 66.203 | 44.782 | 81.791 |  | 4.2708 | 8 | 12.2 | 8.5417 | 0
| 1.4306 | 307.642 | 50.87 | 66.162 | 44.762 | 81.737 |  | 4.2917 | 8.1 | 12.2 | 8.5833 | 0
| 1.4375 | 308.582 | 50.853 | 66.131 | 44.747 | 81.698 |  | 4.3125 | 8 | 12.2 | 8.625 | 0
| 1.4444 | 311.295 | 50.941 | 66.171 | 44.805 | 81.763 |  | 4.3333 | 7.9 | 12.2 | 8.6667 | 0
| 1.4514 | 311.193 | 51.073 | 66.271 | 44.918 | 81.891 |  | 4.3542 | 7.8 | 12.2 | 8.7083 | 0
| 1.4583 | 310.991 | 51.103 | 66.304 | 44.942 | 81.945 |  | 4.375 | 8.2 | 12.2 | 8.75 | 0
| 1.4653 | 310.496 | 51.11 | 66.315 | 44.948 | 81.965 |  | 4.3958 | 8.7 | 12.2 | 8.7917 | 0
| 1.4722 | 310.524 | 51.119 | 66.322 | 44.95 | 81.984 |  | 4.4167 | 9 | 12.2 | 8.8333 | 0
| 1.4792 | 310.82 | 51.121 | 66.336 | 44.952 | 81.992 |  | 4.4375 | 9.2 | 12.2 | 8.875 | 0
| 1.4861 | 309.688 | 51.1 | 66.321 | 44.941 | 81.981 |  | 4.4583 | 9.6 | 12.2 | 8.9167 | 0
| 1.4931 | 310.642 | 51.085 | 66.31 | 44.927 | 81.969 |  | 4.4792 | 10.2 | 12.2 | 8.9583 | 0
| 1.5 | 309.583 | 51.09 | 66.313 | 44.925 | 81.973 |  | 4.5 | 10.9 | 12.2 | 9 | 0
| 1.5069 | 309.655 | 51.062 | 66.292 | 44.903 | 81.943 |  | 4.5208 | 10.9 | 12.2 | 9.0417 | 0
| 1.5139 | 309.938 | 51.046 | 66.275 | 44.893 | 81.931 |  | 4.5417 | 11.1 | 12.2 | 9.0833 | 0
| 1.5208 | 310.218 | 51.058 | 66.279 | 44.899 | 81.937 |  | 4.5625 | 11.2 | 12.2 | 9.125 | 0
| 1.5278 | 309.701 | 51.067 | 66.285 | 44.903 | 81.941 |  | 4.5833 | 11.3 | 12.2 | 9.1667 | 0.2
| 1.5347 | 310.342 | 51.08 | 66.29 | 44.918 | 81.954 |  | 4.6042 | 11.8 | 12.2 | 9.2083 | 0
| 1.5417 | 311.19 | 51.119 | 66.328 | 44.949 | 82.002 |  | 4.625 | 11.8 | 12.2 | 9.25 | 0
| 1.5486 | 311.135 | 51.128 | 66.338 | 44.957 | 82.021 |  | 4.6458 | 11.9 | 12.2 | 9.2917 | 0
| 1.5556 | 311.291 | 51.145 | 66.349 | 44.96 | 82.042 |  | 4.6667 | 11.8 | 12.2 | 9.3333 | 0
| 1.5625 | 311.713 | 51.171 | 66.372 | 44.986 | 82.07 |  | 4.6875 | 11.8 | 12.2 | 9.375 | 0
| 1.5694 | 311.126 | 51.199 | 66.402 | 45.008 | 82.117 |  | 4.7083 | 11.6 | 12.2 | 9.4167 | 0
| 1.5764 | 311.762 | 51.235 | 66.439 | 45.037 | 82.166 |  | 4.7292 | 11.2 | 12.2 | 9.4583 | 0
| 1.5833 | 311.991 | 51.248 | 66.456 | 45.049 | 82.198 |  | 4.75 | 10.7 | 12.2 | 9.5 | 0
| 1.5903 | 312.835 | 51.289 | 66.493 | 45.077 | 82.251 |  | 4.7708 | 10.1 | 12.2 | 9.5417 | 0
| 1.5972 | 313.061 | 51.34 | 66.544 | 45.12 | 82.323 |  | 4.7917 | 9.9 | 12.2 | 9.5833 | 0
| 1.6042 | 313.784 | 51.392 | 66.602 | 45.161 | 82.392 |  | 4.8125 | 9.6 | 12.2 | 9.625 | 0
| 1.6111 | 313.134 | 51.416 | 66.632 | 45.176 | 82.443 |  | 4.8333 | 9.2 | 12.2 | 9.6667 | 0
| 1.6181 | 313.715 | 51.444 | 66.671 | 45.202 | 82.492 |  | 4.8542 | 8.8 | 12.2 | 9.7083 | 0
| 1.625 | 313.398 | 51.447 | 66.691 | 45.201 | 82.523 |  | 4.875 | 8.4 | 12.2 | 9.75 | 0
| 1.6319 | 313.318 | 51.461 | 66.714 | 45.208 | 82.552 |  | 4.8958 | 8.2 | 12.2 | 9.7917 | 0
| 1.6389 | 313.546 | 51.485 | 66.746 | 45.23 | 82.593 |  | 4.9167 | 7.9 | 12.2 | 9.8333 | 0
| 1.6458 | 314.443 | 51.513 | 66.783 | 45.256 | 82.642 |  | 4.9375 | 7.4 | 12.2 | 9.875 | 0
| 1.6528 | 313.331 | 51.532 | 66.813 | 45.273 | 82.685 |  | 4.9583 | 7 | 12.2 | 9.9167 | 0
| 1.6597 | 313.124 | 51.529 | 66.827 | 45.266 | 82.698 |  | 4.9792 | 6.7 | 12.2 | 9.9583 | 0
| 1.6667 | 314.549 | 51.552 | 66.853 | 45.284 | 82.741 |  | 5 | 6.4 | 12.2 | 10 | 0.2
| 1.6736 | 313.452 | 51.569 | 66.876 | 45.302 | 82.773 |  | 5.0208 | 6.3 | 12.2 | 10.0417 | 0
| 1.6806 | 314.04 | 51.583 | 66.904 | 45.311 | 82.801 |  | 5.0417 | 5.8 | 12.2 | 10.0833 | 0
| 1.6875 | 313.479 | 51.585 | 66.922 | 45.317 | 82.82 |  | 5.0625 | 5.6 | 12.2 | 10.125 | 0
| 1.6944 | 313.557 | 51.58 | 66.927 | 45.312 | 82.834 |  | 5.0833 | 5.4 | 12.2 | 10.1667 | 0
| 1.7014 | 312.967 | 51.559 | 66.914 | 45.291 | 82.816 |  | 5.1042 | 5.3 | 12.2 | 10.2083 | 0
| 1.7083 | 313.105 | 51.52 | 66.895 | 45.262 | 82.784 |  | 5.125 | 6.4 | 12.2 | 10.25 | 0
| 1.7153 | 312.383 | 51.491 | 66.882 | 45.248 | 82.757 |  | 5.1458 | 7.1 | 12.2 | 10.2917 | 0
| 1.7222 | 312.321 | 51.477 | 66.871 | 45.231 | 82.742 |  | 5.1667 | 7.4 | 12.2 | 10.3333 | 0
| 1.7292 | 312.373 | 51.456 | 66.854 | 45.213 | 82.718 |  | 5.1875 | 7.7 | 12.2 | 10.375 | 0
| 1.7361 | 310.658 | 51.409 | 66.819 | 45.179 | 82.666 |  | 5.2083 | 7.7 | 12.2 | 10.4167 | 0
| 1.7431 | 310.233 | 51.331 | 66.755 | 45.118 | 82.576 |  | 5.2292 | 7.7 | 12.2 | 10.4583 | 0
| 1.75 | 310.655 | 51.262 | 66.693 | 45.065 | 82.481 |  | 5.25 | 7.6 | 12.2 | 10.5 | 0
| 1.7569 | 308.891 | 51.171 | 66.612 | 44.998 | 82.365 |  | 5.2708 | 7.7 | 12.2 | 10.5417 | 0
| 1.7639 | 309.294 | 51.058 | 66.491 | 44.894 | 82.207 |  | 5.2917 | 7.8 | 12.2 | 10.5833 | 0
| 1.7708 | 312.665 | 51.207 | 66.579 | 45.016 | 82.33 |  | 5.3125 | 7.9 | 12.2 | 10.625 | 0
| 1.7778 | 311.461 | 51.245 | 66.604 | 45.054 | 82.357 |  | 5.3333 | 7.8 | 12.2 | 10.6667 | 0
| 1.7847 | 312.101 | 51.285 | 66.631 | 45.078 | 82.4 |  | 5.3542 | 8.1 | 12.2 | 10.7083 | 0
| 1.7917 | 312.565 | 51.323 | 66.659 | 45.105 | 82.436 |  | 5.375 | 8.4 | 12.2 | 10.75 | 0
| 1.7986 | 312.947 | 51.352 | 66.685 | 45.135 | 82.476 |  | 5.3958 | 8.9 | 12.2 | 10.7917 | 0
| 1.8056 | 312.987 | 51.386 | 66.716 | 45.161 | 82.52 |  | 5.4167 | 9.2 | 12.2 | 10.8333 | 0
| 1.8125 | 313.474 | 51.413 | 66.743 | 45.181 | 82.558 |  | 5.4375 | 10.1 | 12.2 | 10.875 | 0
| 1.8194 | 313.582 | 51.438 | 66.772 | 45.201 | 82.592 |  | 5.4583 | 10.7 | 12.2 | 10.9167 | 0
| 1.8264 | 312.896 | 51.47 | 66.805 | 45.225 | 82.641 |  | 5.4792 | 10.9 | 12.2 | 10.9583 | 0
| 1.8333 | 310.303 | 51.334 | 66.714 | 45.118 | 82.514 |  | 5.5 | 10.7 | 12.2 | 11 | 0
| 1.8403 | 310.339 | 51.264 | 66.658 | 45.067 | 82.439 |  | 5.5208 | 10.8 | 12.2 | 11.0417 | 0
| 1.8472 | 311.459 | 51.25 | 66.634 | 45.049 | 82.401 |  | 5.5417 | 9.9 | 12.2 | 11.0833 | 0
| 1.8542 | 311.024 | 51.24 | 66.623 | 45.054 | 82.384 |  | 5.5625 | 9.9 | 12.2 | 11.125 | 0
| 1.8611 | 312.604 | 51.274 | 66.632 | 45.071 | 82.4 |  | 5.5833 | 9.8 | 12.2 | 11.1667 | 0
| 1.8681 | 310.978 | 51.256 | 66.621 | 45.064 | 82.385 |  | 5.6042 | 10.1 | 12.2 | 11.2083 | 0
| 1.875 | 311.356 | 51.244 | 66.608 | 45.054 | 82.361 |  | 5.625 | 10.5 | 12.2 | 11.25 | 0
| 1.8819 | 311.824 | 51.244 | 66.602 | 45.052 | 82.349 |  | 5.6458 | 10.7 | 12.2 | 11.2917 | 0
| 1.8889 | 311.14 | 51.258 | 66.612 | 45.065 | 82.362 |  | 5.6667 | 10.6 | 12.2 | 11.3333 | 0
| 1.8958 | 310.524 | 51.256 | 66.61 | 45.068 | 82.364 |  | 5.6875 | 10.6 | 12.2 | 11.375 | 0
| 1.9028 | 310.351 | 51.203 | 66.562 | 45.021 | 82.299 |  | 5.7083 | 10.4 | 12.2 | 11.4167 | 0
| 1.9097 | 310.11 | 51.185 | 66.546 | 45.01 | 82.274 |  | 5.7292 | 10.4 | 12.2 | 11.4583 | 0
| 1.9167 | 312.103 | 51.194 | 66.542 | 45.011 | 82.267 |  | 5.75 | 10.3 | 12.2 | 11.5 | 0
| 1.9236 | 311.433 | 51.216 | 66.556 | 45.035 | 82.284 |  | 5.7708 | 10.3 | 12.2 | 11.5417 | 0
| 1.9306 | 311.635 | 51.25 | 66.576 | 45.055 | 82.316 |  | 5.7917 | 10.3 | 12.2 | 11.5833 | 0
| 1.9375 | 312.804 | 51.281 | 66.607 | 45.083 | 82.348 |  | 5.8125 | 10.2 | 12.2 | 11.625 | 0
| 1.9444 | 313.176 | 51.344 | 66.652 | 45.13 | 82.419 |  | 5.8333 | 10.2 | 12.2 | 11.6667 | 0
| 1.9514 | 314.243 | 51.42 | 66.719 | 45.188 | 82.517 |  | 5.8542 | 10.3 | 12.2 | 11.7083 | 0
| 1.9583 | 307.708 | 51.344 | 66.695 | 45.154 | 82.462 |  | 5.875 | 10.3 | 12.2 | 11.75 | 0
| 1.9653 | 311.295 | 51.322 | 66.665 | 45.119 | 82.449 |  | 5.8958 | 10.3 | 12.2 | 11.7917 | 0
| 1.9722 | 311.657 | 51.307 | 66.655 | 45.102 | 82.43 |  | 5.9167 | 10.3 | 12.2 | 11.8333 | 0
| 1.9792 | 312.318 | 51.331 | 66.68 | 45.125 | 82.454 |  | 5.9375 | 10.2 | 12.2 | 11.875 | 0
| 1.9861 | 313.46 | 51.39 | 66.722 | 45.169 | 82.514 |  | 5.9583 | 10.3 | 12.2 | 11.9167 | 0
| 1.9931 | 313.585 | 51.432 | 66.761 | 45.205 | 82.568 |  | 5.9792 | 10.3 | 12.2 | 11.9583 | 0
| 2 | 314.097 | 51.478 | 66.811 | 45.242 | 82.633 |  | 6 | 10.3 | 12.2 | 12 | 0
| 2.0069 | 312.903 | 51.506 | 66.847 | 45.263 | 82.675 |  | 6.0208 | 10.3 | 12.2 | 12.0417 | 0
| 2.0139 | 313.154 | 51.508 | 66.859 | 45.265 | 82.695 |  | 6.0417 | 10.2 | 12.2 | 12.0833 | 0
| 2.0208 | 313.207 | 51.529 | 66.886 | 45.284 | 82.735 |  | 6.0625 | 10.2 | 12.2 | 12.125 | 0
| 2.0278 | 313.444 | 51.545 | 66.911 | 45.298 | 82.761 |  | 6.0833 | 10.2 | 12.2 | 12.1667 | 0
| 2.0347 | 314.165 | 51.57 | 66.941 | 45.319 | 82.797 |  | 6.1042 | 10.3 | 12.2 | 12.2083 | 0
| 2.0417 | 310.108 | 51.58 | 66.96 | 45.332 | 82.829 |  | 6.125 | 10.2 | 12.2 | 12.25 | 0
| 2.0486 | 310.341 | 51.382 | 66.816 | 45.168 | 82.624 |  | 6.1458 | 10.2 | 12.2 | 12.2917 | 0
| 2.0556 | 310.433 | 51.296 | 66.743 | 45.101 | 82.525 |  | 6.1667 | 10.2 | 12.2 | 12.3333 | 0
| 2.0625 | 310.96 | 51.271 | 66.71 | 45.085 | 82.477 |  | 6.1875 | 10.2 | 12.2 | 12.375 | 0
| 2.0694 | 310.846 | 51.241 | 66.678 | 45.066 | 82.425 |  | 6.2083 | 10.1 | 12.2 | 12.4167 | 0
| 2.0764 | 310.126 | 51.235 | 66.66 | 45.052 | 82.395 |  | 6.2292 | 9.9 | 12.2 | 12.4583 | 0
| 2.0833 | 311.206 | 51.228 | 66.638 | 45.055 | 82.373 |  | 6.25 | 9.9 | 12.2 | 12.5 | 0
| 2.0903 | 310.99 | 51.235 | 66.64 | 45.06 | 82.367 |  | 6.2708 | 10 | 12.2 | 12.5417 | 0
| 2.0972 | 310.844 | 51.24 | 66.637 | 45.065 | 82.359 |  | 6.2917 | 9.8 | 12.2 | 12.5833 | 0
| 2.1042 | 310.531 | 51.246 | 66.633 | 45.067 | 82.353 |  | 6.3125 | 9.6 | 12.2 | 12.625 | 0
| 2.1111 | 311.008 | 51.243 | 66.626 | 45.063 | 82.34 |  | 6.3333 | 9.7 | 12.2 | 12.6667 | 0
| 2.1181 | 310.211 | 51.225 | 66.606 | 45.052 | 82.32 |  | 6.3542 | 9.8 | 12.2 | 12.7083 | 0
| 2.125 | 310.442 | 51.222 | 66.599 | 45.053 | 82.314 |  | 6.375 | 10.1 | 12.2 | 12.75 | 0
| 2.1319 | 310.464 | 51.226 | 66.594 | 45.048 | 82.305 |  | 6.3958 | 10.5 | 12.2 | 12.7917 | 0
| 2.1389 | 310.764 | 51.225 | 66.587 | 45.046 | 82.298 |  | 6.4167 | 10.9 | 12.2 | 12.8333 | 0
| 2.1458 | 310.834 | 51.213 | 66.581 | 45.036 | 82.281 |  | 6.4375 | 11.3 | 12.2 | 12.875 | 0
| 2.1528 | 310.226 | 51.185 | 66.552 | 45.019 | 82.247 |  | 6.4583 | 11.6 | 12.2 | 12.9167 | 0
| 2.1597 | 310.096 | 51.153 | 66.525 | 44.994 | 82.211 |  | 6.4792 | 12 | 12.2 | 12.9583 | 0
| 2.1667 | 310.379 | 51.148 | 66.511 | 44.989 | 82.184 |  | 6.5 | 12.7 | 12.2 | 13 | 0
| 2.1736 | 309.786 | 51.149 | 66.5 | 44.983 | 82.179 |  | 6.5208 | 13.3 | 12.2 | 13.0417 | 0
| 2.1806 | 309.951 | 51.14 | 66.492 | 44.981 | 82.158 |  | 6.5417 | 14.1 | 12.2 | 13.0833 | 0
| 2.1875 | 309.625 | 51.114 | 66.461 | 44.963 | 82.128 |  | 6.5625 | 14.7 | 12.2 | 13.125 | 0.2
| 2.1944 | 308.111 | 51.066 | 66.416 | 44.917 | 82.061 |  | 6.5833 | 15.8 | 12.2 | 13.1667 | 0
| 2.2014 | 311.071 | 51.168 | 66.477 | 44.998 | 82.15 |  | 6.6042 | 15.9 | 12.2 | 13.2083 | 0
| 2.2083 | 311.138 | 51.199 | 66.505 | 45.024 | 82.187 |  | 6.625 | 14.8 | 12.2 | 13.25 | 0
| 2.2153 | 310.315 | 51.187 | 66.495 | 45.017 | 82.179 |  | 6.6458 | 14.8 | 12.2 | 13.2917 | 0
| 2.2222 | 309.523 | 51.145 | 66.467 | 44.981 | 82.137 |  | 6.6667 | 15.4 | 12.2 | 13.3333 | 0
| 2.2292 | 308.893 | 51.119 | 66.439 | 44.96 | 82.097 |  | 6.6875 | 14.8 | 12.2 | 13.375 | 0
| 2.2361 | 310.034 | 51.106 | 66.423 | 44.951 | 82.086 |  | 6.7083 | 14.2 | 12.2 | 13.4167 | 0
| 2.2431 | 312.171 | 51.153 | 66.446 | 44.986 | 82.119 |  | 6.7292 | 13.9 | 12.2 | 13.4583 | 0
| 2.25 | 312.342 | 51.287 | 66.551 | 45.094 | 82.262 |  | 6.75 | 12.7 | 12.2 | 13.5 | 0
| 2.2569 | 312.209 | 51.322 | 66.592 | 45.126 | 82.318 |  | 6.7708 | 11.5 | 12.2 | 13.5417 | 0
| 2.2639 | 311.095 | 51.327 | 66.608 | 45.124 | 82.343 |  | 6.7917 | 10.4 | 12.2 | 13.5833 | 0
| 2.2708 | 310.655 | 51.293 | 66.588 | 45.1 | 82.321 |  | 6.8125 | 9.6 | 12.2 | 13.625 | 0
| 2.2778 | 310.718 | 51.287 | 66.589 | 45.087 | 82.32 |  | 6.8333 | 8.9 | 12.2 | 13.6667 | 0
| 2.2847 | 311.238 | 51.28 | 66.589 | 45.083 | 82.319 |  | 6.8542 | 8.5 | 12.2 | 13.7083 | 0
| 2.2917 | 309.994 | 51.235 | 66.559 | 45.051 | 82.277 |  | 6.875 | 7.9 | 12.2 | 13.75 | 0
| 2.2986 | 309.008 | 51.174 | 66.508 | 45 | 82.211 |  | 6.8958 | 7.6 | 12.2 | 13.7917 | 0
| 2.3056 | 310.838 | 51.203 | 66.517 | 45.018 | 82.228 |  | 6.9167 | 7.3 | 12.2 | 13.8333 | 0
| 2.3125 | 310.831 | 51.224 | 66.538 | 45.041 | 82.246 |  | 6.9375 | 7 | 12.2 | 13.875 | 0
| 2.3194 | 310.695 | 51.233 | 66.54 | 45.044 | 82.254 |  | 6.9583 | 6.7 | 12.2 | 13.9167 | 0
| 2.3264 | 309.168 | 51.205 | 66.522 | 45.024 | 82.232 |  | 6.9792 | 6.1 | 12.2 | 13.9583 | 0
| 2.3333 | 309.401 | 51.162 | 66.495 | 44.995 | 82.185 |  | 7 | 5.8 | 12.2 | 14 | 0
| 2.3403 | 310.124 | 51.133 | 66.459 | 44.967 | 82.143 |  | 7.0208 | 5.8 | 12.2 | 14.0417 | 0
| 2.3472 | 309.375 | 51.092 | 66.421 | 44.932 | 82.093 |  | 7.0417 | 6.2 | 12.2 | 14.0833 | 0
| 2.3542 | 313.089 | 51.21 | 66.491 | 45.021 | 82.198 |  | 7.0625 | 6.3 | 12.2 | 14.125 | 0
| 2.3611 | 312.997 | 51.341 | 66.596 | 45.13 | 82.335 |  | 7.0833 | 6.2 | 12.2 | 14.1667 | 0
| 2.3681 | 314.111 | 51.424 | 66.672 | 45.192 | 82.442 |  | 7.1042 | 6.9 | 12.2 | 14.2083 | 0
| 2.375 | 312.5 | 51.463 | 66.727 | 45.229 | 82.521 |  | 7.125 | 7.6 | 12.2 | 14.25 | 0
| 2.3819 | 312.456 | 51.48 | 66.754 | 45.239 | 82.562 |  | 7.1458 | 7.4 | 12.2 | 14.2917 | 0
| 2.3889 | 311.747 | 51.461 | 66.758 | 45.224 | 82.569 |  | 7.1667 | 7.8 | 12.2 | 14.3333 | 0
| 2.3958 | 311.239 | 51.408 | 66.724 | 45.173 | 82.528 |  | 7.1875 | 8.2 | 12.2 | 14.375 | 0
| 2.4028 | 311.458 | 51.387 | 66.715 | 45.159 | 82.512 |  | 7.2083 | 8.2 | 12.2 | 14.4167 | 0
| 2.4097 | 312.137 | 51.389 | 66.721 | 45.162 | 82.52 |  | 7.2292 | 8.3 | 12.2 | 14.4583 | 0.2
| 2.4167 | 312.703 | 51.403 | 66.734 | 45.175 | 82.532 |  | 7.25 | 8.3 | 12.2 | 14.5 | 0
| 2.4236 | 311.57 | 51.414 | 66.751 | 45.179 | 82.558 |  | 7.2708 | 8.5 | 12.2 | 14.5417 | 0
| 2.4306 | 312.808 | 51.414 | 66.752 | 45.183 | 82.568 |  | 7.2917 | 8.4 | 12.2 | 14.5833 | 0
| 2.4375 | 312.082 | 51.391 | 66.738 | 45.16 | 82.547 |  | 7.3125 | 7.6 | 12.2 | 14.625 | 0
| 2.4444 | 312.099 | 51.366 | 66.722 | 45.142 | 82.524 |  | 7.3333 | 6.8 | 12.2 | 14.6667 | 0
| 2.4514 | 312.774 | 51.372 | 66.723 | 45.143 | 82.532 |  | 7.3542 | 6.3 | 12.2 | 14.7083 | 0
| 2.4583 | 312.146 | 51.368 | 66.72 | 45.14 | 82.527 |  | 7.375 | 6.5 | 12.2 | 14.75 | 0
| 2.4653 | 312.666 | 51.382 | 66.726 | 45.147 | 82.535 |  | 7.3958 | 8.1 | 12.2 | 14.7917 | 0
| 2.4722 | 312.364 | 51.374 | 66.723 | 45.144 | 82.531 |  | 7.4167 | 9 | 12.2 | 14.8333 | 0
| 2.4792 | 313.118 | 51.392 | 66.735 | 45.151 | 82.551 |  | 7.4375 | 9.6 | 12.2 | 14.875 | 0
| 2.4861 | 313.433 | 51.449 | 66.772 | 45.195 | 82.616 |  | 7.4583 | 10 | 12.2 | 14.9167 | 0
| 2.4931 | 313.688 | 51.491 | 66.815 | 45.231 | 82.67 |  | 7.4792 | 10.5 | 12.2 | 14.9583 | 0
| 2.5 | 312.728 | 51.499 | 66.827 | 45.229 | 82.694 |  | 7.5 | 11.9 | 12.2 | 15 | 0
| 2.5069 | 313.943 | 51.508 | 66.848 | 45.238 | 82.725 |  | 7.5208 | 12.9 | 12.2 | 15.0417 | 0
| 2.5139 | 311.126 | 51.472 | 66.832 | 45.216 | 82.696 |  | 7.5417 | 13.8 | 12.2 | 15.0833 | 0
| 2.5208 | 310.831 | 51.337 | 66.721 | 45.099 | 82.56 |  | 7.5625 | 14.2 | 12.2 | 15.125 | 0
| 2.5278 | 309.705 | 51.248 | 66.648 | 45.029 | 82.453 |  | 7.5833 | 14.8 | 12.2 | 15.1667 | 0
| 2.5347 | 310.063 | 51.19 | 66.583 | 44.979 | 82.37 |  | 7.6042 | 14.7 | 12.2 | 15.2083 | 0
| 2.5417 | 309.194 | 51.116 | 66.509 | 44.919 | 82.271 |  | 7.625 | 15.3 | 12.2 | 15.25 | 0
| 2.5486 | 308.959 | 51.045 | 66.433 | 44.861 | 82.164 |  | 7.6458 | 15 | 12.2 | 15.2917 | 0
| 2.5556 | 308.127 | 50.952 | 66.34 | 44.789 | 82.04 |  | 7.6667 | 15 | 12.2 | 15.3333 | 0
| 2.5625 | 308.327 | 50.883 | 66.252 | 44.728 | 81.928 |  | 7.6875 | 14.7 | 12.2 | 15.375 | 0
| 2.5694 | 307.89 | 50.856 | 66.204 | 44.708 | 81.859 |  | 7.7083 | 14.8 | 12.2 | 15.4167 | 0
| 2.5764 | 307.876 | 50.83 | 66.156 | 44.685 | 81.8 |  | 7.7292 | 14.5 | 12.2 | 15.4583 | 0
| 2.5833 | 307.146 | 50.757 | 66.071 | 44.621 | 81.686 |  | 7.75 | 12.8 | 12.2 | 15.5 | 0
| 2.5903 | 308.233 | 50.722 | 66.009 | 44.583 | 81.616 |  | 7.7708 | 11.2 | 12.2 | 15.5417 | 0
| 2.5972 | 307.17 | 50.69 | 65.956 | 44.566 | 81.547 |  | 7.7917 | 10.3 | 12.2 | 15.5833 | 0
| 2.6042 | 307.816 | 50.672 | 65.915 | 44.546 | 81.503 |  | 7.8125 | 9.6 | 12.2 | 15.625 | 0
| 2.6111 | 308.61 | 50.693 | 65.908 | 44.554 | 81.493 |  | 7.8333 | 9 | 12.2 | 15.6667 | 0
| 2.6181 | 309.066 | 50.681 | 65.878 | 44.544 | 81.462 |  | 7.8542 | 8.3 | 12.2 | 15.7083 | 0
| 2.625 | 308.635 | 50.701 | 65.869 | 44.557 | 81.461 |  | 7.875 | 7.8 | 12.2 | 15.75 | 0
| 2.6319 | 308.526 | 50.71 | 65.855 | 44.553 | 81.453 |  | 7.8958 | 7.5 | 12.2 | 15.7917 | 0
| 2.6389 | 309.971 | 50.732 | 65.861 | 44.572 | 81.468 |  | 7.9167 | 7.3 | 12.2 | 15.8333 | 0
| 2.6458 | 309.294 | 50.767 | 65.88 | 44.6 | 81.504 |  | 7.9375 | 6.7 | 12.2 | 15.875 | 0
| 2.6528 | 310.068 | 50.788 | 65.884 | 44.61 | 81.521 |  | 7.9583 | 6.2 | 12.2 | 15.9167 | 0
| 2.6597 | 309.887 | 50.799 | 65.888 | 44.617 | 81.54 |  | 7.9792 | 5.8 | 12.2 | 15.9583 | 0.2
| 2.6667 | 311.264 | 50.846 | 65.92 | 44.644 | 81.593 |  | 8 | 5.6 | 12.2 | 16 | 0
| 2.6736 | 310.648 | 50.899 | 65.961 | 44.688 | 81.659 |  | 8.0208 | 5.8 | 12.2 | 16.0417 | 0
| 2.6806 | 311.086 | 50.911 | 65.977 | 44.695 | 81.686 |  | 8.0417 | 5.8 | 12.2 | 16.0833 | 0
| 2.6875 | 310.408 | 50.915 | 65.974 | 44.688 | 81.7 |  | 8.0625 | 6.1 | 12.2 | 16.125 | 0
| 2.6944 | 311.253 | 50.954 | 66.006 | 44.716 | 81.746 |  | 8.0833 | 6.3 | 12.2 | 16.1667 | 0
| 2.7014 | 312.343 | 51.005 | 66.056 | 44.761 | 81.823 |  | 8.1042 | 6.3 | 12.2 | 16.2083 | 0
| 2.7083 | 311.674 | 51.06 | 66.109 | 44.807 | 81.894 |  | 8.125 | 6.9 | 12.2 | 16.25 | 0
| 2.7153 | 312.464 | 51.09 | 66.138 | 44.819 | 81.939 |  | 8.1458 | 7.4 | 12.2 | 16.2917 | 0
| 2.7222 | 311.504 | 51.081 | 66.15 | 44.817 | 81.967 |  | 8.1667 | 7.8 | 12.2 | 16.3333 | 0
| 2.7292 | 311.573 | 51.076 | 66.151 | 44.808 | 81.976 |  | 8.1875 | 8 | 12.2 | 16.375 | 0
| 2.7361 | 312.079 | 51.061 | 66.15 | 44.799 | 81.977 |  | 8.2083 | 8.1 | 12.8 | 16.4167 | 0
| 2.7431 | 312.14 | 51.061 | 66.151 | 44.794 | 81.986 |  | 8.2292 | 8.3 | 12.2 | 16.4583 | 0
| 2.75 | 310.247 | 51.016 | 66.127 | 44.76 | 81.952 |  | 8.25 | 8.7 | 12.8 | 16.5 | 0
| 2.7569 | 309.151 | 50.919 | 66.053 | 44.686 | 81.853 |  | 8.2708 | 8.8 | 12.8 | 16.5417 | 0
| 2.7639 | 308.343 | 50.802 | 65.955 | 44.591 | 81.718 |  | 8.2917 | 9.3 | 12.8 | 16.5833 | 0
| 2.7708 | 307.87 | 50.729 | 65.88 | 44.53 | 81.622 |  | 8.3125 | 9.7 | 12.8 | 16.625 | 0
| 2.7778 | 308.167 | 50.687 | 65.826 | 44.496 | 81.54 |  | 8.3333 | 10.1 | 12.8 | 16.6667 | 0
| 2.7847 | 308.208 | 50.664 | 65.789 | 44.478 | 81.491 |  | 8.3542 | 10.3 | 12.8 | 16.7083 | 0
| 2.7917 | 309.459 | 50.67 | 65.776 | 44.481 | 81.48 |  | 8.375 | 11 | 12.8 | 16.75 | 0
| 2.7986 | 310.306 | 50.691 | 65.778 | 44.501 | 81.487 |  | 8.3958 | 11.6 | 12.8 | 16.7917 | 0
| 2.8056 | 309.627 | 50.726 | 65.795 | 44.524 | 81.505 |  | 8.4167 | 11.8 | 12.8 | 16.8333 | 0
| 2.8125 | 311.289 | 50.778 | 65.827 | 44.565 | 81.553 |  | 8.4375 | 12.2 | 12.8 | 16.875 | 0
| 2.8194 | 312.679 | 50.868 | 65.895 | 44.636 | 81.657 |  | 8.4583 | 12.7 | 12.8 | 16.9167 | 0
| 2.8264 | 313.105 | 50.972 | 65.981 | 44.716 | 81.778 |  | 8.4792 | 13.1 | 12.8 | 16.9583 | 0
| 2.8333 | 313.498 | 51.072 | 66.074 | 44.793 | 81.912 |  | 8.5 | 13.3 | 12.8 | 17 | 0
| 2.8403 | 312.579 | 51.102 | 66.117 | 44.817 | 81.966 |  | 8.5208 | 13.4 | 12.8 | 17.0417 | 0
| 2.8472 | 313.247 | 51.13 | 66.158 | 44.833 | 82.019 |  | 8.5417 | 13.8 | 12.8 | 17.0833 | 0
| 2.8542 | 314.216 | 51.194 | 66.23 | 44.89 | 82.121 |  | 8.5625 | 14 | 12.8 | 17.125 | 0
| 2.8611 | 309.987 | 51.059 | 66.155 | 44.796 | 82.017 |  | 8.5833 | 14.3 | 12.8 | 17.1667 | 0
| 2.8681 | 310.318 | 50.976 | 66.094 | 44.717 | 81.933 |  | 8.6042 | 14.5 | 12.8 | 17.2083 | 0
| 2.875 | 307.985 | 50.849 | 65.998 | 44.626 | 81.808 |  | 8.625 | 14.8 | 12.8 | 17.25 | 0
| 2.8819 | 308.458 | 50.755 | 65.913 | 44.545 | 81.685 |  | 8.6458 | 14.4 | 12.8 | 17.2917 | 0
| 2.8889 | 310.036 | 50.751 | 65.89 | 44.545 | 81.647 |  | 8.6667 | 13.8 | 12.8 | 17.3333 | 0
| 2.8958 | 310.706 | 50.78 | 65.899 | 44.572 | 81.657 |  | 8.6875 | 12.8 | 12.8 | 17.375 | 0.2
| 2.9028 | 310.205 | 50.841 | 65.938 | 44.622 | 81.707 |  | 8.7083 | 11.6 | 12.8 | 17.4167 | 0
| 2.9097 | 311.139 | 50.877 | 65.968 | 44.649 | 81.746 |  | 8.7292 | 10.9 | 12.8 | 17.4583 | 0
| 2.9167 | 311.743 | 50.924 | 66.005 | 44.685 | 81.8 |  | 8.75 | 10.9 | 12.8 | 17.5 | 0
| 2.9236 | 313.321 | 51.014 | 66.075 | 44.755 | 81.897 |  | 8.7708 | 11.1 | 12.8 | 17.5417 | 0
| 2.9306 | 311.12 | 51.056 | 66.129 | 44.797 | 81.956 |  | 8.7917 | 11.4 | 12.8 | 17.5833 | 0
| 2.9375 | 311.609 | 51.026 | 66.119 | 44.77 | 81.944 |  | 8.8125 | 11.4 | 12.8 | 17.625 | 0
| 2.9444 | 312.168 | 51.046 | 66.136 | 44.782 | 81.979 |  | 8.8333 | 11.4 | 12.8 | 17.6667 | 0
| 2.9514 | 313.412 | 51.112 | 66.202 | 44.842 | 82.061 |  | 8.8542 | 11.4 | 12.8 | 17.7083 | 0
| 2.9583 | 309.573 | 50.99 | 66.134 | 44.752 | 81.957 |  | 8.875 | 11.2 | 12.8 | 17.75 | 0
| 2.9653 | 310.065 | 50.919 | 66.072 | 44.689 | 81.875 |  | 8.8958 | 10.9 | 12.8 | 17.7917 | 0
| 2.9722 | 310.404 | 50.899 | 66.051 | 44.674 | 81.842 |  | 8.9167 | 10.6 | 12.8 | 17.8333 | 0
| 2.9792 | 310.328 | 50.904 | 66.051 | 44.684 | 81.83 |  | 8.9375 | 10.7 | 12.8 | 17.875 | 0
| 2.9861 | 310.427 | 50.905 | 66.048 | 44.685 | 81.824 |  | 8.9583 | 10 | 12.8 | 17.9167 | 0
| 2.9931 | 311.928 | 50.937 | 66.073 | 44.71 | 81.861 |  | 8.9792 | 8.9 | 12.8 | 17.9583 | 0
| 3 | 311.753 | 50.977 | 66.107 | 44.749 | 81.898 |  | 9 | 8.2 | 12.8 | 18 | 0
| 3.0069 | 311.426 | 51.009 | 66.133 | 44.77 | 81.936 |  | 9.0208 | 8.2 | 12.8 | 18.0417 | 0
| 3.0139 | 311.653 | 51.004 | 66.141 | 44.771 | 81.934 |  | 9.0417 | 7.3 | 12.8 | 18.0833 | 0
| 3.0208 | 311.678 | 51.006 | 66.153 | 44.773 | 81.946 |  | 9.0625 | 7.4 | 12.8 | 18.125 | 0
| 3.0278 | 311.812 | 51.032 | 66.169 | 44.792 | 81.974 |  | 9.0833 | 6.9 | 12.8 | 18.1667 | 0
| 3.0347 | 312.516 | 51.076 | 66.211 | 44.83 | 82.028 |  | 9.1042 | 5.9 | 12.8 | 18.2083 | 0
| 3.0417 | 312.659 | 51.106 | 66.248 | 44.856 | 82.069 |  | 9.125 | 6 | 12.8 | 18.25 | 0
| 3.0486 | 312.218 | 51.129 | 66.279 | 44.879 | 82.112 |  | 9.1458 | 6.3 | 12.8 | 18.2917 | 0
| 3.0556 | 312.495 | 51.153 | 66.31 | 44.896 | 82.142 |  | 9.1667 | 6.1 | 12.2 | 18.3333 | 0
| 3.0625 | 312.813 | 51.181 | 66.339 | 44.913 | 82.186 |  | 9.1875 | 5.8 | 12.8 | 18.375 | 0
| 3.0694 | 312.462 | 51.201 | 66.369 | 44.936 | 82.221 |  | 9.2083 | 5.8 | 12.8 | 18.4167 | 0
| 3.0764 | 313.344 | 51.2 | 66.386 | 44.941 | 82.242 |  | 9.2292 | 5.7 | 12.8 | 18.4583 | 0
| 3.0833 | 312.954 | 51.231 | 66.417 | 44.958 | 82.277 |  | 9.25 | 5.8 | 12.8 | 18.5 | 0
| 3.0903 | 312.943 | 51.248 | 66.452 | 44.98 | 82.317 |  | 9.2708 | 5.9 | 12.8 | 18.5417 | 0
| 3.0972 | 312.308 | 51.228 | 66.442 | 44.967 | 82.303 |  | 9.2917 | 6.4 | 12.8 | 18.5833 | 0
| 3.1042 | 312.445 | 51.23 | 66.455 | 44.966 | 82.315 |  | 9.3125 | 6.6 | 12.8 | 18.625 | 0
| 3.1111 | 312.031 | 51.22 | 66.456 | 44.962 | 82.314 |  | 9.3333 | 6.6 | 12.8 | 18.6667 | 0
| 3.1181 | 312.563 | 51.21 | 66.457 | 44.955 | 82.306 |  | 9.3542 | 7.8 | 12.8 | 18.7083 | 0
| 3.125 | 311.914 | 51.197 | 66.452 | 44.946 | 82.293 |  | 9.375 | 9.3 | 12.8 | 18.75 | 0
| 3.1319 | 312.243 | 51.195 | 66.457 | 44.945 | 82.296 |  | 9.3958 | 10.1 | 12.8 | 18.7917 | 0
| 3.1389 | 312.573 | 51.201 | 66.464 | 44.953 | 82.301 |  | 9.4167 | 11.3 | 12.8 | 18.8333 | 0
| 3.1458 | 312.72 | 51.206 | 66.474 | 44.958 | 82.308 |  | 9.4375 | 12.7 | 12.8 | 18.875 | 0
| 3.1528 | 311.983 | 51.198 | 66.477 | 44.961 | 82.31 |  | 9.4583 | 14.3 | 12.8 | 18.9167 | 0
| 3.1597 | 312.651 | 51.185 | 66.466 | 44.943 | 82.289 |  | 9.4792 | 15.1 | 12.8 | 18.9583 | 0
| 3.1667 | 311.983 | 51.195 | 66.47 | 44.947 | 82.293 |  | 9.5 | 15.6 | 12.8 | 19 | 0
| 3.1736 | 311.689 | 51.182 | 66.469 | 44.946 | 82.285 |  | 9.5208 | 16.2 | 12.8 | 19.0417 | 0
| 3.1806 | 311.849 | 51.164 | 66.459 | 44.936 | 82.268 |  | 9.5417 | 16.8 | 12.8 | 19.0833 | 0
| 3.1875 | 312.04 | 51.142 | 66.44 | 44.918 | 82.234 |  | 9.5625 | 17.1 | 12.8 | 19.125 | 0
| 3.1944 | 310.276 | 51.106 | 66.412 | 44.888 | 82.192 |  | 9.5833 | 17.6 | 12.8 | 19.1667 | 0
| 3.2014 | 310.082 | 51.036 | 66.354 | 44.838 | 82.102 |  | 9.6042 | 17.6 | 12.8 | 19.2083 | 0
| 3.2083 | 309.219 | 50.961 | 66.295 | 44.781 | 82.022 |  | 9.625 | 17.6 | 12.8 | 19.25 | 0
| 3.2153 | 312.699 | 50.957 | 66.257 | 44.764 | 81.981 |  | 9.6458 | 17.4 | 12.8 | 19.2917 | 0
| 3.2222 | 312.717 | 51.042 | 66.323 | 44.846 | 82.057 |  | 9.6667 | 16.6 | 12.8 | 19.3333 | 0
| 3.2292 | 313.536 | 51.169 | 66.419 | 44.944 | 82.182 |  | 9.6875 | 15.6 | 12.8 | 19.375 | 0
| 3.2361 | 310.339 | 51.143 | 66.414 | 44.931 | 82.171 |  | 9.7083 | 13.9 | 12.8 | 19.4167 | 0
| 3.2431 | 309.9 | 51.038 | 66.328 | 44.839 | 82.061 |  | 9.7292 | 12.3 | 12.8 | 19.4583 | 0
| 3.25 | 311.024 | 51.043 | 66.324 | 44.841 | 82.056 |  | 9.75 | 11.2 | 12.8 | 19.5 | 0
| 3.2569 | 311.261 | 51.056 | 66.335 | 44.859 | 82.065 |  | 9.7708 | 10.4 | 12.8 | 19.5417 | 0
| 3.2639 | 310.889 | 51.031 | 66.316 | 44.84 | 82.031 |  | 9.7917 | 9.8 | 12.8 | 19.5833 | 0
| 3.2708 | 309.767 | 51.007 | 66.288 | 44.821 | 81.998 |  | 9.8125 | 9.3 | 12.2 | 19.625 | 0
| 3.2778 | 309.523 | 50.929 | 66.227 | 44.761 | 81.91 |  | 9.8333 | 8.4 | 12.2 | 19.6667 | 0
| 3.2847 | 308.549 | 50.877 | 66.175 | 44.727 | 81.836 |  | 9.8542 | 7.8 | 12.2 | 19.7083 | 0
| 3.2917 | 311.635 | 50.855 | 66.128 | 44.689 | 81.782 |  | 9.875 | 7.6 | 12.2 | 19.75 | 0
| 3.2986 | 310.375 | 50.904 | 66.167 | 44.742 | 81.815 |  | 9.8958 | 7.1 | 12.2 | 19.7917 | 0
| 3.3056 | 309.868 | 50.882 | 66.14 | 44.725 | 81.782 |  | 9.9167 | 6.8 | 12.2 | 19.8333 | 0
| 3.3125 | 311.413 | 50.993 | 66.214 | 44.813 | 81.883 |  | 9.9375 | 7.1 | 12.2 | 19.875 | 0
| 3.3194 | 311.545 | 51.018 | 66.238 | 44.835 | 81.919 |  | 9.9583 | 7.4 | 12.2 | 19.9167 | 0
| 3.3264 | 311.32 | 51.002 | 66.232 | 44.826 | 81.915 |  | 9.9792 | 6.7 | 12.2 | 19.9583 | 0
| 3.3333 | 310.101 | 50.985 | 66.218 | 44.806 | 81.895 |  | 10 | 6.9 | 12.2 | 20 | 0
| 3.3403 | 310.357 | 50.992 | 66.224 | 44.81 | 81.9 |  | 10.0208 | 7.3 | 12.2 | 20.0417 | 0
| 3.3472 | 310.742 | 50.989 | 66.218 | 44.81 | 81.894 |  | 10.0417 | 7.2 | 12.2 | 20.0833 | 0
| 3.3542 | 311.816 | 51.018 | 66.24 | 44.831 | 81.924 |  | 10.0625 | 6.9 | 12.2 | 20.125 | 0
| 3.3611 | 312.772 | 51.067 | 66.279 | 44.876 | 81.982 |  | 10.0833 | 5.7 | 12.2 | 20.1667 | 0
| 3.3681 | 313.447 | 51.121 | 66.327 | 44.918 | 82.04 |  | 10.1042 | 5.5 | 12.2 | 20.2083 | 0
| 3.375 | 312.488 | 51.165 | 66.375 | 44.959 | 82.102 |  | 10.125 | 5.6 | 12.2 | 20.25 | 0
| 3.3819 | 311.1 | 51.149 | 66.374 | 44.943 | 82.106 |  | 10.1458 | 4.9 | 12.2 | 20.2917 | 0
| 3.3889 | 311.02 | 51.134 | 66.374 | 44.933 | 82.1 |  | 10.1667 | 4.3 | 12.2 | 20.3333 | 0
| 3.3958 | 311.266 | 51.098 | 66.35 | 44.903 | 82.069 |  | 10.1875 | 4 | 12.2 | 20.375 | 0
| 3.4028 | 311.833 | 51.079 | 66.343 | 44.891 | 82.05 |  | 10.2083 | 3.7 | 12.2 | 20.4167 | 0
| 3.4097 | 311.565 | 51.083 | 66.345 | 44.895 | 82.054 |  | 10.2292 | 3.2 | 12.2 | 20.4583 | 0
| 3.4167 | 311.444 | 51.079 | 66.338 | 44.893 | 82.052 |  | 10.25 | 2.9 | 12.2 | 20.5 | 0
| 3.4236 | 310.995 | 51.088 | 66.347 | 44.897 | 82.054 |  | 10.2708 | 2.5 | 12.2 | 20.5417 | 0
| 3.4306 | 311.294 | 51.066 | 66.331 | 44.883 | 82.034 |  | 10.2917 | 2.8 | 12.2 | 20.5833 | 0
| 3.4375 | 311.518 | 51.047 | 66.316 | 44.871 | 82.015 |  | 10.3125 | 3.3 | 12.2 | 20.625 | 0
| 3.4444 | 310.231 | 51.028 | 66.3 | 44.857 | 81.994 |  | 10.3333 | 4.7 | 12.2 | 20.6667 | 0
| 3.4514 | 310.801 | 51.015 | 66.29 | 44.842 | 81.966 |  | 10.3542 | 5.8 | 12.2 | 20.7083 | 0
| 3.4583 | 310.921 | 50.998 | 66.266 | 44.826 | 81.942 |  | 10.375 | 6.4 | 12.2 | 20.75 | 0
| 3.4653 | 310.427 | 50.983 | 66.251 | 44.818 | 81.922 |  | 10.3958 | 7.2 | 12.2 | 20.7917 | 0
| 3.4722 | 310.55 | 50.985 | 66.251 | 44.819 | 81.907 |  | 10.4167 | 7.8 | 12.2 | 20.8333 | 0
| 3.4792 | 311.933 | 51.009 | 66.257 | 44.84 | 81.925 |  | 10.4375 | 8.2 | 12.2 | 20.875 | 0
| 3.4861 | 312.217 | 51.074 | 66.305 | 44.884 | 81.986 |  | 10.4583 | 8.8 | 12.2 | 20.9167 | 0.4
| 3.4931 | 312.351 | 51.118 | 66.345 | 44.921 | 82.045 |  | 10.4792 | 9 | 12.2 | 20.9583 | 0.6
| 3.5 | 312.178 | 51.151 | 66.372 | 44.954 | 82.089 |  | 10.5 | 9.3 | 12.2 | 21 | 0.2
| 3.5069 | 312.861 | 51.169 | 66.401 | 44.961 | 82.118 |  | 10.5208 | 9.4 | 12.2 | 21.0417 | 0
| 3.5139 | 312.057 | 51.16 | 66.398 | 44.959 | 82.124 |  | 10.5417 | 9.7 | 12.2 | 21.0833 | 0.2
| 3.5208 | 312.539 | 51.154 | 66.403 | 44.96 | 82.124 |  | 10.5625 | 9.9 | 12.2 | 21.125 | 0
| 3.5278 | 312.311 | 51.149 | 66.405 | 44.953 | 82.126 |  | 10.5833 | 9.7 | 12.2 | 21.1667 | 0
| 3.5347 | 311.408 | 51.13 | 66.394 | 44.941 | 82.112 |  | 10.6042 | 9.7 | 12.2 | 21.2083 | 0
| 3.5417 | 311.413 | 51.123 | 66.388 | 44.934 | 82.103 |  | 10.625 | 9.6 | 12.2 | 21.25 | 0
| 3.5486 | 312.018 | 51.121 | 66.393 | 44.936 | 82.107 |  | 10.6458 | 9.6 | 12.2 | 21.2917 | 0
| 3.5556 | 312.033 | 51.114 | 66.381 | 44.931 | 82.094 |  | 10.6667 | 9.4 | 12.2 | 21.3333 | 0
| 3.5625 | 310.978 | 51.091 | 66.37 | 44.911 | 82.07 |  | 10.6875 | 9.3 | 12.2 | 21.375 | 0
| 3.5694 | 310.984 | 51.042 | 66.329 | 44.875 | 82.015 |  | 10.7083 | 9.3 | 12.2 | 21.4167 | 0
| 3.5764 | 310.507 | 51.005 | 66.294 | 44.846 | 81.963 |  | 10.7292 | 9.2 | 12.2 | 21.4583 | 0
| 3.5833 | 311.103 | 50.985 | 66.269 | 44.828 | 81.933 |  | 10.75 | 9.1 | 12.2 | 21.5 | 0
| 3.5903 | 310.567 | 50.997 | 66.273 | 44.841 | 81.927 |  | 10.7708 | 9.1 | 12.2 | 21.5417 | 0
| 3.5972 | 310.893 | 51.006 | 66.275 | 44.85 | 81.932 |  | 10.7917 | 9 | 12.2 | 21.5833 | 0
| 3.6042 | 312.265 | 51.031 | 66.285 | 44.862 | 81.946 |  | 10.8125 | 8.9 | 12.2 | 21.625 | 0
| 3.6111 | 312.401 | 51.083 | 66.328 | 44.91 | 82.004 |  | 10.8333 | 8.8 | 12.2 | 21.6667 | 0
| 3.6181 | 311.087 | 51.08 | 66.328 | 44.904 | 82.002 |  | 10.8542 | 8.8 | 12.2 | 21.7083 | 0
| 3.625 | 312.038 | 51.074 | 66.323 | 44.901 | 81.999 |  | 10.875 | 8.8 | 12.2 | 21.75 | 0
| 3.6319 | 312.66 | 51.11 | 66.35 | 44.924 | 82.041 |  | 10.8958 | 8.7 | 12.2 | 21.7917 | 0
| 3.6389 | 312.399 | 51.142 | 66.378 | 44.957 | 82.077 |  | 10.9167 | 8.6 | 12.2 | 21.8333 | 0
| 3.6458 | 313.43 | 51.183 | 66.415 | 44.987 | 82.123 |  | 10.9375 | 8.6 | 12.2 | 21.875 | 0
| 3.6528 | 311.661 | 51.22 | 66.454 | 45.018 | 82.182 |  | 10.9583 | 8.5 | 12.2 | 21.9167 | 0
| 3.6597 | 313.86 | 51.247 | 66.487 | 45.032 | 82.219 |  | 10.9792 | 8.4 | 12.2 | 21.9583 | 0
| 3.6667 | 314.324 | 51.271 | 66.515 | 45.059 | 82.267 |  | 11 | 8.5 | 12.2 | 22 | 0
| 3.6736 | 309.311 | 51.102 | 66.404 | 44.927 | 82.109 |  | 11.0208 | 8.4 | 12.2 | 22.0417 | 0
| 3.6806 | 308.905 | 50.982 | 66.304 | 44.825 | 81.966 |  | 11.0417 | 8.4 | 12.2 | 22.0833 | 0
| 3.6875 | 310.034 | 50.944 | 66.261 | 44.801 | 81.906 |  | 11.0625 | 8.4 | 12.2 | 22.125 | 0
| 3.6944 | 309.301 | 50.896 | 66.207 | 44.762 | 81.829 |  | 11.0833 | 8.5 | 12.2 | 22.1667 | 0
| 3.7014 | 309.811 | 50.867 | 66.167 | 44.741 | 81.77 |  | 11.1042 | 8.5 | 12.2 | 22.2083 | 0
| 3.7083 | 309.983 | 50.869 | 66.153 | 44.743 | 81.744 |  | 11.125 | 8.5 | 12.2 | 22.25 | 0
| 3.7153 | 310.2 | 50.888 | 66.152 | 44.763 | 81.747 |  | 11.1458 | 8.5 | 12.2 | 22.2917 | 0.2
| 3.7222 | 309.809 | 50.885 | 66.142 | 44.764 | 81.736 |  | 11.1667 | 8.4 | 12.2 | 22.3333 | 0
| 3.7292 | 311.216 | 50.911 | 66.155 | 44.776 | 81.747 |  | 11.1875 | 8.4 | 12.2 | 22.375 | 0
| 3.7361 | 310.457 | 50.92 | 66.159 | 44.792 | 81.758 |  | 11.2083 | 8.4 | 12.2 | 22.4167 | 0
| 3.7431 | 309.84 | 50.923 | 66.156 | 44.793 | 81.751 |  | 11.2292 | 8.3 | 12.2 | 22.4583 | 0
| 3.75 | 308.868 | 50.887 | 66.133 | 44.768 | 81.712 |  | 11.25 | 8.3 | 12.2 | 22.5 | 0
| 3.7569 | 308.534 | 50.788 | 66.048 | 44.688 | 81.598 |  | 11.2708 | 8.3 | 12.2 | 22.5417 | 0
| 3.7639 | 308.379 | 50.818 | 66.063 | 44.716 | 81.609 |  | 11.2917 | 8.4 | 12.2 | 22.5833 | 0
| 3.7708 | 308.632 | 50.729 | 65.98 | 44.641 | 81.506 |  | 11.3125 | 8.5 | 12.2 | 22.625 | 0
| 3.7778 | 312.656 | 50.857 | 66.051 | 44.742 | 81.607 |  | 11.3333 | 8.6 | 12.2 | 22.6667 | 0
| 3.7847 | 311.816 | 50.985 | 66.153 | 44.846 | 81.742 |  | 11.3542 | 8.7 | 12.2 | 22.7083 | 0
| 3.7917 | 313.568 | 51.059 | 66.219 | 44.908 | 81.832 |  | 11.375 | 8.8 | 12.2 | 22.75 | 0
| 3.7986 | 313.329 | 51.132 | 66.288 | 44.959 | 81.926 |  | 11.3958 | 8.9 | 12.2 | 22.7917 | 0
| 3.8056 | 313.529 | 51.207 | 66.361 | 45.019 | 82.028 |  | 11.4167 | 9.1 | 12.2 | 22.8333 | 0
| 3.8125 | 310.165 | 51.164 | 66.365 | 45.001 | 82.016 |  | 11.4375 | 9.3 | 12.2 | 22.875 | 0
| 3.8194 | 310.95 | 51.088 | 66.309 | 44.931 | 81.956 |  | 11.4583 | 9.7 | 12.2 | 22.9167 | 0
| 3.8264 | 311.871 | 51.108 | 66.331 | 44.948 | 81.978 |  | 11.4792 | 9.9 | 12.2 | 22.9583 | 0
| 3.8333 | 313.08 | 51.145 | 66.365 | 44.98 | 82.022 |  | 11.5 | 10.1 | 12.2 | 23 | 0
| 3.8403 | 313.613 | 51.212 | 66.431 | 45.038 | 82.102 |  | 11.5208 | 9.9 | 12.2 | 23.0417 | 0
| 3.8472 | 313.842 | 51.268 | 66.49 | 45.083 | 82.182 |  | 11.5417 | 10.1 | 12.2 | 23.0833 | 0
| 3.8542 | 309.412 | 51.26 | 66.511 | 45.089 | 82.195 |  | 11.5625 | 10.1 | 12.2 | 23.125 | 0
| 3.8611 | 310.409 | 51.137 | 66.42 | 44.984 | 82.078 |  | 11.5833 | 10.3 | 12.2 | 23.1667 | 0
| 3.8681 | 309.771 | 51.051 | 66.362 | 44.922 | 81.986 |  | 11.6042 | 10.7 | 12.2 | 23.2083 | 0
| 3.875 | 309.573 | 50.985 | 66.302 | 44.874 | 81.9 |  | 11.625 | 10.9 | 12.2 | 23.25 | 0
| 3.8819 | 309.918 | 50.981 | 66.284 | 44.864 | 81.867 |  | 11.6458 | 11.7 | 12.2 | 23.2917 | 0
| 3.8889 | 310.809 | 51.019 | 66.306 | 44.9 | 81.892 |  | 11.6667 | 11.6 | 12.2 | 23.3333 | 0
| 3.8958 | 312.065 | 51.062 | 66.334 | 44.94 | 81.932 |  | 11.6875 | 11.4 | 12.2 | 23.375 | 0
| 3.9028 | 313.137 | 51.158 | 66.409 | 45.013 | 82.026 |  | 11.7083 | 10.4 | 12.2 | 23.4167 | 0
| 3.9097 | 311.773 | 51.18 | 66.443 | 45.037 | 82.065 |  | 11.7292 | 9.3 | 12.2 | 23.4583 | 0
| 3.9167 | 311.609 | 51.185 | 66.452 | 45.035 | 82.078 |  | 11.75 | 8.8 | 12.2 | 23.5 | 0
| 3.9236 | 309.841 | 51.041 | 66.353 | 44.929 | 81.939 |  | 11.7708 | 8.4 | 12.2 | 23.5417 | 0
| 3.9306 | 310.886 | 51.034 | 66.344 | 44.924 | 81.917 |  | 11.7917 | 8.3 | 12.2 | 23.5833 | 0
| 3.9375 | 308.855 | 50.936 | 66.263 | 44.849 | 81.803 |  | 11.8125 | 7.8 | 12.2 | 23.625 | 0
| 3.9444 | 309.189 | 50.891 | 66.218 | 44.815 | 81.73 |  | 11.8333 | 7.1 | 12.2 | 23.6667 | 0
| 3.9514 | 310.842 | 50.93 | 66.23 | 44.846 | 81.742 |  | 11.8542 | 6.9 | 12.2 | 23.7083 | 0
| 3.9583 | 309.513 | 50.928 | 66.223 | 44.853 | 81.725 |  | 11.875 | 6.8 | 12.2 | 23.75 | 0
| 3.9653 | 309.85 | 50.922 | 66.212 | 44.84 | 81.71 |  | 11.8958 | 6.8 | 12.2 | 23.7917 | 0
| 3.9722 | 310.094 | 50.955 | 66.229 | 44.869 | 81.732 |  | 11.9167 | 7.1 | 12.2 | 23.8333 | 0
| 3.9792 | 310.997 | 50.995 | 66.261 | 44.907 | 81.763 |  | 11.9375 | 7.4 | 12.2 | 23.875 | 0
| 3.9861 | 311.152 | 51.021 | 66.28 | 44.925 | 81.787 |  | 11.9583 | 7.6 | 12.2 | 23.9167 | 0
| 3.9931 | 311.701 | 51.075 | 66.324 | 44.976 | 81.846 |  | 11.9792 | 7.8 | 12.2 | 23.9583 | 0
| 4 | 312.249 | 51.122 | 66.364 | 45.001 | 81.903 |  | 12 | 8 | 12.2 | 24 | 0
| 4.0069 | 311.995 | 51.168 | 66.414 | 45.051 | 81.962 |  | 12.0208 | 8.2 | 12.2 | 24.0417 | 0
| 4.0139 | 311.922 | 51.176 | 66.435 | 45.06 | 81.992 |  | 12.0417 | 8.3 | 12.2 | 24.0833 | 0
| 4.0208 | 312.413 | 51.199 | 66.461 | 45.082 | 82.02 |  | 12.0625 | 8.3 | 12.2 | 24.125 | 0
| 4.0278 | 312.436 | 51.237 | 66.499 | 45.106 | 82.072 |  | 12.0833 | 8.3 | 12.2 | 24.1667 | 0
| 4.0347 | 312.597 | 51.281 | 66.55 | 45.146 | 82.135 |  | 12.1042 | 8.3 | 12.2 | 24.2083 | 0
| 4.0417 | 312.151 | 51.321 | 66.593 | 45.179 | 82.189 |  | 12.125 | 8.4 | 12.2 | 24.25 | 0
| 4.0486 | 312.649 | 51.337 | 66.626 | 45.194 | 82.225 |  | 12.1458 | 8.4 | 12.2 | 24.2917 | 0
| 4.0556 | 312.991 | 51.356 | 66.654 | 45.21 | 82.265 |  | 12.1667 | 8.2 | 12.2 | 24.3333 | 0
| 4.0625 | 313.669 | 51.382 | 66.689 | 45.24 | 82.31 |  | 12.1875 | 8.4 | 12.2 | 24.375 | 0
| 4.0694 | 313.727 | 51.417 | 66.736 | 45.273 | 82.361 |  | 12.2083 | 8.5 | 12.2 | 24.4167 | 0
| 4.0764 | 314.24 | 51.461 | 66.781 | 45.308 | 82.427 |  | 12.2292 | 8.4 | 12.2 | 24.4583 | 0
| 4.0833 | 309.49 | 51.49 | 66.821 | 45.331 | 82.478 |  | 12.25 | 8.4 | 12.2 | 24.5 | 0
| 4.0903 | 309.822 | 51.29 | 66.689 | 45.18 | 82.284 |  | 12.2708 | 8.4 | 12.2 | 24.5417 | 0
| 4.0972 | 309.572 | 51.206 | 66.619 | 45.108 | 82.184 |  | 12.2917 | 8.1 | 12.2 | 24.5833 | 0
| 4.1042 | 310.013 | 51.155 | 66.579 | 45.075 | 82.119 |  | 12.3125 | 8.2 | 12.2 | 24.625 | 0
| 4.1111 | 309.598 | 51.117 | 66.538 | 45.052 | 82.057 |  | 12.3333 | 8.6 | 12.2 | 24.6667 | 0
| 4.1181 | 309.22 | 51.064 | 66.487 | 45.01 | 81.978 |  | 12.3542 | 9.1 | 12.2 | 24.7083 | 0
| 4.125 | 309.183 | 51.047 | 66.455 | 44.995 | 81.931 |  | 12.375 | 9.9 | 12.2 | 24.75 | 0
| 4.1319 | 309.67 | 51.024 | 66.428 | 44.983 | 81.887 |  | 12.3958 | 11.3 | 12.2 | 24.7917 | 0
| 4.1389 | 309.523 | 51.009 | 66.402 | 44.972 | 81.851 |  | 12.4167 | 11.5 | 12.2 | 24.8333 | 0
| 4.1458 | 309.051 | 51.01 | 66.383 | 44.97 | 81.822 |  | 12.4375 | 11.8 | 12.2 | 24.875 | 0
| 4.1528 | 309.15 | 50.994 | 66.363 | 44.957 | 81.788 |  | 12.4583 | 12.1 | 12.2 | 24.9167 | 0
| 4.1597 | 308.576 | 50.983 | 66.343 | 44.95 | 81.756 |  | 12.4792 | 13.1 | 12.2 | 24.9583 | 0
| 4.1667 | 309.15 | 50.953 | 66.31 | 44.926 | 81.707 |  | 12.5 | 13.1 | 12.2 | 25 | 0
| 4.1736 | 308.852 | 50.92 | 66.276 | 44.91 | 81.66 |  | 12.5208 | 13.6 | 12.2 | 25.0417 | 0
| 4.1806 | 308.456 | 50.883 | 66.235 | 44.879 | 81.605 |  | 12.5417 | 14.4 | 12.2 | 25.0833 | 0
| 4.1875 | 308.593 | 50.869 | 66.209 | 44.864 | 81.559 |  | 12.5625 | 14.3 | 12.2 | 25.125 | 0
| 4.1944 | 310.707 | 50.826 | 66.159 | 44.832 | 81.496 |  | 12.5833 | 13.8 | 12.2 | 25.1667 | 0
| 4.2014 | 312.068 | 50.987 | 66.263 | 44.953 | 81.638 |  | 12.6042 | 13.8 | 12.2 | 25.2083 | 0
| 4.2083 | 312.146 | 51.126 | 66.376 | 45.074 | 81.792 |  | 12.625 | 13.8 | 12.2 | 25.25 | 0
| 4.2153 | 310.973 | 51.164 | 66.411 | 45.099 | 81.852 |  | 12.6458 | 13.9 | 12.2 | 25.2917 | 0
| 4.2222 | 313.615 | 51.189 | 66.444 | 45.11 | 81.894 |  | 12.6667 | 14.6 | 12.2 | 25.3333 | 0
| 4.2292 | 312.865 | 51.299 | 66.544 | 45.207 | 82.029 |  | 12.6875 | 14 | 12.2 | 25.375 | 0
| 4.2361 | 309.677 | 51.261 | 66.541 | 45.184 | 82.019 |  | 12.7083 | 12.7 | 12.2 | 25.4167 | 0
| 4.2431 | 308.225 | 51.069 | 66.41 | 45.035 | 81.837 |  | 12.7292 | 11.5 | 12.2 | 25.4583 | 0
| 4.25 | 311.483 | 51.009 | 66.341 | 44.966 | 81.747 |  | 12.75 | 10.8 | 12.2 | 25.5 | 0
| 4.2569 | 309.569 | 51.09 | 66.401 | 45.04 | 81.821 |  | 12.7708 | 10.2 | 12.2 | 25.5417 | 0
| 4.2639 | 309.743 | 51.063 | 66.382 | 45.031 | 81.791 |  | 12.7917 | 9.7 | 12.2 | 25.5833 | 0
| 4.2708 | 310.515 | 51.018 | 66.339 | 44.987 | 81.731 |  | 12.8125 | 9.5 | 12.2 | 25.625 | 0
| 4.2778 | 310.534 | 51.103 | 66.399 | 45.061 | 81.819 |  | 12.8333 | 8.7 | 12.2 | 25.6667 | 0
| 4.2847 | 309.067 | 51.1 | 66.397 | 45.058 | 81.812 |  | 12.8542 | 8.4 | 12.2 | 25.7083 | 0
| 4.2917 | 309.761 | 51.04 | 66.357 | 45.018 | 81.752 |  | 12.875 | 8.5 | 12.2 | 25.75 | 0
| 4.2986 | 307.677 | 50.989 | 66.312 | 44.967 | 81.687 |  | 12.8958 | 8 | 12.2 | 25.7917 | 0
| 4.3056 | 307.659 | 50.923 | 66.252 | 44.915 | 81.607 |  | 12.9167 | 7.5 | 12.2 | 25.8333 | 0
| 4.3125 | 310.722 | 50.984 | 66.283 | 44.968 | 81.65 |  | 12.9375 | 7.2 | 12.2 | 25.875 | 0
| 4.3194 | 310.139 | 51.039 | 66.317 | 45.01 | 81.695 |  | 12.9583 | 6.9 | 12.2 | 25.9167 | 0
| 4.3264 | 309.776 | 51.035 | 66.318 | 45.01 | 81.69 |  | 12.9792 | 7.2 | 12.2 | 25.9583 | 0
| 4.3333 | 309.348 | 51.019 | 66.301 | 44.999 | 81.676 |  | 13 | 6.9 | 12.2 | 26 | 0
| 4.3403 | 309.302 | 50.979 | 66.275 | 44.966 | 81.632 |  | 13.0208 | 6.1 | 12.2 | 26.0417 | 0
| 4.3472 | 308.481 | 50.953 | 66.246 | 44.94 | 81.596 |  | 13.0417 | 5.6 | 12.2 | 26.0833 | 0
| 4.3542 | 310.228 | 50.965 | 66.239 | 44.949 | 81.597 |  | 13.0625 | 5.5 | 12.2 | 26.125 | 0
| 4.3611 | 310.623 | 50.999 | 66.255 | 44.979 | 81.616 |  | 13.0833 | 5.3 | 12.2 | 26.1667 | 0
| 4.3681 | 311.149 | 51.039 | 66.286 | 45.018 | 81.659 |  | 13.1042 | 5.4 | 12.2 | 26.2083 | 0
| 4.375 | 309.965 | 51.073 | 66.318 | 45.041 | 81.701 |  | 13.125 | 5.4 | 12.2 | 26.25 | 0
| 4.3819 | 309.42 | 51.064 | 66.316 | 45.035 | 81.699 |  | 13.1458 | 5.4 | 12.2 | 26.2917 | 0
| 4.3889 | 310.18 | 51.058 | 66.317 | 45.031 | 81.692 |  | 13.1667 | 5.2 | 12.2 | 26.3333 | 0
| 4.3958 | 310.487 | 51.071 | 66.323 | 45.039 | 81.706 |  | 13.1875 | 5.4 | 12.2 | 26.375 | 0
| 4.4028 | 309.581 | 51.069 | 66.327 | 45.042 | 81.712 |  | 13.2083 | 6.2 | 12.2 | 26.4167 | 0
| 4.4097 | 309.812 | 51.058 | 66.323 | 45.039 | 81.707 |  | 13.2292 | 7.9 | 12.2 | 26.4583 | 0
| 4.4167 | 311.879 | 51.103 | 66.35 | 45.063 | 81.745 |  | 13.25 | 9.3 | 12.2 | 26.5 | 0
| 4.4236 | 309.65 | 51.136 | 66.389 | 45.1 | 81.788 |  | 13.2708 | 9.6 | 12.2 | 26.5417 | 0
| 4.4306 | 308.737 | 51.067 | 66.337 | 45.044 | 81.73 |  | 13.2917 | 9.8 | 12.2 | 26.5833 | 0
| 4.4375 | 308.813 | 51.031 | 66.302 | 45.008 | 81.678 |  | 13.3125 | 9.8 | 12.2 | 26.625 | 0
| 4.4444 | 309.386 | 51.026 | 66.29 | 45.002 | 81.662 |  | 13.3333 | 9.9 | 12.2 | 26.6667 | 0
| 4.4514 | 309.524 | 51.038 | 66.304 | 45.02 | 81.68 |  | 13.3542 | 10 | 12.2 | 26.7083 | 0
| 4.4583 | 310.484 | 51.021 | 66.284 | 45.001 | 81.655 |  | 13.375 | 10.2 | 12.2 | 26.75 | 0
| 4.4653 | 308.667 | 51.012 | 66.273 | 44.994 | 81.635 |  | 13.3958 | 10.4 | 12.2 | 26.7917 | 0
| 4.4722 | 309.259 | 50.976 | 66.24 | 44.972 | 81.597 |  | 13.4167 | 11.2 | 12.2 | 26.8333 | 0
| 4.4792 | 310.221 | 50.984 | 66.24 | 44.975 | 81.6 |  | 13.4375 | 12 | 12.2 | 26.875 | 0
| 4.4861 | 311.531 | 51.04 | 66.279 | 45.026 | 81.649 |  | 13.4583 | 12.6 | 12.2 | 26.9167 | 0
| 4.4931 | 308.257 | 50.96 | 66.219 | 44.957 | 81.56 |  | 13.4792 | 13.2 | 12.2 | 26.9583 | 0
| 4.5 | 311.241 | 51.012 | 66.243 | 44.996 | 81.608 |  | 13.5 | 14.2 | 12.2 | 27 | 0
| 4.5069 | 311.65 | 51.117 | 66.326 | 45.079 | 81.714 |  | 13.5208 | 14.4 | 12.2 | 27.0417 | 0
| 4.5139 | 312.218 | 51.189 | 66.386 | 45.137 | 81.798 |  | 13.5417 | 14.6 | 12.2 | 27.0833 | 0
| 4.5208 | 311.4 | 51.213 | 66.417 | 45.156 | 81.85 |  | 13.5625 | 14.8 | 12.2 | 27.125 | 0
| 4.5278 | 311.288 | 51.235 | 66.442 | 45.168 | 81.886 |  | 13.5833 | 14.4 | 12.2 | 27.1667 | 0
| 4.5347 | 311.159 | 51.225 | 66.448 | 45.165 | 81.893 |  | 13.6042 | 14.1 | 12.2 | 27.2083 | 0
| 4.5417 | 311.628 | 51.214 | 66.453 | 45.158 | 81.901 |  | 13.625 | 13.4 | 12.2 | 27.25 | 0
| 4.5486 | 311.8 | 51.255 | 66.483 | 45.188 | 81.946 |  | 13.6458 | 12.4 | 12.2 | 27.2917 | 0
| 4.5556 | 312.203 | 51.295 | 66.526 | 45.216 | 82.001 |  | 13.6667 | 11.7 | 12.2 | 27.3333 | 0
| 4.5625 | 312.372 | 51.329 | 66.562 | 45.249 | 82.049 |  | 13.6875 | 10.9 | 12.2 | 27.375 | 0
| 4.5694 | 312.107 | 51.357 | 66.603 | 45.28 | 82.105 |  | 13.7083 | 10.2 | 12.2 | 27.4167 | 0
| 4.5764 | 311.747 | 51.355 | 66.613 | 45.276 | 82.119 |  | 13.7292 | 9.6 | 12.2 | 27.4583 | 0
| 4.5833 | 311.307 | 51.324 | 66.602 | 45.247 | 82.099 |  | 13.75 | 8.9 | 12.2 | 27.5 | 0
| 4.5903 | 310.272 | 51.379 | 66.64 | 45.28 | 82.155 |  | 13.7708 | 8.9 | 12.2 | 27.5417 | 0
| 4.5972 | 310.227 | 51.272 | 66.576 | 45.214 | 82.064 |  | 13.7917 | 8.2 | 12.2 | 27.5833 | 0
| 4.6042 | 311.029 | 51.256 | 66.56 | 45.195 | 82.045 |  | 13.8125 | 7.6 | 12.2 | 27.625 | 0
| 4.6111 | 310.811 | 51.254 | 66.566 | 45.199 | 82.04 |  | 13.8333 | 6.9 | 12.2 | 27.6667 | 0
| 4.6181 | 311.143 | 51.262 | 66.568 | 45.202 | 82.05 |  | 13.8542 | 6.5 | 12.2 | 27.7083 | 0
| 4.625 | 311.13 | 51.272 | 66.576 | 45.206 | 82.054 |  | 13.875 | 5.9 | 12.2 | 27.75 | 0
| 4.6319 | 310.396 | 51.268 | 66.576 | 45.212 | 82.053 |  | 13.8958 | 5.4 | 12.2 | 27.7917 | 0
| 4.6389 | 310.738 | 51.239 | 66.556 | 45.187 | 82.024 |  | 13.9167 | 5.2 | 12.2 | 27.8333 | 0.6
| 4.6458 | 311.797 | 51.265 | 66.57 | 45.207 | 82.049 |  | 13.9375 | 5.1 | 12.2 | 27.875 | 0
| 4.6528 | 311.714 | 51.288 | 66.596 | 45.226 | 82.074 |  | 13.9583 | 5.4 | 12.2 | 27.9167 | 0
| 4.6597 | 312.465 | 51.324 | 66.618 | 45.254 | 82.111 |  | 13.9792 | 5.2 | 12.2 | 27.9583 | 0
| 4.6667 | 312.474 | 51.344 | 66.641 | 45.273 | 82.141 |  | 14 | 5 | 12.2 | 28 | 0
| 4.6736 | 311.804 | 51.37 | 66.665 | 45.288 | 82.177 |  | 14.0208 | 5 | 12.2 | 28.0417 | 0
| 4.6806 | 311.782 | 51.377 | 66.683 | 45.297 | 82.199 |  | 14.0417 | 4.7 | 12.2 | 28.0833 | 0
| 4.6875 | 312.971 | 51.415 | 66.715 | 45.321 | 82.243 |  | 14.0625 | 5.3 | 12.2 | 28.125 | 0
| 4.6944 | 313.844 | 51.466 | 66.768 | 45.368 | 82.31 |  | 14.0833 | 5.4 | 12.2 | 28.1667 | 0
| 4.7014 | 309.404 | 51.402 | 66.741 | 45.325 | 82.267 |  | 14.1042 | 5.7 | 12.2 | 28.2083 | 0
| 4.7083 | 308.35 | 51.261 | 66.631 | 45.21 | 82.126 |  | 14.125 | 5.9 | 12.2 | 28.25 | 0
| 4.7153 | 309.192 | 51.171 | 66.554 | 45.137 | 82.017 |  | 14.1458 | 6.6 | 12.2 | 28.2917 | 0
| 4.7222 | 309.13 | 51.101 | 66.489 | 45.085 | 81.919 |  | 14.1667 | 6.9 | 12.2 | 28.3333 | 0
| 4.7292 | 308.738 | 51.078 | 66.453 | 45.066 | 81.867 |  | 14.1875 | 7.1 | 12.2 | 28.375 | 0
| 4.7361 | 308.318 | 51.04 | 66.411 | 45.045 | 81.807 |  | 14.2083 | 7.4 | 12.2 | 28.4167 | 0
| 4.7431 | 308.3 | 50.996 | 66.354 | 45.003 | 81.729 |  | 14.2292 | 7.6 | 12.2 | 28.4583 | 0
| 4.75 | 307.597 | 50.926 | 66.286 | 44.956 | 81.632 |  | 14.25 | 7.8 | 12.2 | 28.5 | 0
| 4.7569 | 309.195 | 51.008 | 66.324 | 45.021 | 81.69 |  | 14.2708 | 7.9 | 12.2 | 28.5417 | 0
| 4.7639 | 311.168 | 50.983 | 66.285 | 44.985 | 81.64 |  | 14.2917 | 8.1 | 12.2 | 28.5833 | 0
| 4.7708 | 311.14 | 51.081 | 66.36 | 45.071 | 81.737 |  | 14.3125 | 8.3 | 12.2 | 28.625 | 0
| 4.7778 | 310.915 | 51.158 | 66.412 | 45.131 | 81.815 |  | 14.3333 | 8.4 | 12.2 | 28.6667 | 0
| 4.7847 | 312.591 | 51.227 | 66.473 | 45.193 | 81.899 |  | 14.3542 | 8.7 | 12.2 | 28.7083 | 0
| 4.7917 | 312.262 | 51.294 | 66.537 | 45.253 | 81.982 |  | 14.375 | 9.2 | 12.2 | 28.75 | 0
| 4.7986 | 312.663 | 51.357 | 66.592 | 45.293 | 82.069 |  | 14.3958 | 9.5 | 12.2 | 28.7917 | 0
| 4.8056 | 312.724 | 51.384 | 66.64 | 45.322 | 82.126 |  | 14.4167 | 9.9 | 12.2 | 28.8333 | 0
| 4.8125 | 313.824 | 51.448 | 66.697 | 45.366 | 82.21 |  | 14.4375 | 10.4 | 12.2 | 28.875 | 0
| 4.8194 | 311.3 | 51.397 | 66.687 | 45.334 | 82.192 |  | 14.4583 | 10.8 | 12.2 | 28.9167 | 0
| 4.8264 | 309.287 | 51.291 | 66.62 | 45.253 | 82.096 |  | 14.4792 | 11.2 | 12.2 | 28.9583 | 0
| 4.8333 | 309.426 | 51.21 | 66.556 | 45.186 | 82.002 |  | 14.5 | 11.8 | 12.2 | 29 | 0.2
| 4.8403 | 309.397 | 51.162 | 66.508 | 45.142 | 81.943 |  | 14.5208 | 12.3 | 12.2 | 29.0417 | 0
| 4.8472 | 310.447 | 51.147 | 66.487 | 45.139 | 81.904 |  | 14.5417 | 12.7 | 12.2 | 29.0833 | 0
| 4.8542 | 310.291 | 51.161 | 66.497 | 45.161 | 81.909 |  | 14.5625 | 12.9 | 12.2 | 29.125 | 0
| 4.8611 | 310.014 | 51.18 | 66.505 | 45.172 | 81.915 |  | 14.5833 | 12.7 | 12.2 | 29.1667 | 0
| 4.8681 | 310.332 | 51.178 | 66.502 | 45.175 | 81.909 |  | 14.6042 | 13 | 12.2 | 29.2083 | 0.4
| 4.875 | 310.666 | 51.196 | 66.505 | 45.182 | 81.919 |  | 14.625 | 13.1 | 12.2 | 29.25 | 0
| 4.8819 | 310.844 | 51.242 | 66.548 | 45.223 | 81.964 |  | 14.6458 | 12.8 | 12.2 | 29.2917 | 0
| 4.8889 | 312.443 | 51.311 | 66.599 | 45.279 | 82.041 |  | 14.6667 | 12.8 | 12.2 | 29.3333 | 0
| 4.8958 | 312.3 | 51.363 | 66.647 | 45.32 | 82.109 |  | 14.6875 | 11.5 | 12.2 | 29.375 | 0
| 4.9028 | 314.182 | 51.464 | 66.736 | 45.407 | 82.229 |  | 14.7083 | 10.1 | 12.2 | 29.4167 | 0
| 4.9097 | 307.814 | 51.347 | 66.685 | 45.328 | 82.14 |  | 14.7292 | 8.8 | 12.2 | 29.4583 | 0
| 4.9167 | 308.134 | 51.194 | 66.561 | 45.192 | 81.978 |  | 14.75 | 7.7 | 12.2 | 29.5 | 0
| 4.9236 | 308.659 | 51.139 | 66.511 | 45.153 | 81.907 |  | 14.7708 | 7.1 | 12.2 | 29.5417 | 0
| 4.9306 | 309.296 | 51.136 | 66.494 | 45.154 | 81.881 |  | 14.7917 | 6.5 | 12.2 | 29.5833 | 0
| 4.9375 | 310.357 | 51.158 | 66.504 | 45.173 | 81.885 |  | 14.8125 | 6 | 12.2 | 29.625 | 0
| 4.9444 | 311.024 | 51.206 | 66.532 | 45.216 | 81.918 |  | 14.8333 | 5.4 | 12.2 | 29.6667 | 0
| 4.9514 | 311.314 | 51.299 | 66.603 | 45.29 | 82.015 |  | 14.8542 | 5.1 | 12.2 | 29.7083 | 0
| 4.9583 | 312.318 | 51.341 | 66.645 | 45.325 | 82.079 |  | 14.875 | 4.7 | 12.2 | 29.75 | 0
| 4.9653 | 312.1 | 51.408 | 66.706 | 45.373 | 82.149 |  | 14.8958 | 4.2 | 12.2 | 29.7917 | 0
| 4.9722 | 312.955 | 51.47 | 66.77 | 45.428 | 82.238 |  | 14.9167 | 3.7 | 12.2 | 29.8333 | 0
| 4.9792 | 313.173 | 51.513 | 66.82 | 45.468 | 82.308 |  | 14.9375 | 3.3 | 12.2 | 29.875 | 0
| 4.9861 | 312.653 | 51.557 | 66.873 | 45.504 | 82.375 |  | 14.9583 | 2.8 | 12.2 | 29.9167 | 0
| 4.9931 | 312.97 | 51.577 | 66.914 | 45.52 | 82.422 |  | 14.9792 | 2.4 | 12.2 | 29.9583 | 0
| 5 | 314.011 | 51.623 | 66.961 | 45.556 | 82.492 |  | 15 | 2.3 | 12.2 | 30 | 0
| 5.0069 | 313.645 | 51.663 | 67.01 | 45.591 | 82.557 |  | 15.0208 | 1.8 | 12.2 | 30.0417 | 0
| 5.0139 | 313.29 | 51.656 | 67.033 | 45.592 | 82.581 |  | 15.0417 | 1.9 | 12.2 | 30.0833 | 0
| 5.0208 | 313.724 | 51.682 | 67.067 | 45.608 | 82.621 |  | 15.0625 | 1.7 | 12.2 | 30.125 | 0
| 5.0278 | 314.101 | 51.709 | 67.102 | 45.636 | 82.667 |  | 15.0833 | 0.7 | 12.2 | 30.1667 | 0
| 5.0347 | 313.769 | 51.745 | 67.149 | 45.658 | 82.72 |  | 15.1042 | 0.7 | 12.2 | 30.2083 | 0
| 5.0417 | 313.461 | 51.774 | 67.192 | 45.692 | 82.776 |  | 15.125 | 0.7 | 12.2 | 30.25 | 0
| 5.0486 | 309.978 | 51.614 | 67.099 | 45.578 | 82.638 |  | 15.1458 | 0.2 | 12.2 | 30.2917 | 0
| 5.0556 | 309.639 | 51.501 | 67.006 | 45.476 | 82.513 |  | 15.1667 | 0 | 12.2 | 30.3333 | 0
| 5.0625 | 310.843 | 51.462 | 66.962 | 45.448 | 82.442 |  | 15.1875 | -0.4 | 12.2 | 30.375 | 0
| 5.0694 | 310.653 | 51.433 | 66.934 | 45.432 | 82.397 |  | 15.2083 | -0.4 | 12.2 | 30.4167 | 0
| 5.0764 | 310.129 | 51.428 | 66.92 | 45.431 | 82.371 |  | 15.2292 | -0.1 | 12.2 | 30.4583 | 0
| 5.0833 | 310.728 | 51.433 | 66.916 | 45.437 | 82.362 |  | 15.25 | 0.7 | 12.2 | 30.5 | 0
| 5.0903 | 311.051 | 51.424 | 66.909 | 45.439 | 82.342 |  | 15.2708 | 1.2 | 12.2 | 30.5417 | 0
| 5.0972 | 310.637 | 51.418 | 66.9 | 45.43 | 82.323 |  | 15.2917 | 1.5 | 12.2 | 30.5833 | 0
| 5.1042 | 310.756 | 51.413 | 66.89 | 45.432 | 82.311 |  | 15.3125 | 1.9 | 12.2 | 30.625 | 0
| 5.1111 | 310.702 | 51.414 | 66.883 | 45.423 | 82.294 |  | 15.3333 | 2.6 | 12.2 | 30.6667 | 0
| 5.1181 | 310.107 | 51.41 | 66.871 | 45.421 | 82.283 |  | 15.3542 | 3.1 | 12.2 | 30.7083 | 0
| 5.125 | 310.957 | 51.405 | 66.873 | 45.421 | 82.276 |  | 15.375 | 3.5 | 12.2 | 30.75 | 0
| 5.1319 | 310.612 | 51.419 | 66.874 | 45.433 | 82.279 |  | 15.3958 | 4.1 | 12.2 | 30.7917 | 0
| 5.1389 | 311.164 | 51.41 | 66.867 | 45.432 | 82.271 |  | 15.4167 | 4.7 | 12.2 | 30.8333 | 0
| 5.1458 | 310.483 | 51.421 | 66.871 | 45.435 | 82.276 |  | 15.4375 | 5.1 | 12.2 | 30.875 | 0
| 5.1528 | 309.859 | 51.412 | 66.866 | 45.433 | 82.263 |  | 15.4583 | 5.4 | 12.2 | 30.9167 | 0
| 5.1597 | 309.928 | 51.363 | 66.826 | 45.391 | 82.204 |  | 15.4792 | 5.4 | 12.2 | 30.9583 | 0
| 5.1667 | 309.474 | 51.338 | 66.799 | 45.373 | 82.169 |  | 15.5 | 5.6 | 12.2 | 31 | 0
| 5.1736 | 308.893 | 51.311 | 66.77 | 45.355 | 82.131 |  | 15.5208 | 5.8 | 12.2 | 31.0417 | 0
| 5.1806 | 309.17 | 51.286 | 66.746 | 45.332 | 82.092 |  | 15.5417 | 5.8 | 12.2 | 31.0833 | 0
| 5.1875 | 308.852 | 51.261 | 66.715 | 45.313 | 82.055 |  | 15.5625 | 5.8 | 12.2 | 31.125 | 0
| 5.1944 | 307.714 | 51.197 | 66.657 | 45.269 | 81.966 |  | 15.5833 | 5.8 | 12.2 | 31.1667 | 0
| 5.2014 | 312.124 | 51.332 | 66.741 | 45.369 | 82.091 |  | 15.6042 | 5.9 | 12.2 | 31.2083 | 0.8
| 5.2083 | 310.23 | 51.368 | 66.773 | 45.408 | 82.13 |  | 15.625 | 5.9 | 12.2 | 31.25 | 2.2
| 5.2153 | 309.997 | 51.34 | 66.744 | 45.375 | 82.095 |  | 15.6458 | 5.8 | 12.2 | 31.2917 | 0.6
| 5.2222 | 308.575 | 51.282 | 66.702 | 45.333 | 82.041 |  | 15.6667 | 5.8 | 12.2 | 31.3333 | 0
| 5.2292 | 307.385 | 51.208 | 66.637 | 45.277 | 81.953 |  | 15.6875 | 5.7 | 12.2 | 31.375 | 0
| 5.2361 | 312.131 | 51.45 | 66.809 | 45.465 | 82.192 |  | 15.7083 | 5.8 | 12.2 | 31.4167 | 0
| 5.2431 | 311.353 | 51.448 | 66.821 | 45.467 | 82.207 |  | 15.7292 | 5.7 | 12.2 | 31.4583 | 0.2
| 5.25 | 313.931 | 51.529 | 66.886 | 45.525 | 82.299 |  | 15.75 | 5.6 | 12.2 | 31.5 | 0
| 5.2569 | 312.521 | 51.605 | 66.961 | 45.588 | 82.404 |  | 15.7708 | 5.4 | 12.2 | 31.5417 | 0
| 5.2639 | 311.744 | 51.621 | 66.993 | 45.6 | 82.441 |  | 15.7917 | 5.4 | 12.2 | 31.5833 | 0
| 5.2708 | 312.086 | 51.625 | 67.008 | 45.603 | 82.477 |  | 15.8125 | 5.4 | 12.2 | 31.625 | 0.4
| 5.2778 | 311.815 | 51.634 | 67.027 | 45.609 | 82.502 |  | 15.8333 | 5.3 | 12.2 | 31.6667 | 0
| 5.2847 | 310.415 | 51.595 | 67.011 | 45.58 | 82.479 |  | 15.8542 | 5.2 | 12.2 | 31.7083 | 0.2
| 5.2917 | 310.764 | 51.54 | 66.98 | 45.537 | 82.434 |  | 15.875 | 5.1 | 12.2 | 31.75 | 0
| 5.2986 | 310.265 | 51.513 | 66.956 | 45.511 | 82.404 |  | 15.8958 | 4.8 | 12.2 | 31.7917 | 0
| 5.3056 | 312.47 | 51.538 | 66.968 | 45.532 | 82.426 |  | 15.9167 | 4.5 | 12.2 | 31.8333 | 0
| 5.3125 | 311.914 | 51.593 | 67.012 | 45.581 | 82.479 |  | 15.9375 | 4.4 | 12.2 | 31.875 | 0
| 5.3194 | 311.745 | 51.614 | 67.038 | 45.598 | 82.516 |  | 15.9583 | 3.9 | 12.2 | 31.9167 | 0
| 5.3264 | 311.268 | 51.569 | 67.008 | 45.557 | 82.475 |  | 15.9792 | 3.6 | 12.2 | 31.9583 | 0.2
| 5.3333 | 311.734 | 51.577 | 67.018 | 45.564 | 82.491 |  | 16 | 3.3 | 12.2 | 32 | 0
| 5.3403 | 311.137 | 51.583 | 67.025 | 45.569 | 82.495 |  | 16.0208 | 3.1 | 11.7 | 32.0417 | 0
| 5.3472 | 311.412 | 51.582 | 67.025 | 45.564 | 82.499 |  | 16.0417 | 2.8 | 11.7 | 32.0833 | 0
| 5.3542 | 311.641 | 51.595 | 67.039 | 45.577 | 82.519 |  | 16.0625 | 2.7 | 11.7 | 32.125 | 0
| 5.3611 | 312.474 | 51.623 | 67.055 | 45.603 | 82.553 |  | 16.0833 | 2.5 | 11.7 | 32.1667 | 0
| 5.3681 | 312.127 | 51.684 | 67.115 | 45.651 | 82.628 |  | 16.1042 | 2.5 | 11.7 | 32.2083 | 0
| 5.375 | 311.235 | 51.614 | 67.071 | 45.602 | 82.565 |  | 16.125 | 2.6 | 11.7 | 32.25 | 0
| 5.3819 | 309.939 | 51.548 | 67.026 | 45.54 | 82.502 |  | 16.1458 | 2.6 | 11.7 | 32.2917 | 0
| 5.3889 | 308.059 | 51.485 | 66.964 | 45.492 | 82.427 |  | 16.1667 | 2.6 | 11.7 | 32.3333 | 0
| 5.3958 | 308.899 | 51.428 | 66.913 | 45.442 | 82.352 |  | 16.1875 | 2.4 | 11.7 | 32.375 | 0
| 5.4028 | 309.408 | 51.376 | 66.859 | 45.408 | 82.287 |  | 16.2083 | 2.2 | 11.7 | 32.4167 | 0
| 5.4097 | 309.16 | 51.36 | 66.83 | 45.391 | 82.241 |  | 16.2292 | 1.8 | 11.7 | 32.4583 | 0
| 5.4167 | 309.85 | 51.372 | 66.831 | 45.404 | 82.243 |  | 16.25 | 1.1 | 11.7 | 32.5 | 0
| 5.4236 | 309.736 | 51.358 | 66.804 | 45.39 | 82.208 |  | 16.2708 | 0.6 | 11.7 | 32.5417 | 0
| 5.4306 | 309.142 | 51.323 | 66.766 | 45.361 | 82.163 |  | 16.2917 | 0.9 | 11.7 | 32.5833 | 0
| 5.4375 | 308.577 | 51.291 | 66.729 | 45.333 | 82.116 |  | 16.3125 | 1.1 | 11.7 | 32.625 | 0
| 5.4444 | 308.284 | 51.238 | 66.677 | 45.292 | 82.049 |  | 16.3333 | 1.4 | 11.7 | 32.6667 | 0
| 5.4514 | 308.331 | 51.213 | 66.639 | 45.273 | 81.995 |  | 16.3542 | 2.1 | 11.7 | 32.7083 | 0
| 5.4583 | 309.105 | 51.188 | 66.604 | 45.251 | 81.957 |  | 16.375 | 2.3 | 11.7 | 32.75 | 0
| 5.4653 | 307.838 | 51.178 | 66.576 | 45.234 | 81.92 |  | 16.3958 | 2.6 | 11.7 | 32.7917 | 0
| 5.4722 | 308.436 | 51.148 | 66.538 | 45.212 | 81.869 |  | 16.4167 | 2.8 | 11.7 | 32.8333 | 0
| 5.4792 | 309.459 | 51.15 | 66.516 | 45.214 | 81.85 |  | 16.4375 | 2.9 | 11.7 | 32.875 | 0
| 5.4861 | 310.128 | 51.185 | 66.53 | 45.236 | 81.876 |  | 16.4583 | 3.3 | 11.7 | 32.9167 | 0
| 5.4931 | 310.479 | 51.245 | 66.568 | 45.288 | 81.93 |  | 16.4792 | 3.5 | 11.7 | 32.9583 | 0
| 5.5 | 309.675 | 51.248 | 66.568 | 45.288 | 81.939 |  | 16.5 | 3.6 | 11.7 | 33 | 0
| 5.5069 | 310.404 | 51.259 | 66.575 | 45.294 | 81.954 |  | 16.5208 | 3.8 | 11.7 | 33.0417 | 0
| 5.5139 | 309.355 | 51.265 | 66.579 | 45.298 | 81.959 |  | 16.5417 | 4.2 | 11.7 | 33.0833 | 0
| 5.5208 | 309.957 | 51.251 | 66.567 | 45.286 | 81.95 |  | 16.5625 | 4 | 11.7 | 33.125 | 0
| 5.5278 | 308.84 | 51.239 | 66.549 | 45.274 | 81.942 |  | 16.5833 | 4.1 | 11.7 | 33.1667 | 0
| 5.5347 | 309.022 | 51.212 | 66.529 | 45.244 | 81.909 |  | 16.6042 | 4.1 | 11.7 | 33.2083 | 0
| 5.5417 | 313.196 | 51.255 | 66.543 | 45.272 | 81.944 |  | 16.625 | 4.1 | 11.7 | 33.25 | 0
| 5.5486 | 313.412 | 51.436 | 66.691 | 45.425 | 82.145 |  | 16.6458 | 4.1 | 11.7 | 33.2917 | 0
| 5.5556 | 313.582 | 51.549 | 66.788 | 45.511 | 82.278 |  | 16.6667 | 4.2 | 11.7 | 33.3333 | 0.2
| 5.5625 | 312.807 | 51.606 | 66.846 | 45.556 | 82.377 |  | 16.6875 | 4.2 | 11.7 | 33.375 | 0
| 5.5694 | 313.763 | 51.674 | 66.922 | 45.606 | 82.481 |  | 16.7083 | 4.3 | 11.7 | 33.4167 | 0.4
| 5.5764 | 313.371 | 51.7 | 66.97 | 45.63 | 82.553 |  | 16.7292 | 4.2 | 11.7 | 33.4583 | 0
| 5.5833 | 313.747 | 51.715 | 67.005 | 45.628 | 82.603 |  | 16.75 | 4.3 | 11.7 | 33.5 | 0
| 5.5903 | 313.319 | 51.738 | 67.043 | 45.656 | 82.662 |  | 16.7708 | 4.2 | 11.7 | 33.5417 | 0
| 5.5972 | 313.276 | 51.737 | 67.061 | 45.653 | 82.689 |  | 16.7917 | 4.2 | 11.7 | 33.5833 | 0
| 5.6042 | 313.897 | 51.767 | 67.098 | 45.673 | 82.741 |  | 16.8125 | 4.2 | 11.7 | 33.625 | 0
| 5.6111 | 312.442 | 51.73 | 67.091 | 45.655 | 82.735 |  | 16.8333 | 4.3 | 11.7 | 33.6667 | 0.2
| 5.6181 | 312.656 | 51.726 | 67.098 | 45.64 | 82.748 |  | 16.8542 | 4.3 | 11.7 | 33.7083 | 0
| 5.625 | 313.179 | 51.712 | 67.094 | 45.632 | 82.744 |  | 16.875 | 4.2 | 11.7 | 33.75 | 0.2
| 5.6319 | 312.525 | 51.696 | 67.093 | 45.62 | 82.739 |  | 16.8958 | 4.2 | 11.7 | 33.7917 | 0.2
| 5.6389 | 312.994 | 51.714 | 67.108 | 45.629 | 82.763 |  | 16.9167 | 4.2 | 11.7 | 33.8333 | 0
| 5.6458 | 313.236 | 51.743 | 67.139 | 45.658 | 82.803 |  | 16.9375 | 4 | 11.7 | 33.875 | 0
| 5.6528 | 313.773 | 51.762 | 67.16 | 45.674 | 82.831 |  | 16.9583 | 3.9 | 11.7 | 33.9167 | 0
| 5.6597 | 313.731 | 51.777 | 67.187 | 45.683 | 82.862 |  | 16.9792 | 3.9 | 11.7 | 33.9583 | 4.4
| 5.6667 | 314.224 | 51.808 | 67.216 | 45.711 | 82.917 |  | 17 | 3.3 | 11.7 | 34 | 2.6
| 5.6736 | 314.305 | 51.821 | 67.239 | 45.719 | 82.946 |  | 17.0208 | 3.2 | 11.7 | 34.0417 | 1.2
| 5.6806 | 312.203 | 51.817 | 67.256 | 45.724 | 82.96 |  | 17.0417 | 3 | 11.7 | 34.0833 | 1.6
| 5.6875 | 313.272 | 51.763 | 67.215 | 45.669 | 82.912 |  | 17.0625 | 3.1 | 11.7 | 34.125 | 1
| 5.6944 | 313.689 | 51.76 | 67.213 | 45.667 | 82.91 |  | 17.0833 | 3.2 | 11.7 | 34.1667 | 1.2
| 5.7014 | 312.582 | 51.767 | 67.222 | 45.675 | 82.917 |  | 17.1042 | 3.3 | 11.7 | 34.2083 | 0.6
| 5.7083 | 312.985 | 51.758 | 67.221 | 45.668 | 82.919 |  | 17.125 | 3.1 | 11.7 | 34.25 | 0.4
| 5.7153 | 312.718 | 51.755 | 67.218 | 45.662 | 82.919 |  | 17.1458 | 2.8 | 11.7 | 34.2917 | 0.6
| 5.7222 | 313.016 | 51.752 | 67.223 | 45.663 | 82.917 |  | 17.1667 | 2.6 | 11.7 | 34.3333 | 0.8
| 5.7292 | 312.828 | 51.763 | 67.231 | 45.674 | 82.935 |  | 17.1875 | 2.5 | 11.7 | 34.375 | 0.4
| 5.7361 | 311.759 | 51.736 | 67.218 | 45.653 | 82.907 |  | 17.2083 | 2.5 | 11.7 | 34.4167 | 0.4
| 5.7431 | 312.685 | 51.72 | 67.203 | 45.641 | 82.904 |  | 17.2292 | 2.6 | 11.7 | 34.4583 | 0.6
| 5.75 | 311.624 | 51.696 | 67.181 | 45.617 | 82.863 |  | 17.25 | 2.5 | 11.7 | 34.5 | 0.6
| 5.7569 | 309.267 | 51.669 | 67.165 | 45.602 | 82.836 |  | 17.2708 | 2.2 | 11.7 | 34.5417 | 0.6
| 5.7639 | 311.777 | 51.634 | 67.129 | 45.563 | 82.793 |  | 17.2917 | 1.9 | 11.7 | 34.5833 | 0.6
| 5.7708 | 312.08 | 51.661 | 67.143 | 45.592 | 82.811 |  | 17.3125 | 1.7 | 11.7 | 34.625 | 0.8
| 5.7778 | 312.876 | 51.697 | 67.169 | 45.62 | 82.852 |  | 17.3333 | 1.6 | 11.7 | 34.6667 | 0.6
| 5.7847 | 313.71 | 51.729 | 67.194 | 45.645 | 82.887 |  | 17.3542 | 1.6 | 11.7 | 34.7083 | 0.6
| 5.7917 | 313.57 | 51.775 | 67.235 | 45.684 | 82.938 |  | 17.375 | 1.7 | 11.7 | 34.75 | 0.2
| 5.7986 | 314.04 | 51.818 | 67.27 | 45.715 | 82.993 |  | 17.3958 | 1.9 | 11.7 | 34.7917 | 0
| 5.8056 | 311.828 | 51.673 | 67.168 | 45.597 | 82.852 |  | 17.4167 | 2.1 | 11.7 | 34.8333 | 0
| 5.8125 | 311.339 | 51.616 | 67.121 | 45.55 | 82.784 |  | 17.4375 | 2.8 | 11.7 | 34.875 | 0
| 5.8194 | 311.594 | 51.588 | 67.101 | 45.538 | 82.749 |  | 17.4583 | 3.3 | 11.7 | 34.9167 | 0
| 5.8264 | 311.493 | 51.566 | 67.07 | 45.519 | 82.714 |  | 17.4792 | 3.5 | 11.7 | 34.9583 | 0.2
| 5.8333 | 311.155 | 51.547 | 67.047 | 45.507 | 82.68 |  | 17.5 | 3.9 | 11.7 | 35 | 0
| 5.8403 | 311.136 | 51.546 | 67.037 | 45.506 | 82.666 |  | 17.5208 | 4.1 | 11.7 | 35.0417 | 0
| 5.8472 | 311.949 | 51.548 | 67.029 | 45.508 | 82.658 |  | 17.5417 | 4.4 | 11.7 | 35.0833 | 0
| 5.8542 | 312.81 | 51.592 | 67.053 | 45.533 | 82.694 |  | 17.5625 | 4.9 | 11.7 | 35.125 | 0
| 5.8611 | 313.699 | 51.661 | 67.106 | 45.596 | 82.763 |  | 17.5833 | 5.2 | 11.7 | 35.1667 | 0
| 5.8681 | 314.397 | 51.733 | 67.169 | 45.648 | 82.853 |  | 17.6042 | 5.2 | 11.7 | 35.2083 | 0
| 5.875 | 310.434 | 51.693 | 67.157 | 45.626 | 82.835 |  | 17.625 | 4.8 | 11.7 | 35.25 | 0
| 5.8819 | 312.057 | 51.613 | 67.087 | 45.552 | 82.748 |  | 17.6458 | 4.2 | 11.7 | 35.2917 | 0
| 5.8889 | 309.229 | 51.522 | 67.02 | 45.483 | 82.655 |  | 17.6667 | 3.7 | 11.7 | 35.3333 | 0
| 5.8958 | 309.808 | 51.437 | 66.942 | 45.418 | 82.54 |  | 17.6875 | 3.1 | 11.7 | 35.375 | 0
| 5.9028 | 310.924 | 51.444 | 66.932 | 45.418 | 82.53 |  | 17.7083 | 3.2 | 11.7 | 35.4167 | 0
| 5.9097 | 312.528 | 51.503 | 66.963 | 45.472 | 82.574 |  | 17.7292 | 3.3 | 11.7 | 35.4583 | 0
| 5.9167 | 313.44 | 51.575 | 67.012 | 45.525 | 82.642 |  | 17.75 | 3.3 | 11.7 | 35.5 | 0
| 5.9236 | 313.081 | 51.622 | 67.049 | 45.559 | 82.688 |  | 17.7708 | 3.3 | 11.7 | 35.5417 | 0.2
| 5.9306 | 314.474 | 51.709 | 67.12 | 45.631 | 82.797 |  | 17.7917 | 3.2 | 11.7 | 35.5833 | 0.8
| 5.9375 | 311.888 | 51.617 | 67.067 | 45.564 | 82.72 |  | 17.8125 | 3.3 | 11.7 | 35.625 | 0
| 5.9444 | 312.544 | 51.588 | 67.04 | 45.534 | 82.692 |  | 17.8333 | 3.6 | 11.7 | 35.6667 | 0.2
| 5.9514 | 313.205 | 51.63 | 67.076 | 45.575 | 82.735 |  | 17.8542 | 3.6 | 11.7 | 35.7083 | 0
| 5.9583 | 313.146 | 51.667 | 67.104 | 45.604 | 82.774 |  | 17.875 | 3.6 | 11.7 | 35.75 | 0.8
| 5.9653 | 313.601 | 51.69 | 67.132 | 45.621 | 82.812 |  | 17.8958 | 3.7 | 11.7 | 35.7917 | 0.8
| 5.9722 | 313.466 | 51.73 | 67.164 | 45.646 | 82.858 |  | 17.9167 | 3.7 | 11.7 | 35.8333 | 0.4
| 5.9792 | 313.811 | 51.783 | 67.217 | 45.698 | 82.934 |  | 17.9375 | 3.8 | 11.7 | 35.875 | 0.4
| 5.9861 | 314.939 | 51.829 | 67.262 | 45.726 | 82.992 |  | 17.9583 | 3.8 | 11.7 | 35.9167 | 0
| 5.9931 | 310.918 | 51.731 | 67.213 | 45.66 | 82.919 |  | 17.9792 | 4 | 11.7 | 35.9583 | 0
| 6 | 311.139 | 51.651 | 67.151 | 45.591 | 82.84 |  | 18 | 4.1 | 11.7 | 36 | 0
| 6.0069 | 311.458 | 51.61 | 67.114 | 45.557 | 82.787 |  | 18.0208 | 4.2 | 11.7 | 36.0417 | 0
| 6.0139 | 310.572 | 51.532 | 67.049 | 45.5 | 82.694 |  | 18.0417 | 4.3 | 11.7 | 36.0833 | 0
| 6.0208 | 311.105 | 51.499 | 67.015 | 45.474 | 82.645 |  | 18.0625 | 4.4 | 11.7 | 36.125 | 0
| 6.0278 | 309.983 | 51.452 | 66.961 | 45.439 | 82.571 |  | 18.0833 | 4.4 | 11.7 | 36.1667 | 0.2
| 6.0347 | 310.408 | 51.423 | 66.928 | 45.416 | 82.52 |  | 18.1042 | 4.3 | 11.7 | 36.2083 | 0
| 6.0417 | 310.548 | 51.418 | 66.91 | 45.412 | 82.5 |  | 18.125 | 4.2 | 11.7 | 36.25 | 0
| 6.0486 | 311.086 | 51.42 | 66.898 | 45.415 | 82.48 |  | 18.1458 | 4.2 | 11.7 | 36.2917 | 0
| 6.0556 | 310.969 | 51.416 | 66.881 | 45.411 | 82.462 |  | 18.1667 | 4 | 11.7 | 36.3333 | 0
| 6.0625 | 311.509 | 51.432 | 66.889 | 45.424 | 82.471 |  | 18.1875 | 3.9 | 11.7 | 36.375 | 0
| 6.0694 | 311.268 | 51.448 | 66.892 | 45.433 | 82.47 |  | 18.2083 | 4 | 11.7 | 36.4167 | 0.4
| 6.0764 | 312.517 | 51.481 | 66.914 | 45.464 | 82.508 |  | 18.2292 | 4.1 | 11.7 | 36.4583 | 0
| 6.0833 | 311.247 | 51.48 | 66.916 | 45.467 | 82.503 |  | 18.25 | 4.2 | 11.7 | 36.5 | 0
| 6.0903 | 311.104 | 51.474 | 66.907 | 45.459 | 82.496 |  | 18.2708 | 4.2 | 11.7 | 36.5417 | 0
| 6.0972 | 310.786 | 51.445 | 66.884 | 45.442 | 82.47 |  | 18.2917 | 4.1 | 11.7 | 36.5833 | 0
| 6.1042 | 311.061 | 51.446 | 66.882 | 45.435 | 82.463 |  | 18.3125 | 4.2 | 11.7 | 36.625 | 0
| 6.1111 | 310.7 | 51.436 | 66.872 | 45.432 | 82.457 |  | 18.3333 | 4.3 | 11.7 | 36.6667 | 0
| 6.1181 | 310.919 | 51.417 | 66.849 | 45.413 | 82.423 |  | 18.3542 | 4.4 | 11.1 | 36.7083 | 0
| 6.125 | 310.701 | 51.396 | 66.831 | 45.402 | 82.4 |  | 18.375 | 4.6 | 11.1 | 36.75 | 0
| 6.1319 | 310.58 | 51.385 | 66.815 | 45.392 | 82.372 |  | 18.3958 | 4.7 | 11.1 | 36.7917 | 0
| 6.1389 | 310.64 | 51.372 | 66.798 | 45.376 | 82.357 |  | 18.4167 | 4.7 | 11.1 | 36.8333 | 0
| 6.1458 | 311.155 | 51.375 | 66.796 | 45.389 | 82.352 |  | 18.4375 | 4.9 | 11.1 | 36.875 | 0
| 6.1528 | 310.587 | 51.359 | 66.784 | 45.369 | 82.325 |  | 18.4583 | 5.3 | 11.1 | 36.9167 | 0
| 6.1597 | 310.789 | 51.356 | 66.767 | 45.364 | 82.314 |  | 18.4792 | 5.5 | 11.1 | 36.9583 | 0
| 6.1667 | 310.401 | 51.348 | 66.758 | 45.363 | 82.297 |  | 18.5 | 5.7 | 11.1 | 37 | 0
| 6.1736 | 310.308 | 51.314 | 66.725 | 45.335 | 82.253 |  | 18.5208 | 6.4 | 11.1 | 37.0417 | 0
| 6.1806 | 310.45 | 51.292 | 66.701 | 45.316 | 82.222 |  | 18.5417 | 7.2 | 11.1 | 37.0833 | 0
| 6.1875 | 309.859 | 51.269 | 66.672 | 45.301 | 82.185 |  | 18.5625 | 8.4 | 11.1 | 37.125 | 0
| 6.1944 | 308.301 | 51.216 | 66.625 | 45.259 | 82.12 |  | 18.5833 | 9.8 | 11.1 | 37.1667 | 0
| 6.2014 | 307.769 | 51.132 | 66.543 | 45.188 | 82.012 |  | 18.6042 | 10.2 | 11.1 | 37.2083 | 0
| 6.2083 | 308.156 | 51.088 | 66.491 | 45.154 | 81.941 |  | 18.625 | 9.6 | 11.1 | 37.25 | 0
| 6.2153 | 308.174 | 51.032 | 66.43 | 45.112 | 81.856 |  | 18.6458 | 9.3 | 11.1 | 37.2917 | 0
| 6.2222 | 310.593 | 51.15 | 66.499 | 45.202 | 81.952 |  | 18.6667 | 9.3 | 11.1 | 37.3333 | 0
| 6.2292 | 310.04 | 51.17 | 66.511 | 45.225 | 81.968 |  | 18.6875 | 9.2 | 11.1 | 37.375 | 0
| 6.2361 | 307.014 | 51.111 | 66.464 | 45.182 | 81.908 |  | 18.7083 | 8.9 | 11.1 | 37.4167 | 0
| 6.2431 | 307.142 | 51.032 | 66.392 | 45.115 | 81.81 |  | 18.7292 | 8.6 | 11.1 | 37.4583 | 0
| 6.25 | 308.342 | 50.996 | 66.34 | 45.085 | 81.746 |  | 18.75 | 8.3 | 11.1 | 37.5 | 0
| 6.2569 | 307.583 | 50.964 | 66.3 | 45.056 | 81.694 |  | 18.7708 | 8.3 | 11.1 | 37.5417 | 0
| 6.2639 | 311.03 | 51.048 | 66.335 | 45.112 | 81.748 |  | 18.7917 | 8.2 | 11.1 | 37.5833 | 0
| 6.2708 | 309.251 | 51.106 | 66.377 | 45.172 | 81.803 |  | 18.8125 | 8.3 | 11.1 | 37.625 | 0
| 6.2778 | 308.839 | 51.102 | 66.37 | 45.167 | 81.794 |  | 18.8333 | 8.3 | 11.1 | 37.6667 | 0
| 6.2847 | 308.858 | 51.055 | 66.333 | 45.132 | 81.747 |  | 18.8542 | 8.2 | 11.1 | 37.7083 | 0
| 6.2917 | 308.708 | 51.02 | 66.298 | 45.098 | 81.708 |  | 18.875 | 7.3 | 11.1 | 37.75 | 0
| 6.2986 | 309.798 | 50.997 | 66.268 | 45.077 | 81.67 |  | 18.8958 | 6.5 | 11.1 | 37.7917 | 0
| 6.3056 | 311.757 | 51.066 | 66.305 | 45.128 | 81.728 |  | 18.9167 | 5.8 | 11.1 | 37.8333 | 0
| 6.3125 | 311.285 | 51.182 | 66.395 | 45.226 | 81.844 |  | 18.9375 | 5.4 | 11.1 | 37.875 | 0
| 6.3194 | 312.062 | 51.252 | 66.459 | 45.28 | 81.935 |  | 18.9583 | 5.3 | 11.1 | 37.9167 | 0
| 6.3264 | 311.281 | 51.279 | 66.5 | 45.31 | 81.991 |  | 18.9792 | 5.8 | 11.1 | 37.9583 | 0
| 6.3333 | 311.344 | 51.292 | 66.509 | 45.31 | 82.014 |  | 19 | 5.9 | 11.1 | 38 | 0
| 6.3403 | 310.841 | 51.303 | 66.535 | 45.321 | 82.051 |  | 19.0208 | 6.3 | 11.1 | 38.0417 | 0
| 6.3472 | 311.959 | 51.297 | 66.541 | 45.318 | 82.058 |  | 19.0417 | 6.3 | 11.1 | 38.0833 | 0
| 6.3542 | 311.024 | 51.313 | 66.56 | 45.33 | 82.083 |  | 19.0625 | 6.3 | 11.1 | 38.125 | 0
| 6.3611 | 312.955 | 51.354 | 66.595 | 45.359 | 82.136 |  | 19.0833 | 6.4 | 11.1 | 38.1667 | 0
| 6.3681 | 312.515 | 51.422 | 66.66 | 45.418 | 82.224 |  | 19.1042 | 6.3 | 11.1 | 38.2083 | 0
| 6.375 | 311.845 | 51.436 | 66.682 | 45.427 | 82.252 |  | 19.125 | 6.3 | 11.1 | 38.25 | 0
| 6.3819 | 311.694 | 51.406 | 66.681 | 45.412 | 82.252 |  | 19.1458 | 6.1 | 11.1 | 38.2917 | 0
| 6.3889 | 310.951 | 51.366 | 66.658 | 45.373 | 82.218 |  | 19.1667 | 6.2 | 11.1 | 38.3333 | 0
| 6.3958 | 310.512 | 51.338 | 66.638 | 45.352 | 82.187 |  | 19.1875 | 5.7 | 11.1 | 38.375 | 0
| 6.4028 | 310.542 | 51.318 | 66.623 | 45.338 | 82.172 |  | 19.2083 | 5.2 | 11.1 | 38.4167 | 0
| 6.4097 | 309.299 | 51.269 | 66.589 | 45.305 | 82.118 |  | 19.2292 | 4.8 | 11.1 | 38.4583 | 0.2
| 6.4167 | 310.448 | 51.245 | 66.565 | 45.282 | 82.087 |  | 19.25 | 4.3 | 11.1 | 38.5 | 0
| 6.4236 | 310.819 | 51.226 | 66.548 | 45.266 | 82.056 |  | 19.2708 | 4.2 | 11.1 | 38.5417 | 0
| 6.4306 | 310.375 | 51.235 | 66.546 | 45.271 | 82.05 |  | 19.2917 | 3.9 | 11.1 | 38.5833 | 0
| 6.4375 | 309.579 | 51.223 | 66.533 | 45.268 | 82.036 |  | 19.3125 | 3.6 | 11.1 | 38.625 | 0
| 6.4444 | 310.256 | 51.202 | 66.51 | 45.25 | 82.007 |  | 19.3333 | 3.6 | 11.1 | 38.6667 | 0
| 6.4514 | 310.527 | 51.19 | 66.497 | 45.239 | 81.986 |  | 19.3542 | 4.4 | 11.1 | 38.7083 | 0
| 6.4583 | 310.503 | 51.216 | 66.509 | 45.262 | 82.005 |  | 19.375 | 6 | 11.1 | 38.75 | 0
| 6.4653 | 310.003 | 51.213 | 66.503 | 45.26 | 81.997 |  | 19.3958 | 7.2 | 11.1 | 38.7917 | 0
| 6.4722 | 309.89 | 51.196 | 66.491 | 45.245 | 81.973 |  | 19.4167 | 8.2 | 11.1 | 38.8333 | 0.2
| 6.4792 | 309.741 | 51.167 | 66.462 | 45.217 | 81.937 |  | 19.4375 | 9.5 | 11.1 | 38.875 | 0
| 6.4861 | 310.422 | 51.174 | 66.459 | 45.223 | 81.933 |  | 19.4583 | 11.2 | 11.1 | 38.9167 | 0.4
| 6.4931 | 311.37 | 51.207 | 66.482 | 45.248 | 81.962 |  | 19.4792 | 12.1 | 11.1 | 38.9583 | 0.4
| 6.5 | 311.66 | 51.247 | 66.51 | 45.284 | 82.008 |  | 19.5 | 13.2 | 11.1
| 6.5069 | 311.743 | 51.278 | 66.537 | 45.313 | 82.048 |  | 19.5208 | 13.8 | 11.1
| 6.5139 | 312.669 | 51.301 | 66.562 | 45.324 | 82.078 |  | 19.5417 | 15.1 | 11.1
| 6.5208 | 311.911 | 51.319 | 66.578 | 45.342 | 82.103 |  | 19.5625 | 16.1 | 11.1
| 6.5278 | 312.6 | 51.364 | 66.615 | 45.373 | 82.16 |  | 19.5833 | 16.4 | 11.1
| 6.5347 | 312.375 | 51.417 | 66.667 | 45.41 | 82.219 |  | 19.6042 | 17 | 11.1
| 6.5417 | 312.63 | 51.45 | 66.703 | 45.441 | 82.28 |  | 19.625 | 17.4 | 11.1
| 6.5486 | 308.053 | 51.299 | 66.612 | 45.328 | 82.142 |  | 19.6458 | 17 | 11.1
| 6.5556 | 305.636 | 51.059 | 66.42 | 45.137 | 81.886 |  | 19.6667 | 15.4 | 11.1
| 6.5625 | 309.563 | 51.052 | 66.385 | 45.119 | 81.836 |  | 19.6875 | 14.6 | 11.1
| 6.5694 | 309.482 | 51.088 | 66.4 | 45.159 | 81.851 |  | 19.7083 | 13.3 | 11.1
| 6.5764 | 309.928 | 51.076 | 66.376 | 45.152 | 81.82 |  | 19.7292 | 12.4 | 11.1
| 6.5833 | 309.947 | 51.104 | 66.375 | 45.168 | 81.826 |  | 19.75 | 11.8 | 11.1
| 6.5903 | 311.494 | 51.141 | 66.404 | 45.201 | 81.854 |  | 19.7708 | 10.5 | 11.1
| 6.5972 | 310.927 | 51.191 | 66.437 | 45.239 | 81.908 |  | 19.7917 | 10.1 | 11.1
| 6.6042 | 311.892 | 51.226 | 66.469 | 45.263 | 81.941 |  | 19.8125 | 10.1 | 11.1
| 6.6111 | 311.629 | 51.28 | 66.514 | 45.315 | 82.009 |  | 19.8333 | 9.4 | 11.1
| 6.6181 | 312.407 | 51.339 | 66.563 | 45.358 | 82.078 |  | 19.8542 | 9.6 | 11.1
| 6.625 | 312.244 | 51.384 | 66.612 | 45.395 | 82.152 |  | 19.875 | 9.1 | 11.1
| 6.6319 | 312.629 | 51.41 | 66.646 | 45.414 | 82.199 |  | 19.8958 | 8.6 | 11.1
| 6.6389 | 312.798 | 51.451 | 66.688 | 45.442 | 82.254 |  | 19.9167 | 8.6 | 11.1
| 6.6458 | 310.127 | 51.395 | 66.675 | 45.406 | 82.222 |  | 19.9375 | 8.6 | 11.1
| 6.6528 | 307.95 | 51.245 | 66.563 | 45.289 | 82.08 |  | 19.9583 | 8.3 | 11.1
| 6.6597 | 308.439 | 51.162 | 66.484 | 45.215 | 81.974 |  | 19.9792 | 8.2 | 11.1
| 6.6667 | 309.656 | 51.124 | 66.451 | 45.192 | 81.919 |  | 20 | 8.3 | 11.1
| 6.6736 | 309.915 | 51.131 | 66.438 | 45.194 | 81.902 |  | 20.0208 | 8.2 | 11.1
| 6.6806 | 310.37 | 51.142 | 66.441 | 45.208 | 81.896 |  | 20.0417 | 8.2 | 11.1
| 6.6875 | 308.693 | 51.104 | 66.401 | 45.177 | 81.844 |  | 20.0625 | 8.3 | 11.1
| 6.6944 | 308.24 | 51.062 | 66.357 | 45.145 | 81.782 |  | 20.0833 | 8.9 | 11.1
| 6.7014 | 307.793 | 50.973 | 66.281 | 45.078 | 81.673 |  | 20.1042 | 9.2 | 11.1
| 6.7083 | 308.092 | 50.927 | 66.224 | 45.037 | 81.595 |  | 20.125 | 8.9 | 11.1
| 6.7153 | 307.441 | 50.913 | 66.194 | 45.025 | 81.551 |  | 20.1458 | 9.3 | 11.1
| 6.7222 | 308.385 | 50.877 | 66.153 | 45.006 | 81.493 |  | 20.1667 | 9.3 | 11.1
| 6.7292 | 307.925 | 50.871 | 66.13 | 44.996 | 81.46 |  | 20.1875 | 9.2 | 11.1
| 6.7361 | 311.737 | 50.994 | 66.197 | 45.087 | 81.561 |  | 20.2083 | 9.1 | 11.1
| 6.7431 | 310.933 | 51.127 | 66.306 | 45.202 | 81.696 |  | 20.2292 | 10 | 11.1
| 6.75 | 310.048 | 51.144 | 66.331 | 45.215 | 81.735 |  | 20.25 | 10.8 | 11.1
| 6.7569 | 309.418 | 51.104 | 66.306 | 45.183 | 81.707 |  | 20.2708 | 11.6 | 11.1
| 6.7639 | 309.826 | 51.125 | 66.327 | 45.196 | 81.734 |  | 20.2917 | 11.9 | 11.1
| 6.7708 | 309.625 | 51.082 | 66.306 | 45.167 | 81.695 |  | 20.3125 | 11.9 | 11.1
| 6.7778 | 310.025 | 51.084 | 66.298 | 45.165 | 81.694 |  | 20.3333 | 12.2 | 11.1
| 6.7847 | 311.137 | 51.14 | 66.344 | 45.217 | 81.748 |  | 20.3542 | 13.2 | 11.1
| 6.7917 | 311.6 | 51.208 | 66.404 | 45.269 | 81.826 |  | 20.375 | 13.5 | 11.1
| 6.7986 | 312.367 | 51.287 | 66.472 | 45.334 | 81.92 |  | 20.3958 | 13.8 | 11.1
| 6.8056 | 311.888 | 51.339 | 66.531 | 45.381 | 81.994 |  | 20.4167 | 14.2 | 11.1
| 6.8125 | 311.806 | 51.366 | 66.571 | 45.409 | 82.053 |  | 20.4375 | 14.6 | 11.1
| 6.8194 | 312.121 | 51.388 | 66.604 | 45.417 | 82.099 |  | 20.4583 | 15.5 | 11.1
| 6.8264 | 311.91 | 51.404 | 66.632 | 45.436 | 82.123 |  | 20.4792 | 15.4 | 11.1
| 6.8333 | 312.575 | 51.46 | 66.693 | 45.491 | 82.208 |  | 20.5 | 15.8 | 11.1
| 6.8403 | 313.365 | 51.518 | 66.757 | 45.537 | 82.295 |  | 20.5208 | 15.9 | 11.1
| 6.8472 | 312.872 | 51.582 | 66.827 | 45.586 | 82.382 |  | 20.5417 | 15.9 | 11.1
| 6.8542 | 313.363 | 51.619 | 66.883 | 45.624 | 82.443 |  | 20.5625 | 16 | 11.1
| 6.8611 | 313.482 | 51.65 | 66.929 | 45.649 | 82.511 |  | 20.5833 | 16.4 | 11.1
| 6.8681 | 313.823 | 51.692 | 66.989 | 45.691 | 82.585 |  | 20.6042 | 16.7 | 11.1
| 6.875 | 314.054 | 51.734 | 67.044 | 45.721 | 82.646 |  | 20.625 | 16.9 | 11.1
| 6.8819 | 310.56 | 51.688 | 67.047 | 45.704 | 82.639 |  | 20.6458 | 16.7 | 11.1
| 6.8889 | 310.24 | 51.553 | 66.953 | 45.586 | 82.504 |  | 20.6667 | 16.2 | 11.1
| 6.8958 | 311.424 | 51.528 | 66.932 | 45.566 | 82.469 |  | 20.6875 | 15.8 | 11.1
| 6.9028 | 311.762 | 51.541 | 66.949 | 45.576 | 82.48 |  | 20.7083 | 15.8 | 11.1
| 6.9097 | 312.701 | 51.593 | 66.992 | 45.627 | 82.527 |  | 20.7292 | 15.7 | 11.1
| 6.9167 | 313.242 | 51.606 | 67.011 | 45.642 | 82.549 |  | 20.75 | 15.6 | 11.1
| 6.9236 | 314.162 | 51.681 | 67.079 | 45.703 | 82.631 |  | 20.7708 | 14.8 | 11.1
| 6.9306 | 313.209 | 51.693 | 67.102 | 45.717 | 82.653 |  | 20.7917 | 14.4 | 11.1
| 6.9375 | 313.206 | 51.696 | 67.123 | 45.723 | 82.676 |  | 20.8125 | 14.8 | 11.1
| 6.9444 | 313.107 | 51.721 | 67.157 | 45.745 | 82.712 |  | 20.8333 | 15.1 | 11.1
| 6.9514 | 311.01 | 51.785 | 67.222 | 45.807 | 82.789 |  | 20.8542 | 15.1 | 11.1
| 6.9583 | 310.928 | 51.643 | 67.132 | 45.695 | 82.656 |  | 20.875 | 14.8 | 11.1
| 6.9653 | 311.053 | 51.614 | 67.108 | 45.667 | 82.619 |  | 20.8958 | 14.9 | 11.1
| 6.9722 | 311.366 | 51.601 | 67.103 | 45.666 | 82.595 |  | 20.9167 | 14.6 | 11.1
| 6.9792 | 310.896 | 51.583 | 67.089 | 45.657 | 82.573 |  | 20.9375 | 14.8 | 11.1
| 6.9861 | 310.309 | 51.602 | 67.111 | 45.685 | 82.584 |  | 20.9583 | 14.5 | 11.1
| 6.9931 | 310.011 | 51.53 | 67.048 | 45.621 | 82.496 |  | 20.9792 | 14.3 | 11.1
| 7 | 310.927 | 51.53 | 67.043 | 45.621 | 82.483 |  | 21 | 14.3 | 11.1
| 7.0069 | 310.762 | 51.53 | 67.042 | 45.633 | 82.475 |  | 21.0208 | 14.2 | 11.1
| 7.0139 | 310.447 | 51.514 | 67.029 | 45.619 | 82.447 |  | 21.0417 | 14.2 | 11.1
| 7.0208 | 310.667 | 51.51 | 67.023 | 45.614 | 82.429 |  | 21.0625 | 14.3 | 11.1
| 7.0278 | 310.752 | 51.508 | 67.017 | 45.612 | 82.411 |  | 21.0833 | 14.5 | 11.1
| 7.0347 | 309.338 | 51.481 | 66.998 | 45.605 | 82.383 |  | 21.1042 | 14.4 | 11.1
| 7.0417 | 309.829 | 51.434 | 66.959 | 45.565 | 82.323 |  | 21.125 | 14.5 | 11.1
| 7.0486 | 309.578 | 51.41 | 66.933 | 45.549 | 82.278 |  | 21.1458 | 14.7 | 11.1
| 7.0556 | 310.209 | 51.403 | 66.918 | 45.543 | 82.256 |  | 21.1667 | 14.7 | 11.1
| 7.0625 | 310.68 | 51.417 | 66.92 | 45.563 | 82.251 |  | 21.1875 | 14.8 | 11.1
| 7.0694 | 309.747 | 51.417 | 66.911 | 45.556 | 82.234 |  | 21.2083 | 14.8 | 11.1
| 7.0764 | 310.286 | 51.448 | 66.929 | 45.583 | 82.255 |  | 21.2292 | 14.8 | 11.1
| 7.0833 | 310.493 | 51.466 | 66.944 | 45.607 | 82.27 |  | 21.25 | 14.9 | 11.1
| 7.0903 | 310.675 | 51.458 | 66.944 | 45.598 | 82.264 |  | 21.2708 | 14.9 | 11.1
| 7.0972 | 310.44 | 51.463 | 66.947 | 45.601 | 82.261 |  | 21.2917 | 14.9 | 11.1
| 7.1042 | 310.317 | 51.465 | 66.945 | 45.607 | 82.258 |  | 21.3125 | 14.9 | 11.1
| 7.1111 | 310.735 | 51.466 | 66.939 | 45.608 | 82.253 |  | 21.3333 | 15.1 | 11.1
| 7.1181 | 310.276 | 51.489 | 66.963 | 45.63 | 82.278 |  | 21.3542 | 15.2 | 11.1
| 7.125 | 311.173 | 51.493 | 66.972 | 45.638 | 82.289 |  | 21.375 | 15.4 | 11.1
| 7.1319 | 310.996 | 51.496 | 66.972 | 45.64 | 82.283 |  | 21.3958 | 15.6 | 11.1
| 7.1389 | 310.482 | 51.491 | 66.968 | 45.639 | 82.279 |  | 21.4167 | 15.7 | 11.1
| 7.1458 | 310.977 | 51.496 | 66.973 | 45.641 | 82.286 |  | 21.4375 | 16.2 | 11.1
| 7.1528 | 309.955 | 51.489 | 66.965 | 45.636 | 82.27 |  | 21.4583 | 16.4 | 11.1
| 7.1597 | 310.844 | 51.488 | 66.967 | 45.634 | 82.273 |  | 21.4792 | 17.2 | 11.1
| 7.1667 | 310.232 | 51.487 | 66.965 | 45.639 | 82.27 |  | 21.5 | 16.7 | 11.1
| 7.1736 | 310.197 | 51.488 | 66.962 | 45.635 | 82.266 |  | 21.5208 | 17.4 | 11.1
| 7.1806 | 309.765 | 51.474 | 66.958 | 45.634 | 82.253 |  | 21.5417 | 17.8 | 11.1
| 7.1875 | 309.983 | 51.472 | 66.948 | 45.626 | 82.244 |  | 21.5625 | 18 | 11.1
| 7.1944 | 309.596 | 51.457 | 66.935 | 45.62 | 82.223 |  | 21.5833 | 18.4 | 11.1
| 7.2014 | 309.62 | 51.439 | 66.915 | 45.605 | 82.198 |  | 21.6042 | 17.7 | 11.1
| 7.2083 | 310.045 | 51.41 | 66.889 | 45.583 | 82.164 |  | 21.625 | 17.6 | 11.1
| 7.2153 | 309.3 | 51.39 | 66.871 | 45.572 | 82.135 |  | 21.6458 | 17.7 | 11.1
| 7.2222 | 309.43 | 51.41 | 66.878 | 45.585 | 82.132 |  | 21.6667 | 17.5 | 11.1
| 7.2292 | 309.939 | 51.405 | 66.866 | 45.585 | 82.127 |  | 21.6875 | 16.7 | 11.1
| 7.2361 | 308.844 | 51.361 | 66.829 | 45.551 | 82.077 |  | 21.7083 | 16.7 | 11.1
| 7.2431 | 307.662 | 51.266 | 66.75 | 45.472 | 81.961 |  | 21.7292 | 16.3 | 11.1
| 7.25 | 310.92 | 51.379 | 66.818 | 45.555 | 82.055 |  | 21.75 | 16.3 | 11.1
| 7.2569 | 310.32 | 51.43 | 66.855 | 45.608 | 82.107 |  | 21.7708 | 16.7 | 11.1
| 7.2639 | 309.658 | 51.437 | 66.858 | 45.607 | 82.118 |  | 21.7917 | 16.7 | 11.1
| 7.2708 | 309.808 | 51.405 | 66.836 | 45.578 | 82.094 |  | 21.8125 | 16.9 | 11.1
| 7.2778 | 308.553 | 51.364 | 66.803 | 45.544 | 82.038 |  | 21.8333 | 16.9 | 11.1
| 7.2847 | 307.845 | 51.301 | 66.747 | 45.493 | 81.967 |  | 21.8542 | 16.9 | 11.1
| 7.2917 | 310.846 | 51.388 | 66.799 | 45.564 | 82.046 |  | 21.875 | 17.3 | 11.1
| 7.2986 | 311.189 | 51.433 | 66.832 | 45.596 | 82.094 |  | 21.8958 | 17.3 | 11.1
| 7.3056 | 313.496 | 51.535 | 66.908 | 45.674 | 82.198 |  | 21.9167 | 16.8 | 11.1
| 7.3125 | 313.647 | 51.68 | 67.032 | 45.792 | 82.37 |  | 21.9375 | 16.3 | 11.1
| 7.3194 | 313.582 | 51.77 | 67.121 | 45.86 | 82.501 |  | 21.9583 | 15.4 | 11.1
| 7.3264 | 313.539 | 51.796 | 67.166 | 45.888 | 82.573 |  | 21.9792 | 14.6 | 11.1
| 7.3333 | 312.927 | 51.805 | 67.201 | 45.894 | 82.615 |  | 22 | 15.2 | 11.1
| 7.3403 | 312.554 | 51.812 | 67.219 | 45.892 | 82.648 |  | 22.0208 | 15.2 | 11.1
| 7.3472 | 312.564 | 51.801 | 67.234 | 45.888 | 82.661 |  | 22.0417 | 15.2 | 11.1
| 7.3542 | 311.972 | 51.797 | 67.241 | 45.887 | 82.677 |  | 22.0625 | 15.3 | 11.1
| 7.3611 | 312.106 | 51.794 | 67.253 | 45.882 | 82.691 |  | 22.0833 | 15.1 | 11.1
| 7.3681 | 312.207 | 51.782 | 67.258 | 45.876 | 82.694 |  | 22.1042 | 14.3 | 11.1
| 7.375 | 310.916 | 51.731 | 67.225 | 45.833 | 82.656 |  | 22.125 | 14.1 | 11.1
| 7.3819 | 310.14 | 51.663 | 67.171 | 45.78 | 82.584 |  | 22.1458 | 13.8 | 11.1
| 7.3889 | 309.708 | 51.6 | 67.123 | 45.735 | 82.511 |  | 22.1667 | 13 | 11.1
| 7.3958 | 309.127 | 51.547 | 67.069 | 45.686 | 82.438 |  | 22.1875 | 12.6 | 11.1
| 7.4028 | 308.847 | 51.47 | 66.998 | 45.622 | 82.338 |  | 22.2083 | 12.4 | 11.1
| 7.4097 | 309.379 | 51.447 | 66.965 | 45.611 | 82.292 |  | 22.2292 | 12.1 | 11.1
| 7.4167 | 309.966 | 51.435 | 66.935 | 45.602 | 82.261 |  | 22.25 | 11.6 | 11.1
| 7.4236 | 309.722 | 51.423 | 66.919 | 45.595 | 82.231 |  | 22.2708 | 10.9 | 11.1
| 7.4306 | 310.115 | 51.418 | 66.902 | 45.584 | 82.208 |  | 22.2917 | 10.4 | 11.1
| 7.4375 | 310.576 | 51.431 | 66.892 | 45.598 | 82.205 |  | 22.3125 | 10.1 | 11.1
| 7.4444 | 310.391 | 51.459 | 66.908 | 45.618 | 82.225 |  | 22.3333 | 9.8 | 11.1
| 7.4514 | 310.252 | 51.478 | 66.914 | 45.629 | 82.237 |  | 22.3542 | 10.2 | 11.1
| 7.4583 | 311.092 | 51.482 | 66.913 | 45.635 | 82.252 |  | 22.375 | 10.9 | 11.1
| 7.4653 | 311.375 | 51.495 | 66.922 | 45.639 | 82.259 |  | 22.3958 | 13 | 11.7
| 7.4722 | 311.111 | 51.534 | 66.945 | 45.664 | 82.302 |  | 22.4167 | 13.8 | 11.7
| 7.4792 | 311.246 | 51.561 | 66.971 | 45.694 | 82.331 |  | 22.4375 | 15 | 11.7
| 7.4861 | 312.257 | 51.604 | 67.005 | 45.725 | 82.39 |  | 22.4583 | 16.6 | 11.7
| 7.4931 | 312.271 | 51.629 | 67.028 | 45.74 | 82.426 |  | 22.4792 | 17.6 | 11.7
| 7.5 | 312.044 | 51.634 | 67.043 | 45.745 | 82.442 |  | 22.5 | 18.1 | 11.7
| 7.5069 | 311.404 | 51.641 | 67.048 | 45.752 | 82.466 |  | 22.5208 | 19.2 | 11.7
| 7.5139 | 311.79 | 51.615 | 67.037 | 45.727 | 82.448 |  | 22.5417 | 19 | 11.7
| 7.5208 | 311.865 | 51.593 | 67.029 | 45.715 | 82.438 |  | 22.5625 | 19.1 | 11.7
| 7.5278 | 312.184 | 51.61 | 67.032 | 45.722 | 82.452 |  | 22.5833 | 19 | 11.7
| 7.5347 | 312.047 | 51.648 | 67.067 | 45.75 | 82.494 |  | 22.6042 | 19.1 | 11.7
| 7.5417 | 313.424 | 51.676 | 67.092 | 45.773 | 82.536 |  | 22.625 | 19.2 | 11.7
| 7.5486 | 312.987 | 51.704 | 67.119 | 45.795 | 82.575 |  | 22.6458 | 18.8 | 11.7
| 7.5556 | 310.919 | 51.637 | 67.077 | 45.743 | 82.519 |  | 22.6667 | 18.2 | 11.7
| 7.5625 | 311.325 | 51.602 | 67.046 | 45.718 | 82.487 |  | 22.6875 | 17.3 | 11.7
| 7.5694 | 311.632 | 51.581 | 67.031 | 45.703 | 82.463 |  | 22.7083 | 16 | 11.7
| 7.5764 | 312.481 | 51.614 | 67.051 | 45.722 | 82.49 |  | 22.7292 | 15.3 | 11.7
| 7.5833 | 309.447 | 51.532 | 67 | 45.663 | 82.409 |  | 22.75 | 14.5 | 11.7
| 7.5903 | 310.092 | 51.447 | 66.916 | 45.589 | 82.311 |  | 22.7708 | 13.6 | 11.7
| 7.5972 | 309.447 | 51.419 | 66.881 | 45.566 | 82.265 |  | 22.7917 | 13.2 | 11.7
| 7.6042 | 310.822 | 51.421 | 66.867 | 45.567 | 82.249 |  | 22.8125 | 12.3 | 11.7
| 7.6111 | 309.535 | 51.414 | 66.849 | 45.566 | 82.228 |  | 22.8333 | 11.7 | 11.7
| 7.6181 | 309.248 | 51.382 | 66.818 | 45.542 | 82.189 |  | 22.8542 | 11.7 | 11.7
| 7.625 | 308.789 | 51.332 | 66.765 | 45.492 | 82.117 |  | 22.875 | 11.3 | 11.7
| 7.6319 | 309.789 | 51.295 | 66.723 | 45.462 | 82.052 |  | 22.8958 | 10.8 | 11.7
| 7.6389 | 309.873 | 51.296 | 66.709 | 45.467 | 82.037 |  | 22.9167 | 10.5 | 11.7
| 7.6458 | 309.044 | 51.285 | 66.68 | 45.45 | 82.007 |  | 22.9375 | 11.6 | 11.7
| 7.6528 | 309.525 | 51.267 | 66.657 | 45.442 | 81.979 |  | 22.9583 | 11.7 | 11.7
| 7.6597 | 309.046 | 51.258 | 66.639 | 45.438 | 81.956 |  | 22.9792 | 15 | 11.7
| 7.6667 | 309.63 | 51.267 | 66.632 | 45.438 | 81.957 |  | 23 | 15.3 | 11.7
| 7.6736 | 309.515 | 51.255 | 66.612 | 45.425 | 81.932 |  | 23.0208 | 14.3 | 11.7
| 7.6806 | 310.151 | 51.251 | 66.602 | 45.421 | 81.92 |  | 23.0417 | 14.3 | 11.7
| 7.6875 | 309.264 | 51.256 | 66.599 | 45.428 | 81.926 |  | 23.0625 | 13.9 | 11.7
| 7.6944 | 309.492 | 51.256 | 66.59 | 45.424 | 81.915 |  | 23.0833 | 13.9 | 11.7
| 7.7014 | 309.274 | 51.247 | 66.572 | 45.415 | 81.897 |  | 23.1042 | 14.2 | 11.7
| 7.7083 | 309.369 | 51.217 | 66.544 | 45.392 | 81.865 |  | 23.125 | 13.9 | 11.7
| 7.7153 | 309.194 | 51.185 | 66.506 | 45.362 | 81.818 |  | 23.1458 | 13.8 | 11.7
| 7.7222 | 308.056 | 51.155 | 66.472 | 45.339 | 81.783 |  | 23.1667 | 13.9 | 11.7
| 7.7292 | 307.955 | 51.118 | 66.431 | 45.31 | 81.727 |  | 23.1875 | 14.1 | 11.7
| 7.7361 | 307.187 | 51.074 | 66.392 | 45.277 | 81.667 |  | 23.2083 | 14.3 | 11.7
| 7.7431 | 309.615 | 51.201 | 66.474 | 45.378 | 81.785 |  | 23.2292 | 14.3 | 11.7
| 7.75 | 309.073 | 51.193 | 66.468 | 45.377 | 81.781 |  | 23.25 | 14.4 | 11.7
| 7.7569 | 306.153 | 51.151 | 66.434 | 45.341 | 81.732 |  | 23.2708 | 14.3 | 11.7
| 7.7639 | 312.397 | 51.35 | 66.577 | 45.488 | 81.938 |  | 23.2917 | 14.7 | 11.7
| 7.7708 | 312.17 | 51.435 | 66.656 | 45.556 | 82.039 |  | 23.3125 | 14.8 | 11.7
| 7.7778 | 312.052 | 51.486 | 66.71 | 45.599 | 82.129 |  | 23.3333 | 14.5 | 11.7
| 7.7847 | 312.35 | 51.52 | 66.756 | 45.628 | 82.193 |  | 23.3542 | 14.8 | 11.7
| 7.7917 | 312.144 | 51.545 | 66.788 | 45.642 | 82.246 |  | 23.375 | 15.9 | 11.7
| 7.7986 | 312.547 | 51.563 | 66.824 | 45.663 | 82.293 |  | 23.3958 | 16.3 | 11.7
| 7.8056 | 312.647 | 51.61 | 66.871 | 45.703 | 82.363 |  | 23.4167 | 16.8 | 11.7
| 7.8125 | 312.985 | 51.665 | 66.93 | 45.748 | 82.449 |  | 23.4375 | 17.2 | 11.7
| 7.8194 | 313.928 | 51.707 | 66.992 | 45.782 | 82.515 |  | 23.4583 | 18.6 | 11.7
| 7.8264 | 310.074 | 51.735 | 67.043 | 45.812 | 82.584 |  | 23.4792 | 19 | 11.7
| 7.8333 | 310.106 | 51.6 | 66.957 | 45.703 | 82.469 |  | 23.5 | 18.9 | 11.7
| 7.8403 | 310.515 | 51.564 | 66.927 | 45.674 | 82.428 |  | 23.5208 | 18.9 | 11.7
| 7.8472 | 311.383 | 51.547 | 66.92 | 45.661 | 82.408 |  | 23.5417 | 18.7 | 11.7
| 7.8542 | 312.04 | 51.563 | 66.94 | 45.677 | 82.431 |  | 23.5625 | 18.6 | 11.7
| 7.8611 | 312.512 | 51.58 | 66.956 | 45.691 | 82.442 |  | 23.5833 | 18.3 | 11.7
| 7.8681 | 311.519 | 51.62 | 66.989 | 45.73 | 82.488 |  | 23.6042 | 18.5 | 11.7
| 7.875 | 312.022 | 51.642 | 67.015 | 45.742 | 82.515 |  | 23.625 | 18.4 | 11.7
| 7.8819 | 311.59 | 51.657 | 67.04 | 45.763 | 82.552 |  | 23.6458 | 17.8 | 11.7
| 7.8889 | 312.83 | 51.679 | 67.064 | 45.776 | 82.578 |  | 23.6667 | 17.1 | 11.7
| 7.8958 | 312.359 | 51.713 | 67.101 | 45.81 | 82.626 |  | 23.6875 | 16.8 | 11.7
| 7.9028 | 313.883 | 51.766 | 67.155 | 45.853 | 82.694 |  | 23.7083 | 16.2 | 11.7
| 7.9097 | 313.943 | 51.82 | 67.217 | 45.901 | 82.773 |  | 23.7292 | 15.8 | 11.7
| 7.9167 | 310.658 | 51.701 | 67.144 | 45.811 | 82.672 |  | 23.75 | 15.3 | 11.7
| 7.9236 | 310.997 | 51.645 | 67.101 | 45.756 | 82.612 |  | 23.7708 | 14.6 | 11.7
| 7.9306 | 311.267 | 51.612 | 67.082 | 45.749 | 82.576 |  | 23.7917 | 14.9 | 11.7
| 7.9375 | 311.588 | 51.615 | 67.084 | 45.744 | 82.563 |  | 23.8125 | 13.9 | 11.7
| 7.9444 | 312.154 | 51.628 | 67.1 | 45.769 | 82.581 |  | 23.8333 | 14.6 | 11.7
| 7.9514 | 311.164 | 51.624 | 67.091 | 45.764 | 82.572 |  | 23.8542 | 14.5 | 11.7
| 7.9583 | 311.387 | 51.627 | 67.093 | 45.769 | 82.566 |  | 23.875 | 14.1 | 11.7
| 7.9653 | 311.391 | 51.618 | 67.096 | 45.764 | 82.558 |  | 23.8958 | 14.5 | 11.7
| 7.9722 | 311.811 | 51.635 | 67.109 | 45.774 | 82.577 |  | 23.9167 | 14.4 | 11.7
| 7.9792 | 309.641 | 51.64 | 67.119 | 45.791 | 82.571 |  | 23.9375 | 14.6 | 11.7
| 7.9861 | 310.764 | 51.59 | 67.079 | 45.741 | 82.521 |  | 23.9583 | 14.3 | 11.7
| 7.9931 | 310.583 | 51.602 | 67.082 | 45.751 | 82.521 |  | 23.9792 | 14.4 | 11.7
| 8 | 309.723 | 51.585 | 67.078 | 45.748 | 82.504 |  | 24 | 14.3 | 11.7
| 8.0069 | 310.576 | 51.557 | 67.054 | 45.729 | 82.468 |  | 24.0208 | 14.2 | 11.7
| 8.0139 | 310.32 | 51.539 | 67.035 | 45.713 | 82.437 |  | 24.0417 | 13.9 | 11.7
| 8.0208 | 309.621 | 51.522 | 67.012 | 45.697 | 82.408 |  | 24.0625 | 13.6 | 11.7
| 8.0278 | 310.533 | 51.521 | 67.007 | 45.698 | 82.402 |  | 24.0833 | 13.4 | 11.7
| 8.0347 | 310.299 | 51.535 | 67.016 | 45.716 | 82.405 |  | 24.1042 | 13.3 | 11.7
| 8.0417 | 310.848 | 51.553 | 67.026 | 45.735 | 82.419 |  | 24.125 | 13.2 | 11.7
| 8.0486 | 310.723 | 51.544 | 67.023 | 45.724 | 82.412 |  | 24.1458 | 13.2 | 11.7
| 8.0556 | 310.666 | 51.556 | 67.03 | 45.733 | 82.412 |  | 24.1667 | 13.3 | 11.7
| 8.0625 | 310.836 | 51.582 | 67.045 | 45.753 | 82.432 |  | 24.1875 | 13.3 | 11.7
| 8.0694 | 311.812 | 51.623 | 67.079 | 45.786 | 82.478 |  | 24.2083 | 12.7 | 11.7
| 8.0764 | 312.14 | 51.675 | 67.131 | 45.83 | 82.541 |  | 24.2292 | 13 | 11.7
| 8.0833 | 312.606 | 51.718 | 67.172 | 45.866 | 82.597 |  | 24.25 | 12.9 | 11.7
| 8.0903 | 311.811 | 51.745 | 67.208 | 45.889 | 82.645 |  | 24.2708 | 12.6 | 11.7
| 8.0972 | 311.611 | 51.715 | 67.198 | 45.877 | 82.637 |  | 24.2917 | 12.2 | 11.7
| 8.1042 | 312.025 | 51.725 | 67.212 | 45.874 | 82.652 |  | 24.3125 | 12.4 | 11.7
| 8.1111 | 312.225 | 51.728 | 67.223 | 45.882 | 82.657 |  | 24.3333 | 12.4 | 11.7
| 8.1181 | 311.037 | 51.741 | 67.235 | 45.889 | 82.674 |  | 24.3542 | 12.7 | 11.7
| 8.125 | 312.504 | 51.751 | 67.249 | 45.905 | 82.693 |  | 24.375 | 13 | 11.7
| 8.1319 | 312.359 | 51.772 | 67.275 | 45.916 | 82.722 |  | 24.3958 | 13.3 | 11.7
| 8.1389 | 312.376 | 51.79 | 67.298 | 45.939 | 82.752 |  | 24.4167 | 13.6 | 12.2
| 8.1458 | 311.76 | 51.795 | 67.307 | 45.941 | 82.763 |  | 24.4375 | 13.8 | 12.2
| 8.1528 | 312.53 | 51.803 | 67.324 | 45.948 | 82.777 |  | 24.4583 | 14.2 | 12.2
| 8.1597 | 312.402 | 51.814 | 67.333 | 45.961 | 82.8 |  | 24.4792 | 14.3 | 12.2
| 8.1667 | 313.116 | 51.861 | 67.376 | 45.995 | 82.847 |  | 24.5 | 14.3 | 12.2
| 8.1736 | 313.424 | 51.895 | 67.412 | 46.021 | 82.897 |  | 24.5208 | 14.6 | 12.2
| 8.1806 | 313.385 | 51.932 | 67.459 | 46.053 | 82.959 |  | 24.5417 | 14.6 | 12.2
| 8.1875 | 313.15 | 51.941 | 67.478 | 46.064 | 82.983 |  | 24.5625 | 14.7 | 12.2
| 8.1944 | 312.529 | 51.928 | 67.479 | 46.054 | 82.979 |  | 24.5833 | 14.6 | 12.2
| 8.2014 | 312.831 | 51.91 | 67.471 | 46.035 | 82.972 |  | 24.6042 | 14.4 | 12.2
| 8.2083 | 312.557 | 51.899 | 67.471 | 46.031 | 82.97 |  | 24.625 | 14.4 | 12.2
| 8.2153 | 311.759 | 51.875 | 67.461 | 46.017 | 82.95 |  | 24.6458 | 14.4 | 12.2
| 8.2222 | 312.47 | 51.877 | 67.463 | 46.019 | 82.955 |  | 24.6667 | 14.3 | 12.2
| 8.2292 | 312.153 | 51.882 | 67.47 | 46.022 | 82.958 |  | 24.6875 | 14.2 | 12.2
| 8.2361 | 312.957 | 51.886 | 67.471 | 46.02 | 82.962 |  | 24.7083 | 14.2 | 12.2
| 8.2431 | 311.602 | 51.866 | 67.469 | 46.014 | 82.951 |  | 24.7292 | 13.4 | 12.2
| 8.25 | 311.942 | 51.832 | 67.438 | 45.986 | 82.907 |  | 24.75 | 13.3 | 12.2
| 8.2569 | 311.903 | 51.819 | 67.422 | 45.975 | 82.892 |  | 24.7708 | 13.1 | 12.2
| 8.2639 | 311.676 | 51.793 | 67.408 | 45.96 | 82.871 |  | 24.7917 | 13.2 | 12.2
| 8.2708 | 312.249 | 51.785 | 67.391 | 45.948 | 82.841 |  | 24.8125 | 13.1 | 12.2
| 8.2778 | 311.153 | 51.766 | 67.373 | 45.933 | 82.817 |  | 24.8333 | 13.3 | 12.2
| 8.2847 | 311.234 | 51.722 | 67.336 | 45.896 | 82.763 |  | 24.8542 | 13.3 | 12.2
| 8.2917 | 310.199 | 51.686 | 67.296 | 45.871 | 82.723 |  | 24.875 | 13.2 | 12.2
| 8.2986 | 310.175 | 51.658 | 67.264 | 45.845 | 82.668 |  | 24.8958 | 13.2 | 12.2
| 8.3056 | 309.724 | 51.619 | 67.222 | 45.82 | 82.615 |  | 24.9167 | 13.3 | 12.2
| 8.3125 | 310.47 | 51.613 | 67.203 | 45.809 | 82.592 |  | 24.9375 | 13.2 | 12.2
| 8.3194 | 311.267 | 51.69 | 67.246 | 45.87 | 82.655 |  | 24.9583 | 13.2 | 12.2
| 8.3264 | 311.99 | 51.708 | 67.261 | 45.884 | 82.673 |  | 24.9792 | 13.2 | 12.2
| 8.3333 | 311.626 | 51.722 | 67.27 | 45.896 | 82.684 |  | 25 | 13.2 | 12.2
| 8.3403 | 311.751 | 51.707 | 67.26 | 45.883 | 82.679 |  | 25.0208 | 13.1 | 12.2
| 8.3472 | 311.387 | 51.714 | 67.26 | 45.89 | 82.682 |  | 25.0417 | 12.8 | 12.2
| 8.3542 | 311.721 | 51.714 | 67.262 | 45.887 | 82.684 |  | 25.0625 | 12.3 | 12.2
| 8.3611 | 311.223 | 51.698 | 67.249 | 45.872 | 82.664 |  | 25.0833 | 12.5 | 12.2
| 8.3681 | 311.046 | 51.671 | 67.219 | 45.854 | 82.631 |  | 25.1042 | 12.4 | 12.2
| 8.375 | 310.659 | 51.627 | 67.185 | 45.816 | 82.577 |  | 25.125 | 12.7 | 12.2
| 8.3819 | 309.734 | 51.573 | 67.13 | 45.773 | 82.514 |  | 25.1458 | 12.7 | 12.2
| 8.3889 | 309.653 | 51.524 | 67.081 | 45.732 | 82.451 |  | 25.1667 | 12.6 | 12.2
| 8.3958 | 309.852 | 51.49 | 67.04 | 45.708 | 82.393 |  | 25.1875 | 12.4 | 12.2
| 8.4028 | 308.353 | 51.438 | 66.986 | 45.666 | 82.32 |  | 25.2083 | 12.3 | 12.2
| 8.4097 | 308.151 | 51.363 | 66.913 | 45.606 | 82.221 |  | 25.2292 | 12.3 | 12.2
| 8.4167 | 307.162 | 51.287 | 66.835 | 45.55 | 82.119 |  | 25.25 | 12 | 12.2
| 8.4236 | 307.452 | 51.221 | 66.755 | 45.491 | 82.013 |  | 25.2708 | 11.7 | 12.2
| 8.4306 | 310.673 | 51.348 | 66.827 | 45.59 | 82.116 |  | 25.2917 | 11.7 | 12.2
| 8.4375 | 310.993 | 51.408 | 66.86 | 45.644 | 82.161 |  | 25.3125 | 11.6 | 12.2
| 8.4444 | 310.864 | 51.436 | 66.869 | 45.656 | 82.187 |  | 25.3333 | 11.6 | 12.2
| 8.4514 | 310.312 | 51.435 | 66.864 | 45.653 | 82.185 |  | 25.3542 | 11.6 | 12.2
| 8.4583 | 309.951 | 51.426 | 66.855 | 45.65 | 82.177 |  | 25.375 | 11.8 | 12.2
| 8.4653 | 310.237 | 51.401 | 66.825 | 45.62 | 82.148 |  | 25.3958 | 12 | 12.2
| 8.4722 | 309.906 | 51.39 | 66.809 | 45.61 | 82.127 |  | 25.4167 | 12 | 12.2
| 8.4792 | 308.593 | 51.357 | 66.777 | 45.587 | 82.086 |  | 25.4375 | 11.7 | 12.2
| 8.4861 | 308.948 | 51.312 | 66.737 | 45.553 | 82.039 |  | 25.4583 | 11.6 | 12.2
| 8.4931 | 308.726 | 51.294 | 66.706 | 45.53 | 81.999 |  | 25.4792 | 12.4 | 12.2
| 8.5 | 308.322 | 51.261 | 66.673 | 45.508 | 81.959 |  | 25.5 | 13.2 | 12.2
| 8.5069 | 308.261 | 51.242 | 66.637 | 45.486 | 81.916 |  | 25.5208 | 12.9 | 12.2
| 8.5139 | 308.157 | 51.188 | 66.583 | 45.442 | 81.844 |  | 25.5417 | 14.2 | 12.2
| 8.5208 | 311.16 | 51.31 | 66.661 | 45.538 | 81.957 |  | 25.5625 | 14.4 | 12.2
| 8.5278 | 310.942 | 51.361 | 66.697 | 45.578 | 82.013 |  | 25.5833 | 14.8 | 12.2
| 8.5347 | 311.006 | 51.407 | 66.728 | 45.616 | 82.062 |  | 25.6042 | 14.9 | 12.2
| 8.5417 | 310.599 | 51.42 | 66.747 | 45.626 | 82.087 |  | 25.625 | 14.6 | 12.2
| 8.5486 | 310.854 | 51.418 | 66.745 | 45.611 | 82.098 |  | 25.6458 | 14.6 | 12.2
| 8.5556 | 310.175 | 51.408 | 66.736 | 45.605 | 82.093 |  | 25.6667 | 13.5 | 12.2
| 8.5625 | 310.414 | 51.398 | 66.733 | 45.601 | 82.096 |  | 25.6875 | 12.1 | 12.2
| 8.5694 | 310.511 | 51.404 | 66.73 | 45.599 | 82.099 |  | 25.7083 | 10.6 | 12.2
| 8.5764 | 310.918 | 51.425 | 66.749 | 45.617 | 82.129 |  | 25.7292 | 9.7 | 12.2
| 8.5833 | 310.714 | 51.459 | 66.775 | 45.638 | 82.167 |  | 25.75 | 8.7 | 12.2
| 8.5903 | 311.266 | 51.486 | 66.808 | 45.666 | 82.209 |  | 25.7708 | 7.8 | 12.2
| 8.5972 | 312.343 | 51.518 | 66.826 | 45.689 | 82.248 |  | 25.7917 | 7.8 | 12.2
| 8.6042 | 312.581 | 51.569 | 66.875 | 45.729 | 82.312 |  | 25.8125 | 7.4 | 12.2
| 8.6111 | 312.879 | 51.606 | 66.916 | 45.758 | 82.372 |  | 25.8333 | 8.8 | 12.2
| 8.6181 | 312.461 | 51.631 | 66.946 | 45.774 | 82.412 |  | 25.8542 | 9.4 | 12.2
| 8.625 | 312.916 | 51.66 | 66.988 | 45.805 | 82.474 |  | 25.875 | 10.2 | 12.2
| 8.6319 | 314.348 | 51.712 | 67.038 | 45.841 | 82.542 |  | 25.8958 | 10.8 | 12.2
| 8.6389 | 310.128 | 51.606 | 66.977 | 45.763 | 82.462 |  | 25.9167 | 10.8 | 12.2
| 8.6458 | 310.399 | 51.517 | 66.912 | 45.691 | 82.379 |  | 25.9375 | 10.8 | 12.2
| 8.6528 | 310.009 | 51.49 | 66.879 | 45.665 | 82.338 |  | 25.9583 | 10.9 | 12.2
| 8.6597 | 310.234 | 51.477 | 66.862 | 45.657 | 82.315 |  | 25.9792 | 10.8 | 12.2
| 8.6667 | 310.262 | 51.469 | 66.854 | 45.647 | 82.296 |  | 26 | 10.8 | 12.2
| 8.6736 | 310.68 | 51.452 | 66.838 | 45.635 | 82.277 |  | 26.0208 | 10.8 | 12.2
| 8.6806 | 310.23 | 51.444 | 66.823 | 45.629 | 82.257 |  | 26.0417 | 10.9 | 12.2
| 8.6875 | 310.531 | 51.422 | 66.805 | 45.615 | 82.227 |  | 26.0625 | 11 | 12.2
| 8.6944 | 309.783 | 51.408 | 66.788 | 45.601 | 82.209 |  | 26.0833 | 10.9 | 12.2
| 8.7014 | 310.366 | 51.385 | 66.763 | 45.579 | 82.164 |  | 26.1042 | 11 | 12.2
| 8.7083 | 310.465 | 51.362 | 66.743 | 45.566 | 82.141 |  | 26.125 | 11 | 12.2
| 8.7153 | 310.112 | 51.36 | 66.725 | 45.56 | 82.127 |  | 26.1458 | 10.7 | 12.2
| 8.7222 | 309.737 | 51.327 | 66.699 | 45.536 | 82.083 |  | 26.1667 | 10.6 | 12.2
| 8.7292 | 308.792 | 51.289 | 66.658 | 45.507 | 82.029 |  | 26.1875 | 10.5 | 12.2
| 8.7361 | 308.117 | 51.223 | 66.598 | 45.459 | 81.95 |  | 26.2083 | 10.4 | 12.2
| 8.7431 | 307.95 | 51.169 | 66.54 | 45.413 | 81.865 |  | 26.2292 | 10.6 | 12.2
| 8.75 | 310.529 | 51.281 | 66.611 | 45.497 | 81.967 |  | 26.25 | 10.4 | 12.2
| 8.7569 | 306.419 | 51.243 | 66.58 | 45.469 | 81.928 |  | 26.2708 | 10.6 | 12.2
| 8.7639 | 313.579 | 51.35 | 66.643 | 45.546 | 82.025 |  | 26.2917 | 10.7 | 12.2
| 8.7708 | 311.85 | 51.482 | 66.751 | 45.658 | 82.17 |  | 26.3125 | 10.8 | 12.2
| 8.7778 | 312.113 | 51.521 | 66.796 | 45.69 | 82.232 |  | 26.3333 | 11 | 12.2
| 8.7847 | 312.078 | 51.544 | 66.825 | 45.71 | 82.28 |  | 26.3542 | 11.2 | 12.2
| 8.7917 | 312.467 | 51.573 | 66.865 | 45.734 | 82.329 |  | 26.375 | 11.4 | 12.2
| 8.7986 | 311.675 | 51.598 | 66.898 | 45.756 | 82.376 |  | 26.3958 | 11.7 | 12.2
| 8.8056 | 311.714 | 51.609 | 66.918 | 45.757 | 82.408 |  | 26.4167 | 12.2 | 12.2
| 8.8125 | 313.025 | 51.642 | 66.956 | 45.792 | 82.457 |  | 26.4375 | 12.5 | 12.2
| 8.8194 | 313.527 | 51.692 | 67.013 | 45.831 | 82.527 |  | 26.4583 | 13.1 | 12.2
| 8.8264 | 313.482 | 51.739 | 67.06 | 45.865 | 82.598 |  | 26.4792 | 13.5 | 12.2
| 8.8333 | 313.798 | 51.777 | 67.114 | 45.901 | 82.664 |  | 26.5 | 14.1 | 12.2
| 8.8403 | 313.946 | 51.811 | 67.159 | 45.927 | 82.725 |  | 26.5208 | 14.6 | 12.2
| 8.8472 | 310.338 | 51.739 | 67.136 | 45.887 | 82.685 |  | 26.5417 | 14.3 | 12.2
| 8.8542 | 310.659 | 51.624 | 67.046 | 45.785 | 82.567 |  | 26.5625 | 14.6 | 12.2
| 8.8611 | 310.504 | 51.582 | 67.018 | 45.756 | 82.523 |  | 26.5833 | 15 | 12.2
| 8.8681 | 310.268 | 51.568 | 67.004 | 45.744 | 82.498 |  | 26.6042 | 15.1 | 12.2
| 8.875 | 311.267 | 51.58 | 67.006 | 45.756 | 82.489 |  | 26.625 | 14.5 | 12.2
| 8.8819 | 311.021 | 51.584 | 67.01 | 45.761 | 82.5 |  | 26.6458 | 14.1 | 12.2
| 8.8889 | 312.458 | 51.617 | 67.038 | 45.784 | 82.521 |  | 26.6667 | 13.7 | 12.2
| 8.8958 | 312.081 | 51.663 | 67.075 | 45.829 | 82.571 |  | 26.6875 | 13 | 12.2
| 8.9028 | 313.264 | 51.688 | 67.101 | 45.848 | 82.608 |  | 26.7083 | 12.2 | 12.2
| 8.9097 | 311.674 | 51.7 | 67.121 | 45.861 | 82.627 |  | 26.7292 | 11.3 | 12.2
| 8.9167 | 311.904 | 51.684 | 67.113 | 45.846 | 82.624 |  | 26.75 | 10.2 | 12.2
| 8.9236 | 312.88 | 51.689 | 67.128 | 45.855 | 82.637 |  | 26.7708 | 9.8 | 12.2
| 8.9306 | 313.145 | 51.725 | 67.158 | 45.885 | 82.671 |  | 26.7917 | 9.9 | 12.2
| 8.9375 | 313.12 | 51.762 | 67.195 | 45.915 | 82.724 |  | 26.8125 | 9.9 | 12.2
| 8.9444 | 313.321 | 51.786 | 67.223 | 45.934 | 82.759 |  | 26.8333 | 8.9 | 12.2
| 8.9514 | 313.07 | 51.813 | 67.252 | 45.958 | 82.791 |  | 26.8542 | 8.8 | 12.2
| 8.9583 | 313.569 | 51.845 | 67.29 | 45.976 | 82.84 |  | 26.875 | 8.5 | 12.2
| 8.9653 | 310.529 | 51.683 | 67.192 | 45.856 | 82.696 |  | 26.8958 | 7.8 | 12.2
| 8.9722 | 310.488 | 51.623 | 67.138 | 45.813 | 82.622 |  | 26.9167 | 7.1 | 12.2
| 8.9792 | 308.882 | 51.524 | 67.059 | 45.74 | 82.501 |  | 26.9375 | 6.8 | 12.2
| 8.9861 | 309.684 | 51.466 | 66.992 | 45.687 | 82.41 |  | 26.9583 | 6.6 | 12.2
| 8.9931 | 310.659 | 51.472 | 66.984 | 45.696 | 82.388 |  | 26.9792 | 6.3 | 12.2
| 9 | 310.062 | 51.487 | 66.979 | 45.706 | 82.372 |  | 27 | 5.8 | 12.2
| 9.0069 | 310.273 | 51.498 | 66.975 | 45.715 | 82.374 |  | 27.0208 | 5.3 | 12.2
| 9.0139 | 310.933 | 51.508 | 66.983 | 45.734 | 82.375 |  | 27.0417 | 4.8 | 12.2
| 9.0208 | 311.417 | 51.556 | 67.014 | 45.77 | 82.415 |  | 27.0625 | 4.2 | 12.2
| 9.0278 | 312.343 | 51.614 | 67.055 | 45.813 | 82.473 |  | 27.0833 | 3.8 | 12.2
| 9.0347 | 312.495 | 51.689 | 67.121 | 45.882 | 82.556 |  | 27.1042 | 3.8 | 12.2
| 9.0417 | 312.684 | 51.721 | 67.158 | 45.899 | 82.605 |  | 27.125 | 3.4 | 12.2
| 9.0486 | 312.183 | 51.729 | 67.176 | 45.906 | 82.63 |  | 27.1458 | 3.6 | 12.2
| 9.0556 | 311.628 | 51.741 | 67.193 | 45.92 | 82.654 |  | 27.1667 | 3.8 | 12.2
| 9.0625 | 312.59 | 51.77 | 67.219 | 45.933 | 82.688 |  | 27.1875 | 3.3 | 12.2
| 9.0694 | 311.166 | 51.782 | 67.249 | 45.953 | 82.72 |  | 27.2083 | 3.3 | 12.2
| 9.0764 | 311.589 | 51.751 | 67.234 | 45.934 | 82.7 |  | 27.2292 | 3.4 | 12.2
| 9.0833 | 311.835 | 51.751 | 67.241 | 45.937 | 82.708 |  | 27.25 | 3.4 | 12.2
| 9.0903 | 311.436 | 51.773 | 67.262 | 45.951 | 82.734 |  | 27.2708 | 3.5 | 12.2
| 9.0972 | 311.372 | 51.778 | 67.27 | 45.951 | 82.738 |  | 27.2917 | 5.9 | 12.2
| 9.1042 | 311.665 | 51.785 | 67.285 | 45.962 | 82.758 |  | 27.3125 | 5.4 | 12.2
| 9.1111 | 311.306 | 51.76 | 67.272 | 45.949 | 82.739 |  | 27.3333 | 5.7 | 12.2
| 9.1181 | 311.037 | 51.751 | 67.271 | 45.942 | 82.735 |  | 27.3542 | 6.8 | 12.2
| 9.125 | 311.209 | 51.758 | 67.276 | 45.947 | 82.735 |  | 27.375 | 7.4 | 12.2
| 9.1319 | 311.353 | 51.754 | 67.279 | 45.945 | 82.73 |  | 27.3958 | 7.6 | 12.2
| 9.1389 | 311.735 | 51.757 | 67.279 | 45.944 | 82.731 |  | 27.4167 | 7.8 | 12.2
| 9.1458 | 311.624 | 51.765 | 67.286 | 45.949 | 82.739 |  | 27.4375 | 8.4 | 12.2
| 9.1528 | 311.307 | 51.767 | 67.294 | 45.956 | 82.748 |  | 27.4583 | 8.7 | 12.2
| 9.1597 | 311.183 | 51.769 | 67.3 | 45.96 | 82.749 |  | 27.4792 | 9 | 12.2
| 9.1667 | 311.183 | 51.777 | 67.304 | 45.964 | 82.753 |  | 27.5 | 10.3 | 12.2
| 9.1736 | 311.451 | 51.776 | 67.311 | 45.972 | 82.76 |  | 27.5208 | 10.3 | 12.2
| 9.1806 | 311.25 | 51.773 | 67.315 | 45.969 | 82.754 |  | 27.5417 | 10.4 | 12.2
| 9.1875 | 311.255 | 51.776 | 67.319 | 45.97 | 82.765 |  | 27.5625 | 10.8 | 12.2
| 9.1944 | 310.776 | 51.767 | 67.308 | 45.963 | 82.752 |  | 27.5833 | 10.9 | 12.2
| 9.2014 | 310.707 | 51.729 | 67.286 | 45.933 | 82.716 |  | 27.6042 | 11.3 | 12.2
| 9.2083 | 310.639 | 51.728 | 67.278 | 45.934 | 82.704 |  | 27.625 | 11.4 | 12.2
| 9.2153 | 310.493 | 51.709 | 67.263 | 45.925 | 82.681 |  | 27.6458 | 11.6 | 12.2
| 9.2222 | 310.081 | 51.689 | 67.243 | 45.909 | 82.654 |  | 27.6667 | 11.4 | 12.2
| 9.2292 | 309.953 | 51.662 | 67.224 | 45.892 | 82.621 |  | 27.6875 | 11.2 | 12.2
| 9.2361 | 308.655 | 51.617 | 67.182 | 45.857 | 82.561 |  | 27.7083 | 11.7 | 12.2
| 9.2431 | 308.662 | 51.57 | 67.135 | 45.819 | 82.5 |  | 27.7292 | 11.6 | 12.2
| 9.25 | 309.152 | 51.534 | 67.093 | 45.786 | 82.439 |  | 27.75 | 11.7 | 12.2
| 9.2569 | 308.578 | 51.499 | 67.051 | 45.763 | 82.381 |  | 27.7708 | 12 | 12.2
| 9.2639 | 308.681 | 51.483 | 67.027 | 45.75 | 82.344 |  | 27.7917 | 12.1 | 12.2
| 9.2708 | 311.79 | 51.447 | 66.987 | 45.719 | 82.285 |  | 27.8125 | 12.1 | 12.2
| 9.2778 | 309.248 | 51.58 | 67.08 | 45.833 | 82.414 |  | 27.8333 | 12.2 | 12.2
| 9.2847 | 313.028 | 51.594 | 67.074 | 45.829 | 82.414 |  | 27.8542 | 11.5 | 12.2
| 9.2917 | 312.815 | 51.755 | 67.204 | 45.959 | 82.59 |  | 27.875 | 10.7 | 12.2
| 9.2986 | 313.445 | 51.838 | 67.284 | 46.03 | 82.697 |  | 27.8958 | 10.9 | 12.2
| 9.3056 | 311.322 | 51.847 | 67.309 | 46.038 | 82.741 |  | 27.9167 | 11.1 | 12.2
| 9.3125 | 312.723 | 51.896 | 67.356 | 46.077 | 82.813 |  | 27.9375 | 10.4 | 12.2
| 9.3194 | 312.993 | 51.941 | 67.413 | 46.112 | 82.889 |  | 27.9583 | 9.7 | 12.2
| 9.3264 | 310.235 | 51.935 | 67.434 | 46.112 | 82.909 |  | 27.9792 | 8.6 | 12.2
| 9.3333 | 309.762 | 51.797 | 67.335 | 45.989 | 82.78 |  | 28 | 8.4 | 12.2
| 9.3403 | 308.702 | 51.713 | 67.269 | 45.928 | 82.688 |  | 28.0208 | 7.9 | 12.2
| 9.3472 | 311.957 | 51.7 | 67.248 | 45.907 | 82.667 |  | 28.0417 | 7 | 12.2
| 9.3542 | 312.15 | 51.798 | 67.326 | 45.995 | 82.754 |  | 28.0625 | 6.7 | 12.2
| 9.3611 | 311.823 | 51.793 | 67.326 | 46.003 | 82.761 |  | 28.0833 | 6.4 | 12.2
| 9.3681 | 309.869 | 51.77 | 67.312 | 45.984 | 82.744 |  | 28.1042 | 5.4 | 12.2
| 9.375 | 310.147 | 51.716 | 67.264 | 45.938 | 82.683 |  | 28.125 | 6.7 | 12.2
| 9.3819 | 309.45 | 51.665 | 67.223 | 45.892 | 82.626 |  | 28.1458 | 6.9 | 12.2
| 9.3889 | 310.112 | 51.644 | 67.195 | 45.877 | 82.586 |  | 28.1667 | 6.7 | 12.2
| 9.3958 | 310.35 | 51.632 | 67.175 | 45.862 | 82.563 |  | 28.1875 | 6.9 | 12.2
| 9.4028 | 310.768 | 51.642 | 67.172 | 45.869 | 82.555 |  | 28.2083 | 6.6 | 12.2
| 9.4097 | 311.047 | 51.671 | 67.191 | 45.898 | 82.582 |  | 28.2292 | 6.6 | 12.2
| 9.4167 | 310.989 | 51.687 | 67.203 | 45.908 | 82.599 |  | 28.25 | 6.8 | 12.2
| 9.4236 | 310.978 | 51.675 | 67.185 | 45.897 | 82.585 |  | 28.2708 | 6.8 | 12.2
| 9.4306 | 310.255 | 51.656 | 67.168 | 45.882 | 82.562 |  | 28.2917 | 6.6 | 12.2
| 9.4375 | 310.1 | 51.611 | 67.129 | 45.843 | 82.511 |  | 28.3125 | 6.6 | 12.2
| 9.4444 | 310.352 | 51.561 | 67.084 | 45.808 | 82.45 |  | 28.3333 | 6.8 | 12.2
| 9.4514 | 310.105 | 51.542 | 67.061 | 45.792 | 82.417 |  | 28.3542 | 7.5 | 12.2
| 9.4583 | 310.32 | 51.519 | 67.027 | 45.774 | 82.379 |  | 28.375 | 8.1 | 12.2
| 9.4653 | 309.363 | 51.495 | 67 | 45.755 | 82.342 |  | 28.3958 | 8.6 | 12.2
| 9.4722 | 309.299 | 51.446 | 66.944 | 45.701 | 82.27 |  | 28.4167 | 9.2 | 12.2
| 9.4792 | 309.138 | 51.43 | 66.917 | 45.692 | 82.232 |  | 28.4375 | 9.2 | 12.2
| 9.4861 | 308.806 | 51.393 | 66.876 | 45.666 | 82.181 |  | 28.4583 | 9.4 | 12.2
| 9.4931 | 308.68 | 51.368 | 66.839 | 45.644 | 82.134 |  | 28.4792 | 9.6 | 12.2
| 9.5 | 307.997 | 51.312 | 66.775 | 45.597 | 82.059 |  | 28.5 | 9.9 | 12.2
| 9.5069 | 308.357 | 51.25 | 66.71 | 45.548 | 81.97 |  | 28.5208 | 10.7 | 12.2
| 9.5139 | 307.606 | 51.201 | 66.651 | 45.509 | 81.897 |  | 28.5417 | 10.4 | 12.2
| 9.5208 | 307.566 | 51.168 | 66.606 | 45.482 | 81.833 |  | 28.5625 | 10.1 | 12.2
| 9.5278 | 308.23 | 51.159 | 66.566 | 45.463 | 81.795 |  | 28.5833 | 10.2 | 12.2
| 9.5347 | 309.301 | 51.182 | 66.566 | 45.484 | 81.792 |  | 28.6042 | 10.2 | 12.2
| 9.5417 | 309.199 | 51.208 | 66.569 | 45.501 | 81.799 |  | 28.625 | 10.4 | 12.2
| 9.5486 | 309.506 | 51.223 | 66.563 | 45.508 | 81.803 |  | 28.6458 | 10.4 | 12.2
| 9.5556 | 308.215 | 51.219 | 66.554 | 45.5 | 81.793 |  | 28.6667 | 10.2 | 12.2
| 9.5625 | 308.832 | 51.198 | 66.526 | 45.482 | 81.77 |  | 28.6875 | 10 | 12.2
| 9.5694 | 308.752 | 51.19 | 66.51 | 45.475 | 81.744 |  | 28.7083 | 9.7 | 12.2
| 9.5764 | 308.214 | 51.154 | 66.467 | 45.445 | 81.704 |  | 28.7292 | 9.9 | 12.2
| 9.5833 | 308.233 | 51.11 | 66.428 | 45.408 | 81.649 |  | 28.75 | 9.6 | 12.2
| 9.5903 | 307.433 | 51.079 | 66.385 | 45.38 | 81.602 |  | 28.7708 | 9.5 | 12.2
| 9.5972 | 307.079 | 51.045 | 66.336 | 45.351 | 81.544 |  | 28.7917 | 9.6 | 12.2
| 9.6042 | 307.628 | 51.04 | 66.318 | 45.345 | 81.522 |  | 28.8125 | 9.5 | 12.2
| 9.6111 | 308.388 | 51.023 | 66.286 | 45.325 | 81.489 |  | 28.8333 | 9.4 | 12.2
| 9.6181 | 306.458 | 50.986 | 66.248 | 45.297 | 81.441 |  | 28.8542 | 9.3 | 12.2
| 9.625 | 306.967 | 50.968 | 66.211 | 45.28 | 81.399 |  | 28.875 | 9.3 | 12.2
| 9.6319 | 307.66 | 50.953 | 66.18 | 45.264 | 81.367 |  | 28.8958 | 9.3 | 12.2
| 9.6389 | 307.42 | 50.946 | 66.159 | 45.258 | 81.351 |  | 28.9167 | 9.2 | 12.2
| 9.6458 | 307.761 | 50.961 | 66.156 | 45.267 | 81.35 |  | 28.9375 | 9.3 | 12.2
| 9.6528 | 308.228 | 50.976 | 66.155 | 45.272 | 81.353 |  | 28.9583 | 8.8 | 12.2
| 9.6597 | 307.761 | 50.978 | 66.148 | 45.267 | 81.349 |  | 28.9792 | 8.4 | 12.2
| 9.6667 | 307.175 | 50.98 | 66.135 | 45.269 | 81.342 |  | 29 | 8.1 | 12.2
| 9.6736 | 308.742 | 50.996 | 66.14 | 45.28 | 81.362 |  | 29.0208 | 7.5 | 12.2
| 9.6806 | 308.396 | 51.011 | 66.143 | 45.291 | 81.38 |  | 29.0417 | 7.7 | 12.2
| 9.6875 | 308.73 | 51.048 | 66.172 | 45.317 | 81.42 |  | 29.0625 | 7.9 | 12.2
| 9.6944 | 308.865 | 51.085 | 66.199 | 45.344 | 81.464 |  | 29.0833 | 9.2 | 12.2
| 9.7014 | 310.064 | 51.123 | 66.223 | 45.371 | 81.51 |  | 29.1042 | 9.4 | 12.2
| 9.7083 | 310.733 | 51.175 | 66.269 | 45.41 | 81.582 |  | 29.125 | 9.4 | 12.2
| 9.7153 | 310.766 | 51.215 | 66.308 | 45.437 | 81.64 |  | 29.1458 | 9.5 | 12.2
| 9.7222 | 310.457 | 51.226 | 66.331 | 45.446 | 81.674 |  | 29.1667 | 9.7 | 12.2
| 9.7292 | 309.241 | 51.222 | 66.332 | 45.441 | 81.686 |  | 29.1875 | 9.9 | 12.2
| 9.7361 | 309.95 | 51.227 | 66.346 | 45.451 | 81.709 |  | 29.2083 | 9 | 12.2
| 9.7431 | 309.405 | 51.229 | 66.351 | 45.449 | 81.717 |  | 29.2292 | 9.5 | 12.2
| 9.75 | 308.678 | 51.189 | 66.328 | 45.414 | 81.689 |  | 29.25 | 9.9 | 12.2
| 9.7569 | 307.581 | 51.108 | 66.273 | 45.356 | 81.609 |  | 29.2708 | 10.2 | 11.7
| 9.7639 | 311.594 | 51.205 | 66.323 | 45.42 | 81.699 |  | 29.2917 | 10.3 | 11.7
| 9.7708 | 311.226 | 51.302 | 66.407 | 45.503 | 81.813 |  | 29.3125 | 10.3 | 11.7
| 9.7778 | 312.329 | 51.363 | 66.471 | 45.553 | 81.893 |  | 29.3333 | 10.4 | 11.7
| 9.7847 | 312.311 | 51.437 | 66.544 | 45.614 | 82 |  | 29.3542 | 10.7 | 11.7
| 9.7917 | 311.907 | 51.471 | 66.592 | 45.642 | 82.061 |  | 29.375 | 10.9 | 11.7
| 9.7986 | 312.187 | 51.498 | 66.629 | 45.658 | 82.124 |  | 29.3958 | 11.3 | 11.7
| 9.8056 | 312.826 | 51.528 | 66.673 | 45.679 | 82.179 |  | 29.4167 | 11.4 | 11.7
| 9.8125 | 313.46 | 51.578 | 66.73 | 45.717 | 82.256 |  | 29.4375 | 11.7 | 11.7
| 9.8194 | 313.524 | 51.646 | 66.803 | 45.775 | 82.359 |  | 29.4583 | 12.1 | 11.7
| 9.8264 | 313.998 | 51.689 | 66.865 | 45.814 | 82.438 |  | 29.4792 | 12.3 | 11.7
| 9.8333 | 314.204 | 51.755 | 66.935 | 45.866 | 82.542 |  | 29.5 | 12.6 | 11.7
| 9.8403 | 310.475 | 51.665 | 66.906 | 45.808 | 82.493 |  | 29.5208 | 12.8 | 11.7
| 9.8472 | 310.429 | 51.576 | 66.851 | 45.726 | 82.406 |  | 29.5417 | 12.9 | 11.7
| 9.8542 | 311.532 | 51.549 | 66.837 | 45.71 | 82.383 |  | 29.5625 | 13.3 | 11.7
| 9.8611 | 313.119 | 51.564 | 66.844 | 45.721 | 82.399 |  | 29.5833 | 13.4 | 11.7
| 9.8681 | 309.624 | 51.46 | 66.78 | 45.647 | 82.3 |  | 29.6042 | 13.6 | 11.7
| 9.875 | 309.091 | 51.42 | 66.747 | 45.615 | 82.244 |  | 29.625 | 13.4 | 11.7
| 9.8819 | 310.596 | 51.423 | 66.743 | 45.62 | 82.235 |  | 29.6458 | 13.6 | 11.7
| 9.8889 | 310.462 | 51.458 | 66.768 | 45.656 | 82.265 |  | 29.6667 | 13.3 | 11.7
| 9.8958 | 311.581 | 51.501 | 66.804 | 45.69 | 82.3 |  | 29.6875 | 13 | 11.7
| 9.9028 | 312.366 | 51.557 | 66.853 | 45.735 | 82.371 |  | 29.7083 | 12.8 | 11.7
| 9.9097 | 311.4 | 51.584 | 66.882 | 45.759 | 82.404 |  | 29.7292 | 12.7 | 11.7
| 9.9167 | 312.105 | 51.602 | 66.909 | 45.769 | 82.437 |  | 29.75 | 12.5 | 11.7
| 9.9236 | 311.825 | 51.634 | 66.944 | 45.796 | 82.479 |  | 29.7708 | 11.9 | 11.7
| 9.9306 | 313.341 | 51.687 | 66.998 | 45.841 | 82.549 |  | 29.7917 | 11.6 | 11.7
| 9.9375 | 313.635 | 51.744 | 67.059 | 45.895 | 82.628 |  | 29.8125 | 11.3 | 11.7
| 9.9444 | 311.582 | 51.731 | 67.076 | 45.886 | 82.64 |  | 29.8333 | 11.3 | 11.7
| 9.9514 | 311.989 | 51.717 | 67.08 | 45.876 | 82.645 |  | 29.8542 | 10.7 | 11.7
| 9.9583 | 312.622 | 51.73 | 67.092 | 45.882 | 82.66 |  | 29.875 | 9.4 | 11.7
| 9.9653 | 313.537 | 51.767 | 67.136 | 45.92 | 82.716 |  | 29.8958 | 9.6 | 11.7
| 9.9722 | 314.119 | 51.854 | 67.222 | 45.985 | 82.817 |  | 29.9167 | 9.7 | 11.7
| 9.9792 | 310.803 | 51.793 | 67.198 | 45.94 | 82.772 |  | 29.9375 | 10.1 | 11.7
| 9.9861 | 310.536 | 51.713 | 67.149 | 45.876 | 82.701 |  | 29.9583 | 10.5 | 11.7
| 9.9931 | 311.589 | 51.707 | 67.146 | 45.877 | 82.695 |  | 29.9792 | 10.9 | 11.7
| 10 | 311.255 | 51.714 | 67.159 | 45.889 | 82.696 |  | 30 | 10.8 | 11.7
| 10.0069 | 312.348 | 51.738 | 67.174 | 45.907 | 82.723 |  | 30.0208 | 10.6 | 11.7
| 10.0139 | 312.348 | 51.784 | 67.218 | 45.943 | 82.769 |  | 30.0417 | 10.5 | 11.7
| 10.0208 | 312.731 | 51.824 | 67.261 | 45.985 | 82.821 |  | 30.0625 | 10.8 | 11.7
| 10.0278 | 313.064 | 51.866 | 67.312 | 46.02 | 82.88 |  | 30.0833 | 11 | 11.7
| 10.0347 | 313.3 | 51.913 | 67.359 | 46.056 | 82.94 |  | 30.1042 | 10.5 | 11.7
| 10.0417 | 314.118 | 51.95 | 67.408 | 46.094 | 83.003 |  | 30.125 | 9.3 | 11.7
| 10.0486 | 313.914 | 51.994 | 67.458 | 46.122 | 83.059 |  | 30.1458 | 8.1 | 11.7
| 10.0556 | 310.002 | 51.893 | 67.408 | 46.052 | 82.992 |  | 30.1667 | 8.3 | 11.7
| 10.0625 | 309.965 | 51.773 | 67.321 | 45.959 | 82.859 |  | 30.1875 | 8.2 | 11.7
| 10.0694 | 311.626 | 51.74 | 67.288 | 45.929 | 82.812 |  | 30.2083 | 8.8 | 11.7
| 10.0764 | 311.627 | 51.768 | 67.308 | 45.956 | 82.827 |  | 30.2292 | 8.2 | 11.7
| 10.0833 | 311.42 | 51.769 | 67.307 | 45.96 | 82.819 |  | 30.25 | 6.6 | 11.7
| 10.0903 | 312.397 | 51.778 | 67.313 | 45.966 | 82.825 |  | 30.2708 | 5.6 | 11.7
| 10.0972 | 311.371 | 51.779 | 67.319 | 45.97 | 82.819 |  | 30.2917 | 6.8 | 11.7
| 10.1042 | 311.874 | 51.784 | 67.324 | 45.977 | 82.823 |  | 30.3125 | 6.3 | 11.7
| 10.1111 | 311.856 | 51.812 | 67.345 | 45.996 | 82.848 |  | 30.3333 | 5.3 | 11.7
| 10.1181 | 313.403 | 51.854 | 67.38 | 46.034 | 82.893 |  | 30.3542 | 6.2 | 11.7
| 10.125 | 312.437 | 51.892 | 67.424 | 46.068 | 82.944 |  | 30.375 | 8.7 | 11.7
| 10.1319 | 312.608 | 51.898 | 67.436 | 46.076 | 82.961 |  | 30.3958 | 9.7 | 11.7
| 10.1389 | 312.469 | 51.88 | 67.433 | 46.061 | 82.95 |  | 30.4167 | 10.8 | 11.7
| 10.1458 | 312.344 | 51.87 | 67.419 | 46.049 | 82.94 |  | 30.4375 | 10.5 | 11.7
| 10.1528 | 312.267 | 51.868 | 67.433 | 46.051 | 82.937 |  | 30.4583 | 10.6 | 11.7
| 10.1597 | 312.374 | 51.882 | 67.445 | 46.064 | 82.957 |  | 30.4792 | 10.7 | 11.7
| 10.1667 | 312.464 | 51.905 | 67.468 | 46.085 | 82.982 |  | 30.5 | 10.7 | 11.7
| 10.1736 | 313.114 | 51.922 | 67.483 | 46.094 | 83.005 |  | 30.5208 | 10.5 | 11.7
| 10.1806 | 312.506 | 51.932 | 67.502 | 46.105 | 83.024 |  | 30.5417 | 10.3 | 11.7
| 10.1875 | 312.154 | 51.923 | 67.504 | 46.099 | 83.021 |  | 30.5625 | 10.2 | 11.7
| 10.1944 | 311.776 | 51.905 | 67.493 | 46.089 | 83.008 |  | 30.5833 | 10.3 | 11.7
| 10.2014 | 311.272 | 51.877 | 67.477 | 46.068 | 82.984 |  | 30.6042 | 10.4 | 11.7
| 10.2083 | 311.562 | 51.853 | 67.458 | 46.049 | 82.953 |  | 30.625 | 10.5 | 11.7
| 10.2153 | 311.419 | 51.844 | 67.449 | 46.042 | 82.937 |  | 30.6458 | 10.6 | 11.7
| 10.2222 | 311.287 | 51.824 | 67.43 | 46.022 | 82.911 |  | 30.6667 | 10.6 | 11.7
| 10.2292 | 310.17 | 51.794 | 67.402 | 46.002 | 82.87 |  | 30.6875 | 10.6 | 11.7
| 10.2361 | 309.719 | 51.753 | 67.364 | 45.97 | 82.813 |  | 30.7083 | 10.4 | 11.7
| 10.2431 | 311.91 | 51.788 | 67.379 | 45.994 | 82.838 |  | 30.7292 | 10.4 | 11.7
| 10.25 | 311.849 | 51.824 | 67.411 | 46.028 | 82.871 |  | 30.75 | 10.4 | 11.7
| 10.2569 | 311.874 | 51.837 | 67.41 | 46.034 | 82.879 |  | 30.7708 | 10.4 | 11.7
| 10.2639 | 311.318 | 51.83 | 67.413 | 46.038 | 82.878 |  | 30.7917 | 10.6 | 11.7
| 10.2708 | 310.754 | 51.801 | 67.386 | 46.006 | 82.845 |  | 30.8125 | 10.7 | 11.7
| 10.2778 | 312.203 | 51.816 | 67.394 | 46.019 | 82.853 |  | 30.8333 | 10.4 | 11.7
| 10.2847 | 308.615 | 51.735 | 67.339 | 45.965 | 82.778 |  | 30.8542 | 10.5 | 11.7
| 10.2917 | 312.016 | 51.623 | 67.246 | 45.868 | 82.644 |  | 30.875 | 10.8 | 11.7
| 10.2986 | 311.949 | 51.737 | 67.308 | 45.952 | 82.743 |  | 30.8958 | 10.8 | 11.7
| 10.3056 | 311.555 | 51.746 | 67.312 | 45.961 | 82.749 |  | 30.9167 | 10.4 | 11.7
| 10.3125 | 308.506 | 51.659 | 67.253 | 45.9 | 82.665 |  | 30.9375 | 10.5 | 11.7
| 10.3194 | 307.679 | 51.563 | 67.165 | 45.821 | 82.552 |  | 30.9583 | 10.4 | 11.7
| 10.3264 | 309.185 | 51.518 | 67.099 | 45.772 | 82.469 |  | 30.9792 | 10.6 | 11.7
| 10.3333 | 308.98 | 51.539 | 67.101 | 45.795 | 82.469 |  | 31 | 10.6 | 11.7
| 10.3403 | 309.412 | 51.515 | 67.075 | 45.781 | 82.432 |  | 31.0208 | 10.7 | 11.7
| 10.3472 | 308.625 | 51.489 | 67.036 | 45.759 | 82.381 |  | 31.0417 | 10 | 11.7
| 10.3542 | 307.318 | 51.449 | 66.995 | 45.725 | 82.32 |  | 31.0625 | 10.1 | 11.7
| 10.3611 | 306.469 | 51.362 | 66.91 | 45.656 | 82.212 |  | 31.0833 | 10.3 | 11.7
| 10.3681 | 308.894 | 51.379 | 66.896 | 45.662 | 82.201 |  | 31.1042 | 10.5 | 11.7
| 10.375 | 308.365 | 51.406 | 66.898 | 45.689 | 82.211 |  | 31.125 | 10.4 | 11.7
| 10.3819 | 308.945 | 51.418 | 66.892 | 45.69 | 82.202 |  | 31.1458 | 10.3 | 11.7
| 10.3889 | 310.089 | 51.441 | 66.898 | 45.71 | 82.218 |  | 31.1667 | 10.3 | 11.7
| 10.3958 | 311.841 | 51.586 | 66.998 | 45.827 | 82.369 |  | 31.1875 | 10.3 | 11.7
| 10.4028 | 309.434 | 51.652 | 67.063 | 45.881 | 82.455 |  | 31.2083 | 9.7 | 11.7
| 10.4097 | 309.558 | 51.554 | 66.993 | 45.798 | 82.37 |  | 31.2292 | 9.6 | 11.7
| 10.4167 | 307.735 | 51.476 | 66.935 | 45.733 | 82.295 |  | 31.25 | 9.7 | 11.7
| 10.4236 | 308.561 | 51.417 | 66.874 | 45.682 | 82.217 |  | 31.2708 | 9.8 | 11.7
| 10.4306 | 307.484 | 51.322 | 66.78 | 45.602 | 82.095 |  | 31.2917 | 10 | 11.7
| 10.4375 | 306.634 | 51.253 | 66.709 | 45.541 | 82.002 |  | 31.3125 | 10.1 | 11.7
| 10.4444 | 307.147 | 51.183 | 66.634 | 45.496 | 81.904 |  | 31.3333 | 10.3 | 11.7
| 10.4514 | 307.162 | 51.18 | 66.61 | 45.492 | 81.867 |  | 31.3542 | 10.6 | 11.7
| 10.4583 | 307.487 | 51.156 | 66.561 | 45.464 | 81.811 |  | 31.375 | 10.9 | 11.7
| 10.4653 | 306.085 | 51.123 | 66.514 | 45.44 | 81.753 |  | 31.3958 | 11.2 | 11.7
| 10.4722 | 309.095 | 51.104 | 66.46 | 45.402 | 81.7 |  | 31.4167 | 11.4 | 11.7
| 10.4792 | 309.738 | 51.232 | 66.551 | 45.515 | 81.819 |  | 31.4375 | 11.7 | 11.7
| 10.4861 | 309.079 | 51.274 | 66.575 | 45.547 | 81.86 |  | 31.4583 | 11.7 | 11.7
| 10.4931 | 310.058 | 51.321 | 66.612 | 45.579 | 81.915 |  | 31.4792 | 11.6 | 11.7
| 10.5 | 309.333 | 51.334 | 66.619 | 45.588 | 81.936 |  | 31.5 | 11.9 | 11.7
| 10.5069 | 309.614 | 51.327 | 66.611 | 45.578 | 81.937 |  | 31.5208 | 13.1 | 11.7
| 10.5139 | 308.947 | 51.311 | 66.6 | 45.57 | 81.933 |  | 31.5417 | 13.5 | 11.7
| 10.5208 | 309.875 | 51.348 | 66.622 | 45.591 | 81.976 |  | 31.5625 | 13.6 | 11.7
| 10.5278 | 311.57 | 51.42 | 66.674 | 45.644 | 82.052 |  | 31.5833 | 13.2 | 11.7
| 10.5347 | 311.254 | 51.486 | 66.73 | 45.693 | 82.131 |  | 31.6042 | 13.1 | 11.7
| 10.5417 | 311.266 | 51.539 | 66.782 | 45.731 | 82.213 |  | 31.625 | 13.6 | 11.7
| 10.5486 | 311.942 | 51.552 | 66.804 | 45.736 | 82.254 |  | 31.6458 | 12.9 | 11.7
| 10.5556 | 311.359 | 51.57 | 66.832 | 45.758 | 82.296 |  | 31.6667 | 13 | 11.7
| 10.5625 | 311.79 | 51.583 | 66.852 | 45.764 | 82.332 |  | 31.6875 | 13.4 | 11.7
| 10.5694 | 310.823 | 51.586 | 66.859 | 45.759 | 82.343 |  | 31.7083 | 13.8 | 11.7
| 10.5764 | 310.597 | 51.558 | 66.848 | 45.739 | 82.333 |  | 31.7292 | 13.1 | 11.7
| 10.5833 | 308.377 | 51.459 | 66.786 | 45.662 | 82.24 |  | 31.75 | 12.8 | 11.7
| 10.5903 | 311.527 | 51.509 | 66.807 | 45.689 | 82.292 |  | 31.7708 | 13 | 11.7
| 10.5972 | 312.744 | 51.587 | 66.873 | 45.754 | 82.381 |  | 31.7917 | 13.3 | 11.7
| 10.6042 | 309.324 | 51.519 | 66.833 | 45.706 | 82.335 |  | 31.8125 | 13.6 | 11.7
| 10.6111 | 309.99 | 51.465 | 66.781 | 45.649 | 82.272 |  | 31.8333 | 13.6 | 11.7
| 10.6181 | 309.979 | 51.44 | 66.762 | 45.636 | 82.246 |  | 31.8542 | 13.8 | 11.7
| 10.625 | 309.609 | 51.422 | 66.735 | 45.616 | 82.222 |  | 31.875 | 13.6 | 11.7
| 10.6319 | 310.602 | 51.444 | 66.746 | 45.632 | 82.238 |  | 31.8958 | 13.1 | 11.7
| 10.6389 | 310.544 | 51.437 | 66.747 | 45.636 | 82.236 |  | 31.9167 | 13.4 | 11.7
| 10.6458 | 310.581 | 51.463 | 66.765 | 45.645 | 82.265 |  | 31.9375 | 14.2 | 11.7
| 10.6528 | 310.589 | 51.509 | 66.796 | 45.681 | 82.311 |  | 31.9583 | 14.4 | 11.7
| 10.6597 | 310.966 | 51.533 | 66.817 | 45.698 | 82.348 |  | 31.9792 | 14.8 | 11.7
| 10.6667 | 312.868 | 51.582 | 66.859 | 45.736 | 82.41 |  | 32 | 15.2 | 11.7
| 10.6736 | 312.442 | 51.619 | 66.89 | 45.761 | 82.465 |  | 32.0208 | 15.3 | 11.7
| 10.6806 | 310.652 | 51.633 | 66.918 | 45.774 | 82.503 |  | 32.0417 | 15.3 | 11.7
| 10.6875 | 307.82 | 51.509 | 66.838 | 45.684 | 82.389 |  | 32.0625 | 15.2 | 11.7
| 10.6944 | 308.643 | 51.4 | 66.737 | 45.583 | 82.272 |  | 32.0833 | 15.3 | 11.7
| 10.7014 | 308.957 | 51.337 | 66.684 | 45.532 | 82.193 |  | 32.1042 | 15.3 | 11.7
| 10.7083 | 308.592 | 51.306 | 66.645 | 45.509 | 82.138 |  | 32.125 | 15.2 | 11.7
| 10.7153 | 309.219 | 51.3 | 66.616 | 45.499 | 82.108 |  | 32.1458 | 15.1 | 11.7
| 10.7222 | 307.969 | 51.27 | 66.589 | 45.482 | 82.072 |  | 32.1667 | 15.2 | 11.7
| 10.7292 | 308.341 | 51.239 | 66.548 | 45.45 | 82.017 |  | 32.1875 | 15.1 | 11.7
| 10.7361 | 308.302 | 51.177 | 66.489 | 45.404 | 81.941 |  | 32.2083 | 14.9 | 11.7
| 10.7431 | 306.313 | 51.117 | 66.425 | 45.355 | 81.859 |  | 32.2292 | 14.3 | 11.7
| 10.75 | 311.048 | 51.02 | 66.326 | 45.269 | 81.724 |  | 32.25 | 13.9 | 11.7
| 10.7569 | 310.68 | 51.227 | 66.461 | 45.435 | 81.917 |  | 32.2708 | 13.6 | 11.7
| 10.7639 | 310.378 | 51.302 | 66.512 | 45.491 | 81.993 |  | 32.2917 | 13.2 | 11.7
| 10.7708 | 311.325 | 51.339 | 66.55 | 45.522 | 82.048 |  | 32.3125 | 13.2 | 11.7
| 10.7778 | 311.129 | 51.385 | 66.579 | 45.551 | 82.103 |  | 32.3333 | 13.1 | 11.7
| 10.7847 | 310.65 | 51.432 | 66.627 | 45.592 | 82.17 |  | 32.3542 | 13.3 | 11.7
| 10.7917 | 312.124 | 51.446 | 66.649 | 45.598 | 82.206 |  | 32.375 | 12.8 | 11.7
| 10.7986 | 311.039 | 51.458 | 66.673 | 45.611 | 82.245 |  | 32.3958 | 13.4 | 11.7
| 10.8056 | 311.856 | 51.489 | 66.701 | 45.629 | 82.287 |  | 32.4167 | 13.7 | 11.7
| 10.8125 | 311.935 | 51.506 | 66.727 | 45.646 | 82.335 |  | 32.4375 | 13.8 | 11.7
| 10.8194 | 312.596 | 51.526 | 66.753 | 45.656 | 82.365 |  | 32.4583 | 13.9 | 11.7
| 10.8264 | 308.482 | 51.362 | 66.638 | 45.528 | 82.21 |  | 32.4792 | 14 | 11.7
| 10.8333 | 309.306 | 51.315 | 66.589 | 45.49 | 82.151 |  | 32.5 | 13.9 | 11.7
| 10.8403 | 310.738 | 51.315 | 66.583 | 45.49 | 82.143 |  | 32.5208 | 13.8 | 11.7
| 10.8472 | 310.849 | 51.354 | 66.613 | 45.521 | 82.175 |  | 32.5417 | 13.8 | 11.7
| 10.8542 | 310.985 | 51.387 | 66.629 | 45.543 | 82.206 |  | 32.5625 | 14.2 | 11.7
| 10.8611 | 310.596 | 51.392 | 66.641 | 45.556 | 82.223 |  | 32.5833 | 14.1 | 11.7
| 10.8681 | 310.82 | 51.388 | 66.637 | 45.544 | 82.217 |  | 32.6042 | 13.8 | 11.7
| 10.875 | 310.88 | 51.397 | 66.644 | 45.549 | 82.231 |  | 32.625 | 13.8 | 11.7
| 10.8819 | 312.067 | 51.426 | 66.674 | 45.577 | 82.272 |  | 32.6458 | 13.6 | 11.7
| 10.8889 | 308.349 | 51.45 | 66.697 | 45.602 | 82.305 |  | 32.6667 | 13.2 | 11.7
| 10.8958 | 308.805 | 51.275 | 66.561 | 45.454 | 82.123 |  | 32.6875 | 13.1 | 11.7
| 10.9028 | 308.421 | 51.262 | 66.543 | 45.445 | 82.095 |  | 32.7083 | 12.8 | 11.7
| 10.9097 | 308.66 | 51.224 | 66.505 | 45.417 | 82.042 |  | 32.7292 | 12.7 | 11.7
| 10.9167 | 308.151 | 51.185 | 66.469 | 45.39 | 81.986 |  | 32.75 | 11.8 | 11.7
| 10.9236 | 308.372 | 51.151 | 66.424 | 45.357 | 81.93 |  | 32.7708 | 11.4 | 11.7
| 10.9306 | 309.332 | 51.168 | 66.424 | 45.367 | 81.935 |  | 32.7917 | 11.4 | 11.7
| 10.9375 | 310.841 | 51.228 | 66.462 | 45.415 | 81.984 |  | 32.8125 | 11.8 | 11.7
| 10.9444 | 311.604 | 51.295 | 66.505 | 45.474 | 82.048 |  | 32.8333 | 12.6 | 11.7
| 10.9514 | 308.075 | 51.253 | 66.486 | 45.445 | 82.021 |  | 32.8542 | 12.2 | 11.7
| 10.9583 | 308.321 | 51.183 | 66.428 | 45.38 | 81.947 |  | 32.875 | 12.4 | 11.7
| 10.9653 | 309.315 | 51.151 | 66.395 | 45.353 | 81.902 |  | 32.8958 | 12.7 | 11.7
| 10.9722 | 310.292 | 51.197 | 66.419 | 45.387 | 81.938 |  | 32.9167 | 12.6 | 11.7
| 10.9792 | 310.861 | 51.264 | 66.47 | 45.443 | 82.005 |  | 32.9375 | 12.4 | 11.7
| 10.9861 | 311.997 | 51.346 | 66.534 | 45.511 | 82.097 |  | 32.9583 | 12.6 | 11.7
| 10.9931 | 308.89 | 51.258 | 66.482 | 45.434 | 82.026 |  | 32.9792 | 12.7 | 11.7
| 11 | 308.816 | 51.208 | 66.437 | 45.394 | 81.969 |  | 33 | 13.1 | 11.7
| 11.0069 | 308.716 | 51.186 | 66.417 | 45.38 | 81.941 |  | 33.0208 | 13.5 | 11.7
| 11.0139 | 309.257 | 51.198 | 66.42 | 45.39 | 81.943 |  | 33.0417 | 13.7 | 11.7
| 11.0208 | 309.587 | 51.199 | 66.423 | 45.396 | 81.942 |  | 33.0625 | 13.8 | 11.7
| 11.0278 | 310.302 | 51.213 | 66.428 | 45.405 | 81.954 |  | 33.0833 | 13.8 | 11.7
| 11.0347 | 310.079 | 51.234 | 66.442 | 45.422 | 81.973 |  | 33.1042 | 14.1 | 11.7
| 11.0417 | 309.767 | 51.249 | 66.457 | 45.439 | 81.999 |  | 33.125 | 13.9 | 11.7
| 11.0486 | 305 | 51.149 | 66.394 | 45.37 | 81.9 |  | 33.1458 | 14.1 | 11.7
| 11.0556 | 307.622 | 51.049 | 66.302 | 45.271 | 81.781 |  | 33.1667 | 14.1 | 11.7
| 11.0625 | 307.089 | 50.978 | 66.236 | 45.218 | 81.689 |  | 33.1875 | 14.3 | 11.7
| 11.0694 | 307.012 | 50.948 | 66.191 | 45.197 | 81.629 |  | 33.2083 | 14.3 | 11.7
| 11.0764 | 307.729 | 50.941 | 66.161 | 45.19 | 81.592 |  | 33.2292 | 14.2 | 11.7
| 11.0833 | 307.462 | 50.932 | 66.143 | 45.19 | 81.562 |  | 33.25 | 14.3 | 11.7
| 11.0903 | 308.046 | 50.918 | 66.119 | 45.174 | 81.533 |  | 33.2708 | 14.2 | 11.7
| 11.0972 | 307.226 | 50.911 | 66.103 | 45.162 | 81.509 |  | 33.2917 | 13.7 | 11.7
| 11.1042 | 307.688 | 50.914 | 66.084 | 45.172 | 81.491 |  | 33.3125 | 13.3 | 11.7
| 11.1111 | 308.022 | 50.913 | 66.078 | 45.159 | 81.474 |  | 33.3333 | 12.7 | 11.7
| 11.1181 | 308.578 | 50.942 | 66.094 | 45.186 | 81.505 |  | 33.3542 | 12.6 | 11.7
| 11.125 | 307.985 | 50.963 | 66.099 | 45.204 | 81.514 |  | 33.375 | 13.1 | 11.7
| 11.1319 | 308.519 | 50.967 | 66.098 | 45.204 | 81.516 |  | 33.3958 | 12.8 | 11.7
| 11.1389 | 308.043 | 50.962 | 66.094 | 45.2 | 81.511 |  | 33.4167 | 12.3 | 11.7
| 11.1458 | 308.167 | 50.956 | 66.083 | 45.191 | 81.497 |  | 33.4375 | 12.7 | 11.7
| 11.1528 | 308.032 | 50.947 | 66.072 | 45.187 | 81.482 |  | 33.4583 | 13.2 | 11.7
| 11.1597 | 308.314 | 50.938 | 66.061 | 45.176 | 81.475 |  | 33.4792 | 12.9 | 11.7
| 11.1667 | 308.074 | 50.931 | 66.054 | 45.171 | 81.461 |  | 33.5 | 13.7 | 11.7
| 11.1736 | 308.098 | 50.943 | 66.054 | 45.178 | 81.465 |  | 33.5208 | 13.9 | 11.7
| 11.1806 | 308.623 | 50.954 | 66.064 | 45.193 | 81.476 |  | 33.5417 | 14.3 | 11.7
| 11.1875 | 308.91 | 50.962 | 66.068 | 45.196 | 81.491 |  | 33.5625 | 14.3 | 11.7
| 11.1944 | 307.545 | 50.94 | 66.05 | 45.179 | 81.462 |  | 33.5833 | 14.2 | 11.7
| 11.2014 | 308.292 | 50.921 | 66.035 | 45.164 | 81.44 |  | 33.6042 | 14.3 | 11.7
| 11.2083 | 308.255 | 50.912 | 66.016 | 45.153 | 81.423 |  | 33.625 | 13.9 | 11.7
| 11.2153 | 307.592 | 50.891 | 65.999 | 45.141 | 81.399 |  | 33.6458 | 13.8 | 11.7
| 11.2222 | 307.759 | 50.871 | 65.982 | 45.127 | 81.375 |  | 33.6667 | 12.6 | 11.7
| 11.2292 | 307.606 | 50.857 | 65.961 | 45.109 | 81.351 |  | 33.6875 | 11.7 | 11.7
| 11.2361 | 306.01 | 50.801 | 65.917 | 45.069 | 81.283 |  | 33.7083 | 11.2 | 11.7
| 11.2431 | 310.141 | 50.845 | 65.928 | 45.102 | 81.308 |  | 33.7292 | 11.1 | 11.7
| 11.25 | 310.491 | 51.01 | 66.052 | 45.234 | 81.481 |  | 33.75 | 11 | 11.7
| 11.2569 | 309.648 | 51.042 | 66.094 | 45.258 | 81.53 |  | 33.7708 | 11.3 | 11.7
| 11.2639 | 309.867 | 51.083 | 66.129 | 45.285 | 81.591 |  | 33.7917 | 11.3 | 11.7
| 11.2708 | 312.993 | 51.154 | 66.201 | 45.345 | 81.689 |  | 33.8125 | 11.9 | 11.7
| 11.2778 | 308.351 | 51.073 | 66.159 | 45.28 | 81.622 |  | 33.8333 | 12.8 | 11.7
| 11.2847 | 306.463 | 50.952 | 66.07 | 45.183 | 81.506 |  | 33.8542 | 13.5 | 11.7
| 11.2917 | 305.979 | 50.848 | 65.989 | 45.106 | 81.394 |  | 33.875 | 13.9 | 11.7
| 11.2986 | 306.828 | 50.799 | 65.935 | 45.058 | 81.318 |  | 33.8958 | 14.7 | 11.7
| 11.3056 | 305.787 | 50.745 | 65.876 | 45.019 | 81.238 |  | 33.9167 | 14.8 | 11.7
| 11.3125 | 308.959 | 50.809 | 65.899 | 45.064 | 81.272 |  | 33.9375 | 15.1 | 11.7
| 11.3194 | 309.904 | 50.911 | 65.979 | 45.155 | 81.373 |  | 33.9583 | 14.6 | 11.7
| 11.3264 | 307.094 | 50.883 | 65.963 | 45.139 | 81.358 |  | 33.9792 | 11.9 | 11.7
| 11.3333 | 306.471 | 50.854 | 65.934 | 45.1 | 81.318 |  | 34 | 11.3 | 11.7
| 11.3403 | 311.727 | 50.831 | 65.896 | 45.069 | 81.285 |  | 34.0208 | 10.9 | 11.7
| 11.3472 | 311.634 | 51.021 | 66.043 | 45.24 | 81.478 |  | 34.0417 | 10.7 | 11.7
| 11.3542 | 310.343 | 51.082 | 66.11 | 45.284 | 81.559 |  | 34.0625 | 10.4 | 11.7
| 11.3611 | 310.747 | 51.112 | 66.146 | 45.31 | 81.621 |  | 34.0833 | 10.1 | 11.7
| 11.3681 | 308.562 | 51.07 | 66.13 | 45.276 | 81.606 |  | 34.1042 | 9.8 | 11.7
| 11.375 | 309.009 | 51.024 | 66.105 | 45.24 | 81.565 |  | 34.125 | 9.7 | 11.7
| 11.3819 | 309.5 | 51.019 | 66.102 | 45.233 | 81.567 |  | 34.1458 | 9.8 | 11.7
| 11.3889 | 309.198 | 51.011 | 66.102 | 45.236 | 81.565 |  | 34.1667 | 9.8 | 11.7
| 11.3958 | 308.544 | 51.017 | 66.11 | 45.231 | 81.574 |  | 34.1875 | 10 | 11.7
| 11.4028 | 308.965 | 50.994 | 66.096 | 45.221 | 81.554 |  | 34.2083 | 10 | 11.7
| 11.4097 | 308.845 | 51.026 | 66.117 | 45.241 | 81.579 |  | 34.2292 | 9.8 | 11.7
| 11.4167 | 308.082 | 51.011 | 66.109 | 45.23 | 81.571 |  | 34.25 | 9.8 | 11.7
| 11.4236 | 307.221 | 50.943 | 66.058 | 45.173 | 81.498 |  | 34.2708 | 9.6 | 11.7
| 11.4306 | 306.113 | 50.842 | 65.974 | 45.099 | 81.389 |  | 34.2917 | 9.2 | 11.7
| 11.4375 | 305.335 | 50.763 | 65.905 | 45.034 | 81.289 |  | 34.3125 | 8.6 | 11.7
| 11.4444 | 306.152 | 50.691 | 65.832 | 44.975 | 81.186 |  | 34.3333 | 8.2 | 11.7
| 11.4514 | 306.055 | 50.665 | 65.795 | 44.96 | 81.129 |  | 34.3542 | 8 | 11.7
| 11.4583 | 306.174 | 50.647 | 65.755 | 44.94 | 81.081 |  | 34.375 | 7.9 | 11.7
| 11.4653 | 305.474 | 50.623 | 65.72 | 44.921 | 81.025 |  | 34.3958 | 7.8 | 11.7
| 11.4722 | 309.412 | 50.625 | 65.695 | 44.914 | 81.004 |  | 34.4167 | 7.8 | 11.7
| 11.4792 | 310.022 | 50.792 | 65.819 | 45.055 | 81.165 |  | 34.4375 | 7.8 | 11.7
| 11.4861 | 309.156 | 50.879 | 65.883 | 45.124 | 81.259 |  | 34.4583 | 7.6 | 11.7
| 11.4931 | 309.256 | 50.917 | 65.923 | 45.155 | 81.318 |  | 34.4792 | 7.7 | 11.7
| 11.5 | 309.593 | 50.943 | 65.949 | 45.165 | 81.36 |  | 34.5 | 7.7 | 11.7
| 11.5069 | 310.127 | 50.98 | 65.986 | 45.197 | 81.419 |  | 34.5208 | 7.5 | 11.7
| 11.5139 | 309.416 | 51.029 | 66.037 | 45.24 | 81.485 |  | 34.5417 | 7.4 | 11.7
| 11.5208 | 310.374 | 51.045 | 66.065 | 45.249 | 81.526 |  | 34.5625 | 7.2 | 11.7
| 11.5278 | 311.985 | 51.092 | 66.11 | 45.287 | 81.589 |  | 34.5833 | 7.2 | 11.7
| 11.5347 | 310.822 | 51.154 | 66.177 | 45.337 | 81.684 |  | 34.6042 | 7.1 | 11.7
| 11.5417 | 308.314 | 51.066 | 66.132 | 45.272 | 81.62 |  | 34.625 | 6.9 | 11.7
| 11.5486 | 308.829 | 50.989 | 66.073 | 45.201 | 81.545 |  | 34.6458 | 6.9 | 11.7
| 11.5556 | 308.945 | 50.944 | 66.039 | 45.168 | 81.492 |  | 34.6667 | 6.7 | 11.7
| 11.5625 | 309.461 | 50.939 | 66.033 | 45.166 | 81.484 |  | 34.6875 | 6.5 | 11.7
| 11.5694 | 308.818 | 50.922 | 66.023 | 45.16 | 81.461 |  | 34.7083 | 6 | 11.7
| 11.5764 | 308.011 | 50.883 | 65.984 | 45.125 | 81.413 |  | 34.7292 | 5.8 | 11.7
| 11.5833 | 308.261 | 50.854 | 65.961 | 45.1 | 81.375 |  | 34.75 | 5.8 | 11.7
| 11.5903 | 309.252 | 50.861 | 65.954 | 45.107 | 81.37 |  | 34.7708 | 5.8 | 11.7
| 11.5972 | 306.391 | 50.799 | 65.908 | 45.061 | 81.304 |  | 34.7917 | 5.6 | 11.7
| 11.6042 | 307.745 | 50.756 | 65.857 | 45.017 | 81.231 |  | 34.8125 | 5.4 | 11.7
| 11.6111 | 308.265 | 50.759 | 65.85 | 45.026 | 81.221 |  | 34.8333 | 5.2 | 11.7
| 11.6181 | 307.744 | 50.759 | 65.837 | 45.034 | 81.208 |  | 34.8542 | 5.5 | 11.7
| 11.625 | 307.073 | 50.771 | 65.836 | 45.036 | 81.209 |  | 34.875 | 5.4 | 11.7
| 11.6319 | 308.117 | 50.774 | 65.833 | 45.036 | 81.204 |  | 34.8958 | 4.8 | 11.7
| 11.6389 | 308.306 | 50.789 | 65.843 | 45.049 | 81.212 |  | 34.9167 | 4.6 | 11.7
| 11.6458 | 308.54 | 50.8 | 65.849 | 45.059 | 81.235 |  | 34.9375 | 4.1 | 11.7
| 11.6528 | 307.586 | 50.745 | 65.803 | 45.016 | 81.167 |  | 34.9583 | 3.5 | 11.7
| 11.6597 | 307.666 | 50.728 | 65.779 | 44.996 | 81.13 |  | 34.9792 | 3.4 | 11.7
| 11.6667 | 307.661 | 50.747 | 65.786 | 45.012 | 81.147 |  | 35 | 2.9 | 11.7
| 11.6736 | 307.349 | 50.746 | 65.783 | 45.013 | 81.136 |  | 35.0208 | 3.2 | 11.7
| 11.6806 | 308.972 | 50.766 | 65.795 | 45.031 | 81.163 |  | 35.0417 | 3.8 | 11.7
| 11.6875 | 308.806 | 50.823 | 65.836 | 45.067 | 81.213 |  | 35.0625 | 4.2 | 11.7
| 11.6944 | 310.31 | 50.872 | 65.876 | 45.108 | 81.269 |  | 35.0833 | 3.7 | 11.7
| 11.7014 | 309.68 | 50.909 | 65.911 | 45.138 | 81.322 |  | 35.1042 | 3.2 | 11.7
| 11.7083 | 310.229 | 50.946 | 65.947 | 45.165 | 81.371 |  | 35.125 | 2.1 | 11.7
| 11.7153 | 310.435 | 50.978 | 65.983 | 45.191 | 81.422 |  | 35.1458 | 1.7 | 11.7
| 11.7222 | 308.983 | 50.956 | 65.979 | 45.181 | 81.42 |  | 35.1667 | 2.8 | 11.7
| 11.7292 | 308.123 | 50.916 | 65.963 | 45.151 | 81.388 |  | 35.1875 | 3.2 | 11.7
| 11.7361 | 308.855 | 50.89 | 65.944 | 45.128 | 81.367 |  | 35.2083 | 2.4 | 11.7
| 11.7431 | 307.898 | 50.865 | 65.924 | 45.107 | 81.342 |  | 35.2292 | 2.3 | 11.7
| 11.75 | 306.798 | 50.795 | 65.873 | 45.057 | 81.263 |  | 35.25 | 1.9 | 11.7
| 11.7569 | 308.448 | 51.11 | 66.087 | 45.287 | 81.57 |  | 35.2708 | 2.1 | 11.7
| 11.7639 | 308.353 | 50.933 | 65.982 | 45.169 | 81.416 |  | 35.2917 | 2.6 | 11.7
| 11.7708 | 308.45 | 50.886 | 65.954 | 45.125 | 81.376 |  | 35.3125 | 2.3 | 11.7
| 11.7778 | 309.874 | 50.913 | 65.966 | 45.146 | 81.394 |  | 35.3333 | 2.2 | 11.7
| 11.7847 | 310.507 | 50.97 | 66.013 | 45.198 | 81.46 |  | 35.3542 | 3 | 11.7
| 11.7917 | 309.694 | 51.007 | 66.053 | 45.225 | 81.513 |  | 35.375 | 3.6 | 11.7
| 11.7986 | 309.718 | 51.03 | 66.078 | 45.249 | 81.547 |  | 35.3958 | 4.1 | 11.7
| 11.8056 | 309.951 | 51.03 | 66.096 | 45.249 | 81.558 |  | 35.4167 | 4.6 | 11.7
| 11.8125 | 310.288 | 51.054 | 66.118 | 45.263 | 81.598 |  | 35.4375 | 4.9 | 11.7
| 11.8194 | 311.347 | 51.117 | 66.173 | 45.313 | 81.669 |  | 35.4583 | 5.2 | 11.7
| 11.8264 | 311.413 | 51.157 | 66.223 | 45.348 | 81.733 |  | 35.4792 | 5.4 | 11.7
| 11.8333 | 311.486 | 51.213 | 66.282 | 45.394 | 81.812 |  | 35.5 | 5.4 | 11.7
| 11.8403 | 312.072 | 51.271 | 66.345 | 45.435 | 81.9 |  | 35.5208 | 5.7 | 11.7
| 11.8472 | 312.096 | 51.312 | 66.404 | 45.477 | 81.973 |  | 35.5417 | 5.6 | 11.7
| 11.8542 | 308.818 | 51.19 | 66.333 | 45.384 | 81.877 |  | 35.5625 | 5.4 | 11.7
| 11.8611 | 310.252 | 51.129 | 66.289 | 45.332 | 81.809 |  | 35.5833 | 4.3 | 11.7
| 11.8681 | 309.337 | 51.125 | 66.292 | 45.332 | 81.81 |  | 35.6042 | 4.4 | 11.7
| 11.875 | 309.816 | 51.105 | 66.273 | 45.318 | 81.78 |  | 35.625 | 3.9 | 11.7
| 11.8819 | 311.103 | 51.145 | 66.306 | 45.347 | 81.817 |  | 35.6458 | 3.8 | 11.7
| 11.8889 | 310.076 | 51.167 | 66.33 | 45.365 | 81.85 |  | 35.6667 | 3.9 | 11.7
| 11.8958 | 311.382 | 51.223 | 66.381 | 45.418 | 81.909 |  | 35.6875 | 3.8 | 11.7
| 11.9028 | 311.931 | 51.27 | 66.425 | 45.459 | 81.977 |  | 35.7083 | 3.9 | 11.7
| 11.9097 | 311.043 | 51.281 | 66.453 | 45.465 | 82.005 |  | 35.7292 | 3.8 | 11.7
| 11.9167 | 311.734 | 51.324 | 66.492 | 45.491 | 82.062 |  | 35.75 | 3.3 | 11.7
| 11.9236 | 312.336 | 51.343 | 66.53 | 45.517 | 82.099 |  | 35.7708 | 2.9 | 11.7
| 11.9306 | 307.787 | 51.248 | 66.483 | 45.454 | 82.031 |  | 35.7917 | 2.2 | 11.7
| 11.9375 | 308.844 | 51.135 | 66.389 | 45.35 | 81.904 |  | 35.8125 | 1.9 | 11.7
| 11.9444 | 308.703 | 51.114 | 66.364 | 45.335 | 81.872 |  | 35.8333 | 1.9 | 11.7
| 11.9514 | 310.221 | 51.173 | 66.404 | 45.391 | 81.917 |  | 35.8542 | 2 | 11.7
| 11.9583 | 308.711 | 51.128 | 66.384 | 45.366 | 81.878 |  | 35.875 | 1.8 | 11.7
| 11.9653 | 308.921 | 51.071 | 66.331 | 45.309 | 81.804 |  | 35.8958 | 1.8 | 11.7
| 11.9722 | 309.744 | 51.075 | 66.326 | 45.319 | 81.794 |  | 35.9167 | 1.4 | 11.7
| 11.9792 | 310.594 | 51.126 | 66.363 | 45.36 | 81.83 |  | 35.9375 | 1.2 | 11.7
| 11.9861 | 312.33 | 51.204 | 66.419 | 45.418 | 81.91 |  | 35.9583 | 1.3 | 11.7
| 11.9931 | 306.963 | 51.132 | 66.385 | 45.372 | 81.849 |  | 35.9792 | 0.8 | 11.7
| 12 | 307.647 | 51.001 | 66.27 | 45.255 | 81.699 |  | 36 | 0.8 | 11.7
| 12.0069 | 307.368 | 50.939 | 66.22 | 45.212 | 81.623 |  | 36.0208 | 0.3 | 11.7
| 12.0139 | 308.162 | 50.911 | 66.179 | 45.19 | 81.567 |  | 36.0417 | 0.3 | 11.7
| 12.0208 | 307.919 | 50.91 | 66.164 | 45.196 | 81.545 |  | 36.0625 | 0.6 | 11.7
| 12.0278 | 309.11 | 50.92 | 66.156 | 45.198 | 81.534 |  | 36.0833 | 0.9 | 11.7
| 12.0347 | 309.685 | 50.958 | 66.175 | 45.229 | 81.556 |  | 36.1042 | 1.1 | 11.7
| 12.0417 | 309.128 | 50.989 | 66.193 | 45.253 | 81.579 |  | 36.125 | 1.3 | 11.7
| 12.0486 | 309.987 | 50.997 | 66.2 | 45.266 | 81.589 |  | 36.1458 | 1.2 | 11.7
| 12.0556 | 308.73 | 50.974 | 66.182 | 45.24 | 81.555 |  | 36.1667 | 0.5 | 11.7
| 12.0625 | 309.074 | 50.979 | 66.179 | 45.246 | 81.562 |  | 36.1875 | 0.3 | 11.7
| 12.0694 | 309.796 | 51.001 | 66.198 | 45.266 | 81.583 |  | 36.2083 | 0.3 | 11.7
| 12.0764 | 310.412 | 51.055 | 66.235 | 45.31 | 81.635 |  | 36.2292 | -0.1 | 11.7
| 12.0833 | 310.769 | 51.1 | 66.277 | 45.346 | 81.689 |  | 36.25 | 0.7 | 11.7
| 12.0903 | 311.254 | 51.134 | 66.314 | 45.372 | 81.736 |  | 36.2708 | 0.6 | 11.7
| 12.0972 | 311.267 | 51.165 | 66.341 | 45.4 | 81.781 |  | 36.2917 | 0.1 | 11.7
| 12.1042 | 310.294 | 51.187 | 66.366 | 45.415 | 81.819 |  | 36.3125 | 0.3 | 11.7
| 12.1111 | 310.982 | 51.221 | 66.409 | 45.443 | 81.871 |  | 36.3333 | 0.4 | 11.7
| 12.1181 | 311.958 | 51.265 | 66.448 | 45.477 | 81.927 |  | 36.3542 | 0.5 | 11.1
| 12.125 | 311.421 | 51.293 | 66.486 | 45.501 | 81.98 |  | 36.375 | 0.8 | 11.1
| 12.1319 | 311.726 | 51.306 | 66.512 | 45.514 | 82.006 |  | 36.3958 | 1.1 | 11.1
| 12.1389 | 310.76 | 51.305 | 66.527 | 45.514 | 82.023 |  | 36.4167 | 2.7 | 11.1
| 12.1458 | 311.109 | 51.303 | 66.534 | 45.512 | 82.037 |  | 36.4375 | 3.3 | 11.1
| 12.1528 | 311.214 | 51.289 | 66.537 | 45.505 | 82.037 |  | 36.4583 | 3.6 | 11.1
| 12.1597 | 311.088 | 51.286 | 66.541 | 45.501 | 82.038 |  | 36.4792 | 3.7 | 11.1
| 12.1667 | 310.848 | 51.291 | 66.548 | 45.507 | 82.052 |  | 36.5 | 4 | 11.1
| 12.1736 | 310.892 | 51.294 | 66.557 | 45.509 | 82.06 |  | 36.5208 | 4.7 | 11.1
| 12.1806 | 310.638 | 51.276 | 66.552 | 45.498 | 82.047 |  | 36.5417 | 4.6 | 11.1
| 12.1875 | 310.085 | 51.27 | 66.551 | 45.491 | 82.044 |  | 36.5625 | 4.8 | 11.1
| 12.1944 | 310.382 | 51.243 | 66.538 | 45.48 | 82.019 |  | 36.5833 | 5.7 | 11.1
| 12.2014 | 310.537 | 51.231 | 66.526 | 45.464 | 82.003 |  | 36.6042 | 5.9 | 11.1
| 12.2083 | 310.031 | 51.223 | 66.521 | 45.464 | 81.999 |  | 36.625 | 6.2 | 11.1
| 12.2153 | 309.785 | 51.229 | 66.521 | 45.458 | 81.992 |  | 36.6458 | 5.4 | 11.1
| 12.2222 | 309.319 | 51.197 | 66.507 | 45.448 | 81.966 |  | 36.6667 | 4.8 | 11.1
| 12.2292 | 308.85 | 51.153 | 66.458 | 45.406 | 81.906 |  | 36.6875 | 4 | 11.1
| 12.2361 | 307.623 | 51.102 | 66.417 | 45.359 | 81.842 |  | 36.7083 | 3.3 | 11.1
| 12.2431 | 306.57 | 50.989 | 66.319 | 45.275 | 81.715 |  | 36.7292 | 2.6 | 11.1
| 12.25 | 305.765 | 50.88 | 66.223 | 45.189 | 81.574 |  | 36.75 | 1.9 | 11.1
| 12.2569 | 309.016 | 50.916 | 66.216 | 45.21 | 81.565 |  | 36.7708 | 1.7 | 11.1
| 12.2639 | 309.784 | 50.963 | 66.235 | 45.247 | 81.591 |  | 36.7917 | 1.8 | 11.1
| 12.2708 | 309.291 | 50.99 | 66.252 | 45.277 | 81.612 |  | 36.8125 | 3.8 | 11.1
| 12.2778 | 309.367 | 50.993 | 66.238 | 45.274 | 81.601 |  | 36.8333 | 2.9 | 11.1
| 12.2847 | 306.59 | 50.906 | 66.177 | 45.209 | 81.511 |  | 36.8542 | 2.5 | 11.1
| 12.2917 | 306.125 | 50.819 | 66.095 | 45.137 | 81.406 |  | 36.875 | 2.3 | 11.1
| 12.2986 | 307.01 | 50.751 | 66.021 | 45.085 | 81.311 |  | 36.8958 | 1.5 | 11.1
| 12.3056 | 310.091 | 50.711 | 65.969 | 45.044 | 81.235 |  | 36.9167 | 1.1 | 11.1
| 12.3125 | 310.071 | 50.844 | 66.043 | 45.149 | 81.336 |  | 36.9375 | 0.4 | 11.1
| 12.3194 | 309.989 | 50.933 | 66.108 | 45.216 | 81.425 |  | 36.9583 | 0.2 | 11.1
| 12.3264 | 311.074 | 50.965 | 66.136 | 45.252 | 81.473 |  | 36.9792 | 0.5 | 11.1
| 12.3333 | 308.576 | 50.961 | 66.136 | 45.248 | 81.475 |  | 37 | 0.7 | 11.1
| 12.3403 | 307.745 | 50.912 | 66.104 | 45.203 | 81.431 |  | 37.0208 | 0.5 | 11.1
| 12.3472 | 307.487 | 50.856 | 66.054 | 45.16 | 81.367 |  | 37.0417 | 0.5 | 11.1
| 12.3542 | 306.719 | 50.813 | 66.008 | 45.118 | 81.313 |  | 37.0625 | 0.9 | 11.1
| 12.3611 | 309.072 | 50.8 | 65.985 | 45.108 | 81.28 |  | 37.0833 | 1.1 | 11.1
| 12.3681 | 308.611 | 50.856 | 66.021 | 45.158 | 81.331 |  | 37.1042 | 1.3 | 11.1
| 12.375 | 308.232 | 50.853 | 66.019 | 45.163 | 81.327 |  | 37.125 | 1.4 | 11.1
| 12.3819 | 308.133 | 50.827 | 65.994 | 45.134 | 81.286 |  | 37.1458 | 1.6 | 11.1
| 12.3889 | 307.424 | 50.8 | 65.968 | 45.118 | 81.254 |  | 37.1667 | 1.8 | 11.1
| 12.3958 | 307.25 | 50.782 | 65.948 | 45.103 | 81.234 |  | 37.1875 | 1.8 | 11.1
| 12.4028 | 308.182 | 50.797 | 65.938 | 45.108 | 81.234 |  | 37.2083 | 1.8 | 11.1
| 12.4097 | 308.819 | 50.841 | 65.972 | 45.144 | 81.276 |  | 37.2292 | 2 | 11.1
| 12.4167 | 308.784 | 50.892 | 66.008 | 45.182 | 81.316 |  | 37.25 | 2.2 | 11.1
| 12.4236 | 309.912 | 50.926 | 66.031 | 45.206 | 81.366 |  | 37.2708 | 2.4 | 11.1
| 12.4306 | 308.39 | 50.9 | 66.026 | 45.192 | 81.352 |  | 37.2917 | 2.4 | 11.1
| 12.4375 | 308.049 | 50.878 | 66.008 | 45.173 | 81.33 |  | 37.3125 | 2.4 | 11.1
| 12.4444 | 308.61 | 50.877 | 66.003 | 45.167 | 81.334 |  | 37.3333 | 2.4 | 11.1
| 12.4514 | 308.607 | 50.893 | 66.016 | 45.179 | 81.344 |  | 37.3542 | 2.7 | 11.1
| 12.4583 | 308.796 | 50.881 | 66.004 | 45.171 | 81.34 |  | 37.375 | 2.9 | 10.6
| 12.4653 | 309.772 | 50.976 | 66.076 | 45.249 | 81.435 |  | 37.3958 | 3.2 | 10.6
| 12.4722 | 309.563 | 50.994 | 66.105 | 45.269 | 81.467 |  | 37.4167 | 3.5 | 10.6
| 12.4792 | 309.296 | 51.003 | 66.112 | 45.264 | 81.485 |  | 37.4375 | 3.8 | 10.6
| 12.4861 | 309.227 | 51.002 | 66.118 | 45.268 | 81.498 |  | 37.4583 | 4.1 | 10.6
| 12.4931 | 309.32 | 50.991 | 66.119 | 45.256 | 81.496 |  | 37.4792 | 5.2 | 10.6
| 12.5 | 309.503 | 51.001 | 66.13 | 45.265 | 81.513 |  | 37.5 | 4.8 | 10.6
| 12.5069 | 308.756 | 50.994 | 66.13 | 45.266 | 81.515 |  | 37.5208 | 5 | 10.6
| 12.5139 | 309.306 | 50.998 | 66.128 | 45.269 | 81.516 |  | 37.5417 | 5.2 | 10.6
| 12.5208 | 309.621 | 50.992 | 66.132 | 45.261 | 81.522 |  | 37.5625 | 5.3 | 10.6
| 12.5278 | 310.064 | 51 | 66.136 | 45.26 | 81.526 |  | 37.5833 | 5.4 | 10.6
| 12.5347 | 310.147 | 51.044 | 66.175 | 45.299 | 81.581 |  | 37.6042 | 5.3 | 10.6
| 12.5417 | 310.232 | 51.09 | 66.223 | 45.341 | 81.638 |  | 37.625 | 5 | 10.6
| 12.5486 | 310.124 | 51.11 | 66.237 | 45.352 | 81.672 |  | 37.6458 | 4.7 | 10.6
| 12.5556 | 309.597 | 51.08 | 66.226 | 45.327 | 81.656 |  | 37.6667 | 4.4 | 10.6
| 12.5625 | 309.083 | 51.048 | 66.209 | 45.306 | 81.634 |  | 37.6875 | 3.9 | 10.6
| 12.5694 | 308.515 | 51.013 | 66.188 | 45.273 | 81.599 |  | 37.7083 | 3.3 | 10.6
| 12.5764 | 308.253 | 50.97 | 66.149 | 45.243 | 81.549 |  | 37.7292 | 2.8 | 10.6
| 12.5833 | 308.053 | 50.92 | 66.112 | 45.201 | 81.498 |  | 37.75 | 2.2 | 10.6
| 12.5903 | 307.698 | 50.884 | 66.079 | 45.181 | 81.445 |  | 37.7708 | 1.8 | 10.6
| 12.5972 | 307.888 | 50.841 | 66.032 | 45.143 | 81.387 |  | 37.7917 | 1.7 | 10.6
| 12.6042 | 307.391 | 50.813 | 65.999 | 45.121 | 81.342 |  | 37.8125 | 1.7 | 10.6
| 12.6111 | 308.547 | 50.799 | 65.98 | 45.105 | 81.31 |  | 37.8333 | 1.8 | 10.6
| 12.6181 | 307.413 | 50.757 | 65.931 | 45.071 | 81.243 |  | 37.8542 | 1.7 | 10.6
| 12.625 | 307.736 | 50.729 | 65.896 | 45.053 | 81.197 |  | 37.875 | 1.3 | 10.6
| 12.6319 | 307.378 | 50.714 | 65.869 | 45.038 | 81.164 |  | 37.8958 | 0.8 | 10.6
| 12.6389 | 307.161 | 50.696 | 65.841 | 45.025 | 81.125 |  | 37.9167 | 0.4 | 10.6
| 12.6458 | 308.338 | 50.704 | 65.835 | 45.033 | 81.113 |  | 37.9375 | 0.1 | 10.6
| 12.6528 | 308.68 | 50.714 | 65.833 | 45.033 | 81.112 |  | 37.9583 | -0.6 | 10.6
| 12.6597 | 308.572 | 50.732 | 65.833 | 45.047 | 81.124 |  | 37.9792 | -0.9 | 10.6
| 12.6667 | 308.535 | 50.759 | 65.855 | 45.075 | 81.144 |  | 38 | -1.2 | 10.6
| 12.6736 | 309.406 | 50.797 | 65.877 | 45.098 | 81.186 |  | 38.0208 | -1.2 | 10.6
| 12.6806 | 308.648 | 50.802 | 65.885 | 45.103 | 81.198 |  | 38.0417 | -1.4 | 10.6
| 12.6875 | 310.034 | 50.853 | 65.929 | 45.145 | 81.254 |  | 38.0625 | -1.6 | 10.6
| 12.6944 | 310.671 | 50.903 | 65.969 | 45.187 | 81.314 |  | 38.0833 | -1 | 10.6
| 12.7014 | 310.32 | 50.945 | 66.007 | 45.217 | 81.373 |  | 38.1042 | -1.2 | 10.6
| 12.7083 | 309.21 | 50.977 | 66.043 | 45.243 | 81.418 |  | 38.125 | -1.3 | 10.6
| 12.7153 | 309.761 | 50.97 | 66.049 | 45.239 | 81.434 |  | 38.1458 | -1.4 | 10.6
| 12.7222 | 310.261 | 50.966 | 66.059 | 45.236 | 81.439 |  | 38.1667 | -1.7 | 10.6
| 12.7292 | 309.029 | 50.976 | 66.074 | 45.244 | 81.455 |  | 38.1875 | -2.2 | 10.6
| 12.7361 | 309.615 | 50.973 | 66.076 | 45.24 | 81.468 |  | 38.2083 | -1.2 | 10.6
| 12.7431 | 308.678 | 50.924 | 66.051 | 45.211 | 81.426 |  | 38.2292 | -1.3 | 10.6
| 12.75 | 309.009 | 50.937 | 66.057 | 45.22 | 81.431 |  | 38.25 | -0.9 | 10.6
| 12.7569 | 308.143 | 50.84 | 65.98 | 45.137 | 81.334 |  | 38.2708 | -0.9 | 10.6
| 12.7639 | 311.424 | 50.992 | 66.097 | 45.26 | 81.487 |  | 38.2917 | -1.5 | 10.6
| 12.7708 | 311.286 | 51.07 | 66.158 | 45.323 | 81.568 |  | 38.3125 | -1.9 | 10.6
| 12.7778 | 312.233 | 51.158 | 66.245 | 45.394 | 81.69 |  | 38.3333 | -2.1 | 10.6
| 12.7847 | 312.532 | 51.225 | 66.315 | 45.451 | 81.786 |  | 38.3542 | -0.8 | 10.6
| 12.7917 | 311.806 | 51.257 | 66.369 | 45.476 | 81.851 |  | 38.375 | -0.3 | 10.6
| 12.7986 | 311.88 | 51.272 | 66.401 | 45.491 | 81.896 |  | 38.3958 | 0.1 | 10.6
| 12.8056 | 312.165 | 51.287 | 66.43 | 45.502 | 81.935 |  | 38.4167 | 0.1 | 10.6
| 12.8125 | 312.592 | 51.314 | 66.466 | 45.521 | 81.989 |  | 38.4375 | 0.1 | 10.6
| 12.8194 | 308.886 | 51.347 | 66.518 | 45.553 | 82.049 |  | 38.4583 | 0.5 | 10.6
| 12.8264 | 309.132 | 51.197 | 66.425 | 45.444 | 81.913 |  | 38.4792 | 1.1 | 10.6
| 12.8333 | 310.665 | 51.164 | 66.398 | 45.416 | 81.876 |  | 38.5 | 2 | 10
| 12.8403 | 307.062 | 50.983 | 66.265 | 45.268 | 81.677 |  | 38.5208 | 1.9 | 10
| 12.8472 | 307.586 | 50.884 | 66.176 | 45.197 | 81.55 |  | 38.5417 | 2.1 | 10
| 12.8542 | 307.732 | 50.859 | 66.135 | 45.178 | 81.49 |  | 38.5625 | 2.1 | 10
| 12.8611 | 308.271 | 50.861 | 66.112 | 45.182 | 81.454 |  | 38.5833 | 2.4 | 10
| 12.8681 | 308.552 | 50.869 | 66.112 | 45.19 | 81.443 |  | 38.6042 | 2.5 | 10
| 12.875 | 309.422 | 50.906 | 66.128 | 45.217 | 81.461 |  | 38.625 | 2.7 | 10
| 12.8819 | 309.762 | 50.958 | 66.165 | 45.267 | 81.507 |  | 38.6458 | 2.7 | 10
| 12.8889 | 310.426 | 51.013 | 66.209 | 45.314 | 81.568 |  | 38.6667 | 2.5 | 10
| 12.8958 | 310.342 | 51.076 | 66.258 | 45.364 | 81.644 |  | 38.6875 | 2.4 | 10
| 12.9028 | 311.206 | 51.144 | 66.323 | 45.416 | 81.723 |  | 38.7083 | 2.4 | 10
| 12.9097 | 310.519 | 51.168 | 66.36 | 45.443 | 81.771 |  | 38.7292 | 2.4 | 10
| 12.9167 | 310.574 | 51.176 | 66.373 | 45.443 | 81.793 |  | 38.75 | 2.1 | 10
| 12.9236 | 311.648 | 51.225 | 66.426 | 45.488 | 81.854 |  | 38.7708 | 1.9 | 10
| 12.9306 | 308.761 | 51.177 | 66.414 | 45.462 | 81.823 |  | 38.7917 | 1.9 | 10
| 12.9375 | 306.219 | 51.037 | 66.312 | 45.345 | 81.682 |  | 38.8125 | 1.8 | 10
| 12.9444 | 306.981 | 50.937 | 66.228 | 45.261 | 81.564 |  | 38.8333 | 1.8 | 10
| 12.9514 | 308.038 | 50.925 | 66.212 | 45.26 | 81.534 |  | 38.8542 | 2 | 10
| 12.9583 | 308.807 | 50.942 | 66.213 | 45.28 | 81.527 |  | 38.875 | 1.7 | 10
| 12.9653 | 309.327 | 50.97 | 66.221 | 45.297 | 81.541 |  | 38.8958 | 1.7 | 10
| 12.9722 | 308.089 | 51.005 | 66.252 | 45.337 | 81.572 |  | 38.9167 | 1.8 | 10
| 12.9792 | 308.296 | 50.953 | 66.21 | 45.288 | 81.508 |  | 38.9375 | 1.1 | 10
| 12.9861 | 308.903 | 50.965 | 66.211 | 45.298 | 81.514 |  | 38.9583 | 0.4 | 10
| 12.9931 | 310.049 | 51.038 | 66.271 | 45.358 | 81.586 |  | 38.9792 | 0.3 | 10
| 13 | 307.977 | 51.048 | 66.29 | 45.375 | 81.605
| 13.0069 | 307.928 | 50.981 | 66.233 | 45.315 | 81.532
| 13.0139 | 308.906 | 50.97 | 66.228 | 45.311 | 81.517
| 13.0208 | 309.333 | 50.998 | 66.238 | 45.329 | 81.533
| 13.0278 | 309.679 | 51.03 | 66.269 | 45.355 | 81.568
| 13.0347 | 309.237 | 51.058 | 66.29 | 45.376 | 81.599
| 13.0417 | 310.085 | 51.078 | 66.313 | 45.398 | 81.622
| 13.0486 | 309.423 | 51.116 | 66.346 | 45.425 | 81.667
| 13.0556 | 310.026 | 51.117 | 66.359 | 45.432 | 81.684
| 13.0625 | 309.183 | 51.118 | 66.368 | 45.437 | 81.685
| 13.0694 | 309.919 | 51.119 | 66.374 | 45.44 | 81.697
| 13.0764 | 311.096 | 51.159 | 66.412 | 45.471 | 81.742
| 13.0833 | 309.52 | 51.18 | 66.434 | 45.495 | 81.777
| 13.0903 | 310.063 | 51.175 | 66.439 | 45.484 | 81.775
| 13.0972 | 311.02 | 51.222 | 66.482 | 45.52 | 81.83
| 13.1042 | 310.445 | 51.232 | 66.501 | 45.536 | 81.853
| 13.1111 | 310.155 | 51.223 | 66.509 | 45.529 | 81.854
| 13.1181 | 311.147 | 51.268 | 66.546 | 45.564 | 81.907
| 13.125 | 310.914 | 51.305 | 66.584 | 45.595 | 81.96
| 13.1319 | 311.313 | 51.321 | 66.613 | 45.611 | 81.991
| 13.1389 | 310.922 | 51.327 | 66.628 | 45.612 | 82.01
| 13.1458 | 310.262 | 51.32 | 66.635 | 45.608 | 82.014
| 13.1528 | 310.527 | 51.318 | 66.642 | 45.61 | 82.025
| 13.1597 | 310.995 | 51.334 | 66.659 | 45.625 | 82.049
| 13.1667 | 311.089 | 51.351 | 66.682 | 45.637 | 82.073
| 13.1736 | 311.445 | 51.374 | 66.707 | 45.656 | 82.103
| 13.1806 | 310.879 | 51.387 | 66.73 | 45.668 | 82.128
| 13.1875 | 311.324 | 51.39 | 66.738 | 45.674 | 82.146
| 13.1944 | 310.394 | 51.382 | 66.747 | 45.671 | 82.146
| 13.2014 | 310.047 | 51.352 | 66.723 | 45.647 | 82.119
| 13.2083 | 309.82 | 51.346 | 66.726 | 45.637 | 82.117
| 13.2153 | 310.09 | 51.326 | 66.714 | 45.624 | 82.09
| 13.2222 | 309.578 | 51.291 | 66.687 | 45.6 | 82.055
| 13.2292 | 309.427 | 51.265 | 66.675 | 45.588 | 82.027
| 13.2361 | 308.13 | 51.233 | 66.641 | 45.555 | 81.982
| 13.2431 | 308.054 | 51.151 | 66.569 | 45.494 | 81.886
| 13.25 | 307.713 | 51.082 | 66.505 | 45.438 | 81.792
| 13.2569 | 310.398 | 51.084 | 66.484 | 45.432 | 81.774
| 13.2639 | 308.819 | 51.126 | 66.51 | 45.476 | 81.794
| 13.2708 | 308.224 | 51.103 | 66.481 | 45.456 | 81.763
| 13.2778 | 306.613 | 51.042 | 66.433 | 45.412 | 81.685
| 13.2847 | 311.383 | 51.077 | 66.429 | 45.422 | 81.696
| 13.2917 | 311.108 | 51.193 | 66.518 | 45.526 | 81.814
| 13.2986 | 309.708 | 51.22 | 66.541 | 45.547 | 81.85
| 13.3056 | 309.126 | 51.178 | 66.511 | 45.513 | 81.812
| 13.3125 | 308.48 | 51.121 | 66.466 | 45.457 | 81.745
| 13.3194 | 311.454 | 51.133 | 66.462 | 45.469 | 81.757
| 13.3264 | 311.071 | 51.213 | 66.529 | 45.539 | 81.837
| 13.3333 | 310.664 | 51.229 | 66.546 | 45.552 | 81.864
| 13.3403 | 309.076 | 51.213 | 66.538 | 45.535 | 81.843
| 13.3472 | 308.568 | 51.133 | 66.484 | 45.47 | 81.778
| 13.3542 | 307.081 | 51.048 | 66.408 | 45.404 | 81.678
| 13.3611 | 306.888 | 50.967 | 66.334 | 45.339 | 81.581
| 13.3681 | 306.599 | 50.889 | 66.258 | 45.277 | 81.473
| 13.375 | 305.885 | 50.823 | 66.188 | 45.229 | 81.38
| 13.3819 | 309.837 | 50.869 | 66.184 | 45.251 | 81.39
| 13.3889 | 310.128 | 50.982 | 66.259 | 45.349 | 81.482
| 13.3958 | 309.249 | 51.014 | 66.283 | 45.377 | 81.516
| 13.4028 | 310.571 | 51.061 | 66.314 | 45.406 | 81.572
| 13.4097 | 310.603 | 51.121 | 66.365 | 45.456 | 81.646
| 13.4167 | 310.35 | 51.148 | 66.39 | 45.473 | 81.684
| 13.4236 | 310.056 | 51.136 | 66.391 | 45.464 | 81.686
| 13.4306 | 309.031 | 51.115 | 66.38 | 45.45 | 81.681
| 13.4375 | 308.989 | 51.098 | 66.362 | 45.428 | 81.656
| 13.4444 | 308.949 | 51.068 | 66.342 | 45.406 | 81.632
| 13.4514 | 307.704 | 51.023 | 66.305 | 45.377 | 81.585
| 13.4583 | 308.24 | 50.995 | 66.274 | 45.346 | 81.55
| 13.4653 | 309.523 | 51 | 66.265 | 45.344 | 81.542
| 13.4722 | 309.477 | 51.005 | 66.264 | 45.346 | 81.542
| 13.4792 | 308.595 | 51.008 | 66.263 | 45.355 | 81.543
| 13.4861 | 308.997 | 51.017 | 66.262 | 45.356 | 81.547
| 13.4931 | 309.116 | 51.012 | 66.258 | 45.35 | 81.546
| 13.5 | 309.569 | 51.023 | 66.266 | 45.359 | 81.554
| 13.5069 | 310.056 | 51.035 | 66.266 | 45.364 | 81.565
| 13.5139 | 310.419 | 51.076 | 66.299 | 45.395 | 81.611
| 13.5208 | 310.215 | 51.11 | 66.324 | 45.422 | 81.655
| 13.5278 | 311.758 | 51.16 | 66.363 | 45.461 | 81.717
| 13.5347 | 307.854 | 51.08 | 66.322 | 45.403 | 81.652
| 13.5417 | 307.404 | 50.982 | 66.241 | 45.317 | 81.55
| 13.5486 | 308.653 | 50.932 | 66.191 | 45.278 | 81.488
| 13.5556 | 309.061 | 50.919 | 66.17 | 45.265 | 81.457
| 13.5625 | 308.758 | 50.914 | 66.154 | 45.262 | 81.437
| 13.5694 | 308.658 | 50.903 | 66.135 | 45.255 | 81.414
| 13.5764 | 308.32 | 50.867 | 66.097 | 45.225 | 81.363
| 13.5833 | 308.562 | 50.868 | 66.089 | 45.223 | 81.358
| 13.5903 | 308.614 | 50.883 | 66.085 | 45.228 | 81.358
| 13.5972 | 308.102 | 50.871 | 66.072 | 45.222 | 81.343
| 13.6042 | 308.542 | 50.84 | 66.041 | 45.198 | 81.309
| 13.6111 | 307.654 | 50.822 | 66.017 | 45.183 | 81.275
| 13.6181 | 307.198 | 50.778 | 65.972 | 45.141 | 81.217
| 13.625 | 307.441 | 50.748 | 65.934 | 45.114 | 81.173
| 13.6319 | 308.112 | 50.749 | 65.925 | 45.119 | 81.157
| 13.6389 | 308.27 | 50.77 | 65.93 | 45.134 | 81.173
| 13.6458 | 307.782 | 50.772 | 65.926 | 45.135 | 81.17
| 13.6528 | 308.19 | 50.759 | 65.912 | 45.126 | 81.156
| 13.6597 | 307.054 | 50.745 | 65.892 | 45.106 | 81.13
| 13.6667 | 307.824 | 50.735 | 65.878 | 45.103 | 81.116
| 13.6736 | 308.103 | 50.737 | 65.864 | 45.096 | 81.104
| 13.6806 | 308.674 | 50.763 | 65.878 | 45.123 | 81.125
| 13.6875 | 307.6 | 50.772 | 65.88 | 45.13 | 81.139
| 13.6944 | 308.164 | 50.772 | 65.884 | 45.124 | 81.142
| 13.7014 | 308.007 | 50.765 | 65.871 | 45.118 | 81.13
| 13.7083 | 308.415 | 50.783 | 65.882 | 45.13 | 81.148
| 13.7153 | 311.068 | 50.935 | 66 | 45.256 | 81.313
| 13.7222 | 310.395 | 50.987 | 66.056 | 45.299 | 81.385
| 13.7292 | 309.788 | 51 | 66.08 | 45.309 | 81.428
| 13.7361 | 310.85 | 51.018 | 66.107 | 45.318 | 81.465
| 13.7431 | 310.737 | 51.029 | 66.127 | 45.33 | 81.487
| 13.75 | 308.891 | 50.988 | 66.106 | 45.298 | 81.469
| 13.7569 | 306.028 | 50.828 | 66.002 | 45.177 | 81.317
| 13.7639 | 306.531 | 50.739 | 65.917 | 45.1 | 81.205
| 13.7708 | 305.414 | 50.668 | 65.85 | 45.045 | 81.106
| 13.7778 | 306.731 | 50.651 | 65.819 | 45.029 | 81.063
| 13.7847 | 306.782 | 50.627 | 65.786 | 45.023 | 81.014
| 13.7917 | 307.352 | 50.635 | 65.78 | 45.03 | 80.999
| 13.7986 | 306.876 | 50.651 | 65.774 | 45.041 | 80.999
| 13.8056 | 307.476 | 50.657 | 65.777 | 45.044 | 80.998
| 13.8125 | 307.845 | 50.665 | 65.774 | 45.048 | 80.999
| 13.8194 | 308.548 | 50.727 | 65.811 | 45.09 | 81.048
| 13.8264 | 309.701 | 50.82 | 65.885 | 45.174 | 81.147
| 13.8333 | 310.072 | 50.895 | 65.956 | 45.237 | 81.247
| 13.8403 | 310.203 | 50.927 | 65.99 | 45.26 | 81.298
| 13.8472 | 310.736 | 50.989 | 66.055 | 45.309 | 81.382
| 13.8542 | 311.15 | 51.088 | 66.147 | 45.383 | 81.508
| 13.8611 | 309.258 | 51.093 | 66.186 | 45.409 | 81.549
| 13.8681 | 310.236 | 51.068 | 66.176 | 45.37 | 81.542
| 13.875 | 309.995 | 51.09 | 66.211 | 45.391 | 81.591
| 13.8819 | 311.548 | 51.146 | 66.269 | 45.442 | 81.664
| 13.8889 | 312.226 | 51.209 | 66.332 | 45.488 | 81.747
| 13.8958 | 312.279 | 51.284 | 66.411 | 45.552 | 81.85
| 13.9028 | 312.222 | 51.323 | 66.473 | 45.59 | 81.924
| 13.9097 | 310.957 | 51.307 | 66.49 | 45.578 | 81.944
| 13.9167 | 311.503 | 51.323 | 66.521 | 45.596 | 81.987
| 13.9236 | 311.214 | 51.349 | 66.556 | 45.614 | 82.029
| 13.9306 | 310.931 | 51.32 | 66.559 | 45.59 | 82.02
| 13.9375 | 312.302 | 51.37 | 66.608 | 45.628 | 82.088
| 13.9444 | 312.729 | 51.425 | 66.675 | 45.689 | 82.167
| 13.9514 | 310.272 | 51.327 | 66.626 | 45.613 | 82.087
| 13.9583 | 310.243 | 51.299 | 66.61 | 45.59 | 82.059
| 13.9653 | 310.879 | 51.319 | 66.63 | 45.603 | 82.079
| 13.9722 | 309.787 | 51.367 | 66.679 | 45.656 | 82.134
| 13.9792 | 308.83 | 51.247 | 66.601 | 45.557 | 82.018
| 13.9861 | 310.4 | 51.224 | 66.577 | 45.537 | 81.985
| 13.9931 | 310.541 | 51.248 | 66.597 | 45.558 | 82.003
| 14 | 310.866 | 51.28 | 66.627 | 45.589 | 82.03
| 14.0069 | 310.761 | 51.335 | 66.674 | 45.637 | 82.085
| 14.0139 | 311.357 | 51.359 | 66.699 | 45.654 | 82.126
| 14.0208 | 311.839 | 51.38 | 66.73 | 45.669 | 82.154
| 14.0278 | 313.141 | 51.433 | 66.78 | 45.713 | 82.225
| 14.0347 | 309.46 | 51.368 | 66.758 | 45.669 | 82.174
| 14.0417 | 310.006 | 51.314 | 66.717 | 45.626 | 82.116
| 14.0486 | 310.049 | 51.273 | 66.685 | 45.595 | 82.071
| 14.0556 | 309.702 | 51.231 | 66.655 | 45.566 | 82.019
| 14.0625 | 310.101 | 51.23 | 66.643 | 45.564 | 82.005
| 14.0694 | 309.866 | 51.226 | 66.644 | 45.563 | 81.988
| 14.0764 | 309.333 | 51.201 | 66.621 | 45.544 | 81.955
| 14.0833 | 308.865 | 51.196 | 66.613 | 45.546 | 81.943
| 14.0903 | 309.336 | 51.203 | 66.618 | 45.549 | 81.94
| 14.0972 | 309.435 | 51.236 | 66.639 | 45.578 | 81.967
| 14.1042 | 310.537 | 51.254 | 66.653 | 45.592 | 81.991
| 14.1111 | 310.145 | 51.262 | 66.662 | 45.599 | 81.994
| 14.1181 | 310.806 | 51.278 | 66.68 | 45.611 | 82.016
| 14.125 | 310.08 | 51.317 | 66.709 | 45.643 | 82.058
| 14.1319 | 310.534 | 51.331 | 66.729 | 45.656 | 82.085
| 14.1389 | 311.101 | 51.342 | 66.741 | 45.662 | 82.097
| 14.1458 | 311.305 | 51.366 | 66.765 | 45.68 | 82.127
| 14.1528 | 311.165 | 51.393 | 66.793 | 45.703 | 82.165
| 14.1597 | 311.011 | 51.422 | 66.825 | 45.727 | 82.2
| 14.1667 | 311.813 | 51.449 | 66.857 | 45.747 | 82.244
| 14.1736 | 311.484 | 51.448 | 66.865 | 45.751 | 82.262
| 14.1806 | 310.581 | 51.454 | 66.882 | 45.756 | 82.275
| 14.1875 | 310.828 | 51.446 | 66.885 | 45.748 | 82.279
| 14.1944 | 311.357 | 51.433 | 66.886 | 45.745 | 82.28
| 14.2014 | 311.221 | 51.442 | 66.892 | 45.744 | 82.285
| 14.2083 | 311.89 | 51.455 | 66.91 | 45.755 | 82.304
| 14.2153 | 310.804 | 51.449 | 66.911 | 45.754 | 82.31
| 14.2222 | 310.283 | 51.428 | 66.903 | 45.74 | 82.292
| 14.2292 | 310.965 | 51.414 | 66.89 | 45.726 | 82.277
| 14.2361 | 310.076 | 51.389 | 66.869 | 45.704 | 82.252
| 14.2431 | 309.328 | 51.344 | 66.84 | 45.672 | 82.198
| 14.25 | 310.026 | 51.313 | 66.807 | 45.647 | 82.164
| 14.2569 | 310.073 | 51.289 | 66.786 | 45.631 | 82.124
| 14.2639 | 308.913 | 51.246 | 66.738 | 45.594 | 82.065
| 14.2708 | 308.728 | 51.207 | 66.697 | 45.56 | 82.011
| 14.2778 | 307.228 | 51.14 | 66.64 | 45.51 | 81.921
| 14.2847 | 305.909 | 51.008 | 66.522 | 45.405 | 81.759
| 14.2917 | 306.834 | 50.927 | 66.435 | 45.333 | 81.647
| 14.2986 | 306.649 | 50.886 | 66.371 | 45.305 | 81.564
| 14.3056 | 305.819 | 50.817 | 66.292 | 45.251 | 81.447
| 14.3125 | 308.907 | 50.865 | 66.292 | 45.28 | 81.46
| 14.3194 | 311.128 | 51.003 | 66.376 | 45.389 | 81.577
| 14.3264 | 310.743 | 51.109 | 66.457 | 45.478 | 81.688
| 14.3333 | 310.358 | 51.165 | 66.502 | 45.52 | 81.758
| 14.3403 | 310.818 | 51.23 | 66.555 | 45.567 | 81.842
| 14.3472 | 310.804 | 51.272 | 66.602 | 45.598 | 81.907
| 14.3542 | 310.264 | 51.286 | 66.623 | 45.606 | 81.947
| 14.3611 | 311.168 | 51.276 | 66.625 | 45.599 | 81.956
| 14.3681 | 309.519 | 51.257 | 66.617 | 45.576 | 81.944
| 14.375 | 309.544 | 51.201 | 66.58 | 45.535 | 81.897
| 14.3819 | 307.883 | 51.135 | 66.53 | 45.483 | 81.832
| 14.3889 | 308.371 | 51.069 | 66.473 | 45.422 | 81.755
| 14.3958 | 307.719 | 51.013 | 66.41 | 45.383 | 81.677
| 14.4028 | 307.268 | 50.968 | 66.366 | 45.349 | 81.614
| 14.4097 | 306.176 | 50.905 | 66.301 | 45.294 | 81.526
| 14.4167 | 306.645 | 50.861 | 66.245 | 45.26 | 81.457
| 14.4236 | 307.538 | 50.835 | 66.208 | 45.24 | 81.412
| 14.4306 | 308.475 | 50.869 | 66.207 | 45.257 | 81.417
| 14.4375 | 307.472 | 50.871 | 66.202 | 45.266 | 81.406
| 14.4444 | 306.584 | 50.821 | 66.143 | 45.218 | 81.339
| 14.4514 | 305.22 | 50.753 | 66.078 | 45.166 | 81.254
| 14.4583 | 310.551 | 50.917 | 66.181 | 45.285 | 81.405
| 14.4653 | 309.42 | 50.991 | 66.239 | 45.35 | 81.483
| 14.4722 | 311.777 | 51.14 | 66.35 | 45.46 | 81.651
| 14.4792 | 312.241 | 51.216 | 66.427 | 45.521 | 81.764
| 14.4861 | 311.778 | 51.265 | 66.489 | 45.559 | 81.851
| 14.4931 | 311.941 | 51.275 | 66.51 | 45.558 | 81.892
| 14.5 | 312.444 | 51.306 | 66.551 | 45.582 | 81.958
| 14.5069 | 311.934 | 51.328 | 66.584 | 45.599 | 82.007
| 14.5139 | 312.287 | 51.343 | 66.617 | 45.611 | 82.048
| 14.5208 | 311.937 | 51.344 | 66.627 | 45.613 | 82.073
| 14.5278 | 309.116 | 51.273 | 66.595 | 45.56 | 82.022
| 14.5347 | 308.741 | 51.157 | 66.502 | 45.459 | 81.905
| 14.5417 | 307.916 | 51.083 | 66.445 | 45.4 | 81.817
| 14.5486 | 309.078 | 51.016 | 66.381 | 45.346 | 81.737
| 14.5556 | 308.835 | 50.997 | 66.346 | 45.334 | 81.693
| 14.5625 | 308.798 | 50.969 | 66.311 | 45.306 | 81.645
| 14.5694 | 309.664 | 50.972 | 66.3 | 45.309 | 81.636
| 14.5764 | 310.183 | 51.019 | 66.324 | 45.347 | 81.674
| 14.5833 | 309.359 | 51.053 | 66.351 | 45.373 | 81.703
| 14.5903 | 309.235 | 51.029 | 66.327 | 45.349 | 81.676
| 14.5972 | 308.887 | 51.003 | 66.304 | 45.328 | 81.648
| 14.6042 | 310.075 | 51.016 | 66.303 | 45.334 | 81.661
| 14.6111 | 310.735 | 51.059 | 66.335 | 45.371 | 81.703
| 14.6181 | 309.974 | 51.089 | 66.358 | 45.392 | 81.743
| 14.625 | 310.752 | 51.131 | 66.392 | 45.424 | 81.789
| 14.6319 | 312.021 | 51.173 | 66.427 | 45.45 | 81.845
| 14.6389 | 311.106 | 51.18 | 66.447 | 45.461 | 81.87
| 14.6458 | 311.439 | 51.213 | 66.474 | 45.483 | 81.922
| 14.6528 | 310.676 | 51.2 | 66.481 | 45.474 | 81.922
| 14.6597 | 311.276 | 51.183 | 66.474 | 45.47 | 81.922
| 14.6667 | 309.817 | 51.155 | 66.46 | 45.445 | 81.903
| 14.6736 | 309.298 | 51.103 | 66.419 | 45.402 | 81.852
| 14.6806 | 309.624 | 51.083 | 66.398 | 45.381 | 81.827
| 14.6875 | 309.904 | 51.06 | 66.372 | 45.361 | 81.792
| 14.6944 | 309.298 | 51.025 | 66.349 | 45.341 | 81.755
| 14.7014 | 309.05 | 50.964 | 66.293 | 45.286 | 81.68
| 14.7083 | 308.303 | 50.937 | 66.263 | 45.269 | 81.64
| 14.7153 | 308.061 | 50.894 | 66.219 | 45.236 | 81.581
| 14.7222 | 308.374 | 50.866 | 66.183 | 45.209 | 81.53
| 14.7292 | 308.332 | 50.832 | 66.143 | 45.182 | 81.48
| 14.7361 | 307.101 | 50.776 | 66.085 | 45.141 | 81.404
| 14.7431 | 310.126 | 50.81 | 66.087 | 45.154 | 81.414
| 14.75 | 307.945 | 50.819 | 66.089 | 45.172 | 81.409
| 14.7569 | 310.961 | 50.95 | 66.175 | 45.269 | 81.529
| 14.7639 | 310.608 | 51.014 | 66.234 | 45.32 | 81.616
| 14.7708 | 310.19 | 51.038 | 66.259 | 45.343 | 81.656
| 14.7778 | 310.054 | 51.026 | 66.255 | 45.325 | 81.652
| 14.7847 | 310.278 | 51.023 | 66.267 | 45.318 | 81.662
| 14.7917 | 310.282 | 51.007 | 66.258 | 45.312 | 81.662
| 14.7986 | 310.224 | 51.023 | 66.271 | 45.323 | 81.676
| 14.8056 | 310.492 | 51.05 | 66.3 | 45.345 | 81.719
| 14.8125 | 310.447 | 51.083 | 66.332 | 45.38 | 81.762
| 14.8194 | 311.04 | 51.125 | 66.37 | 45.41 | 81.814
| 14.8264 | 309.578 | 51.12 | 66.379 | 45.409 | 81.825
| 14.8333 | 310.478 | 51.114 | 66.379 | 45.398 | 81.819
| 14.8403 | 310.907 | 51.137 | 66.409 | 45.421 | 81.865
| 14.8472 | 311.853 | 51.18 | 66.446 | 45.452 | 81.916
| 14.8542 | 312.184 | 51.258 | 66.519 | 45.514 | 82.012
| 14.8611 | 313.234 | 51.304 | 66.57 | 45.555 | 82.077
| 14.8681 | 309.673 | 51.234 | 66.542 | 45.501 | 82.038
| 14.875 | 310.905 | 51.196 | 66.521 | 45.47 | 82.005
| 14.8819 | 311.144 | 51.195 | 66.522 | 45.468 | 82.009
| 14.8889 | 312.454 | 51.254 | 66.575 | 45.519 | 82.077
| 14.8958 | 312.473 | 51.328 | 66.639 | 45.571 | 82.159
| 14.9028 | 307.16 | 51.163 | 66.541 | 45.458 | 82.012
| 14.9097 | 309.932 | 51.17 | 66.539 | 45.457 | 82.016
| 14.9167 | 310.83 | 51.2 | 66.562 | 45.482 | 82.042
| 14.9236 | 311.476 | 51.235 | 66.59 | 45.509 | 82.072
| 14.9306 | 311.403 | 51.274 | 66.631 | 45.552 | 82.126
| 14.9375 | 312.179 | 51.324 | 66.681 | 45.585 | 82.186
| 14.9444 | 312.741 | 51.36 | 66.722 | 45.617 | 82.237
| 14.9514 | 313.25 | 51.409 | 66.77 | 45.65 | 82.306
| 14.9583 | 309.128 | 51.303 | 66.717 | 45.579 | 82.22
| 14.9653 | 309.452 | 51.196 | 66.632 | 45.486 | 82.107
| 14.9722 | 310.724 | 51.198 | 66.629 | 45.488 | 82.09
| 14.9792 | 310.972 | 51.232 | 66.653 | 45.519 | 82.119
| 14.9861 | 309.893 | 51.241 | 66.665 | 45.539 | 82.135
| 14.9931 | 311.311 | 51.26 | 66.677 | 45.543 | 82.151
| 15 | 309.705 | 51.206 | 66.646 | 45.509 | 82.098
| 15.0069 | 308.977 | 51.158 | 66.61 | 45.473 | 82.046
| 15.0139 | 309.569 | 51.155 | 66.598 | 45.468 | 82.03
| 15.0208 | 310.538 | 51.191 | 66.629 | 45.498 | 82.06
| 15.0278 | 309.747 | 51.18 | 66.614 | 45.488 | 82.047
| 15.0347 | 311.361 | 51.212 | 66.638 | 45.515 | 82.075
| 15.0417 | 310.92 | 51.268 | 66.683 | 45.564 | 82.131
| 15.0486 | 311.237 | 51.295 | 66.709 | 45.58 | 82.164
| 15.0556 | 310.59 | 51.293 | 66.715 | 45.582 | 82.176
| 15.0625 | 310.769 | 51.306 | 66.735 | 45.592 | 82.199
| 15.0694 | 310.194 | 51.3 | 66.737 | 45.585 | 82.194
| 15.0764 | 311.176 | 51.314 | 66.758 | 45.596 | 82.219
| 15.0833 | 311.715 | 51.377 | 66.81 | 45.65 | 82.289
| 15.0903 | 312.658 | 51.439 | 66.864 | 45.692 | 82.362
| 15.0972 | 312.605 | 51.46 | 66.901 | 45.717 | 82.406
| 15.1042 | 312.696 | 51.49 | 66.94 | 45.746 | 82.462
| 15.1111 | 310.225 | 51.458 | 66.936 | 45.722 | 82.449
| 15.1181 | 311.077 | 51.406 | 66.902 | 45.672 | 82.41
| 15.125 | 310.666 | 51.39 | 66.891 | 45.663 | 82.387
| 15.1319 | 311.291 | 51.379 | 66.89 | 45.653 | 82.384
| 15.1389 | 310.932 | 51.383 | 66.896 | 45.655 | 82.38
| 15.1458 | 311.297 | 51.392 | 66.899 | 45.667 | 82.393
| 15.1528 | 310.911 | 51.401 | 66.913 | 45.671 | 82.401
| 15.1597 | 311.578 | 51.422 | 66.928 | 45.686 | 82.426
| 15.1667 | 311.747 | 51.438 | 66.943 | 45.7 | 82.445
| 15.1736 | 312.095 | 51.446 | 66.96 | 45.708 | 82.463
| 15.1806 | 312.109 | 51.454 | 66.97 | 45.715 | 82.48
| 15.1875 | 311.713 | 51.466 | 66.988 | 45.725 | 82.507
| 15.1944 | 311.75 | 51.475 | 67.002 | 45.731 | 82.52
| 15.2014 | 311.454 | 51.474 | 67.003 | 45.73 | 82.531
| 15.2083 | 312.435 | 51.504 | 67.033 | 45.75 | 82.565
| 15.2153 | 311.917 | 51.517 | 67.05 | 45.764 | 82.587
| 15.2222 | 311.438 | 51.508 | 67.043 | 45.752 | 82.587
| 15.2292 | 311.463 | 51.499 | 67.047 | 45.746 | 82.587
| 15.2361 | 311.143 | 51.481 | 67.042 | 45.736 | 82.577
| 15.2431 | 311.572 | 51.474 | 67.036 | 45.728 | 82.57
| 15.25 | 311.345 | 51.451 | 67.025 | 45.707 | 82.546
| 15.2569 | 311.826 | 51.429 | 67.005 | 45.691 | 82.521
| 15.2639 | 311.313 | 51.413 | 66.988 | 45.679 | 82.507
| 15.2708 | 310.978 | 51.398 | 66.973 | 45.664 | 82.488
| 15.2778 | 310.62 | 51.36 | 66.946 | 45.637 | 82.438
| 15.2847 | 309.564 | 51.326 | 66.907 | 45.603 | 82.392
| 15.2917 | 309.741 | 51.282 | 66.865 | 45.57 | 82.335
| 15.2986 | 310.099 | 51.264 | 66.844 | 45.561 | 82.31
| 15.3056 | 309.775 | 51.248 | 66.821 | 45.544 | 82.275
| 15.3125 | 310.437 | 51.257 | 66.814 | 45.549 | 82.272
| 15.3194 | 311.891 | 51.322 | 66.85 | 45.595 | 82.333
| 15.3264 | 312.014 | 51.393 | 66.907 | 45.647 | 82.404
| 15.3333 | 312.799 | 51.444 | 66.95 | 45.688 | 82.473
| 15.3403 | 312.134 | 51.469 | 66.981 | 45.71 | 82.518
| 15.3472 | 311.771 | 51.443 | 66.97 | 45.686 | 82.503
| 15.3542 | 311.494 | 51.421 | 66.956 | 45.663 | 82.493
| 15.3611 | 311.087 | 51.39 | 66.93 | 45.638 | 82.464
| 15.3681 | 309.999 | 51.348 | 66.903 | 45.601 | 82.42
| 15.375 | 309.661 | 51.287 | 66.855 | 45.559 | 82.358
| 15.3819 | 309.482 | 51.228 | 66.791 | 45.506 | 82.278
| 15.3889 | 309.088 | 51.175 | 66.739 | 45.461 | 82.21
| 15.3958 | 308.449 | 51.118 | 66.681 | 45.412 | 82.125
| 15.4028 | 307.291 | 51.06 | 66.616 | 45.37 | 82.046
| 15.4097 | 307.473 | 50.991 | 66.541 | 45.313 | 81.948
| 15.4167 | 311.35 | 51.102 | 66.591 | 45.381 | 82.029
| 15.4236 | 311.018 | 51.161 | 66.631 | 45.44 | 82.087
| 15.4306 | 310.62 | 51.197 | 66.653 | 45.461 | 82.123
| 15.4375 | 310.51 | 51.209 | 66.663 | 45.469 | 82.144
| 15.4444 | 310.683 | 51.21 | 66.661 | 45.462 | 82.146
| 15.4514 | 310.273 | 51.179 | 66.638 | 45.438 | 82.121
| 15.4583 | 310.088 | 51.155 | 66.615 | 45.412 | 82.095
| 15.4653 | 309.092 | 51.108 | 66.571 | 45.38 | 82.051
| 15.4722 | 309.399 | 51.077 | 66.538 | 45.356 | 82.011
| 15.4792 | 309.693 | 51.079 | 66.529 | 45.348 | 81.998
| 15.4861 | 308.429 | 51.028 | 66.483 | 45.304 | 81.943
| 15.4931 | 308.263 | 50.98 | 66.435 | 45.268 | 81.882
| 15.5 | 308.272 | 50.94 | 66.38 | 45.228 | 81.819
| 15.5069 | 308.383 | 50.88 | 66.325 | 45.186 | 81.744
| 15.5139 | 307.535 | 50.854 | 66.276 | 45.153 | 81.696
| 15.5208 | 307.182 | 50.816 | 66.24 | 45.127 | 81.639
| 15.5278 | 308.429 | 50.772 | 66.175 | 45.084 | 81.561
| 15.5347 | 307.365 | 50.748 | 66.138 | 45.063 | 81.521
| 15.5417 | 310.998 | 50.953 | 66.276 | 45.225 | 81.724
| 15.5486 | 310.425 | 50.96 | 66.28 | 45.218 | 81.729
| 15.5556 | 309.596 | 50.943 | 66.267 | 45.21 | 81.73
| 15.5625 | 310.128 | 50.938 | 66.253 | 45.196 | 81.728
| 15.5694 | 310.317 | 50.943 | 66.255 | 45.196 | 81.731
| 15.5764 | 310.189 | 50.968 | 66.271 | 45.208 | 81.761
| 15.5833 | 310.688 | 50.985 | 66.285 | 45.224 | 81.796
| 15.5903 | 310.19 | 51.009 | 66.304 | 45.241 | 81.826
| 15.5972 | 311.08 | 51.041 | 66.326 | 45.26 | 81.871
| 15.6042 | 311.05 | 51.071 | 66.354 | 45.283 | 81.919
| 15.6111 | 312.586 | 51.127 | 66.402 | 45.321 | 81.99
| 15.6181 | 312.581 | 51.169 | 66.446 | 45.356 | 82.063
| 15.625 | 312.457 | 51.198 | 66.476 | 45.372 | 82.107
| 15.6319 | 312.851 | 51.226 | 66.507 | 45.392 | 82.165
| 15.6389 | 312.714 | 51.264 | 66.552 | 45.424 | 82.229
| 15.6458 | 313.295 | 51.285 | 66.588 | 45.443 | 82.277
| 15.6528 | 312.409 | 51.314 | 66.625 | 45.455 | 82.339
| 15.6597 | 312.858 | 51.35 | 66.664 | 45.485 | 82.399
| 15.6667 | 313.351 | 51.378 | 66.699 | 45.502 | 82.454
| 15.6736 | 313.782 | 51.397 | 66.735 | 45.52 | 82.508
| 15.6806 | 313.242 | 51.416 | 66.757 | 45.521 | 82.545
| 15.6875 | 313.679 | 51.424 | 66.777 | 45.531 | 82.577
| 15.6944 | 313.273 | 51.427 | 66.794 | 45.531 | 82.61
| 15.7014 | 311.603 | 51.374 | 66.775 | 45.493 | 82.573
| 15.7083 | 312.521 | 51.351 | 66.755 | 45.473 | 82.562
| 15.7153 | 311.469 | 51.313 | 66.738 | 45.442 | 82.532
| 15.7222 | 311.691 | 51.274 | 66.706 | 45.409 | 82.489
| 15.7292 | 310.82 | 51.211 | 66.656 | 45.357 | 82.424
| 15.7361 | 310.456 | 51.127 | 66.591 | 45.291 | 82.331
| 15.7431 | 307.992 | 51.03 | 66.501 | 45.216 | 82.212
| 15.75 | 310.28 | 50.901 | 66.378 | 45.103 | 82.05
| 15.7569 | 309.496 | 50.939 | 66.388 | 45.139 | 82.06
| 15.7639 | 311.448 | 50.973 | 66.389 | 45.158 | 82.068
| 15.7708 | 313.21 | 51.098 | 66.476 | 45.262 | 82.189
| 15.7778 | 312.004 | 51.172 | 66.535 | 45.323 | 82.267
| 15.7847 | 312.353 | 51.185 | 66.55 | 45.328 | 82.302
| 15.7917 | 312.839 | 51.19 | 66.556 | 45.326 | 82.31
| 15.7986 | 311.695 | 51.182 | 66.558 | 45.314 | 82.322
| 15.8056 | 312.375 | 51.188 | 66.568 | 45.317 | 82.341
| 15.8125 | 312.048 | 51.195 | 66.578 | 45.327 | 82.352
| 15.8194 | 311.905 | 51.215 | 66.599 | 45.341 | 82.39
| 15.8264 | 312.85 | 51.244 | 66.625 | 45.357 | 82.427
| 15.8333 | 313.111 | 51.267 | 66.648 | 45.378 | 82.461
| 15.8403 | 313.299 | 51.295 | 66.683 | 45.402 | 82.508
| 15.8472 | 309.404 | 51.118 | 66.555 | 45.26 | 82.341
| 15.8542 | 310.354 | 51.052 | 66.497 | 45.196 | 82.258
| 15.8611 | 310.277 | 51.019 | 66.461 | 45.175 | 82.214
| 15.8681 | 310.666 | 50.997 | 66.437 | 45.157 | 82.174
| 15.875 | 310.881 | 51.013 | 66.43 | 45.171 | 82.175
| 15.8819 | 311.6 | 51.03 | 66.438 | 45.18 | 82.184
| 15.8889 | 311.835 | 51.044 | 66.441 | 45.195 | 82.191
| 15.8958 | 311.461 | 51.076 | 66.458 | 45.215 | 82.221
| 15.9028 | 312.526 | 51.106 | 66.482 | 45.238 | 82.26
| 15.9097 | 312.159 | 51.118 | 66.504 | 45.248 | 82.284
| 15.9167 | 312.552 | 51.141 | 66.519 | 45.265 | 82.311
| 15.9236 | 313.101 | 51.157 | 66.535 | 45.274 | 82.339
| 15.9306 | 313.135 | 51.189 | 66.565 | 45.303 | 82.387
| 15.9375 | 313.334 | 51.215 | 66.6 | 45.325 | 82.422
| 15.9444 | 313.535 | 51.25 | 66.627 | 45.347 | 82.473
| 15.9514 | 313.564 | 51.274 | 66.66 | 45.361 | 82.516
| 15.9583 | 309.654 | 51.095 | 66.538 | 45.226 | 82.346
| 15.9653 | 311.145 | 51.034 | 66.481 | 45.17 | 82.268
| 15.9722 | 310.723 | 51.023 | 66.465 | 45.168 | 82.248
| 15.9792 | 308.299 | 50.877 | 66.349 | 45.052 | 82.08
| 15.9861 | 309.643 | 50.851 | 66.303 | 45.031 | 82.029
| 15.9931 | 310.211 | 50.859 | 66.29 | 45.035 | 82.004
| 16 | 308.519 | 50.815 | 66.252 | 45.007 | 81.943
| 16.0069 | 308.557 | 50.793 | 66.213 | 44.982 | 81.899
| 16.0139 | 309.112 | 50.767 | 66.181 | 44.969 | 81.858
| 16.0208 | 309.126 | 50.747 | 66.144 | 44.944 | 81.814
| 16.0278 | 309.453 | 50.743 | 66.125 | 44.944 | 81.788
| 16.0347 | 310.002 | 50.785 | 66.146 | 44.971 | 81.818
| 16.0417 | 310.643 | 50.825 | 66.168 | 44.999 | 81.849
| 16.0486 | 310.587 | 50.86 | 66.196 | 45.027 | 81.888
| 16.0556 | 310.717 | 50.857 | 66.196 | 45.029 | 81.892
| 16.0625 | 309.681 | 50.861 | 66.193 | 45.023 | 81.897
| 16.0694 | 310.458 | 50.859 | 66.2 | 45.029 | 81.897
| 16.0764 | 310.903 | 50.864 | 66.197 | 45.024 | 81.905
| 16.0833 | 311.072 | 50.882 | 66.213 | 45.041 | 81.928
| 16.0903 | 311.401 | 50.894 | 66.22 | 45.049 | 81.948
| 16.0972 | 310.871 | 50.911 | 66.234 | 45.06 | 81.965
| 16.1042 | 310.976 | 50.925 | 66.248 | 45.071 | 81.99
| 16.1111 | 311.347 | 50.933 | 66.262 | 45.073 | 82.003
| 16.1181 | 311.32 | 50.951 | 66.281 | 45.089 | 82.029
| 16.125 | 311.275 | 50.963 | 66.291 | 45.099 | 82.053
| 16.1319 | 312.021 | 50.967 | 66.302 | 45.101 | 82.067
| 16.1389 | 312.054 | 50.999 | 66.328 | 45.126 | 82.105
| 16.1458 | 312.26 | 51.028 | 66.36 | 45.144 | 82.143
| 16.1528 | 312.18 | 51.029 | 66.37 | 45.155 | 82.171
| 16.1597 | 312.799 | 51.061 | 66.401 | 45.173 | 82.209
| 16.1667 | 311.666 | 51.066 | 66.418 | 45.183 | 82.226
| 16.1736 | 311.849 | 51.083 | 66.438 | 45.189 | 82.256
| 16.1806 | 312.471 | 51.086 | 66.446 | 45.195 | 82.273
| 16.1875 | 312.294 | 51.088 | 66.455 | 45.194 | 82.283
| 16.1944 | 311.585 | 51.072 | 66.457 | 45.187 | 82.288
| 16.2014 | 311.145 | 51.026 | 66.427 | 45.15 | 82.239
| 16.2083 | 310.736 | 50.999 | 66.404 | 45.124 | 82.217
| 16.2153 | 311.477 | 50.97 | 66.383 | 45.1 | 82.182
| 16.2222 | 310.783 | 50.939 | 66.354 | 45.08 | 82.142
| 16.2292 | 309.886 | 50.901 | 66.318 | 45.043 | 82.091
| 16.2361 | 308.966 | 50.823 | 66.254 | 44.984 | 81.998
| 16.2431 | 306.992 | 50.691 | 66.143 | 44.877 | 81.846
| 16.25 | 307.161 | 50.604 | 66.049 | 44.811 | 81.721
| 16.2569 | 311.042 | 50.584 | 66.005 | 44.786 | 81.663
| 16.2639 | 309.934 | 50.707 | 66.079 | 44.889 | 81.764
| 16.2708 | 309.399 | 50.736 | 66.095 | 44.913 | 81.784
| 16.2778 | 310.884 | 50.753 | 66.094 | 44.918 | 81.792
| 16.2847 | 308.49 | 50.643 | 66.014 | 44.838 | 81.682
| 16.2917 | 308.88 | 50.628 | 65.986 | 44.822 | 81.65
| 16.2986 | 307.496 | 50.593 | 65.956 | 44.792 | 81.603
| 16.3056 | 311.065 | 50.615 | 65.941 | 44.797 | 81.605
| 16.3125 | 310.585 | 50.702 | 66.007 | 44.872 | 81.68
| 16.3194 | 310.598 | 50.732 | 66.026 | 44.902 | 81.72
| 16.3264 | 310.232 | 50.729 | 66.028 | 44.89 | 81.722
| 16.3333 | 308.45 | 50.695 | 65.998 | 44.863 | 81.686
| 16.3403 | 308.362 | 50.645 | 65.962 | 44.818 | 81.641
| 16.3472 | 308.029 | 50.564 | 65.894 | 44.76 | 81.548
| 16.3542 | 314.409 | 50.681 | 65.955 | 44.834 | 81.642
| 16.3611 | 310.948 | 50.752 | 66.019 | 44.906 | 81.731
| 16.3681 | 310.51 | 50.722 | 66.003 | 44.879 | 81.713
| 16.375 | 309.438 | 50.712 | 65.997 | 44.876 | 81.699
| 16.3819 | 307.985 | 50.661 | 65.961 | 44.829 | 81.654
| 16.3889 | 309.38 | 50.606 | 65.908 | 44.778 | 81.589
| 16.3958 | 309.832 | 50.604 | 65.9 | 44.777 | 81.582
| 16.4028 | 309.883 | 50.618 | 65.906 | 44.784 | 81.584
| 16.4097 | 309.154 | 50.609 | 65.893 | 44.782 | 81.572
| 16.4167 | 308.775 | 50.576 | 65.859 | 44.751 | 81.529
| 16.4236 | 308.148 | 50.515 | 65.805 | 44.702 | 81.463
| 16.4306 | 307.33 | 50.449 | 65.748 | 44.653 | 81.378
| 16.4375 | 306.852 | 50.397 | 65.685 | 44.604 | 81.303
| 16.4444 | 313.717 | 50.58 | 65.788 | 44.732 | 81.459
| 16.4514 | 309.491 | 50.636 | 65.853 | 44.8 | 81.531
| 16.4583 | 310.044 | 50.637 | 65.862 | 44.799 | 81.553
| 16.4653 | 310.706 | 50.657 | 65.873 | 44.807 | 81.579
| 16.4722 | 309.741 | 50.622 | 65.853 | 44.775 | 81.555
| 16.4792 | 310.249 | 50.621 | 65.854 | 44.774 | 81.563
| 16.4861 | 310.182 | 50.628 | 65.855 | 44.776 | 81.568
| 16.4931 | 308.897 | 50.601 | 65.837 | 44.759 | 81.547
| 16.5 | 309.485 | 50.589 | 65.828 | 44.745 | 81.544
| 16.5069 | 310.971 | 50.616 | 65.843 | 44.758 | 81.559
| 16.5139 | 310.993 | 50.647 | 65.871 | 44.785 | 81.602
| 16.5208 | 310.866 | 50.679 | 65.895 | 44.811 | 81.641
| 16.5278 | 309.964 | 50.683 | 65.908 | 44.817 | 81.655
| 16.5347 | 309.823 | 50.66 | 65.892 | 44.793 | 81.636
| 16.5417 | 310.229 | 50.648 | 65.884 | 44.784 | 81.631
| 16.5486 | 310.626 | 50.634 | 65.868 | 44.765 | 81.623
| 16.5556 | 310.098 | 50.653 | 65.883 | 44.78 | 81.643
| 16.5625 | 310.728 | 50.675 | 65.909 | 44.799 | 81.666
| 16.5694 | 310.551 | 50.662 | 65.894 | 44.79 | 81.665
| 16.5764 | 309.797 | 50.639 | 65.876 | 44.762 | 81.637
| 16.5833 | 310.338 | 50.631 | 65.869 | 44.755 | 81.635
| 16.5903 | 310.527 | 50.627 | 65.867 | 44.753 | 81.633
| 16.5972 | 311.14 | 50.637 | 65.875 | 44.755 | 81.648
| 16.6042 | 311.036 | 50.646 | 65.88 | 44.765 | 81.657
| 16.6111 | 311.146 | 50.673 | 65.901 | 44.782 | 81.694
| 16.6181 | 310.877 | 50.694 | 65.92 | 44.799 | 81.717
| 16.625 | 310.181 | 50.659 | 65.902 | 44.769 | 81.694
| 16.6319 | 310.684 | 50.588 | 65.844 | 44.706 | 81.617
| 16.6389 | 309.869 | 50.574 | 65.828 | 44.698 | 81.598
| 16.6458 | 309.637 | 50.55 | 65.803 | 44.681 | 81.573
| 16.6528 | 309.84 | 50.551 | 65.798 | 44.678 | 81.566
| 16.6597 | 310.181 | 50.535 | 65.782 | 44.663 | 81.543
| 16.6667 | 309.89 | 50.531 | 65.775 | 44.663 | 81.539
| 16.6736 | 309.831 | 50.527 | 65.764 | 44.65 | 81.525
| 16.6806 | 310.602 | 50.543 | 65.767 | 44.662 | 81.531
| 16.6875 | 310.71 | 50.559 | 65.779 | 44.676 | 81.551
| 16.6944 | 309.632 | 50.574 | 65.788 | 44.685 | 81.568
| 16.7014 | 309.9 | 50.571 | 65.788 | 44.683 | 81.567
| 16.7083 | 309.363 | 50.584 | 65.794 | 44.697 | 81.584
| 16.7153 | 309.711 | 50.565 | 65.779 | 44.675 | 81.568
| 16.7222 | 310.285 | 50.566 | 65.782 | 44.674 | 81.574
| 16.7292 | 309.574 | 50.532 | 65.756 | 44.642 | 81.536
| 16.7361 | 310.846 | 50.547 | 65.76 | 44.655 | 81.551
| 16.7431 | 307.456 | 50.522 | 65.745 | 44.641 | 81.532
| 16.75 | 310.998 | 50.467 | 65.692 | 44.584 | 81.463
| 16.7569 | 309.598 | 50.489 | 65.706 | 44.604 | 81.479
| 16.7639 | 310.715 | 50.515 | 65.716 | 44.621 | 81.503
| 16.7708 | 310.922 | 50.551 | 65.742 | 44.653 | 81.546
| 16.7778 | 311.962 | 50.594 | 65.779 | 44.686 | 81.597
| 16.7847 | 312.6 | 50.674 | 65.847 | 44.748 | 81.694
| 16.7917 | 312.353 | 50.741 | 65.912 | 44.795 | 81.78
| 16.7986 | 312.64 | 50.783 | 65.959 | 44.83 | 81.854
| 16.8056 | 312.896 | 50.812 | 65.997 | 44.854 | 81.913
| 16.8125 | 313.139 | 50.833 | 66.031 | 44.866 | 81.956
| 16.8194 | 313.544 | 50.856 | 66.063 | 44.88 | 82.004
| 16.8264 | 313.529 | 50.891 | 66.105 | 44.91 | 82.063
| 16.8333 | 309.955 | 50.713 | 65.995 | 44.776 | 81.91
| 16.8403 | 310.626 | 50.659 | 65.945 | 44.727 | 81.844
| 16.8472 | 311.879 | 50.654 | 65.943 | 44.727 | 81.835
| 16.8542 | 310.679 | 50.673 | 65.952 | 44.743 | 81.849
| 16.8611 | 307.45 | 50.515 | 65.83 | 44.622 | 81.68
| 16.8681 | 307.22 | 50.384 | 65.715 | 44.512 | 81.528
| 16.875 | 308.175 | 50.312 | 65.633 | 44.447 | 81.409
| 16.8819 | 309.049 | 50.305 | 65.599 | 44.441 | 81.365
| 16.8889 | 309.076 | 50.306 | 65.578 | 44.446 | 81.343
| 16.8958 | 310.597 | 50.35 | 65.6 | 44.483 | 81.364
| 16.9028 | 310.341 | 50.386 | 65.617 | 44.506 | 81.389
| 16.9097 | 310.481 | 50.411 | 65.628 | 44.524 | 81.411
| 16.9167 | 310.356 | 50.434 | 65.643 | 44.538 | 81.436
| 16.9236 | 312.681 | 50.503 | 65.693 | 44.592 | 81.506
| 16.9306 | 313.334 | 50.597 | 65.765 | 44.667 | 81.613
| 16.9375 | 309.444 | 50.49 | 65.706 | 44.581 | 81.528
| 16.9444 | 308.794 | 50.355 | 65.595 | 44.47 | 81.381
| 16.9514 | 309.424 | 50.344 | 65.578 | 44.462 | 81.354
| 16.9583 | 310.08 | 50.37 | 65.582 | 44.482 | 81.367
| 16.9653 | 310.203 | 50.38 | 65.586 | 44.488 | 81.376
| 16.9722 | 311.518 | 50.449 | 65.634 | 44.542 | 81.442
| 16.9792 | 311.418 | 50.515 | 65.692 | 44.599 | 81.517
| 16.9861 | 312.645 | 50.565 | 65.74 | 44.635 | 81.59
| 16.9931 | 308.787 | 50.56 | 65.756 | 44.638 | 81.604
| 17 | 310.075 | 50.36 | 65.589 | 44.463 | 81.404
| 17.0069 | 310.465 | 50.397 | 65.616 | 44.493 | 81.425
| 17.0139 | 311.007 | 50.427 | 65.638 | 44.527 | 81.454
| 17.0208 | 311.373 | 50.483 | 65.672 | 44.564 | 81.51
| 17.0278 | 311.693 | 50.512 | 65.704 | 44.595 | 81.551
| 17.0347 | 311.409 | 50.524 | 65.718 | 44.595 | 81.572
| 17.0417 | 311.223 | 50.525 | 65.723 | 44.599 | 81.583
| 17.0486 | 310.825 | 50.514 | 65.723 | 44.591 | 81.581
| 17.0556 | 310.512 | 50.505 | 65.717 | 44.583 | 81.58
| 17.0625 | 310.681 | 50.497 | 65.709 | 44.575 | 81.574
| 17.0694 | 311.063 | 50.511 | 65.726 | 44.583 | 81.588
| 17.0764 | 311.603 | 50.548 | 65.756 | 44.604 | 81.631
| 17.0833 | 311.462 | 50.577 | 65.783 | 44.631 | 81.668
| 17.0903 | 311.544 | 50.574 | 65.794 | 44.633 | 81.678
| 17.0972 | 312.065 | 50.582 | 65.806 | 44.637 | 81.702
| 17.1042 | 311.81 | 50.611 | 65.83 | 44.658 | 81.735
| 17.1111 | 313.18 | 50.652 | 65.87 | 44.688 | 81.794
| 17.1181 | 309.245 | 50.541 | 65.802 | 44.604 | 81.698
| 17.125 | 309.778 | 50.456 | 65.731 | 44.532 | 81.602
| 17.1319 | 310.182 | 50.417 | 65.694 | 44.502 | 81.547
| 17.1389 | 309.675 | 50.369 | 65.65 | 44.466 | 81.489
| 17.1458 | 309.746 | 50.34 | 65.618 | 44.442 | 81.436
| 17.1528 | 310.08 | 50.34 | 65.601 | 44.442 | 81.419
| 17.1597 | 310.262 | 50.348 | 65.597 | 44.444 | 81.415
| 17.1667 | 307.683 | 50.331 | 65.588 | 44.441 | 81.392
| 17.1736 | 307.435 | 50.227 | 65.496 | 44.352 | 81.277
| 17.1806 | 307.764 | 50.158 | 65.425 | 44.293 | 81.18
| 17.1875 | 307.359 | 50.124 | 65.378 | 44.261 | 81.116
| 17.1944 | 307.515 | 50.098 | 65.336 | 44.242 | 81.059
| 17.2014 | 306.815 | 50.039 | 65.275 | 44.197 | 80.973
| 17.2083 | 310.947 | 50.05 | 65.253 | 44.193 | 80.956
| 17.2153 | 309.823 | 50.19 | 65.352 | 44.316 | 81.094
| 17.2222 | 310.502 | 50.241 | 65.394 | 44.352 | 81.145
| 17.2292 | 309.791 | 50.254 | 65.401 | 44.36 | 81.168
| 17.2361 | 309.706 | 50.253 | 65.409 | 44.36 | 81.179
| 17.2431 | 309.842 | 50.217 | 65.375 | 44.326 | 81.141
| 17.25 | 309.807 | 50.221 | 65.381 | 44.332 | 81.151
| 17.2569 | 309.959 | 50.219 | 65.374 | 44.324 | 81.143
| 17.2639 | 308.564 | 50.198 | 65.364 | 44.306 | 81.123
| 17.2708 | 308.713 | 50.159 | 65.326 | 44.278 | 81.08
| 17.2778 | 309.855 | 50.148 | 65.305 | 44.257 | 81.051
| 17.2847 | 310.224 | 50.149 | 65.296 | 44.255 | 81.048
| 17.2917 | 311.474 | 50.289 | 65.4 | 44.376 | 81.193
| 17.2986 | 310.912 | 50.348 | 65.46 | 44.422 | 81.276
| 17.3056 | 310.629 | 50.349 | 65.473 | 44.425 | 81.295
| 17.3125 | 309.461 | 50.312 | 65.452 | 44.392 | 81.273
| 17.3194 | 310.234 | 50.244 | 65.406 | 44.334 | 81.211
| 17.3264 | 308.893 | 50.238 | 65.402 | 44.334 | 81.203
| 17.3333 | 308.177 | 50.181 | 65.363 | 44.292 | 81.143
| 17.3403 | 307.766 | 50.121 | 65.304 | 44.239 | 81.069
| 17.3472 | 307.809 | 50.071 | 65.252 | 44.198 | 81.004
| 17.3542 | 307.251 | 50.016 | 65.194 | 44.148 | 80.924
| 17.3611 | 310.936 | 50.113 | 65.246 | 44.215 | 80.998
| 17.3681 | 310.122 | 50.199 | 65.321 | 44.306 | 81.092
| 17.375 | 310.619 | 50.224 | 65.343 | 44.314 | 81.132
| 17.3819 | 309.671 | 50.244 | 65.365 | 44.331 | 81.167
| 17.3889 | 310.038 | 50.251 | 65.373 | 44.33 | 81.187
| 17.3958 | 310.558 | 50.247 | 65.373 | 44.327 | 81.186
| 17.4028 | 313.596 | 50.285 | 65.397 | 44.345 | 81.229
| 17.4097 | 314.017 | 50.459 | 65.549 | 44.494 | 81.432
| 17.4167 | 312.471 | 50.535 | 65.629 | 44.554 | 81.539
| 17.4236 | 312.394 | 50.556 | 65.667 | 44.571 | 81.598
| 17.4306 | 312.423 | 50.564 | 65.696 | 44.576 | 81.645
| 17.4375 | 311.931 | 50.575 | 65.727 | 44.581 | 81.682
| 17.4444 | 311.589 | 50.541 | 65.722 | 44.557 | 81.675
| 17.4514 | 311.837 | 50.56 | 65.745 | 44.572 | 81.712
| 17.4583 | 312.489 | 50.575 | 65.771 | 44.582 | 81.745
| 17.4653 | 312.018 | 50.591 | 65.796 | 44.597 | 81.776
| 17.4722 | 311.765 | 50.568 | 65.791 | 44.578 | 81.77
| 17.4792 | 311.887 | 50.562 | 65.798 | 44.575 | 81.778
| 17.4861 | 311.801 | 50.514 | 65.774 | 44.541 | 81.746
| 17.4931 | 311.284 | 50.493 | 65.754 | 44.517 | 81.719
| 17.5 | 312.077 | 50.478 | 65.744 | 44.501 | 81.702
| 17.5069 | 311.627 | 50.467 | 65.739 | 44.498 | 81.693
| 17.5139 | 311.744 | 50.453 | 65.722 | 44.482 | 81.673
| 17.5208 | 311.607 | 50.459 | 65.733 | 44.489 | 81.682
| 17.5278 | 314.058 | 50.509 | 65.769 | 44.53 | 81.734
| 17.5347 | 309.688 | 50.436 | 65.729 | 44.481 | 81.674
| 17.5417 | 309.624 | 50.363 | 65.661 | 44.406 | 81.583
| 17.5486 | 310.541 | 50.313 | 65.612 | 44.366 | 81.523
| 17.5556 | 310.357 | 50.284 | 65.58 | 44.346 | 81.472
| 17.5625 | 309.664 | 50.27 | 65.56 | 44.334 | 81.45
| 17.5694 | 310.723 | 50.246 | 65.529 | 44.314 | 81.401
| 17.5764 | 310.197 | 50.222 | 65.503 | 44.294 | 81.369
| 17.5833 | 310.276 | 50.208 | 65.479 | 44.279 | 81.339
| 17.5903 | 310.334 | 50.225 | 65.487 | 44.293 | 81.343
| 17.5972 | 310.479 | 50.235 | 65.485 | 44.294 | 81.352
| 17.6042 | 311.683 | 50.263 | 65.496 | 44.313 | 81.366
| 17.6111 | 311.101 | 50.295 | 65.514 | 44.344 | 81.4
| 17.6181 | 310.664 | 50.299 | 65.522 | 44.349 | 81.409
| 17.625 | 311.064 | 50.3 | 65.519 | 44.341 | 81.412
| 17.6319 | 311.914 | 50.294 | 65.526 | 44.342 | 81.418
| 17.6389 | 310.865 | 50.311 | 65.534 | 44.342 | 81.432
| 17.6458 | 311.169 | 50.3 | 65.528 | 44.346 | 81.433
| 17.6528 | 310.555 | 50.302 | 65.53 | 44.344 | 81.439
| 17.6597 | 310.756 | 50.283 | 65.514 | 44.324 | 81.416
| 17.6667 | 309.016 | 50.208 | 65.452 | 44.266 | 81.335
| 17.6736 | 308.42 | 50.126 | 65.387 | 44.197 | 81.24
| 17.6806 | 308.585 | 50.08 | 65.336 | 44.161 | 81.171
| 17.6875 | 309.545 | 50.054 | 65.297 | 44.138 | 81.123
| 17.6944 | 309.531 | 50.047 | 65.281 | 44.135 | 81.101
| 17.7014 | 308.537 | 50.041 | 65.265 | 44.133 | 81.082
| 17.7083 | 308.47 | 50.048 | 65.254 | 44.127 | 81.069
| 17.7153 | 309.319 | 50.045 | 65.25 | 44.127 | 81.057
| 17.7222 | 309.37 | 50.05 | 65.241 | 44.134 | 81.058
| 17.7292 | 308.006 | 50.018 | 65.204 | 44.103 | 81.013
| 17.7361 | 307.842 | 49.969 | 65.162 | 44.057 | 80.952
| 17.7431 | 310.176 | 49.971 | 65.148 | 44.058 | 80.943
| 17.75 | 309.681 | 50.015 | 65.175 | 44.095 | 80.972
| 17.7569 | 309.63 | 50.029 | 65.182 | 44.106 | 80.988
| 17.7639 | 309.797 | 50.052 | 65.196 | 44.12 | 81.013
| 17.7708 | 310.634 | 50.074 | 65.206 | 44.136 | 81.039
| 17.7778 | 310.976 | 50.112 | 65.236 | 44.167 | 81.082
| 17.7847 | 311.069 | 50.178 | 65.297 | 44.216 | 81.168
| 17.7917 | 311.428 | 50.198 | 65.313 | 44.23 | 81.193
| 17.7986 | 311.128 | 50.208 | 65.337 | 44.239 | 81.224
| 17.8056 | 309.102 | 50.16 | 65.313 | 44.206 | 81.192
| 17.8125 | 309.262 | 50.073 | 65.242 | 44.133 | 81.101
| 17.8194 | 309.994 | 50.058 | 65.228 | 44.118 | 81.076
| 17.8264 | 310.963 | 50.092 | 65.249 | 44.145 | 81.105
| 17.8333 | 310.901 | 50.137 | 65.285 | 44.185 | 81.156
| 17.8403 | 311.962 | 50.165 | 65.299 | 44.2 | 81.184
| 17.8472 | 311.009 | 50.195 | 65.333 | 44.232 | 81.237
| 17.8542 | 312.301 | 50.223 | 65.368 | 44.255 | 81.272
| 17.8611 | 309.107 | 50.201 | 65.369 | 44.241 | 81.266
| 17.8681 | 309.543 | 50.113 | 65.3 | 44.162 | 81.184
| 17.875 | 309.947 | 50.088 | 65.277 | 44.142 | 81.159
| 17.8819 | 310.206 | 50.107 | 65.289 | 44.157 | 81.161
| 17.8889 | 310.179 | 50.136 | 65.312 | 44.18 | 81.188
| 17.8958 | 311.166 | 50.14 | 65.309 | 44.182 | 81.189
| 17.9028 | 310.682 | 50.164 | 65.335 | 44.207 | 81.219
| 17.9097 | 311.216 | 50.18 | 65.347 | 44.218 | 81.244
| 17.9167 | 310.692 | 50.185 | 65.361 | 44.221 | 81.259
| 17.9236 | 311.404 | 50.194 | 65.373 | 44.221 | 81.272
| 17.9306 | 312.189 | 50.236 | 65.409 | 44.261 | 81.325
| 17.9375 | 312.882 | 50.318 | 65.478 | 44.328 | 81.421
| 17.9444 | 309.202 | 50.217 | 65.426 | 44.252 | 81.338
| 17.9514 | 307.072 | 50.097 | 65.347 | 44.162 | 81.225
| 17.9583 | 307.469 | 49.966 | 65.226 | 44.045 | 81.067
| 17.9653 | 308.996 | 49.902 | 65.161 | 43.998 | 80.97
| 17.9722 | 309.895 | 49.935 | 65.159 | 44.02 | 80.973
| 17.9792 | 309.582 | 49.97 | 65.173 | 44.051 | 80.992
| 17.9861 | 310.884 | 49.998 | 65.186 | 44.068 | 81.011
| 17.9931 | 311.691 | 50.07 | 65.239 | 44.128 | 81.075
| 18 | 311.641 | 50.134 | 65.299 | 44.184 | 81.159
| 18.0069 | 311.233 | 50.179 | 65.339 | 44.219 | 81.22
| 18.0139 | 309.081 | 50.164 | 65.346 | 44.211 | 81.222
| 18.0208 | 308.486 | 50.052 | 65.264 | 44.114 | 81.108
| 18.0278 | 309.668 | 50.027 | 65.244 | 44.093 | 81.074
| 18.0347 | 309.313 | 50.026 | 65.234 | 44.092 | 81.066
| 18.0417 | 310.757 | 49.988 | 65.191 | 44.052 | 81.016
| 18.0486 | 310.931 | 50.039 | 65.226 | 44.102 | 81.061
| 18.0556 | 309.728 | 50.032 | 65.229 | 44.096 | 81.054
| 18.0625 | 313.306 | 50.122 | 65.281 | 44.155 | 81.141
| 18.0694 | 309.685 | 50.045 | 65.236 | 44.104 | 81.075
| 18.0764 | 309.627 | 50.012 | 65.209 | 44.072 | 81.036
| 18.0833 | 309.267 | 49.992 | 65.187 | 44.055 | 81.003
| 18.0903 | 309.353 | 49.967 | 65.17 | 44.039 | 80.975
| 18.0972 | 309.834 | 49.959 | 65.161 | 44.035 | 80.961
| 18.1042 | 310.091 | 49.961 | 65.149 | 44.031 | 80.951
| 18.1111 | 310.708 | 50.009 | 65.183 | 44.08 | 81
| 18.1181 | 310.725 | 50.046 | 65.213 | 44.102 | 81.04
| 18.125 | 310.465 | 50.064 | 65.226 | 44.112 | 81.061
| 18.1319 | 310.412 | 50.046 | 65.222 | 44.101 | 81.057
| 18.1389 | 310.419 | 50.037 | 65.219 | 44.086 | 81.046
| 18.1458 | 311.099 | 50.053 | 65.226 | 44.098 | 81.065
| 18.1528 | 310.336 | 50.074 | 65.249 | 44.12 | 81.092
| 18.1597 | 310.908 | 50.089 | 65.266 | 44.134 | 81.118
| 18.1667 | 310.766 | 50.096 | 65.273 | 44.132 | 81.134
| 18.1736 | 310.384 | 50.097 | 65.285 | 44.138 | 81.14
| 18.1806 | 310.998 | 50.111 | 65.294 | 44.144 | 81.156
| 18.1875 | 310.216 | 50.094 | 65.287 | 44.13 | 81.145
| 18.1944 | 309.794 | 50.076 | 65.277 | 44.12 | 81.134
| 18.2014 | 309.16 | 50.042 | 65.25 | 44.087 | 81.095
| 18.2083 | 310.497 | 50.03 | 65.235 | 44.077 | 81.081
| 18.2153 | 310.613 | 50.034 | 65.235 | 44.082 | 81.079
| 18.2222 | 309.879 | 50.01 | 65.223 | 44.068 | 81.056
| 18.2292 | 308.778 | 49.972 | 65.191 | 44.036 | 81.014
| 18.2361 | 309.133 | 49.937 | 65.156 | 44.004 | 80.968
| 18.2431 | 308.311 | 49.881 | 65.107 | 43.955 | 80.898
| 18.25 | 309.489 | 49.829 | 65.052 | 43.912 | 80.826
| 18.2569 | 308.595 | 49.848 | 65.052 | 43.926 | 80.825
| 18.2639 | 308.127 | 49.819 | 65.022 | 43.912 | 80.782
| 18.2708 | 309.855 | 49.878 | 65.056 | 43.953 | 80.834
| 18.2778 | 308.311 | 49.893 | 65.067 | 43.965 | 80.836
| 18.2847 | 308.266 | 49.83 | 65.008 | 43.912 | 80.776
| 18.2917 | 309.189 | 49.831 | 65.005 | 43.915 | 80.766
| 18.2986 | 309.878 | 49.873 | 65.026 | 43.941 | 80.797
| 18.3056 | 309.6 | 49.855 | 65.015 | 43.928 | 80.785
| 18.3125 | 309.501 | 49.836 | 64.998 | 43.914 | 80.764
| 18.3194 | 308.481 | 49.8 | 64.965 | 43.88 | 80.719
| 18.3264 | 308.729 | 49.789 | 64.949 | 43.871 | 80.699
| 18.3333 | 308.137 | 49.78 | 64.933 | 43.867 | 80.68
| 18.3403 | 307.877 | 49.724 | 64.887 | 43.82 | 80.615
| 18.3472 | 307.975 | 49.673 | 64.835 | 43.783 | 80.549
| 18.3542 | 308.784 | 49.709 | 64.846 | 43.803 | 80.566
| 18.3611 | 309.263 | 49.73 | 64.854 | 43.815 | 80.582
| 18.3681 | 307.299 | 49.716 | 64.846 | 43.813 | 80.563
| 18.375 | 306.935 | 49.678 | 64.806 | 43.786 | 80.511
| 18.3819 | 307.857 | 49.622 | 64.757 | 43.738 | 80.451
| 18.3889 | 311.563 | 49.796 | 64.871 | 43.865 | 80.61
| 18.3958 | 310.794 | 49.884 | 64.946 | 43.933 | 80.71
| 18.4028 | 311.888 | 49.965 | 65.015 | 43.999 | 80.821
| 18.4097 | 312.881 | 50.098 | 65.129 | 44.1 | 80.98
| 18.4167 | 312.16 | 50.163 | 65.212 | 44.152 | 81.092
| 18.4236 | 312.99 | 50.174 | 65.246 | 44.164 | 81.147
| 18.4306 | 311.915 | 50.165 | 65.265 | 44.155 | 81.171
| 18.4375 | 312.544 | 50.173 | 65.29 | 44.156 | 81.207
| 18.4444 | 311.928 | 50.176 | 65.31 | 44.166 | 81.233
| 18.4514 | 312.457 | 50.195 | 65.337 | 44.174 | 81.272
| 18.4583 | 313.04 | 50.217 | 65.368 | 44.193 | 81.321
| 18.4653 | 313.06 | 50.238 | 65.399 | 44.209 | 81.363
| 18.4722 | 311.408 | 50.228 | 65.411 | 44.202 | 81.373
| 18.4792 | 312.185 | 50.23 | 65.419 | 44.204 | 81.39
| 18.4861 | 312.06 | 50.227 | 65.428 | 44.198 | 81.398
| 18.4931 | 312.429 | 50.202 | 65.424 | 44.189 | 81.391
| 18.5 | 312.639 | 50.226 | 65.449 | 44.198 | 81.419
| 18.5069 | 312.31 | 50.25 | 65.474 | 44.222 | 81.456
| 18.5139 | 313.615 | 50.279 | 65.506 | 44.246 | 81.496
| 18.5208 | 309.002 | 50.147 | 65.418 | 44.141 | 81.371
| 18.5278 | 310.223 | 50.059 | 65.349 | 44.062 | 81.274
| 18.5347 | 310.781 | 50.033 | 65.317 | 44.042 | 81.233
| 18.5417 | 310.205 | 50.013 | 65.297 | 44.031 | 81.201
| 18.5486 | 312.171 | 50.014 | 65.286 | 44.032 | 81.184
| 18.5556 | 311.29 | 50.024 | 65.288 | 44.033 | 81.187
| 18.5625 | 310.736 | 50.009 | 65.27 | 44.026 | 81.161
| 18.5694 | 310.667 | 50.021 | 65.279 | 44.033 | 81.165
| 18.5764 | 309.826 | 49.989 | 65.251 | 44.013 | 81.133
| 18.5833 | 310.201 | 49.95 | 65.216 | 43.98 | 81.089
| 18.5903 | 310.084 | 49.936 | 65.195 | 43.966 | 81.057
| 18.5972 | 308.14 | 49.858 | 65.135 | 43.904 | 80.975
| 18.6042 | 308.731 | 49.8 | 65.073 | 43.856 | 80.891
| 18.6111 | 309.978 | 49.786 | 65.047 | 43.839 | 80.857
| 18.6181 | 309.589 | 49.76 | 65.015 | 43.828 | 80.809
| 18.625 | 310.145 | 49.769 | 65.002 | 43.824 | 80.799
| 18.6319 | 309.08 | 49.747 | 64.977 | 43.813 | 80.755
| 18.6389 | 308.998 | 49.752 | 64.969 | 43.813 | 80.758
| 18.6458 | 309.653 | 49.748 | 64.957 | 43.81 | 80.737
| 18.6528 | 308.942 | 49.728 | 64.926 | 43.788 | 80.704
| 18.6597 | 308.474 | 49.694 | 64.894 | 43.757 | 80.659
| 18.6667 | 309.293 | 49.673 | 64.866 | 43.741 | 80.629
| 18.6736 | 309.094 | 49.669 | 64.852 | 43.743 | 80.609
| 18.6806 | 309.301 | 49.653 | 64.828 | 43.723 | 80.582
| 18.6875 | 308.994 | 49.652 | 64.819 | 43.72 | 80.567
| 18.6944 | 309.569 | 49.647 | 64.802 | 43.718 | 80.55
| 18.7014 | 309.433 | 49.643 | 64.788 | 43.712 | 80.535
| 18.7083 | 309.516 | 49.672 | 64.807 | 43.737 | 80.56
| 18.7153 | 309.416 | 49.659 | 64.791 | 43.724 | 80.543
| 18.7222 | 309.989 | 49.664 | 64.792 | 43.725 | 80.546
| 18.7292 | 308.684 | 49.634 | 64.765 | 43.708 | 80.517
| 18.7361 | 307.85 | 49.586 | 64.723 | 43.665 | 80.462
| 18.7431 | 305.75 | 49.499 | 64.652 | 43.603 | 80.361
| 18.75 | 310.497 | 49.58 | 64.683 | 43.653 | 80.417
| 18.7569 | 310.257 | 49.661 | 64.754 | 43.73 | 80.498
| 18.7639 | 310.297 | 49.701 | 64.779 | 43.752 | 80.541
| 18.7708 | 311.108 | 49.732 | 64.814 | 43.778 | 80.592
| 18.7778 | 311.153 | 49.787 | 64.854 | 43.82 | 80.656
| 18.7847 | 312.143 | 49.85 | 64.912 | 43.871 | 80.735
| 18.7917 | 312.071 | 49.885 | 64.955 | 43.895 | 80.795
| 18.7986 | 311.982 | 49.91 | 64.997 | 43.922 | 80.847
| 18.8056 | 312.088 | 49.923 | 65.018 | 43.925 | 80.881
| 18.8125 | 311.939 | 49.934 | 65.045 | 43.944 | 80.917
| 18.8194 | 312.001 | 49.965 | 65.074 | 43.965 | 80.965
| 18.8264 | 312.759 | 50.013 | 65.131 | 44.005 | 81.029
| 18.8333 | 308.826 | 49.947 | 65.106 | 43.963 | 80.987
| 18.8403 | 309.3 | 49.847 | 65.025 | 43.872 | 80.893
| 18.8472 | 311.146 | 49.829 | 65.016 | 43.861 | 80.861
| 18.8542 | 306.987 | 49.693 | 64.915 | 43.763 | 80.724
| 18.8611 | 308.156 | 49.625 | 64.847 | 43.705 | 80.627
| 18.8681 | 309.69 | 49.633 | 64.83 | 43.711 | 80.602
| 18.875 | 310.185 | 49.648 | 64.837 | 43.723 | 80.598
| 18.8819 | 310.584 | 49.702 | 64.868 | 43.769 | 80.64
| 18.8889 | 310.726 | 49.746 | 64.9 | 43.798 | 80.68
| 18.8958 | 311.866 | 49.809 | 64.949 | 43.851 | 80.753
| 18.9028 | 312.522 | 49.867 | 65.007 | 43.902 | 80.819
| 18.9097 | 312.562 | 49.923 | 65.061 | 43.948 | 80.896
| 18.9167 | 312.371 | 49.951 | 65.098 | 43.965 | 80.942
| 18.9236 | 312.621 | 49.987 | 65.14 | 44 | 81
| 18.9306 | 312.931 | 50.028 | 65.189 | 44.038 | 81.068
| 18.9375 | 309.869 | 50.014 | 65.205 | 44.03 | 81.074
| 18.9444 | 309.824 | 49.912 | 65.13 | 43.943 | 80.98
| 18.9514 | 310.694 | 49.891 | 65.114 | 43.926 | 80.958
| 18.9583 | 310.951 | 49.894 | 65.124 | 43.933 | 80.956
| 18.9653 | 311.796 | 49.942 | 65.158 | 43.97 | 81.007
| 18.9722 | 312.128 | 50.006 | 65.22 | 44.035 | 81.082
| 18.9792 | 312.054 | 50.037 | 65.259 | 44.053 | 81.125
| 18.9861 | 313.1 | 50.084 | 65.299 | 44.083 | 81.183
| 18.9931 | 309.442 | 50.002 | 65.272 | 44.038 | 81.13
| 19 | 308.923 | 49.91 | 65.202 | 43.96 | 81.028
| 19.0069 | 309.031 | 49.839 | 65.143 | 43.901 | 80.943
| 19.0139 | 307.91 | 49.702 | 65.03 | 43.793 | 80.782
| 19.0208 | 307.304 | 49.642 | 64.966 | 43.747 | 80.682
| 19.0278 | 308.269 | 49.617 | 64.929 | 43.736 | 80.63
| 19.0347 | 308.644 | 49.601 | 64.902 | 43.722 | 80.583
| 19.0417 | 309.297 | 49.635 | 64.905 | 43.75 | 80.583
| 19.0486 | 308.98 | 49.643 | 64.906 | 43.755 | 80.58
| 19.0556 | 308.139 | 49.612 | 64.878 | 43.735 | 80.529
| 19.0625 | 308.436 | 49.591 | 64.847 | 43.715 | 80.491
| 19.0694 | 308.437 | 49.596 | 64.837 | 43.718 | 80.477
| 19.0764 | 309.271 | 49.627 | 64.857 | 43.752 | 80.505
| 19.0833 | 308.973 | 49.653 | 64.874 | 43.771 | 80.526
| 19.0903 | 309.415 | 49.652 | 64.868 | 43.773 | 80.515
| 19.0972 | 309.117 | 49.663 | 64.88 | 43.779 | 80.526
| 19.1042 | 309.039 | 49.67 | 64.881 | 43.783 | 80.526
| 19.1111 | 308.964 | 49.674 | 64.886 | 43.787 | 80.53
| 19.1181 | 309.836 | 49.685 | 64.892 | 43.799 | 80.541
| 19.125 | 309.426 | 49.698 | 64.904 | 43.806 | 80.552
| 19.1319 | 309.775 | 49.708 | 64.916 | 43.814 | 80.566
| 19.1389 | 309.278 | 49.688 | 64.897 | 43.801 | 80.539
| 19.1458 | 309.472 | 49.675 | 64.892 | 43.797 | 80.533
| 19.1528 | 308.883 | 49.656 | 64.88 | 43.778 | 80.506
| 19.1597 | 309.549 | 49.663 | 64.879 | 43.782 | 80.504
| 19.1667 | 310.474 | 49.701 | 64.903 | 43.809 | 80.539
| 19.1736 | 310.252 | 49.718 | 64.922 | 43.826 | 80.562
| 19.1806 | 310.538 | 49.74 | 64.942 | 43.851 | 80.588
| 19.1875 | 310.276 | 49.74 | 64.951 | 43.843 | 80.593
| 19.1944 | 309.294 | 49.742 | 64.95 | 43.851 | 80.591
| 19.2014 | 308.971 | 49.705 | 64.93 | 43.822 | 80.559
| 19.2083 | 308.529 | 49.673 | 64.908 | 43.8 | 80.524
| 19.2153 | 308.293 | 49.651 | 64.887 | 43.781 | 80.491
| 19.2222 | 308.212 | 49.617 | 64.859 | 43.758 | 80.452
| 19.2292 | 309.113 | 49.616 | 64.852 | 43.756 | 80.435
| 19.2361 | 307.776 | 49.586 | 64.822 | 43.735 | 80.394
| 19.2431 | 306.091 | 49.505 | 64.756 | 43.676 | 80.304
| 19.25 | 306.548 | 49.447 | 64.697 | 43.624 | 80.218
| 19.2569 | 310.598 | 49.553 | 64.752 | 43.704 | 80.292
| 19.2639 | 308.932 | 49.594 | 64.785 | 43.742 | 80.332
| 19.2708 | 308.419 | 49.613 | 64.804 | 43.758 | 80.359
| 19.2778 | 308.995 | 49.597 | 64.787 | 43.741 | 80.339
| 19.2847 | 309.659 | 49.558 | 64.755 | 43.7 | 80.291
| 19.2917 | 312.335 | 49.762 | 64.904 | 43.864 | 80.5
| 19.2986 | 311.593 | 49.878 | 65.013 | 43.968 | 80.648
| 19.3056 | 312.602 | 49.937 | 65.078 | 44.01 | 80.738
| 19.3125 | 311.874 | 49.963 | 65.121 | 44.026 | 80.797
| 19.3194 | 310.587 | 49.91 | 65.112 | 43.991 | 80.778
| 19.3264 | 312.084 | 49.991 | 65.178 | 44.054 | 80.878
| 19.3333 | 312.304 | 50.075 | 65.269 | 44.125 | 80.997
| 19.3403 | 312.793 | 50.117 | 65.319 | 44.149 | 81.065
| 19.3472 | 312.316 | 50.142 | 65.369 | 44.178 | 81.128
| 19.3542 | 313.07 | 50.172 | 65.415 | 44.206 | 81.186
| 19.3611 | 313.011 | 50.175 | 65.438 | 44.21 | 81.218
| 19.3681 | 312.001 | 50.188 | 65.472 | 44.22 | 81.259
| 19.375 | 312.337 | 50.198 | 65.492 | 44.225 | 81.288
| 19.3819 | 312.473 | 50.211 | 65.524 | 44.239 | 81.324
| 19.3889 | 312.15 | 50.211 | 65.539 | 44.238 | 81.338
| 19.3958 | 313.513 | 50.216 | 65.557 | 44.243 | 81.362
| 19.4028 | 309.517 | 50.235 | 65.597 | 44.276 | 81.405
| 19.4097 | 308.714 | 50.004 | 65.429 | 44.084 | 81.167
| 19.4167 | 306.794 | 49.825 | 65.284 | 43.946 | 80.963
| 19.4236 | 310.213 | 49.875 | 65.298 | 43.978 | 80.981
| 19.4306 | 309.83 | 49.887 | 65.294 | 43.992 | 80.97
| 19.4375 | 310.334 | 49.895 | 65.292 | 44.001 | 80.965
| 19.4444 | 310.345 | 49.865 | 65.264 | 43.981 | 80.916
| 19.4514 | 310.374 | 49.881 | 65.267 | 43.988 | 80.916
| 19.4583 | 310.56 | 49.876 | 65.256 | 43.985 | 80.908
| 19.4653 | 309.55 | 49.859 | 65.238 | 43.972 | 80.885
| 19.4722 | 310.299 | 49.839 | 65.215 | 43.954 | 80.848
| 19.4792 | 309.823 | 49.855 | 65.213 | 43.96 | 80.852
| 19.4861 | 310.603 | 49.857 | 65.216 | 43.97 | 80.854
| 19.4931 | 309.21 | 49.834 | 65.194 | 43.95 | 80.82
| 19.5 | 310.128 | 49.806 | 65.166 | 43.928 | 80.785
| 19.5069 | 310.056 | 49.776 | 65.14 | 43.906 | 80.745
| 19.5139 | 309.465 | 49.751 | 65.11 | 43.88 | 80.705
| 19.5208 | 309.517 | 49.745 | 65.094 | 43.876 | 80.683
| 19.5278 | 310.896 | 49.764 | 65.102 | 43.893 | 80.695
| 19.5347 | 309.242 | 49.773 | 65.102 | 43.899 | 80.69
| 19.5417 | 310.387 | 49.75 | 65.077 | 43.875 | 80.662
| 19.5486 | 310.793 | 49.728 | 65.057 | 43.861 | 80.636
| 19.5556 | 309.49 | 49.717 | 65.046 | 43.849 | 80.615
| 19.5625 | 309.145 | 49.696 | 65.015 | 43.827 | 80.576
| 19.5694 | 309.099 | 49.666 | 64.985 | 43.811 | 80.542
| 19.5764 | 308.224 | 49.601 | 64.929 | 43.76 | 80.462
| 19.5833 | 308.689 | 49.554 | 64.875 | 43.719 | 80.385
| 19.5903 | 308.396 | 49.546 | 64.851 | 43.708 | 80.36
| 19.5972 | 308.248 | 49.502 | 64.806 | 43.671 | 80.299
| 19.6042 | 309.417 | 49.522 | 64.796 | 43.685 | 80.294
| 19.6111 | 309.866 | 49.55 | 64.809 | 43.711 | 80.312
| 19.6181 | 308.127 | 49.542 | 64.795 | 43.703 | 80.301
| 19.625 | 308.375 | 49.514 | 64.769 | 43.684 | 80.259
| 19.6319 | 308.951 | 49.486 | 64.736 | 43.66 | 80.214
| 19.6389 | 308.749 | 49.51 | 64.739 | 43.668 | 80.225
| 19.6458 | 309.52 | 49.528 | 64.746 | 43.686 | 80.24
| 19.6528 | 309.263 | 49.53 | 64.742 | 43.687 | 80.24
| 19.6597 | 309.483 | 49.519 | 64.725 | 43.674 | 80.219
| 19.6667 | 308.528 | 49.51 | 64.711 | 43.665 | 80.206
| 19.6736 | 309.003 | 49.494 | 64.696 | 43.652 | 80.187
| 19.6806 | 309.291 | 49.48 | 64.679 | 43.647 | 80.166
| 19.6875 | 309.565 | 49.495 | 64.682 | 43.654 | 80.174
| 19.6944 | 309.44 | 49.491 | 64.676 | 43.648 | 80.17
| 19.7014 | 309.724 | 49.488 | 64.665 | 43.643 | 80.16
| 19.7083 | 308.863 | 49.501 | 64.673 | 43.656 | 80.171
| 19.7153 | 308.904 | 49.48 | 64.655 | 43.639 | 80.149
| 19.7222 | 307.161 | 49.45 | 64.627 | 43.618 | 80.111
| 19.7292 | 307.67 | 49.361 | 64.556 | 43.541 | 80.008
| 19.7361 | 310.399 | 49.476 | 64.625 | 43.636 | 80.115
| 19.7431 | 309.017 | 49.517 | 64.656 | 43.668 | 80.159
| 19.75 | 306.483 | 49.374 | 64.553 | 43.554 | 80.015
| 19.7569 | 306.422 | 49.295 | 64.48 | 43.49 | 79.918
| 19.7639 | 310.414 | 49.345 | 64.495 | 43.522 | 79.944
| 19.7708 | 311.373 | 49.491 | 64.599 | 43.651 | 80.089
| 19.7778 | 311.74 | 49.597 | 64.69 | 43.732 | 80.207
| 19.7847 | 311.98 | 49.704 | 64.785 | 43.82 | 80.341
| 19.7917 | 311.754 | 49.765 | 64.847 | 43.861 | 80.432
| 19.7986 | 311.514 | 49.794 | 64.891 | 43.886 | 80.499
| 19.8056 | 312.01 | 49.842 | 64.957 | 43.926 | 80.586
| 19.8125 | 312.757 | 49.892 | 65.022 | 43.972 | 80.672
| 19.8194 | 312.986 | 49.934 | 65.072 | 44.002 | 80.745
| 19.8264 | 313.24 | 50.002 | 65.152 | 44.055 | 80.852
| 19.8333 | 309.314 | 49.86 | 65.066 | 43.951 | 80.726
| 19.8403 | 309.827 | 49.794 | 65.03 | 43.898 | 80.674
| 19.8472 | 309.974 | 49.755 | 65.002 | 43.865 | 80.63
| 19.8542 | 310.798 | 49.765 | 65.008 | 43.876 | 80.635
| 19.8611 | 311.297 | 49.794 | 65.035 | 43.9 | 80.662
| 19.8681 | 312.95 | 49.875 | 65.104 | 43.964 | 80.749
| 19.875 | 309.55 | 49.884 | 65.131 | 43.985 | 80.775
| 19.8819 | 309.878 | 49.793 | 65.063 | 43.907 | 80.687
| 19.8889 | 307.03 | 49.769 | 65.051 | 43.893 | 80.664
| 19.8958 | 307.11 | 49.627 | 64.94 | 43.779 | 80.503
| 19.9028 | 308.018 | 49.561 | 64.886 | 43.732 | 80.414
| 19.9097 | 307.89 | 49.548 | 64.86 | 43.728 | 80.371
| 19.9167 | 308.079 | 49.517 | 64.822 | 43.704 | 80.317
| 19.9236 | 308.696 | 49.531 | 64.821 | 43.714 | 80.309
| 19.9306 | 309.935 | 49.569 | 64.84 | 43.744 | 80.33
| 19.9375 | 309.513 | 49.62 | 64.878 | 43.787 | 80.375
| 19.9444 | 310.482 | 49.672 | 64.92 | 43.837 | 80.436
| 19.9514 | 311.889 | 49.758 | 64.99 | 43.906 | 80.524
| 19.9583 | 311.647 | 49.829 | 65.061 | 43.963 | 80.611
| 19.9653 | 312.411 | 49.892 | 65.123 | 44.012 | 80.695
| 19.9722 | 306.358 | 49.759 | 65.062 | 43.923 | 80.588
| 19.9792 | 310.01 | 49.575 | 64.91 | 43.76 | 80.394
| 19.9861 | 311.409 | 49.686 | 64.982 | 43.85 | 80.484
| 19.9931 | 311.305 | 49.772 | 65.049 | 43.926 | 80.563
| 20 | 311.373 | 49.811 | 65.092 | 43.963 | 80.617
| 20.0069 | 308.951 | 49.781 | 65.083 | 43.941 | 80.6
| 20.0139 | 309.065 | 49.725 | 65.042 | 43.893 | 80.54
| 20.0208 | 309.51 | 49.725 | 65.047 | 43.903 | 80.537
| 20.0278 | 310.628 | 49.759 | 65.073 | 43.929 | 80.568
| 20.0347 | 310.867 | 49.796 | 65.105 | 43.966 | 80.608
| 20.0417 | 310.858 | 49.807 | 65.12 | 43.97 | 80.62
| 20.0486 | 311.52 | 49.838 | 65.151 | 44.003 | 80.657
| 20.0556 | 310.166 | 49.85 | 65.174 | 44.016 | 80.678
| 20.0625 | 310.499 | 49.852 | 65.183 | 44.016 | 80.691
| 20.0694 | 310.242 | 49.847 | 65.189 | 44.014 | 80.687
| 20.0764 | 309.928 | 49.848 | 65.193 | 44.018 | 80.693
| 20.0833 | 309.419 | 49.821 | 65.185 | 44.002 | 80.673
| 20.0903 | 309.909 | 49.816 | 65.182 | 43.997 | 80.664
| 20.0972 | 310.917 | 49.83 | 65.198 | 44.013 | 80.669
| 20.1042 | 311.087 | 49.874 | 65.236 | 44.049 | 80.718
| 20.1111 | 311.239 | 49.917 | 65.269 | 44.083 | 80.761
| 20.1181 | 311.276 | 49.946 | 65.308 | 44.113 | 80.806
| 20.125 | 311.455 | 49.963 | 65.335 | 44.127 | 80.837
| 20.1319 | 311.442 | 49.99 | 65.365 | 44.154 | 80.876
| 20.1389 | 311.242 | 50.006 | 65.395 | 44.165 | 80.91
| 20.1458 | 311.936 | 50.018 | 65.412 | 44.176 | 80.925
| 20.1528 | 311.794 | 50.029 | 65.431 | 44.189 | 80.952
| 20.1597 | 311.567 | 50.031 | 65.444 | 44.191 | 80.963
| 20.1667 | 310.729 | 50.018 | 65.442 | 44.183 | 80.952
| 20.1736 | 311.545 | 50.021 | 65.454 | 44.182 | 80.962
| 20.1806 | 310.976 | 50.018 | 65.46 | 44.186 | 80.965
| 20.1875 | 311.034 | 50.02 | 65.471 | 44.187 | 80.967
| 20.1944 | 311.145 | 50.024 | 65.479 | 44.201 | 80.98
| 20.2014 | 311.429 | 50.029 | 65.484 | 44.202 | 80.981
| 20.2083 | 311.581 | 50.058 | 65.509 | 44.224 | 81.017
| 20.2153 | 310.63 | 50.036 | 65.51 | 44.215 | 81.003
| 20.2222 | 310.548 | 50.019 | 65.498 | 44.198 | 80.982
| 20.2292 | 309.79 | 49.994 | 65.481 | 44.179 | 80.951
| 20.2361 | 310.103 | 49.953 | 65.45 | 44.153 | 80.906
| 20.2431 | 308.546 | 49.865 | 65.388 | 44.086 | 80.807
| 20.25 | 307.606 | 49.793 | 65.317 | 44.03 | 80.708
| 20.2569 | 309.292 | 49.835 | 65.333 | 44.059 | 80.729
| 20.2639 | 309.415 | 49.823 | 65.314 | 44.059 | 80.699
| 20.2708 | 308.932 | 49.836 | 65.318 | 44.066 | 80.694
| 20.2778 | 306.863 | 49.76 | 65.254 | 44.007 | 80.609
| 20.2847 | 306.779 | 49.697 | 65.199 | 43.963 | 80.529
| 20.2917 | 310.516 | 49.768 | 65.23 | 44.009 | 80.575
| 20.2986 | 309.155 | 49.858 | 65.291 | 44.084 | 80.653
| 20.3056 | 307.116 | 49.742 | 65.209 | 44.002 | 80.535
| 20.3125 | 306.199 | 49.631 | 65.115 | 43.905 | 80.406
| 20.3194 | 308.84 | 49.69 | 65.135 | 43.948 | 80.433
| 20.3264 | 309.732 | 49.779 | 65.203 | 44.023 | 80.516
| 20.3333 | 310.299 | 49.816 | 65.226 | 44.06 | 80.558
| 20.3403 | 310.013 | 49.842 | 65.247 | 44.079 | 80.585
| 20.3472 | 310.792 | 49.856 | 65.263 | 44.085 | 80.601
| 20.3542 | 310.179 | 49.866 | 65.278 | 44.094 | 80.62
| 20.3611 | 309.46 | 49.85 | 65.275 | 44.088 | 80.608
| 20.3681 | 308.115 | 49.796 | 65.235 | 44.046 | 80.556
| 20.375 | 308.156 | 49.761 | 65.198 | 44.018 | 80.511
| 20.3819 | 309.004 | 49.752 | 65.186 | 44.006 | 80.492
| 20.3889 | 308.442 | 49.724 | 65.161 | 43.986 | 80.453
| 20.3958 | 308.202 | 49.706 | 65.14 | 43.977 | 80.417
| 20.4028 | 310.41 | 49.75 | 65.162 | 44.009 | 80.451
| 20.4097 | 309.714 | 49.811 | 65.212 | 44.063 | 80.512
| 20.4167 | 310.18 | 49.838 | 65.234 | 44.087 | 80.537
| 20.4236 | 309.37 | 49.84 | 65.241 | 44.085 | 80.551
| 20.4306 | 308.78 | 49.824 | 65.229 | 44.069 | 80.537
| 20.4375 | 308.833 | 49.809 | 65.217 | 44.059 | 80.518
| 20.4444 | 308.531 | 49.784 | 65.204 | 44.046 | 80.495
| 20.4514 | 308.079 | 49.766 | 65.179 | 44.027 | 80.462
| 20.4583 | 308.636 | 49.725 | 65.145 | 43.997 | 80.411
| 20.4653 | 307.684 | 49.691 | 65.116 | 43.969 | 80.371
| 20.4722 | 308.441 | 49.669 | 65.09 | 43.955 | 80.33
| 20.4792 | 308.767 | 49.655 | 65.065 | 43.949 | 80.304
| 20.4861 | 309.566 | 49.695 | 65.087 | 43.977 | 80.33
| 20.4931 | 308.293 | 49.688 | 65.076 | 43.973 | 80.311
| 20.5 | 308.512 | 49.665 | 65.056 | 43.954 | 80.289
| 20.5069 | 308.208 | 49.667 | 65.05 | 43.952 | 80.273
| 20.5139 | 308.707 | 49.695 | 65.066 | 43.975 | 80.295
| 20.5208 | 308.529 | 49.687 | 65.058 | 43.972 | 80.292
| 20.5278 | 309.408 | 49.714 | 65.075 | 43.993 | 80.308
| 20.5347 | 309.732 | 49.731 | 65.086 | 44.004 | 80.322
| 20.5417 | 308.773 | 49.751 | 65.102 | 44.022 | 80.346
| 20.5486 | 308.907 | 49.736 | 65.099 | 44.012 | 80.338
| 20.5556 | 309.092 | 49.74 | 65.096 | 44.017 | 80.341
| 20.5625 | 309.022 | 49.743 | 65.097 | 44.018 | 80.345
| 20.5694 | 309.903 | 49.766 | 65.116 | 44.029 | 80.367
| 20.5764 | 310.075 | 49.785 | 65.13 | 44.049 | 80.393
| 20.5833 | 309.879 | 49.807 | 65.161 | 44.075 | 80.425
| 20.5903 | 310.089 | 49.839 | 65.179 | 44.092 | 80.459
| 20.5972 | 310.496 | 49.859 | 65.198 | 44.103 | 80.491
| 20.6042 | 309.617 | 49.855 | 65.207 | 44.113 | 80.497
| 20.6111 | 309.94 | 49.846 | 65.204 | 44.101 | 80.492
| 20.6181 | 309.922 | 49.851 | 65.218 | 44.106 | 80.509
| 20.625 | 310.056 | 49.847 | 65.215 | 44.1 | 80.505
| 20.6319 | 308.99 | 49.831 | 65.212 | 44.094 | 80.496
| 20.6389 | 308.321 | 49.773 | 65.167 | 44.049 | 80.436
| 20.6458 | 307.643 | 49.712 | 65.115 | 44 | 80.36
| 20.6528 | 308.633 | 49.678 | 65.084 | 43.982 | 80.314
| 20.6597 | 307.872 | 49.65 | 65.051 | 43.957 | 80.268
| 20.6667 | 307.898 | 49.632 | 65.028 | 43.942 | 80.232
| 20.6736 | 307.031 | 49.609 | 64.999 | 43.923 | 80.193
| 20.6806 | 307.469 | 49.587 | 64.966 | 43.908 | 80.15
| 20.6875 | 307.417 | 49.578 | 64.955 | 43.907 | 80.128
| 20.6944 | 306.952 | 49.541 | 64.917 | 43.873 | 80.072
| 20.7014 | 306.628 | 49.532 | 64.894 | 43.868 | 80.042
| 20.7083 | 306.488 | 49.511 | 64.868 | 43.855 | 80.005
| 20.7153 | 307.773 | 49.54 | 64.879 | 43.874 | 80.016
| 20.7222 | 307.736 | 49.537 | 64.864 | 43.869 | 80.002
| 20.7292 | 307.149 | 49.511 | 64.844 | 43.852 | 79.971
| 20.7361 | 306.901 | 49.499 | 64.822 | 43.843 | 79.94
| 20.7431 | 310.756 | 49.656 | 64.928 | 43.966 | 80.086
| 20.75 | 309.892 | 49.73 | 64.997 | 44.031 | 80.175
| 20.7569 | 310.028 | 49.776 | 65.043 | 44.062 | 80.243
| 20.7639 | 309.936 | 49.819 | 65.089 | 44.104 | 80.308
| 20.7708 | 310.964 | 49.857 | 65.135 | 44.135 | 80.371
| 20.7778 | 309.794 | 49.899 | 65.188 | 44.173 | 80.436
| 20.7847 | 309.346 | 49.867 | 65.191 | 44.156 | 80.428
| 20.7917 | 309.394 | 49.823 | 65.16 | 44.116 | 80.393
| 20.7986 | 309.518 | 49.84 | 65.186 | 44.132 | 80.412
| 20.8056 | 309.65 | 49.853 | 65.2 | 44.147 | 80.432
| 20.8125 | 310.073 | 49.87 | 65.218 | 44.158 | 80.452
| 20.8194 | 310.483 | 49.919 | 65.26 | 44.197 | 80.515
| 20.8264 | 311.928 | 50.005 | 65.335 | 44.266 | 80.613
| 20.8333 | 311.371 | 50.072 | 65.404 | 44.321 | 80.7
| 20.8403 | 312.228 | 50.119 | 65.464 | 44.362 | 80.781
| 20.8472 | 308.73 | 50.121 | 65.5 | 44.374 | 80.813
| 20.8542 | 310.685 | 50.025 | 65.433 | 44.295 | 80.731
| 20.8611 | 309.185 | 50.001 | 65.429 | 44.277 | 80.703
| 20.8681 | 312.228 | 50.051 | 65.463 | 44.321 | 80.754
| 20.875 | 311.652 | 50.099 | 65.515 | 44.362 | 80.811
| 20.8819 | 308.21 | 49.985 | 65.449 | 44.281 | 80.705
| 20.8889 | 308.496 | 49.92 | 65.397 | 44.227 | 80.632
| 20.8958 | 308.556 | 49.932 | 65.4 | 44.236 | 80.625
| 20.9028 | 307.88 | 49.938 | 65.405 | 44.245 | 80.621
| 20.9097 | 307.788 | 49.819 | 65.316 | 44.156 | 80.495
| 20.9167 | 307.234 | 49.778 | 65.274 | 44.121 | 80.427
| 20.9236 | 307.884 | 49.762 | 65.249 | 44.116 | 80.387
| 20.9306 | 308.369 | 49.782 | 65.251 | 44.133 | 80.386
| 20.9375 | 307.74 | 49.75 | 65.22 | 44.113 | 80.337
| 20.9444 | 309.235 | 49.781 | 65.24 | 44.139 | 80.355
| 20.9514 | 309.271 | 49.851 | 65.286 | 44.2 | 80.413
| 20.9583 | 310.781 | 49.923 | 65.339 | 44.251 | 80.484
| 20.9653 | 310.576 | 49.975 | 65.389 | 44.296 | 80.554
| 20.9722 | 311.574 | 50.076 | 65.483 | 44.382 | 80.668
| 20.9792 | 312.668 | 50.183 | 65.58 | 44.459 | 80.799
| 20.9861 | 310.081 | 50.206 | 65.635 | 44.494 | 80.86
| 20.9931 | 307.482 | 50.087 | 65.572 | 44.4 | 80.761
| 21 | 308.193 | 49.966 | 65.48 | 44.298 | 80.633
| 21.0069 | 308.249 | 49.926 | 65.443 | 44.271 | 80.582
| 21.0139 | 307.966 | 49.9 | 65.419 | 44.255 | 80.54
| 21.0208 | 308.741 | 49.903 | 65.415 | 44.263 | 80.526
| 21.0278 | 309.617 | 49.91 | 65.414 | 44.265 | 80.514
| 21.0347 | 309.457 | 49.943 | 65.437 | 44.299 | 80.54
| 21.0417 | 309.393 | 49.973 | 65.464 | 44.323 | 80.562
| 21.0486 | 308.021 | 49.955 | 65.45 | 44.314 | 80.546
| 21.0556 | 308.758 | 49.935 | 65.437 | 44.3 | 80.522
| 21.0625 | 308.332 | 49.904 | 65.419 | 44.28 | 80.486
| 21.0694 | 308.707 | 49.9 | 65.415 | 44.28 | 80.474
| 21.0764 | 308.973 | 49.923 | 65.428 | 44.302 | 80.487
| 21.0833 | 309.319 | 49.956 | 65.456 | 44.328 | 80.518
| 21.0903 | 309.348 | 49.984 | 65.478 | 44.348 | 80.542
| 21.0972 | 309.323 | 49.991 | 65.489 | 44.358 | 80.557
| 21.1042 | 308.791 | 49.983 | 65.489 | 44.357 | 80.547
| 21.1111 | 309.726 | 49.985 | 65.492 | 44.367 | 80.557
| 21.1181 | 310.199 | 50.042 | 65.532 | 44.407 | 80.607
| 21.125 | 310.113 | 50.077 | 65.577 | 44.44 | 80.651
| 21.1319 | 310.73 | 50.111 | 65.61 | 44.469 | 80.69
| 21.1389 | 311.162 | 50.168 | 65.667 | 44.516 | 80.761
| 21.1458 | 310.645 | 50.205 | 65.71 | 44.55 | 80.819
| 21.1528 | 310.914 | 50.222 | 65.733 | 44.559 | 80.846
| 21.1597 | 309.616 | 50.218 | 65.755 | 44.567 | 80.864
| 21.1667 | 309.232 | 50.164 | 65.719 | 44.52 | 80.816
| 21.1736 | 309.33 | 50.138 | 65.71 | 44.511 | 80.798
| 21.1806 | 309.772 | 50.141 | 65.71 | 44.511 | 80.793
| 21.1875 | 310.291 | 50.163 | 65.729 | 44.527 | 80.818
| 21.1944 | 309.354 | 50.143 | 65.727 | 44.518 | 80.799
| 21.2014 | 308.367 | 50.098 | 65.695 | 44.492 | 80.748
| 21.2083 | 308.776 | 50.097 | 65.694 | 44.49 | 80.74
| 21.2153 | 308.722 | 50.087 | 65.687 | 44.484 | 80.727
| 21.2222 | 310.068 | 50.098 | 65.69 | 44.498 | 80.727
| 21.2292 | 309.285 | 50.126 | 65.713 | 44.521 | 80.748
| 21.2361 | 309.784 | 50.131 | 65.722 | 44.528 | 80.748
| 21.2431 | 309.346 | 50.107 | 65.708 | 44.512 | 80.725
| 21.25 | 308.525 | 50.098 | 65.703 | 44.508 | 80.71
| 21.2569 | 308.813 | 50.079 | 65.688 | 44.498 | 80.687
| 21.2639 | 308.898 | 50.072 | 65.686 | 44.494 | 80.67
| 21.2708 | 308.849 | 50.076 | 65.685 | 44.498 | 80.667
| 21.2778 | 307.814 | 50.06 | 65.665 | 44.483 | 80.631
| 21.2847 | 306.382 | 49.931 | 65.564 | 44.385 | 80.491
| 21.2917 | 309.446 | 49.997 | 65.6 | 44.437 | 80.536
| 21.2986 | 308.77 | 50.044 | 65.638 | 44.484 | 80.57
| 21.3056 | 309.426 | 50.075 | 65.654 | 44.505 | 80.595
| 21.3125 | 308.281 | 50.06 | 65.648 | 44.5 | 80.591
| 21.3194 | 308.013 | 50.027 | 65.621 | 44.473 | 80.548
| 21.3264 | 308.909 | 49.991 | 65.584 | 44.433 | 80.494
| 21.3333 | 308.577 | 50.036 | 65.617 | 44.483 | 80.528
| 21.3403 | 309.394 | 50.057 | 65.633 | 44.504 | 80.546
| 21.3472 | 308.974 | 50.077 | 65.644 | 44.519 | 80.566
| 21.3542 | 308.732 | 50.076 | 65.65 | 44.525 | 80.566
| 21.3611 | 308.734 | 50.085 | 65.664 | 44.529 | 80.573
| 21.3681 | 308.353 | 50.075 | 65.651 | 44.52 | 80.561
| 21.375 | 308.166 | 50.051 | 65.635 | 44.504 | 80.528
| 21.3819 | 308.146 | 50.041 | 65.628 | 44.503 | 80.515
| 21.3889 | 308.395 | 50.028 | 65.618 | 44.494 | 80.499
| 21.3958 | 308.932 | 50.048 | 65.629 | 44.515 | 80.508
| 21.4028 | 307.734 | 50.035 | 65.614 | 44.507 | 80.491
| 21.4097 | 307.815 | 50.019 | 65.603 | 44.496 | 80.472
| 21.4167 | 307.64 | 49.99 | 65.578 | 44.476 | 80.429
| 21.4236 | 306.14 | 49.927 | 65.523 | 44.427 | 80.353
| 21.4306 | 306.57 | 49.864 | 65.465 | 44.377 | 80.274
| 21.4375 | 310.963 | 50.041 | 65.581 | 44.517 | 80.432
| 21.4444 | 308.696 | 50.091 | 65.627 | 44.567 | 80.491
| 21.4514 | 311.762 | 50.181 | 65.696 | 44.636 | 80.593
| 21.4583 | 312.027 | 50.309 | 65.815 | 44.738 | 80.742
| 21.4653 | 311.756 | 50.369 | 65.883 | 44.792 | 80.841
| 21.4722 | 311.565 | 50.404 | 65.927 | 44.815 | 80.904
| 21.4792 | 311.318 | 50.404 | 65.954 | 44.818 | 80.932
| 21.4861 | 310.149 | 50.394 | 65.966 | 44.805 | 80.944
| 21.4931 | 310.308 | 50.356 | 65.95 | 44.785 | 80.92
| 21.5 | 310.68 | 50.343 | 65.953 | 44.781 | 80.915
| 21.5069 | 309.779 | 50.353 | 65.966 | 44.785 | 80.933
| 21.5139 | 309.208 | 50.323 | 65.954 | 44.772 | 80.912
| 21.5208 | 310.011 | 50.323 | 65.958 | 44.77 | 80.913
| 21.5278 | 310.518 | 50.353 | 65.986 | 44.794 | 80.944
| 21.5347 | 311.053 | 50.399 | 66.021 | 44.83 | 80.985
| 21.5417 | 311.477 | 50.452 | 66.071 | 44.878 | 81.052
| 21.5486 | 312.13 | 50.503 | 66.126 | 44.916 | 81.118
| 21.5556 | 311.532 | 50.533 | 66.166 | 44.954 | 81.172
| 21.5625 | 311.132 | 50.515 | 66.17 | 44.936 | 81.17
| 21.5694 | 311.018 | 50.519 | 66.182 | 44.95 | 81.191
| 21.5764 | 310.994 | 50.516 | 66.194 | 44.942 | 81.189
| 21.5833 | 311.106 | 50.524 | 66.205 | 44.955 | 81.21
| 21.5903 | 311.218 | 50.541 | 66.229 | 44.974 | 81.234
| 21.5972 | 311.937 | 50.561 | 66.252 | 44.989 | 81.266
| 21.6042 | 312.373 | 50.586 | 66.282 | 45.012 | 81.292
| 21.6111 | 308.178 | 50.405 | 66.156 | 44.874 | 81.116
| 21.6181 | 307.674 | 50.321 | 66.089 | 44.812 | 81.017
| 21.625 | 308.375 | 50.257 | 66.026 | 44.759 | 80.922
| 21.6319 | 307.857 | 50.195 | 65.962 | 44.716 | 80.833
| 21.6389 | 307.814 | 50.162 | 65.915 | 44.69 | 80.764
| 21.6458 | 307.827 | 50.131 | 65.869 | 44.666 | 80.703
| 21.6528 | 308.218 | 50.112 | 65.841 | 44.657 | 80.655
| 21.6597 | 307.541 | 50.1 | 65.814 | 44.65 | 80.61
| 21.6667 | 306.628 | 50.059 | 65.77 | 44.611 | 80.543
| 21.6736 | 306.825 | 50.041 | 65.739 | 44.605 | 80.494
| 21.6806 | 307.469 | 50.034 | 65.712 | 44.598 | 80.459
| 21.6875 | 307.63 | 50.033 | 65.698 | 44.602 | 80.446
| 21.6944 | 307.691 | 50.02 | 65.674 | 44.591 | 80.41
| 21.7014 | 308.557 | 50.046 | 65.679 | 44.613 | 80.418
| 21.7083 | 307.424 | 50.044 | 65.671 | 44.619 | 80.405
| 21.7153 | 306.082 | 49.996 | 65.631 | 44.581 | 80.347
| 21.7222 | 306.733 | 49.956 | 65.583 | 44.549 | 80.293
| 21.7292 | 310.494 | 50.054 | 65.634 | 44.621 | 80.371
| 21.7361 | 310.488 | 50.22 | 65.763 | 44.762 | 80.537
| 21.7431 | 307.929 | 50.276 | 65.818 | 44.808 | 80.607
| 21.75 | 309.955 | 50.239 | 65.8 | 44.774 | 80.595
| 21.7569 | 308.629 | 50.224 | 65.801 | 44.767 | 80.582
| 21.7639 | 309.297 | 50.251 | 65.824 | 44.795 | 80.616
| 21.7708 | 308.588 | 50.239 | 65.822 | 44.789 | 80.607
| 21.7778 | 308.294 | 50.233 | 65.82 | 44.783 | 80.604
| 21.7847 | 308.791 | 50.247 | 65.834 | 44.804 | 80.618
| 21.7917 | 309.131 | 50.238 | 65.833 | 44.794 | 80.606
| 21.7986 | 308.802 | 50.228 | 65.824 | 44.789 | 80.598
| 21.8056 | 308.888 | 50.263 | 65.858 | 44.824 | 80.634
| 21.8125 | 309.055 | 50.263 | 65.856 | 44.822 | 80.633
| 21.8194 | 309.692 | 50.332 | 65.906 | 44.876 | 80.706
| 21.8264 | 308.73 | 50.339 | 65.931 | 44.892 | 80.729
| 21.8333 | 309.38 | 50.338 | 65.931 | 44.891 | 80.726
| 21.8403 | 309.453 | 50.337 | 65.943 | 44.895 | 80.735
| 21.8472 | 309.389 | 50.349 | 65.952 | 44.904 | 80.744
| 21.8542 | 310.865 | 50.4 | 65.997 | 44.954 | 80.8
| 21.8611 | 312.251 | 50.514 | 66.092 | 45.04 | 80.928
| 21.8681 | 307.196 | 50.381 | 66.021 | 44.953 | 80.815
| 21.875 | 307.252 | 50.319 | 65.973 | 44.893 | 80.748
| 21.8819 | 307.382 | 50.255 | 65.919 | 44.85 | 80.669
| 21.8889 | 308.818 | 50.253 | 65.906 | 44.848 | 80.646
| 21.8958 | 307.899 | 50.255 | 65.905 | 44.861 | 80.645
| 21.9028 | 309.668 | 50.281 | 65.916 | 44.875 | 80.651
| 21.9097 | 309.628 | 50.327 | 65.953 | 44.92 | 80.689
| 21.9167 | 309.303 | 50.349 | 65.974 | 44.942 | 80.715
| 21.9236 | 309.566 | 50.375 | 65.991 | 44.964 | 80.741
| 21.9306 | 309.638 | 50.389 | 66.008 | 44.979 | 80.756
| 21.9375 | 310.198 | 50.442 | 66.054 | 45.021 | 80.813
| 21.9444 | 311.785 | 50.49 | 66.099 | 45.06 | 80.872
| 21.9514 | 312.107 | 50.625 | 66.22 | 45.177 | 81.029
| 21.9583 | 312.022 | 50.694 | 66.298 | 45.237 | 81.127
| 21.9653 | 309.559 | 50.605 | 66.256 | 45.168 | 81.06
| 21.9722 | 310.454 | 50.589 | 66.254 | 45.161 | 81.055
| 21.9792 | 309.919 | 50.584 | 66.264 | 45.167 | 81.062
| 21.9861 | 311.088 | 50.591 | 66.278 | 45.173 | 81.073
| 21.9931 | 312.033 | 50.666 | 66.339 | 45.233 | 81.149
| 22 | 310.105 | 50.635 | 66.334 | 45.219 | 81.133
| 22.0069 | 308.84 | 50.602 | 66.311 | 45.193 | 81.094
| 22.0139 | 309.373 | 50.549 | 66.278 | 45.154 | 81.039
| 22.0208 | 310.183 | 50.568 | 66.284 | 45.161 | 81.053
| 22.0278 | 312.095 | 50.598 | 66.304 | 45.193 | 81.073
| 22.0347 | 308.267 | 50.623 | 66.348 | 45.238 | 81.108
| 22.0417 | 308.155 | 50.514 | 66.263 | 45.143 | 81
| 22.0486 | 306.662 | 50.433 | 66.205 | 45.082 | 80.902
| 22.0556 | 306.828 | 50.355 | 66.121 | 45.015 | 80.791
| 22.0625 | 307.099 | 50.317 | 66.079 | 44.996 | 80.724
| 22.0694 | 305.998 | 50.282 | 66.042 | 44.976 | 80.659
| 22.0764 | 306.15 | 50.243 | 65.988 | 44.944 | 80.585
| 22.0833 | 306.229 | 50.203 | 65.945 | 44.915 | 80.515
| 22.0903 | 306.604 | 50.21 | 65.929 | 44.93 | 80.487
| 22.0972 | 306.179 | 50.194 | 65.903 | 44.914 | 80.446
| 22.1042 | 307.139 | 50.223 | 65.905 | 44.937 | 80.442
| 22.1111 | 307.067 | 50.257 | 65.924 | 44.967 | 80.465
| 22.1181 | 307.849 | 50.309 | 65.953 | 45.009 | 80.511
| 22.125 | 308.201 | 50.327 | 65.967 | 45.029 | 80.525
| 22.1319 | 307.874 | 50.331 | 65.97 | 45.028 | 80.521
| 22.1389 | 308.617 | 50.372 | 65.992 | 45.06 | 80.563
| 22.1458 | 308.634 | 50.41 | 66.031 | 45.099 | 80.611
| 22.1528 | 308.355 | 50.445 | 66.058 | 45.125 | 80.646
| 22.1597 | 308.794 | 50.473 | 66.086 | 45.155 | 80.692
| 22.1667 | 309.118 | 50.532 | 66.141 | 45.203 | 80.758
| 22.1736 | 309.162 | 50.57 | 66.177 | 45.234 | 80.81
| 22.1806 | 309.93 | 50.603 | 66.226 | 45.266 | 80.865
| 22.1875 | 309.83 | 50.636 | 66.258 | 45.294 | 80.912
| 22.1944 | 309.925 | 50.659 | 66.295 | 45.312 | 80.954
| 22.2014 | 309.703 | 50.657 | 66.298 | 45.31 | 80.966
| 22.2083 | 309.893 | 50.672 | 66.328 | 45.333 | 80.995
| 22.2153 | 310.144 | 50.678 | 66.342 | 45.338 | 81.009
| 22.2222 | 308.852 | 50.652 | 66.334 | 45.316 | 80.99
| 22.2292 | 308.396 | 50.616 | 66.308 | 45.296 | 80.951
| 22.2361 | 307.946 | 50.594 | 66.294 | 45.282 | 80.931
| 22.2431 | 308.126 | 50.558 | 66.266 | 45.253 | 80.886
| 22.25 | 306.797 | 50.499 | 66.216 | 45.217 | 80.814
| 22.2569 | 306.847 | 50.44 | 66.17 | 45.169 | 80.734
| 22.2639 | 307.741 | 50.439 | 66.148 | 45.168 | 80.716
| 22.2708 | 307.375 | 50.442 | 66.148 | 45.177 | 80.7
| 22.2778 | 306.634 | 50.436 | 66.126 | 45.17 | 80.672
| 22.2847 | 306.266 | 50.383 | 66.08 | 45.127 | 80.605
| 22.2917 | 306.802 | 50.349 | 66.043 | 45.106 | 80.549
| 22.2986 | 307.003 | 50.365 | 66.043 | 45.118 | 80.548
| 22.3056 | 307.53 | 50.388 | 66.051 | 45.146 | 80.56
| 22.3125 | 307.425 | 50.432 | 66.077 | 45.173 | 80.586
| 22.3194 | 308.422 | 50.471 | 66.104 | 45.211 | 80.622
| 22.3264 | 311.417 | 50.624 | 66.216 | 45.332 | 80.78
| 22.3333 | 309.967 | 50.701 | 66.288 | 45.397 | 80.879
| 22.3403 | 309.945 | 50.773 | 66.36 | 45.453 | 80.98
| 22.3472 | 311.345 | 50.832 | 66.426 | 45.505 | 81.069
| 22.3542 | 309.929 | 50.843 | 66.46 | 45.513 | 81.109
| 22.3611 | 308.44 | 50.834 | 66.473 | 45.51 | 81.131
| 22.3681 | 308.816 | 50.775 | 66.442 | 45.463 | 81.086
| 22.375 | 308.637 | 50.759 | 66.436 | 45.447 | 81.072
| 22.3819 | 308.627 | 50.73 | 66.417 | 45.429 | 81.046
| 22.3889 | 307.668 | 50.713 | 66.405 | 45.424 | 81.03
| 22.3958 | 308.431 | 50.693 | 66.393 | 45.411 | 81.012
| 22.4028 | 308.714 | 50.693 | 66.391 | 45.411 | 80.999
| 22.4097 | 308.732 | 50.677 | 66.379 | 45.398 | 80.976
| 22.4167 | 308.919 | 50.687 | 66.382 | 45.412 | 80.978
| 22.4236 | 307.727 | 50.682 | 66.378 | 45.406 | 80.973
| 22.4306 | 307.721 | 50.622 | 66.333 | 45.367 | 80.908
| 22.4375 | 306.68 | 50.559 | 66.276 | 45.316 | 80.83
| 22.4444 | 309.466 | 50.518 | 66.223 | 45.275 | 80.763
| 22.4514 | 309.475 | 50.634 | 66.31 | 45.377 | 80.872
| 22.4583 | 310.069 | 50.703 | 66.358 | 45.431 | 80.939
| 22.4653 | 309.215 | 50.731 | 66.381 | 45.457 | 80.974
| 22.4722 | 309.632 | 50.75 | 66.405 | 45.47 | 81.002
| 22.4792 | 309.083 | 50.724 | 66.39 | 45.45 | 80.985
| 22.4861 | 309.053 | 50.724 | 66.392 | 45.449 | 80.986
| 22.4931 | 307.587 | 50.688 | 66.366 | 45.428 | 80.952
| 22.5 | 308.244 | 50.667 | 66.345 | 45.406 | 80.92
| 22.5069 | 308.502 | 50.667 | 66.345 | 45.41 | 80.917
| 22.5139 | 307.943 | 50.635 | 66.317 | 45.386 | 80.877
| 22.5208 | 308.044 | 50.617 | 66.289 | 45.369 | 80.851
| 22.5278 | 308.184 | 50.603 | 66.268 | 45.357 | 80.821
| 22.5347 | 307.544 | 50.581 | 66.251 | 45.344 | 80.784
| 22.5417 | 306.983 | 50.558 | 66.224 | 45.325 | 80.757
| 22.5486 | 306.302 | 50.521 | 66.186 | 45.291 | 80.701
| 22.5556 | 306.645 | 50.518 | 66.168 | 45.294 | 80.683
| 22.5625 | 306.151 | 50.491 | 66.142 | 45.275 | 80.646
| 22.5694 | 306.85 | 50.475 | 66.117 | 45.259 | 80.611
| 22.5764 | 306.997 | 50.475 | 66.098 | 45.259 | 80.593
| 22.5833 | 307.08 | 50.504 | 66.115 | 45.281 | 80.613
| 22.5903 | 307.048 | 50.522 | 66.117 | 45.294 | 80.621
| 22.5972 | 307.59 | 50.565 | 66.146 | 45.331 | 80.664
| 22.6042 | 308.611 | 50.618 | 66.187 | 45.371 | 80.718
| 22.6111 | 308.451 | 50.654 | 66.215 | 45.406 | 80.771
| 22.6181 | 307.719 | 50.644 | 66.221 | 45.396 | 80.773
| 22.625 | 307.958 | 50.65 | 66.216 | 45.393 | 80.779
| 22.6319 | 308.332 | 50.663 | 66.234 | 45.407 | 80.799
| 22.6389 | 307.567 | 50.68 | 66.252 | 45.419 | 80.826
| 22.6458 | 308.178 | 50.705 | 66.277 | 45.446 | 80.87
| 22.6528 | 308.446 | 50.719 | 66.287 | 45.451 | 80.876
| 22.6597 | 307.896 | 50.715 | 66.288 | 45.444 | 80.88
| 22.6667 | 307.492 | 50.688 | 66.27 | 45.426 | 80.865
| 22.6736 | 307.446 | 50.653 | 66.24 | 45.403 | 80.83
| 22.6806 | 307.396 | 50.624 | 66.22 | 45.378 | 80.799
| 22.6875 | 306.899 | 50.614 | 66.203 | 45.366 | 80.771
| 22.6944 | 307.729 | 50.606 | 66.195 | 45.365 | 80.761
| 22.7014 | 307.134 | 50.596 | 66.176 | 45.355 | 80.741
| 22.7083 | 306.945 | 50.583 | 66.162 | 45.344 | 80.725
| 22.7153 | 307.348 | 50.579 | 66.157 | 45.349 | 80.717
| 22.7222 | 308.208 | 50.567 | 66.137 | 45.333 | 80.694
| 22.7292 | 307.822 | 50.604 | 66.166 | 45.366 | 80.734
| 22.7361 | 307.246 | 50.58 | 66.139 | 45.347 | 80.701
| 22.7431 | 306.509 | 50.529 | 66.1 | 45.313 | 80.639
| 22.75 | 309.062 | 50.464 | 66.037 | 45.252 | 80.567
| 22.7569 | 309.128 | 50.601 | 66.133 | 45.362 | 80.695
| 22.7639 | 308.641 | 50.663 | 66.176 | 45.409 | 80.758
| 22.7708 | 308.769 | 50.675 | 66.194 | 45.423 | 80.779
| 22.7778 | 308.793 | 50.688 | 66.21 | 45.438 | 80.806
| 22.7847 | 308.844 | 50.779 | 66.284 | 45.504 | 80.909
| 22.7917 | 308.752 | 50.778 | 66.298 | 45.504 | 80.927
| 22.7986 | 309.571 | 50.784 | 66.315 | 45.517 | 80.948
| 22.8056 | 308.907 | 50.804 | 66.336 | 45.528 | 80.977
| 22.8125 | 309.221 | 50.811 | 66.354 | 45.54 | 81
| 22.8194 | 309.942 | 50.861 | 66.391 | 45.574 | 81.059
| 22.8264 | 309.995 | 50.905 | 66.446 | 45.615 | 81.126
| 22.8333 | 310.407 | 50.936 | 66.483 | 45.639 | 81.173
| 22.8403 | 310.275 | 50.955 | 66.511 | 45.664 | 81.213
| 22.8472 | 309.736 | 50.972 | 66.54 | 45.674 | 81.249
| 22.8542 | 310.931 | 51.004 | 66.579 | 45.708 | 81.304
| 22.8611 | 310.87 | 51.053 | 66.63 | 45.74 | 81.362
| 22.8681 | 311.062 | 51.084 | 66.67 | 45.768 | 81.419
| 22.875 | 312.105 | 51.133 | 66.719 | 45.805 | 81.492
| 22.8819 | 311.743 | 51.188 | 66.783 | 45.856 | 81.568
| 22.8889 | 308.277 | 51.097 | 66.75 | 45.8 | 81.511
| 22.8958 | 308.042 | 51.004 | 66.684 | 45.715 | 81.415
| 22.9028 | 307.934 | 50.955 | 66.648 | 45.686 | 81.366
| 22.9097 | 307.416 | 50.907 | 66.611 | 45.651 | 81.305
| 22.9167 | 309.967 | 50.933 | 66.622 | 45.674 | 81.313
| 22.9236 | 307.666 | 50.857 | 66.559 | 45.613 | 81.225
| 22.9306 | 307.363 | 50.808 | 66.515 | 45.577 | 81.157
| 22.9375 | 308.212 | 50.793 | 66.498 | 45.57 | 81.123
| 22.9444 | 309.065 | 50.804 | 66.496 | 45.578 | 81.114
| 22.9514 | 309.138 | 50.843 | 66.515 | 45.614 | 81.137
| 22.9583 | 308.178 | 50.871 | 66.538 | 45.638 | 81.159
| 22.9653 | 308.901 | 50.875 | 66.545 | 45.639 | 81.162
| 22.9722 | 308.523 | 50.891 | 66.556 | 45.656 | 81.179
| 22.9792 | 309.102 | 50.918 | 66.578 | 45.682 | 81.211
| 22.9861 | 310.461 | 50.955 | 66.608 | 45.71 | 81.245
| 22.9931 | 310.664 | 51.029 | 66.676 | 45.771 | 81.327
| 23 | 310.655 | 51.073 | 66.714 | 45.806 | 81.389
| 23.0069 | 310.59 | 51.108 | 66.761 | 45.835 | 81.443
| 23.0139 | 309.975 | 51.133 | 66.794 | 45.858 | 81.481
| 23.0208 | 310.71 | 51.152 | 66.821 | 45.874 | 81.519
| 23.0278 | 312.021 | 51.209 | 66.875 | 45.924 | 81.586
| 23.0347 | 312.766 | 51.289 | 66.958 | 45.987 | 81.691
| 23.0417 | 312.03 | 51.339 | 67.029 | 46.035 | 81.778
| 23.0486 | 311.938 | 51.371 | 67.067 | 46.064 | 81.83
| 23.0556 | 311.701 | 51.361 | 67.081 | 46.055 | 81.842
| 23.0625 | 312.049 | 51.373 | 67.111 | 46.066 | 81.876
| 23.0694 | 308.7 | 51.368 | 67.128 | 46.072 | 81.892
| 23.0764 | 305.758 | 51.127 | 66.956 | 45.876 | 81.646
| 23.0833 | 306.718 | 50.976 | 66.827 | 45.757 | 81.471
| 23.0903 | 305.952 | 50.903 | 66.753 | 45.705 | 81.356
| 23.0972 | 306.639 | 50.863 | 66.704 | 45.681 | 81.28
| 23.1042 | 306.728 | 50.858 | 66.67 | 45.672 | 81.225
| 23.1111 | 306.811 | 50.83 | 66.629 | 45.653 | 81.17
| 23.1181 | 306.917 | 50.812 | 66.605 | 45.645 | 81.121
| 23.125 | 307.176 | 50.805 | 66.581 | 45.643 | 81.094
| 23.1319 | 306.627 | 50.833 | 66.581 | 45.66 | 81.089
| 23.1389 | 307.767 | 50.839 | 66.581 | 45.668 | 81.084
| 23.1458 | 307.54 | 50.853 | 66.579 | 45.677 | 81.087
| 23.1528 | 307.411 | 50.874 | 66.587 | 45.693 | 81.09
| 23.1597 | 307.961 | 50.886 | 66.594 | 45.707 | 81.104
| 23.1667 | 308.25 | 50.919 | 66.615 | 45.729 | 81.131
| 23.1736 | 308.356 | 50.937 | 66.63 | 45.749 | 81.152
| 23.1806 | 307.929 | 50.94 | 66.635 | 45.754 | 81.156
| 23.1875 | 308.209 | 50.953 | 66.639 | 45.759 | 81.162
| 23.1944 | 306.974 | 50.939 | 66.628 | 45.754 | 81.149
| 23.2014 | 306.217 | 50.879 | 66.59 | 45.705 | 81.089
| 23.2083 | 306.872 | 50.844 | 66.548 | 45.68 | 81.037
| 23.2153 | 306.405 | 50.788 | 66.505 | 45.638 | 80.968
| 23.2222 | 306.008 | 50.756 | 66.464 | 45.613 | 80.921
| 23.2292 | 309.053 | 50.812 | 66.488 | 45.651 | 80.956
| 23.2361 | 305.102 | 50.854 | 66.527 | 45.702 | 80.993
| 23.2431 | 310.243 | 50.975 | 66.602 | 45.784 | 81.109
| 23.25 | 310.242 | 51.099 | 66.712 | 45.887 | 81.256
| 23.2569 | 310.877 | 51.149 | 66.77 | 45.92 | 81.334
| 23.2639 | 309.85 | 51.201 | 66.823 | 45.96 | 81.414
| 23.2708 | 309.127 | 51.209 | 66.848 | 45.972 | 81.448
| 23.2778 | 307.463 | 51.126 | 66.801 | 45.911 | 81.389
| 23.2847 | 310.772 | 51.074 | 66.753 | 45.849 | 81.334
| 23.2917 | 309.469 | 51.173 | 66.839 | 45.947 | 81.438
| 23.2986 | 310.099 | 51.18 | 66.858 | 45.955 | 81.463
| 23.3056 | 309.421 | 51.232 | 66.906 | 45.994 | 81.523
| 23.3125 | 309.869 | 51.214 | 66.906 | 45.981 | 81.521
| 23.3194 | 308.229 | 51.203 | 66.906 | 45.98 | 81.527
| 23.3264 | 307.156 | 51.082 | 66.825 | 45.884 | 81.41
| 23.3333 | 309.308 | 51.116 | 66.842 | 45.903 | 81.435
| 23.3403 | 308.429 | 51.114 | 66.836 | 45.906 | 81.429
| 23.3472 | 307.802 | 51.097 | 66.818 | 45.889 | 81.4
| 23.3542 | 307.466 | 51.067 | 66.801 | 45.875 | 81.372
| 23.3611 | 307.375 | 51.025 | 66.768 | 45.84 | 81.32
| 23.3681 | 307.886 | 50.964 | 66.71 | 45.785 | 81.245
| 23.375 | 308.309 | 51.059 | 66.774 | 45.868 | 81.329
| 23.3819 | 308.702 | 51.067 | 66.769 | 45.871 | 81.336
| 23.3889 | 308.463 | 51.059 | 66.77 | 45.872 | 81.331
| 23.3958 | 308.038 | 51.058 | 66.754 | 45.86 | 81.322
| 23.4028 | 307.964 | 51.046 | 66.752 | 45.854 | 81.311
| 23.4097 | 307.914 | 51.053 | 66.755 | 45.864 | 81.31
| 23.4167 | 307.372 | 51.01 | 66.717 | 45.829 | 81.263
| 23.4236 | 306.458 | 50.95 | 66.669 | 45.782 | 81.195
| 23.4306 | 309.343 | 50.927 | 66.639 | 45.75 | 81.151
| 23.4375 | 311.768 | 51.136 | 66.783 | 45.927 | 81.353
| 23.4444 | 311.829 | 51.259 | 66.892 | 46.025 | 81.501
| 23.4514 | 309.894 | 51.323 | 66.954 | 46.076 | 81.586
| 23.4583 | 309.981 | 51.273 | 66.941 | 46.037 | 81.567
| 23.4653 | 309.872 | 51.248 | 66.924 | 46.007 | 81.546
| 23.4722 | 308.418 | 51.27 | 66.955 | 46.034 | 81.589
| 23.4792 | 309.859 | 51.245 | 66.941 | 46.007 | 81.571
| 23.4861 | 309.755 | 51.257 | 66.956 | 46.02 | 81.587
| 23.4931 | 309.416 | 51.203 | 66.92 | 45.98 | 81.541
| 23.5 | 308.547 | 51.205 | 66.918 | 45.977 | 81.538
| 23.5069 | 309.919 | 51.212 | 66.929 | 45.986 | 81.547
| 23.5139 | 312.157 | 51.3 | 66.988 | 46.052 | 81.635
| 23.5208 | 312.335 | 51.412 | 67.088 | 46.15 | 81.768
| 23.5278 | 309.313 | 51.285 | 67.008 | 46.043 | 81.651
| 23.5347 | 308.997 | 51.145 | 66.896 | 45.925 | 81.514
| 23.5417 | 309.797 | 51.185 | 66.919 | 45.962 | 81.54
| 23.5486 | 310.147 | 51.218 | 66.948 | 45.993 | 81.576
| 23.5556 | 310.113 | 51.264 | 66.978 | 46.03 | 81.618
| 23.5625 | 310.246 | 51.291 | 67.005 | 46.056 | 81.662
| 23.5694 | 310.611 | 51.309 | 67.03 | 46.067 | 81.691
| 23.5764 | 309.443 | 51.277 | 67.007 | 46.041 | 81.67
| 23.5833 | 308.986 | 51.234 | 66.979 | 46.013 | 81.632
| 23.5903 | 309.334 | 51.242 | 66.991 | 46.019 | 81.645
| 23.5972 | 309.152 | 51.24 | 66.99 | 46.024 | 81.644
| 23.6042 | 309.557 | 51.243 | 66.989 | 46.021 | 81.644
| 23.6111 | 309.832 | 51.283 | 67.017 | 46.055 | 81.69
| 23.6181 | 309.074 | 51.274 | 67.021 | 46.058 | 81.687
| 23.625 | 309.176 | 51.256 | 67.004 | 46.037 | 81.669
| 23.6319 | 309.315 | 51.262 | 67.001 | 46.032 | 81.672
| 23.6389 | 310.005 | 51.287 | 67.034 | 46.065 | 81.716
| 23.6458 | 310.202 | 51.327 | 67.065 | 46.088 | 81.754
| 23.6528 | 309.924 | 51.348 | 67.085 | 46.103 | 81.787
| 23.6597 | 311.602 | 51.402 | 67.128 | 46.148 | 81.845
| 23.6667 | 310.943 | 51.438 | 67.17 | 46.177 | 81.906
| 23.6736 | 311.407 | 51.459 | 67.204 | 46.2 | 81.953
| 23.6806 | 312.108 | 51.497 | 67.242 | 46.238 | 82.012
| 23.6875 | 310.643 | 51.471 | 67.24 | 46.215 | 82.004
| 23.6944 | 310.204 | 51.481 | 67.258 | 46.22 | 82.026
| 23.7014 | 311.369 | 51.504 | 67.281 | 46.236 | 82.062
| 23.7083 | 310.906 | 51.517 | 67.3 | 46.257 | 82.09
| 23.7153 | 310.956 | 51.537 | 67.326 | 46.268 | 82.119
| 23.7222 | 310.852 | 51.543 | 67.345 | 46.283 | 82.148
| 23.7292 | 310.382 | 51.513 | 67.328 | 46.252 | 82.117
| 23.7361 | 308.209 | 51.432 | 67.272 | 46.189 | 82.042
| 23.7431 | 305.671 | 51.25 | 67.131 | 46.046 | 81.846
| 23.75 | 309.591 | 51.257 | 67.11 | 46.044 | 81.822
| 23.7569 | 309.916 | 51.326 | 67.155 | 46.111 | 81.869
| 23.7639 | 310.364 | 51.369 | 67.184 | 46.144 | 81.909
| 23.7708 | 310.02 | 51.402 | 67.207 | 46.168 | 81.943
| 23.7778 | 310.633 | 51.428 | 67.232 | 46.191 | 81.976
| 23.7847 | 311.017 | 51.476 | 67.275 | 46.229 | 82.031
| 23.7917 | 311.574 | 51.501 | 67.303 | 46.248 | 82.062
| 23.7986 | 310.231 | 51.518 | 67.324 | 46.262 | 82.096
| 23.8056 | 309.904 | 51.47 | 67.299 | 46.234 | 82.062
| 23.8125 | 309.65 | 51.461 | 67.302 | 46.227 | 82.053
| 23.8194 | 310.65 | 51.475 | 67.301 | 46.231 | 82.065
| 23.8264 | 310.771 | 51.506 | 67.336 | 46.261 | 82.101
| 23.8333 | 311.813 | 51.547 | 67.368 | 46.289 | 82.152
| 23.8403 | 312.224 | 51.6 | 67.417 | 46.331 | 82.216
| 23.8472 | 307.285 | 51.428 | 67.307 | 46.206 | 82.052
| 23.8542 | 308.157 | 51.345 | 67.236 | 46.136 | 81.95
| 23.8611 | 309.356 | 51.331 | 67.211 | 46.126 | 81.92
| 23.8681 | 310.079 | 51.376 | 67.233 | 46.169 | 81.951
| 23.875 | 309.912 | 51.435 | 67.275 | 46.218 | 82
| 23.8819 | 310.472 | 51.47 | 67.304 | 46.24 | 82.038
| 23.8889 | 311.605 | 51.517 | 67.351 | 46.283 | 82.091
| 23.8958 | 310.898 | 51.567 | 67.401 | 46.326 | 82.152
| 23.9028 | 312.495 | 51.614 | 67.44 | 46.357 | 82.208
| 23.9097 | 306.796 | 51.477 | 67.357 | 46.268 | 82.094
| 23.9167 | 307.094 | 51.345 | 67.259 | 46.152 | 81.949
| 23.9236 | 307.667 | 51.279 | 67.197 | 46.106 | 81.858
| 23.9306 | 308.416 | 51.252 | 67.163 | 46.087 | 81.801
| 23.9375 | 308.749 | 51.291 | 67.175 | 46.117 | 81.822
| 23.9444 | 311.466 | 51.347 | 67.201 | 46.154 | 81.856
| 23.9514 | 310.852 | 51.468 | 67.296 | 46.261 | 81.981
| 23.9583 | 310.723 | 51.489 | 67.325 | 46.279 | 82.018
| 23.9653 | 311.4 | 51.553 | 67.382 | 46.329 | 82.096
| 23.9722 | 306.241 | 51.412 | 67.301 | 46.233 | 81.973
| 23.9792 | 306.403 | 51.241 | 67.164 | 46.095 | 81.79
| 23.9861 | 306.471 | 51.172 | 67.096 | 46.034 | 81.682
| 23.9931 | 306.798 | 51.173 | 67.077 | 46.042 | 81.652
| 24 | 307.316 | 51.153 | 67.044 | 46.025 | 81.602
| 24.0069 | 306.608 | 51.104 | 66.996 | 45.991 | 81.524
| 24.0139 | 306.2 | 51.075 | 66.958 | 45.965 | 81.471
| 24.0208 | 306.785 | 51.078 | 66.936 | 45.968 | 81.442
| 24.0278 | 307.345 | 51.093 | 66.931 | 45.976 | 81.428
| 24.0347 | 307.229 | 51.145 | 66.964 | 46.022 | 81.464
| 24.0417 | 307.278 | 51.141 | 66.953 | 46.02 | 81.444
| 24.0486 | 307.467 | 51.136 | 66.953 | 46.02 | 81.439
| 24.0556 | 307.528 | 51.138 | 66.95 | 46.018 | 81.425
| 24.0625 | 307.656 | 51.173 | 66.961 | 46.038 | 81.448
| 24.0694 | 307.754 | 51.191 | 66.983 | 46.065 | 81.47
| 24.0764 | 308.837 | 51.221 | 67.001 | 46.079 | 81.497
| 24.0833 | 308.598 | 51.244 | 67.02 | 46.106 | 81.526
| 24.0903 | 308.736 | 51.263 | 67.038 | 46.121 | 81.548
| 24.0972 | 309.111 | 51.285 | 67.058 | 46.133 | 81.579
| 24.1042 | 308.786 | 51.314 | 67.091 | 46.161 | 81.617
| 24.1111 | 308.638 | 51.323 | 67.099 | 46.171 | 81.638
| 24.1181 | 309.807 | 51.38 | 67.154 | 46.215 | 81.704
| 24.125 | 310.16 | 51.403 | 67.183 | 46.239 | 81.739
| 24.1319 | 309.496 | 51.419 | 67.211 | 46.254 | 81.773
| 24.1389 | 308.813 | 51.406 | 67.209 | 46.24 | 81.771
| 24.1458 | 308.815 | 51.393 | 67.208 | 46.235 | 81.767
| 24.1528 | 309.191 | 51.377 | 67.201 | 46.217 | 81.757
| 24.1597 | 308.754 | 51.383 | 67.214 | 46.232 | 81.774
| 24.1667 | 308.889 | 51.388 | 67.225 | 46.238 | 81.78
| 24.1736 | 309.039 | 51.398 | 67.236 | 46.248 | 81.794
| 24.1806 | 309.658 | 51.418 | 67.256 | 46.268 | 81.815
| 24.1875 | 309.674 | 51.424 | 67.266 | 46.274 | 81.817
| 24.1944 | 309.408 | 51.432 | 67.284 | 46.283 | 81.838
| 24.2014 | 308.8 | 51.443 | 67.295 | 46.289 | 81.852
| 24.2083 | 310.329 | 51.466 | 67.318 | 46.301 | 81.88
| 24.2153 | 307.993 | 51.441 | 67.314 | 46.293 | 81.869
| 24.2222 | 308.771 | 51.413 | 67.293 | 46.266 | 81.841
| 24.2292 | 308.172 | 51.38 | 67.273 | 46.246 | 81.81
| 24.2361 | 306.58 | 51.318 | 67.225 | 46.197 | 81.739
| 24.2431 | 309.448 | 51.362 | 67.246 | 46.23 | 81.771
| 24.25 | 309.449 | 51.401 | 67.273 | 46.259 | 81.802
| 24.2569 | 307.82 | 51.382 | 67.264 | 46.254 | 81.797
| 24.2639 | 307.27 | 51.351 | 67.248 | 46.229 | 81.761
| 24.2708 | 306.389 | 51.275 | 67.184 | 46.171 | 81.675
| 24.2778 | 309.975 | 51.373 | 67.244 | 46.242 | 81.765
| 24.2847 | 311.117 | 51.461 | 67.31 | 46.31 | 81.847
| 24.2917 | 310.641 | 51.528 | 67.381 | 46.369 | 81.935
| 24.2986 | 310.735 | 51.583 | 67.432 | 46.41 | 82.012
| 24.3056 | 309.887 | 51.599 | 67.467 | 46.428 | 82.056
| 24.3125 | 309.039 | 51.553 | 67.444 | 46.387 | 82.023
| 24.3194 | 307.769 | 51.458 | 67.384 | 46.315 | 81.94
| 24.3264 | 306.336 | 51.332 | 67.292 | 46.221 | 81.807
| 24.3333 | 309.013 | 51.402 | 67.328 | 46.273 | 81.863
| 24.3403 | 309.608 | 51.43 | 67.344 | 46.298 | 81.881
| 24.3472 | 311.573 | 51.5 | 67.4 | 46.351 | 81.959
| 24.3542 | 311.193 | 51.556 | 67.448 | 46.398 | 82.026
| 24.3611 | 310.989 | 51.58 | 67.483 | 46.417 | 82.067
| 24.3681 | 309.301 | 51.56 | 67.483 | 46.406 | 82.07
| 24.375 | 309.322 | 51.526 | 67.462 | 46.38 | 82.034
| 24.3819 | 308.814 | 51.493 | 67.441 | 46.347 | 81.998
| 24.3889 | 308.999 | 51.474 | 67.426 | 46.335 | 81.979
| 24.3958 | 309.025 | 51.461 | 67.415 | 46.325 | 81.961
| 24.4028 | 309.478 | 51.47 | 67.416 | 46.324 | 81.955
| 24.4097 | 309.985 | 51.476 | 67.42 | 46.339 | 81.966
| 24.4167 | 309.768 | 51.496 | 67.443 | 46.36 | 81.996
| 24.4236 | 308.333 | 51.497 | 67.447 | 46.357 | 81.991
| 24.4306 | 308.756 | 51.463 | 67.421 | 46.333 | 81.961
| 24.4375 | 308.865 | 51.454 | 67.408 | 46.321 | 81.943
| 24.4444 | 308.864 | 51.443 | 67.399 | 46.308 | 81.926
| 24.4514 | 308.156 | 51.426 | 67.382 | 46.302 | 81.906
| 24.4583 | 309.058 | 51.426 | 67.377 | 46.295 | 81.897
| 24.4653 | 308.789 | 51.42 | 67.372 | 46.29 | 81.889
| 24.4722 | 307.724 | 51.377 | 67.333 | 46.257 | 81.838
| 24.4792 | 307.919 | 51.348 | 67.306 | 46.233 | 81.793
| 24.4861 | 308.048 | 51.32 | 67.28 | 46.21 | 81.761
| 24.4931 | 307.758 | 51.301 | 67.253 | 46.198 | 81.725
| 24.5 | 308.701 | 51.307 | 67.245 | 46.199 | 81.714
| 24.5069 | 309.069 | 51.321 | 67.243 | 46.202 | 81.712
| 24.5139 | 307.904 | 51.316 | 67.243 | 46.212 | 81.708
| 24.5208 | 308.815 | 51.314 | 67.235 | 46.202 | 81.699
| 24.5278 | 308.852 | 51.363 | 67.267 | 46.23 | 81.744
| 24.5347 | 309.921 | 51.426 | 67.317 | 46.293 | 81.818
| 24.5417 | 308.9 | 51.467 | 67.36 | 46.329 | 81.866
| 24.5486 | 310.15 | 51.487 | 67.381 | 46.344 | 81.907
| 24.5556 | 310.352 | 51.518 | 67.411 | 46.364 | 81.946
| 24.5625 | 310.805 | 51.535 | 67.436 | 46.374 | 81.985
| 24.5694 | 309.815 | 51.55 | 67.454 | 46.386 | 82.018
| 24.5764 | 309.272 | 51.512 | 67.44 | 46.36 | 81.991
| 24.5833 | 308.637 | 51.482 | 67.418 | 46.331 | 81.96
| 24.5903 | 309.94 | 51.485 | 67.417 | 46.337 | 81.97
| 24.5972 | 310.171 | 51.473 | 67.413 | 46.329 | 81.959
| 24.6042 | 309.229 | 51.489 | 67.429 | 46.339 | 81.975
| 24.6111 | 309.557 | 51.509 | 67.445 | 46.355 | 82.003
| 24.6181 | 309.115 | 51.481 | 67.428 | 46.335 | 81.98
| 24.625 | 309.112 | 51.462 | 67.412 | 46.318 | 81.961
| 24.6319 | 309.214 | 51.452 | 67.405 | 46.311 | 81.951
| 24.6389 | 308.723 | 51.428 | 67.387 | 46.296 | 81.927
| 24.6458 | 306.226 | 51.342 | 67.32 | 46.225 | 81.836
| 24.6528 | 306.947 | 51.287 | 67.263 | 46.179 | 81.759
| 24.6597 | 308.13 | 51.306 | 67.263 | 46.189 | 81.762
| 24.6667 | 308.051 | 51.322 | 67.265 | 46.201 | 81.769
| 24.6736 | 309.149 | 51.353 | 67.287 | 46.23 | 81.792
| 24.6806 | 309.173 | 51.388 | 67.306 | 46.253 | 81.834
| 24.6875 | 309.071 | 51.414 | 67.328 | 46.274 | 81.862
| 24.6944 | 309.714 | 51.42 | 67.34 | 46.278 | 81.872
| 24.7014 | 309.837 | 51.458 | 67.371 | 46.309 | 81.925
| 24.7083 | 309.475 | 51.48 | 67.394 | 46.325 | 81.949
| 24.7153 | 309.552 | 51.494 | 67.405 | 46.338 | 81.971
| 24.7222 | 309.04 | 51.468 | 67.394 | 46.318 | 81.957
| 24.7292 | 309.031 | 51.429 | 67.375 | 46.288 | 81.93
| 24.7361 | 306.544 | 51.331 | 67.3 | 46.211 | 81.825
| 24.7431 | 308.786 | 51.303 | 67.261 | 46.18 | 81.781
| 24.75 | 308.981 | 51.34 | 67.276 | 46.218 | 81.799
| 24.7569 | 308.917 | 51.366 | 67.298 | 46.237 | 81.825
| 24.7639 | 310.038 | 51.387 | 67.31 | 46.253 | 81.85
| 24.7708 | 310.853 | 51.439 | 67.349 | 46.292 | 81.904
| 24.7778 | 310.326 | 51.483 | 67.391 | 46.329 | 81.957
| 24.7847 | 311.401 | 51.551 | 67.452 | 46.384 | 82.045
| 24.7917 | 312.239 | 51.638 | 67.531 | 46.45 | 82.156
| 24.7986 | 311.861 | 51.69 | 67.589 | 46.489 | 82.232
| 24.8056 | 308.33 | 51.632 | 67.578 | 46.461 | 82.215
| 24.8125 | 308.305 | 51.496 | 67.479 | 46.337 | 82.082
| 24.8194 | 308.557 | 51.451 | 67.435 | 46.298 | 82.02
| 24.8264 | 306.092 | 51.316 | 67.335 | 46.198 | 81.872
| 24.8333 | 306.467 | 51.226 | 67.25 | 46.124 | 81.758
| 24.8403 | 307.189 | 51.187 | 67.193 | 46.098 | 81.683
| 24.8472 | 307.622 | 51.181 | 67.173 | 46.097 | 81.647
| 24.8542 | 307.457 | 51.202 | 67.171 | 46.109 | 81.641
| 24.8611 | 308.531 | 51.21 | 67.164 | 46.111 | 81.625
| 24.8681 | 308.362 | 51.234 | 67.177 | 46.141 | 81.648
| 24.875 | 308.197 | 51.223 | 67.162 | 46.127 | 81.625
| 24.8819 | 308.652 | 51.23 | 67.16 | 46.132 | 81.623
| 24.8889 | 308.299 | 51.259 | 67.175 | 46.156 | 81.65
| 24.8958 | 309.755 | 51.312 | 67.216 | 46.196 | 81.697
| 24.9028 | 309.093 | 51.32 | 67.225 | 46.203 | 81.711
| 24.9097 | 308.203 | 51.287 | 67.207 | 46.18 | 81.69
| 24.9167 | 307.931 | 51.279 | 67.195 | 46.172 | 81.676
| 24.9236 | 309.491 | 51.327 | 67.23 | 46.203 | 81.727
| 24.9306 | 309.749 | 51.366 | 67.265 | 46.239 | 81.771
| 24.9375 | 309.619 | 51.391 | 67.295 | 46.257 | 81.806
| 24.9444 | 311.364 | 51.432 | 67.324 | 46.283 | 81.853
| 24.9514 | 308.373 | 51.546 | 67.428 | 46.385 | 81.988
| 24.9583 | 308.212 | 51.398 | 67.331 | 46.265 | 81.855
| 24.9653 | 309.163 | 51.357 | 67.305 | 46.23 | 81.814
| 24.9722 | 308.916 | 51.354 | 67.302 | 46.235 | 81.813
| 24.9792 | 309.182 | 51.383 | 67.321 | 46.253 | 81.84
| 24.9861 | 310.119 | 51.42 | 67.346 | 46.283 | 81.873
| 24.9931 | 311.164 | 51.523 | 67.431 | 46.368 | 81.984
| 25 | 310.863 | 51.575 | 67.494 | 46.417 | 82.062
| 25.0069 | 311.129 | 51.614 | 67.538 | 46.445 | 82.128
| 25.0139 | 310.813 | 51.626 | 67.565 | 46.453 | 82.156
| 25.0208 | 309.91 | 51.59 | 67.556 | 46.421 | 82.135
| 25.0278 | 312.114 | 51.599 | 67.565 | 46.429 | 82.159
| 25.0347 | 306.864 | 51.656 | 67.622 | 46.479 | 82.233
| 25.0417 | 306.766 | 51.479 | 67.498 | 46.336 | 82.054
| 25.0486 | 306.738 | 51.39 | 67.427 | 46.273 | 81.952
| 25.0556 | 307.238 | 51.33 | 67.375 | 46.218 | 81.865
| 25.0625 | 306.122 | 51.263 | 67.31 | 46.175 | 81.779
| 25.0694 | 305.449 | 51.179 | 67.223 | 46.109 | 81.658
| 25.0764 | 306.752 | 51.158 | 67.187 | 46.086 | 81.606
| 25.0833 | 306.942 | 51.174 | 67.18 | 46.098 | 81.594
| 25.0903 | 308.118 | 51.202 | 67.188 | 46.123 | 81.604
| 25.0972 | 307.733 | 51.237 | 67.207 | 46.158 | 81.625
| 25.1042 | 308.608 | 51.281 | 67.226 | 46.18 | 81.646
| 25.1111 | 307.985 | 51.301 | 67.244 | 46.193 | 81.671
| 25.1181 | 309.427 | 51.349 | 67.282 | 46.236 | 81.715
| 25.125 | 309.001 | 51.401 | 67.325 | 46.279 | 81.778
| 25.1319 | 309.046 | 51.423 | 67.354 | 46.293 | 81.817
| 25.1389 | 309.075 | 51.423 | 67.364 | 46.293 | 81.829
| 25.1458 | 309.683 | 51.454 | 67.391 | 46.326 | 81.869
| 25.1528 | 309.686 | 51.469 | 67.414 | 46.333 | 81.901
| 25.1597 | 306.691 | 51.371 | 67.353 | 46.262 | 81.808
| 25.1667 | 306.641 | 51.283 | 67.284 | 46.186 | 81.719
| 25.1736 | 307.518 | 51.255 | 67.25 | 46.166 | 81.673
| 25.1806 | 307.469 | 51.247 | 67.234 | 46.16 | 81.648
| 25.1875 | 307.347 | 51.248 | 67.229 | 46.164 | 81.637
| 25.1944 | 306.97 | 51.242 | 67.215 | 46.158 | 81.622
| 25.2014 | 307.154 | 51.2 | 67.178 | 46.127 | 81.565
| 25.2083 | 307.112 | 51.205 | 67.174 | 46.129 | 81.561
| 25.2153 | 306.845 | 51.177 | 67.142 | 46.11 | 81.519
| 25.2222 | 306.539 | 51.142 | 67.107 | 46.079 | 81.467
| 25.2292 | 306.783 | 51.114 | 67.073 | 46.053 | 81.428
| 25.2361 | 304.969 | 51.085 | 67.04 | 46.034 | 81.379
| 25.2431 | 308.773 | 51.218 | 67.126 | 46.141 | 81.505
| 25.25 | 308.142 | 51.258 | 67.161 | 46.176 | 81.548
| 25.2569 | 306.683 | 51.251 | 67.162 | 46.172 | 81.557
| 25.2639 | 306.678 | 51.231 | 67.152 | 46.152 | 81.534
| 25.2708 | 306.145 | 51.158 | 67.097 | 46.097 | 81.465
| 25.2778 | 307.283 | 51.155 | 67.075 | 46.086 | 81.445
| 25.2847 | 311.911 | 51.323 | 67.201 | 46.22 | 81.618
| 25.2917 | 310.253 | 51.429 | 67.296 | 46.309 | 81.748
| 25.2986 | 309.276 | 51.448 | 67.328 | 46.325 | 81.79
| 25.3056 | 308.906 | 51.435 | 67.337 | 46.314 | 81.802
| 25.3125 | 308.713 | 51.432 | 67.342 | 46.311 | 81.815
| 25.3194 | 308.618 | 51.41 | 67.337 | 46.292 | 81.804
| 25.3264 | 307.616 | 51.362 | 67.312 | 46.258 | 81.768
| 25.3333 | 309.281 | 51.383 | 67.327 | 46.276 | 81.789
| 25.3403 | 309.124 | 51.398 | 67.344 | 46.284 | 81.802
| 25.3472 | 308.714 | 51.369 | 67.324 | 46.266 | 81.778
| 25.3542 | 308.539 | 51.375 | 67.329 | 46.271 | 81.787
| 25.3611 | 308.622 | 51.371 | 67.332 | 46.27 | 81.786
| 25.3681 | 307.135 | 51.352 | 67.318 | 46.255 | 81.769
| 25.375 | 307.893 | 51.297 | 67.279 | 46.215 | 81.71
| 25.3819 | 307.336 | 51.301 | 67.27 | 46.213 | 81.697
| 25.3889 | 307.9 | 51.292 | 67.261 | 46.206 | 81.678
| 25.3958 | 307.333 | 51.272 | 67.25 | 46.195 | 81.66
| 25.4028 | 307.918 | 51.249 | 67.219 | 46.17 | 81.62
| 25.4097 | 308.431 | 51.262 | 67.226 | 46.186 | 81.628
| 25.4167 | 307.652 | 51.29 | 67.239 | 46.204 | 81.645
| 25.4236 | 307.812 | 51.271 | 67.225 | 46.194 | 81.625
| 25.4306 | 306.16 | 51.234 | 67.196 | 46.158 | 81.585
| 25.4375 | 307.44 | 51.2 | 67.165 | 46.134 | 81.537
| 25.4444 | 307.195 | 51.178 | 67.139 | 46.115 | 81.502
| 25.4514 | 306.906 | 51.17 | 67.13 | 46.115 | 81.488
| 25.4583 | 306.414 | 51.154 | 67.113 | 46.104 | 81.459
| 25.4653 | 306.929 | 51.16 | 67.101 | 46.105 | 81.451
| 25.4722 | 306.544 | 51.151 | 67.086 | 46.091 | 81.431
| 25.4792 | 306.963 | 51.155 | 67.079 | 46.096 | 81.424
| 25.4861 | 306.635 | 51.159 | 67.083 | 46.104 | 81.423
| 25.4931 | 306.601 | 51.171 | 67.083 | 46.109 | 81.425
| 25.5 | 310.908 | 51.225 | 67.116 | 46.141 | 81.472
| 25.5069 | 310.626 | 51.391 | 67.252 | 46.284 | 81.661
| 25.5139 | 311.456 | 51.512 | 67.358 | 46.373 | 81.803
| 25.5208 | 311.618 | 51.582 | 67.432 | 46.426 | 81.913
| 25.5278 | 311.862 | 51.667 | 67.526 | 46.493 | 82.039
| 25.5347 | 313.097 | 51.759 | 67.623 | 46.573 | 82.183
| 25.5417 | 308.704 | 51.646 | 67.575 | 46.485 | 82.109
| 25.5486 | 308.648 | 51.54 | 67.512 | 46.4 | 82.022
| 25.5556 | 309.788 | 51.531 | 67.506 | 46.394 | 82.018
| 25.5625 | 310.605 | 51.565 | 67.534 | 46.421 | 82.057
| 25.5694 | 309.165 | 51.565 | 67.549 | 46.423 | 82.067
| 25.5764 | 309.064 | 51.527 | 67.533 | 46.395 | 82.043
| 25.5833 | 308.877 | 51.484 | 67.5 | 46.366 | 82.001
| 25.5903 | 309.378 | 51.486 | 67.499 | 46.362 | 81.995
| 25.5972 | 309.307 | 51.5 | 67.512 | 46.375 | 82.01
| 25.6042 | 310.088 | 51.526 | 67.53 | 46.391 | 82.041
| 25.6111 | 310.346 | 51.544 | 67.553 | 46.409 | 82.066
| 25.6181 | 309.56 | 51.55 | 67.56 | 46.413 | 82.072
| 25.625 | 309.73 | 51.53 | 67.551 | 46.404 | 82.071
| 25.6319 | 310.176 | 51.548 | 67.567 | 46.413 | 82.088
| 25.6389 | 309.044 | 51.564 | 67.587 | 46.431 | 82.113
| 25.6458 | 308.515 | 51.492 | 67.54 | 46.372 | 82.051
| 25.6528 | 308.887 | 51.466 | 67.515 | 46.352 | 82.019
| 25.6597 | 309.686 | 51.492 | 67.526 | 46.37 | 82.031
| 25.6667 | 309.695 | 51.49 | 67.528 | 46.369 | 82.04
| 25.6736 | 309.201 | 51.493 | 67.53 | 46.371 | 82.037
| 25.6806 | 309.2 | 51.487 | 67.526 | 46.369 | 82.029
| 25.6875 | 308.639 | 51.47 | 67.509 | 46.355 | 82.013
| 25.6944 | 310.055 | 51.483 | 67.516 | 46.359 | 82.023
| 25.7014 | 309.296 | 51.487 | 67.518 | 46.365 | 82.021
| 25.7083 | 310.034 | 51.515 | 67.544 | 46.392 | 82.054
| 25.7153 | 309.459 | 51.525 | 67.555 | 46.4 | 82.067
| 25.7222 | 309.269 | 51.511 | 67.544 | 46.386 | 82.056
| 25.7292 | 309.508 | 51.482 | 67.527 | 46.361 | 82.031
| 25.7361 | 307.644 | 51.407 | 67.47 | 46.308 | 81.953
| 25.7431 | 311.007 | 51.362 | 67.415 | 46.255 | 81.886
| 25.75 | 309.831 | 51.459 | 67.49 | 46.35 | 81.981
| 25.7569 | 309.067 | 51.456 | 67.489 | 46.344 | 81.981
| 25.7639 | 309.702 | 51.469 | 67.498 | 46.361 | 82
| 25.7708 | 310.628 | 51.519 | 67.532 | 46.394 | 82.041
| 25.7778 | 312.409 | 51.609 | 67.609 | 46.465 | 82.149
| 25.7847 | 311.508 | 51.682 | 67.681 | 46.528 | 82.245
| 25.7917 | 312.254 | 51.756 | 67.755 | 46.584 | 82.347
| 25.7986 | 307.92 | 51.628 | 67.68 | 46.486 | 82.238
| 25.8056 | 308.345 | 51.548 | 67.625 | 46.416 | 82.161
| 25.8125 | 308.628 | 51.498 | 67.588 | 46.383 | 82.105
| 25.8194 | 309.13 | 51.487 | 67.569 | 46.374 | 82.083
| 25.8264 | 309.304 | 51.485 | 67.561 | 46.369 | 82.068
| 25.8333 | 309.697 | 51.473 | 67.55 | 46.363 | 82.049
| 25.8403 | 310.152 | 51.523 | 67.583 | 46.406 | 82.102
| 25.8472 | 311.275 | 51.59 | 67.636 | 46.46 | 82.167
| 25.8542 | 310.906 | 51.674 | 67.71 | 46.526 | 82.267
| 25.8611 | 312.124 | 51.722 | 67.752 | 46.558 | 82.327
| 25.8681 | 306.227 | 51.602 | 67.699 | 46.482 | 82.235
| 25.875 | 306.009 | 51.39 | 67.531 | 46.307 | 82.024
| 25.8819 | 306.834 | 51.278 | 67.424 | 46.214 | 81.866
| 25.8889 | 306.095 | 51.255 | 67.389 | 46.199 | 81.81
| 25.8958 | 308.018 | 51.255 | 67.36 | 46.2 | 81.776
| 25.9028 | 307.248 | 51.271 | 67.355 | 46.21 | 81.766
| 25.9097 | 308.361 | 51.318 | 67.375 | 46.247 | 81.794
| 25.9167 | 308.996 | 51.356 | 67.399 | 46.272 | 81.824
| 25.9236 | 310.083 | 51.405 | 67.436 | 46.317 | 81.87
| 25.9306 | 310.441 | 51.482 | 67.494 | 46.374 | 81.95
| 25.9375 | 306.182 | 51.364 | 67.422 | 46.29 | 81.848
| 25.9444 | 307.335 | 51.319 | 67.376 | 46.244 | 81.789
| 25.9514 | 309.395 | 51.354 | 67.395 | 46.276 | 81.816
| 25.9583 | 308.771 | 51.407 | 67.435 | 46.313 | 81.86
| 25.9653 | 309.784 | 51.413 | 67.435 | 46.315 | 81.86
| 25.9722 | 310.112 | 51.46 | 67.478 | 46.361 | 81.923
| 25.9792 | 309.934 | 51.509 | 67.516 | 46.399 | 81.979
| 25.9861 | 311.445 | 51.559 | 67.565 | 46.436 | 82.043
| 25.9931 | 311.185 | 51.632 | 67.638 | 46.494 | 82.142
| 26 | 310.747 | 51.672 | 67.683 | 46.531 | 82.205
| 26.0069 | 309.609 | 51.646 | 67.691 | 46.517 | 82.204
| 26.0139 | 309.351 | 51.592 | 67.651 | 46.465 | 82.161
| 26.0208 | 309.05 | 51.58 | 67.641 | 46.453 | 82.151
| 26.0278 | 308.953 | 51.545 | 67.625 | 46.43 | 82.118
| 26.0347 | 310.302 | 51.575 | 67.65 | 46.46 | 82.155
| 26.0417 | 311.307 | 51.647 | 67.71 | 46.51 | 82.23
| 26.0486 | 310.467 | 51.694 | 67.754 | 46.55 | 82.292
| 26.0556 | 310.47 | 51.677 | 67.755 | 46.54 | 82.294
| 26.0625 | 309.729 | 51.653 | 67.745 | 46.517 | 82.277
| 26.0694 | 310.381 | 51.658 | 67.752 | 46.521 | 82.286
| 26.0764 | 311.028 | 51.694 | 67.787 | 46.548 | 82.332
| 26.0833 | 311.998 | 51.735 | 67.827 | 46.58 | 82.386
| 26.0903 | 312.243 | 51.77 | 67.864 | 46.607 | 82.436
| 26.0972 | 307.247 | 51.622 | 67.765 | 46.494 | 82.294
| 26.1042 | 307.66 | 51.531 | 67.69 | 46.416 | 82.195
| 26.1111 | 309.437 | 51.507 | 67.664 | 46.401 | 82.159
| 26.1181 | 309.553 | 51.531 | 67.668 | 46.42 | 82.164
| 26.125 | 309.5 | 51.533 | 67.668 | 46.423 | 82.156
| 26.1319 | 309.074 | 51.525 | 67.656 | 46.415 | 82.141
| 26.1389 | 309.124 | 51.502 | 67.63 | 46.391 | 82.11
| 26.1458 | 307.895 | 51.496 | 67.624 | 46.394 | 82.098
| 26.1528 | 309.636 | 51.499 | 67.625 | 46.397 | 82.099
| 26.1597 | 309.424 | 51.53 | 67.644 | 46.412 | 82.122
| 26.1667 | 309.656 | 51.521 | 67.64 | 46.412 | 82.115
| 26.1736 | 309.364 | 51.513 | 67.624 | 46.399 | 82.105
| 26.1806 | 310.047 | 51.534 | 67.634 | 46.412 | 82.11
| 26.1875 | 309.671 | 51.564 | 67.659 | 46.437 | 82.15
| 26.1944 | 308.934 | 51.56 | 67.658 | 46.436 | 82.153
| 26.2014 | 309.269 | 51.525 | 67.633 | 46.403 | 82.119
| 26.2083 | 309.144 | 51.518 | 67.625 | 46.394 | 82.103
| 26.2153 | 308.81 | 51.506 | 67.615 | 46.389 | 82.093
| 26.2222 | 308.518 | 51.471 | 67.584 | 46.358 | 82.05
| 26.2292 | 308.386 | 51.458 | 67.565 | 46.348 | 82.031
| 26.2361 | 307.697 | 51.412 | 67.525 | 46.309 | 81.974
| 26.2431 | 305.867 | 51.329 | 67.456 | 46.243 | 81.874
| 26.25 | 305.552 | 51.254 | 67.379 | 46.181 | 81.777
| 26.2569 | 307.118 | 51.283 | 67.378 | 46.204 | 81.784
| 26.2639 | 308.589 | 51.32 | 67.397 | 46.239 | 81.807
| 26.2708 | 307.302 | 51.301 | 67.373 | 46.223 | 81.775
| 26.2778 | 305.291 | 51.235 | 67.319 | 46.171 | 81.699
| 26.2847 | 310.544 | 51.393 | 67.417 | 46.281 | 81.841
| 26.2917 | 310.93 | 51.5 | 67.503 | 46.369 | 81.963
| 26.2986 | 311.746 | 51.605 | 67.592 | 46.449 | 82.096
| 26.3056 | 310.287 | 51.624 | 67.629 | 46.47 | 82.147
| 26.3125 | 309.055 | 51.589 | 67.622 | 46.435 | 82.13
| 26.3194 | 309.455 | 51.552 | 67.596 | 46.401 | 82.101
| 26.3264 | 308.466 | 51.507 | 67.572 | 46.368 | 82.064
| 26.3333 | 309.005 | 51.496 | 67.558 | 46.35 | 82.059
| 26.3403 | 309.188 | 51.514 | 67.572 | 46.37 | 82.075
| 26.3472 | 308.676 | 51.493 | 67.561 | 46.358 | 82.062
| 26.3542 | 308.214 | 51.483 | 67.551 | 46.349 | 82.047
| 26.3611 | 308.864 | 51.482 | 67.551 | 46.346 | 82.045
| 26.3681 | 308.941 | 51.445 | 67.525 | 46.318 | 82.009
| 26.375 | 308.037 | 51.431 | 67.506 | 46.302 | 81.991
| 26.3819 | 308.491 | 51.413 | 67.485 | 46.291 | 81.965
| 26.3889 | 308.199 | 51.411 | 67.485 | 46.29 | 81.952
| 26.3958 | 307.879 | 51.378 | 67.451 | 46.258 | 81.915
| 26.4028 | 307.486 | 51.357 | 67.429 | 46.244 | 81.883
| 26.4097 | 307.987 | 51.341 | 67.41 | 46.231 | 81.855
| 26.4167 | 307.555 | 51.31 | 67.373 | 46.2 | 81.808
| 26.4236 | 307.759 | 51.284 | 67.342 | 46.175 | 81.773
| 26.4306 | 307.131 | 51.263 | 67.311 | 46.159 | 81.736
| 26.4375 | 306.548 | 51.191 | 67.254 | 46.105 | 81.654
| 26.4444 | 310.453 | 51.357 | 67.368 | 46.233 | 81.808
| 26.4514 | 310.665 | 51.424 | 67.418 | 46.289 | 81.886
| 26.4583 | 310.424 | 51.495 | 67.478 | 46.342 | 81.97
| 26.4653 | 310.5 | 51.512 | 67.503 | 46.349 | 82.011
| 26.4722 | 309.677 | 51.517 | 67.513 | 46.349 | 82.025
| 26.4792 | 309.842 | 51.494 | 67.509 | 46.336 | 82.026
| 26.4861 | 310.333 | 51.502 | 67.521 | 46.343 | 82.041
| 26.4931 | 310.311 | 51.52 | 67.54 | 46.35 | 82.069
| 26.5 | 309.758 | 51.536 | 67.56 | 46.372 | 82.101
| 26.5069 | 310.06 | 51.549 | 67.573 | 46.372 | 82.121
| 26.5139 | 310.847 | 51.556 | 67.589 | 46.379 | 82.14
| 26.5208 | 310.779 | 51.574 | 67.607 | 46.388 | 82.174
| 26.5278 | 311.443 | 51.631 | 67.657 | 46.435 | 82.239
| 26.5347 | 308.785 | 51.575 | 67.629 | 46.393 | 82.204
| 26.5417 | 309.403 | 51.538 | 67.599 | 46.358 | 82.17
| 26.5486 | 310.949 | 51.548 | 67.612 | 46.365 | 82.184
| 26.5556 | 305.298 | 51.379 | 67.493 | 46.246 | 82.015
| 26.5625 | 307.941 | 51.371 | 67.46 | 46.227 | 81.987
| 26.5694 | 311.264 | 51.466 | 67.521 | 46.3 | 82.064
| 26.5764 | 311.188 | 51.506 | 67.559 | 46.336 | 82.117
| 26.5833 | 310.518 | 51.531 | 67.576 | 46.35 | 82.145
| 26.5903 | 311.571 | 51.604 | 67.637 | 46.407 | 82.232
| 26.5972 | 311.444 | 51.658 | 67.688 | 46.451 | 82.296
| 26.6042 | 307.745 | 51.552 | 67.627 | 46.372 | 82.216
| 26.6111 | 308.008 | 51.456 | 67.553 | 46.294 | 82.121
| 26.6181 | 307.595 | 51.354 | 67.467 | 46.203 | 82.004
| 26.625 | 307.295 | 51.315 | 67.422 | 46.176 | 81.945
| 26.6319 | 307.664 | 51.265 | 67.368 | 46.139 | 81.871
| 26.6389 | 308.221 | 51.255 | 67.344 | 46.127 | 81.831
| 26.6458 | 307.92 | 51.254 | 67.328 | 46.128 | 81.819
| 26.6528 | 307.131 | 51.23 | 67.299 | 46.109 | 81.776
| 26.6597 | 306.621 | 51.19 | 67.253 | 46.078 | 81.717
| 26.6667 | 307.903 | 51.189 | 67.237 | 46.068 | 81.697
| 26.6736 | 308.696 | 51.198 | 67.229 | 46.078 | 81.692
| 26.6806 | 307.642 | 51.197 | 67.223 | 46.077 | 81.679
| 26.6875 | 307.487 | 51.205 | 67.214 | 46.078 | 81.677
| 26.6944 | 308.922 | 51.222 | 67.225 | 46.09 | 81.693
| 26.7014 | 309.268 | 51.25 | 67.243 | 46.111 | 81.721
| 26.7083 | 309.038 | 51.247 | 67.235 | 46.11 | 81.718
| 26.7153 | 308.363 | 51.243 | 67.233 | 46.113 | 81.723
| 26.7222 | 308.097 | 51.224 | 67.212 | 46.087 | 81.695
| 26.7292 | 306.727 | 51.163 | 67.164 | 46.04 | 81.63
| 26.7361 | 306.791 | 51.098 | 67.099 | 45.988 | 81.554
| 26.7431 | 317.747 | 51.375 | 67.279 | 46.186 | 81.811
| 26.75 | 308.782 | 51.347 | 67.293 | 46.193 | 81.814
| 26.7569 | 310.18 | 51.339 | 67.291 | 46.172 | 81.812
| 26.7639 | 311.044 | 51.393 | 67.339 | 46.212 | 81.884
| 26.7708 | 310.885 | 51.447 | 67.391 | 46.261 | 81.961
| 26.7778 | 311.436 | 51.499 | 67.444 | 46.302 | 82.042
| 26.7847 | 311.575 | 51.541 | 67.49 | 46.33 | 82.101
| 26.7917 | 309.926 | 51.549 | 67.523 | 46.345 | 82.136
| 26.7986 | 310.976 | 51.55 | 67.536 | 46.342 | 82.167
| 26.8056 | 311.343 | 51.572 | 67.569 | 46.364 | 82.208
| 26.8125 | 312.018 | 51.606 | 67.606 | 46.378 | 82.252
| 26.8194 | 308.328 | 51.522 | 67.571 | 46.331 | 82.196
| 26.8264 | 308.48 | 51.435 | 67.498 | 46.251 | 82.102
| 26.8333 | 308.515 | 51.389 | 67.462 | 46.22 | 82.052
| 26.8403 | 309.051 | 51.4 | 67.463 | 46.231 | 82.05
| 26.8472 | 309.215 | 51.411 | 67.467 | 46.238 | 82.053
| 26.8542 | 310.165 | 51.467 | 67.513 | 46.286 | 82.103
| 26.8611 | 310.343 | 51.506 | 67.547 | 46.317 | 82.152
| 26.8681 | 310.036 | 51.531 | 67.578 | 46.343 | 82.19
| 26.875 | 309.955 | 51.529 | 67.588 | 46.341 | 82.2
| 26.8819 | 311.376 | 51.566 | 67.62 | 46.366 | 82.245
| 26.8889 | 310.981 | 51.599 | 67.657 | 46.395 | 82.295
| 26.8958 | 307.732 | 51.478 | 67.58 | 46.302 | 82.18
| 26.9028 | 308.868 | 51.418 | 67.526 | 46.244 | 82.107
| 26.9097 | 304.766 | 51.314 | 67.455 | 46.179 | 81.995
| 26.9167 | 310.192 | 51.376 | 67.475 | 46.214 | 82.025
| 26.9236 | 311.209 | 51.486 | 67.564 | 46.311 | 82.138
| 26.9306 | 312.948 | 51.613 | 67.664 | 46.408 | 82.275
| 26.9375 | 313.144 | 51.759 | 67.794 | 46.529 | 82.453
| 26.9444 | 312.333 | 51.789 | 67.847 | 46.559 | 82.531
| 26.9514 | 312.322 | 51.805 | 67.873 | 46.565 | 82.574
| 26.9583 | 312.698 | 51.862 | 67.924 | 46.607 | 82.66
| 26.9653 | 312.785 | 51.884 | 67.964 | 46.632 | 82.716
| 26.9722 | 314.059 | 51.978 | 68.044 | 46.703 | 82.842
| 26.9792 | 308.668 | 51.828 | 67.962 | 46.594 | 82.724
| 26.9861 | 308.706 | 51.647 | 67.819 | 46.444 | 82.54
| 26.9931 | 310.066 | 51.6 | 67.771 | 46.409 | 82.479
| 27 | 310.396 | 51.621 | 67.773 | 46.428 | 82.479
| 27.0069 | 308.033 | 51.611 | 67.766 | 46.433 | 82.463
| 27.0139 | 308.955 | 51.522 | 67.683 | 46.361 | 82.357
| 27.0208 | 308.315 | 51.499 | 67.651 | 46.337 | 82.309
| 27.0278 | 308.573 | 51.488 | 67.631 | 46.328 | 82.284
| 27.0347 | 308.415 | 51.472 | 67.6 | 46.318 | 82.247
| 27.0417 | 309.063 | 51.383 | 67.52 | 46.248 | 82.142
| 27.0486 | 308.531 | 51.406 | 67.524 | 46.269 | 82.143
| 27.0556 | 308.022 | 51.379 | 67.488 | 46.241 | 82.091
| 27.0625 | 308.057 | 51.382 | 67.477 | 46.249 | 82.079
| 27.0694 | 308.977 | 51.402 | 67.472 | 46.254 | 82.081
| 27.0764 | 309.167 | 51.445 | 67.504 | 46.293 | 82.12
| 27.0833 | 309.211 | 51.44 | 67.497 | 46.292 | 82.114
| 27.0903 | 308.762 | 51.452 | 67.498 | 46.299 | 82.115
| 27.0972 | 308.468 | 51.454 | 67.498 | 46.298 | 82.122
| 27.1042 | 309.646 | 51.481 | 67.516 | 46.323 | 82.149
| 27.1111 | 310.394 | 51.52 | 67.545 | 46.35 | 82.19
| 27.1181 | 310.245 | 51.528 | 67.558 | 46.357 | 82.202
| 27.125 | 309.366 | 51.522 | 67.554 | 46.354 | 82.204
| 27.1319 | 309.803 | 51.527 | 67.562 | 46.356 | 82.212
| 27.1389 | 309.029 | 51.523 | 67.564 | 46.364 | 82.213
| 27.1458 | 309.784 | 51.51 | 67.556 | 46.343 | 82.199
| 27.1528 | 310.61 | 51.566 | 67.593 | 46.384 | 82.25
| 27.1597 | 311.007 | 51.603 | 67.627 | 46.418 | 82.305
| 27.1667 | 310.912 | 51.636 | 67.663 | 46.445 | 82.351
| 27.1736 | 311.376 | 51.653 | 67.685 | 46.458 | 82.383
| 27.1806 | 310.367 | 51.683 | 67.722 | 46.485 | 82.425
| 27.1875 | 310.279 | 51.675 | 67.73 | 46.476 | 82.434
| 27.1944 | 310.152 | 51.676 | 67.732 | 46.478 | 82.441
| 27.2014 | 310.495 | 51.654 | 67.722 | 46.46 | 82.425
| 27.2083 | 309.88 | 51.623 | 67.708 | 46.435 | 82.403
| 27.2153 | 309.319 | 51.613 | 67.707 | 46.427 | 82.395
| 27.2222 | 308.715 | 51.567 | 67.67 | 46.393 | 82.349
| 27.2292 | 307.488 | 51.522 | 67.632 | 46.353 | 82.293
| 27.2361 | 307.149 | 51.415 | 67.546 | 46.272 | 82.175
| 27.2431 | 309 | 51.493 | 67.586 | 46.328 | 82.229
| 27.25 | 308.694 | 51.474 | 67.567 | 46.32 | 82.204
| 27.2569 | 309.641 | 51.47 | 67.56 | 46.309 | 82.187
| 27.2639 | 308.311 | 51.433 | 67.529 | 46.284 | 82.142
| 27.2708 | 308.252 | 51.404 | 67.5 | 46.259 | 82.101
| 27.2778 | 307.19 | 51.34 | 67.441 | 46.2 | 82.019
| 27.2847 | 309.211 | 51.243 | 67.352 | 46.127 | 81.901
| 27.2917 | 309.212 | 51.367 | 67.422 | 46.222 | 82
| 27.2986 | 309.648 | 51.458 | 67.493 | 46.297 | 82.092
| 27.3056 | 309.105 | 51.481 | 67.509 | 46.309 | 82.112
| 27.3125 | 308.211 | 51.443 | 67.491 | 46.283 | 82.087
| 27.3194 | 307.922 | 51.35 | 67.418 | 46.206 | 81.998
| 27.3264 | 309.887 | 51.465 | 67.495 | 46.29 | 82.102
| 27.3333 | 310.794 | 51.605 | 67.603 | 46.395 | 82.245
| 27.3403 | 311.785 | 51.666 | 67.661 | 46.446 | 82.34
| 27.3472 | 310.554 | 51.687 | 67.696 | 46.465 | 82.385
| 27.3542 | 310.762 | 51.707 | 67.723 | 46.475 | 82.425
| 27.3611 | 311.044 | 51.715 | 67.749 | 46.481 | 82.461
| 27.3681 | 310.419 | 51.697 | 67.75 | 46.464 | 82.467
| 27.375 | 309.984 | 51.676 | 67.739 | 46.446 | 82.449
| 27.3819 | 309.903 | 51.638 | 67.72 | 46.423 | 82.422
| 27.3889 | 309.663 | 51.629 | 67.716 | 46.413 | 82.42
| 27.3958 | 309.999 | 51.611 | 67.705 | 46.396 | 82.396
| 27.4028 | 309.934 | 51.598 | 67.692 | 46.38 | 82.376
| 27.4097 | 309.391 | 51.581 | 67.675 | 46.37 | 82.354
| 27.4167 | 309.325 | 51.576 | 67.677 | 46.369 | 82.353
| 27.4236 | 308.178 | 51.522 | 67.634 | 46.324 | 82.298
| 27.4306 | 306.085 | 51.454 | 67.571 | 46.263 | 82.21
| 27.4375 | 310.635 | 51.456 | 67.554 | 46.254 | 82.185
| 27.4444 | 310.98 | 51.551 | 67.622 | 46.335 | 82.281
| 27.4514 | 310.851 | 51.616 | 67.673 | 46.392 | 82.358
| 27.4583 | 310.477 | 51.635 | 67.689 | 46.401 | 82.382
| 27.4653 | 310.127 | 51.625 | 67.687 | 46.387 | 82.388
| 27.4722 | 309.258 | 51.597 | 67.674 | 46.365 | 82.363
| 27.4792 | 309.216 | 51.568 | 67.653 | 46.347 | 82.343
| 27.4861 | 309.15 | 51.544 | 67.632 | 46.32 | 82.308
| 27.4931 | 310.218 | 51.541 | 67.629 | 46.319 | 82.312
| 27.5 | 309.536 | 51.54 | 67.628 | 46.312 | 82.309
| 27.5069 | 308.877 | 51.534 | 67.614 | 46.3 | 82.304
| 27.5139 | 308.804 | 51.5 | 67.588 | 46.274 | 82.267
| 27.5208 | 309.538 | 51.501 | 67.578 | 46.265 | 82.269
| 27.5278 | 311.439 | 51.559 | 67.613 | 46.31 | 82.329
| 27.5347 | 309.044 | 51.478 | 67.562 | 46.253 | 82.251
| 27.5417 | 309.617 | 51.482 | 67.554 | 46.251 | 82.249
| 27.5486 | 309.435 | 51.456 | 67.538 | 46.232 | 82.222
| 27.5556 | 309.411 | 51.451 | 67.52 | 46.219 | 82.205
| 27.5625 | 309.031 | 51.455 | 67.516 | 46.219 | 82.203
| 27.5694 | 308.405 | 51.439 | 67.503 | 46.211 | 82.188
| 27.5764 | 307.611 | 51.36 | 67.435 | 46.146 | 82.104
| 27.5833 | 308.77 | 51.362 | 67.422 | 46.143 | 82.094
| 27.5903 | 308.248 | 51.357 | 67.41 | 46.138 | 82.08
| 27.5972 | 308.918 | 51.336 | 67.383 | 46.112 | 82.044
| 27.6042 | 310.027 | 51.334 | 67.37 | 46.107 | 82.034
| 27.6111 | 309.892 | 51.369 | 67.384 | 46.134 | 82.06
| 27.6181 | 309.415 | 51.386 | 67.4 | 46.148 | 82.086
| 27.625 | 309.961 | 51.384 | 67.392 | 46.141 | 82.084
| 27.6319 | 310.156 | 51.44 | 67.431 | 46.182 | 82.147
| 27.6389 | 308.769 | 51.439 | 67.44 | 46.18 | 82.156
| 27.6458 | 310.273 | 51.413 | 67.421 | 46.156 | 82.135
| 27.6528 | 309.819 | 51.426 | 67.428 | 46.167 | 82.152
| 27.6597 | 309.706 | 51.406 | 67.417 | 46.152 | 82.135
| 27.6667 | 309.117 | 51.389 | 67.399 | 46.129 | 82.121
| 27.6736 | 310.81 | 51.442 | 67.432 | 46.172 | 82.176
| 27.6806 | 310.475 | 51.494 | 67.478 | 46.207 | 82.237
| 27.6875 | 310.6 | 51.492 | 67.479 | 46.202 | 82.25
| 27.6944 | 310.405 | 51.501 | 67.49 | 46.208 | 82.278
| 27.7014 | 309.669 | 51.467 | 67.476 | 46.182 | 82.255
| 27.7083 | 309.845 | 51.437 | 67.452 | 46.156 | 82.226
| 27.7153 | 309.301 | 51.412 | 67.425 | 46.131 | 82.207
| 27.7222 | 309.535 | 51.363 | 67.391 | 46.097 | 82.158
| 27.7292 | 307.457 | 51.312 | 67.342 | 46.048 | 82.095
| 27.7361 | 307.647 | 51.208 | 67.255 | 45.965 | 81.979
| 27.7431 | 307.721 | 51.179 | 67.213 | 45.94 | 81.925
| 27.75 | 307.168 | 51.139 | 67.162 | 45.907 | 81.866
| 27.7569 | 306.689 | 51.103 | 67.116 | 45.877 | 81.807
| 27.7639 | 307.494 | 51.091 | 67.09 | 45.865 | 81.766
| 27.7708 | 308.209 | 51.082 | 67.065 | 45.855 | 81.743
| 27.7778 | 307.616 | 51.087 | 67.057 | 45.86 | 81.731
| 27.7847 | 308.42 | 51.106 | 67.055 | 45.871 | 81.736
| 27.7917 | 307.921 | 51.103 | 67.047 | 45.867 | 81.728
| 27.7986 | 308.142 | 51.092 | 67.032 | 45.856 | 81.708
| 27.8056 | 307.087 | 51.073 | 67.003 | 45.834 | 81.674
| 27.8125 | 308.109 | 51.067 | 66.991 | 45.833 | 81.67
| 27.8194 | 308.561 | 51.107 | 67.013 | 45.857 | 81.702
| 27.8264 | 308.369 | 51.141 | 67.039 | 45.887 | 81.737
| 27.8333 | 309.279 | 51.172 | 67.063 | 45.908 | 81.78
| 27.8403 | 310.426 | 51.227 | 67.104 | 45.946 | 81.841
| 27.8472 | 309.813 | 51.299 | 67.166 | 46.005 | 81.928
| 27.8542 | 310.241 | 51.315 | 67.191 | 46.015 | 81.967
| 27.8611 | 310.768 | 51.345 | 67.226 | 46.035 | 82.012
| 27.8681 | 308.964 | 51.387 | 67.278 | 46.085 | 82.084
| 27.875 | 307.936 | 51.245 | 67.183 | 45.961 | 81.964
| 27.8819 | 308.885 | 51.19 | 67.139 | 45.914 | 81.906
| 27.8889 | 309.723 | 51.209 | 67.151 | 45.928 | 81.923
| 27.8958 | 309.385 | 51.229 | 67.165 | 45.949 | 81.944
| 27.9028 | 309.087 | 51.198 | 67.145 | 45.924 | 81.914
| 27.9097 | 309.41 | 51.204 | 67.146 | 45.927 | 81.92
| 27.9167 | 309.696 | 51.181 | 67.133 | 45.909 | 81.899
| 27.9236 | 309.629 | 51.183 | 67.125 | 45.904 | 81.898
| 27.9306 | 309.829 | 51.219 | 67.15 | 45.931 | 81.933
| 27.9375 | 307.701 | 51.198 | 67.147 | 45.923 | 81.921
| 27.9444 | 309.316 | 51.101 | 67.072 | 45.84 | 81.822
| 27.9514 | 308.863 | 51.096 | 67.057 | 45.836 | 81.808
| 27.9583 | 308.899 | 51.101 | 67.059 | 45.845 | 81.805
| 27.9653 | 308.907 | 51.089 | 67.038 | 45.833 | 81.783
| 27.9722 | 309.203 | 51.114 | 67.056 | 45.848 | 81.806
| 27.9792 | 309.143 | 51.133 | 67.068 | 45.87 | 81.827
| 27.9861 | 310.095 | 51.162 | 67.088 | 45.887 | 81.863
| 27.9931 | 311.103 | 51.215 | 67.132 | 45.924 | 81.917
| 28 | 307.891 | 51.227 | 67.156 | 45.948 | 81.953
| 28.0069 | 308.269 | 51.145 | 67.089 | 45.865 | 81.864
| 28.0139 | 308.531 | 51.103 | 67.063 | 45.836 | 81.824
| 28.0208 | 309.243 | 51.104 | 67.053 | 45.832 | 81.819
| 28.0278 | 311.782 | 51.164 | 67.095 | 45.883 | 81.876
| 28.0347 | 312.832 | 51.322 | 67.213 | 46 | 82.037
| 28.0417 | 311.045 | 51.39 | 67.293 | 46.062 | 82.139
| 28.0486 | 309.85 | 51.362 | 67.29 | 46.045 | 82.144
| 28.0556 | 309.382 | 51.294 | 67.249 | 45.982 | 82.089
| 28.0625 | 309.298 | 51.275 | 67.238 | 45.959 | 82.07
| 28.0694 | 310.566 | 51.293 | 67.254 | 45.977 | 82.095
| 28.0764 | 310.562 | 51.34 | 67.293 | 46.022 | 82.156
| 28.0833 | 310.814 | 51.38 | 67.339 | 46.046 | 82.211
| 28.0903 | 311.18 | 51.384 | 67.354 | 46.052 | 82.228
| 28.0972 | 311.068 | 51.4 | 67.377 | 46.061 | 82.267
| 28.1042 | 311.097 | 51.427 | 67.398 | 46.075 | 82.297
| 28.1111 | 311.602 | 51.437 | 67.419 | 46.09 | 82.328
| 28.1181 | 310.801 | 51.452 | 67.444 | 46.101 | 82.361
| 28.125 | 310.816 | 51.448 | 67.453 | 46.101 | 82.363
| 28.1319 | 311.13 | 51.441 | 67.452 | 46.092 | 82.368
| 28.1389 | 310.7 | 51.446 | 67.467 | 46.097 | 82.384
| 28.1458 | 311.148 | 51.456 | 67.479 | 46.106 | 82.409
| 28.1528 | 311.049 | 51.469 | 67.496 | 46.109 | 82.423
| 28.1597 | 311.026 | 51.445 | 67.489 | 46.094 | 82.416
| 28.1667 | 310.987 | 51.439 | 67.492 | 46.09 | 82.42
| 28.1736 | 310.863 | 51.435 | 67.492 | 46.084 | 82.417
| 28.1806 | 311.401 | 51.451 | 67.51 | 46.101 | 82.44
| 28.1875 | 311.027 | 51.448 | 67.514 | 46.101 | 82.446
| 28.1944 | 311.361 | 51.45 | 67.522 | 46.105 | 82.456
| 28.2014 | 310.834 | 51.448 | 67.517 | 46.098 | 82.447
| 28.2083 | 310.824 | 51.466 | 67.536 | 46.111 | 82.474
| 28.2153 | 310.674 | 51.438 | 67.522 | 46.086 | 82.45
| 28.2222 | 310.527 | 51.427 | 67.516 | 46.079 | 82.446
| 28.2292 | 310.55 | 51.408 | 67.505 | 46.066 | 82.428
| 28.2361 | 310.5 | 51.394 | 67.485 | 46.048 | 82.408
| 28.2431 | 309.131 | 51.371 | 67.472 | 46.031 | 82.386
| 28.25 | 309.632 | 51.356 | 67.458 | 46.022 | 82.364
| 28.2569 | 309.827 | 51.342 | 67.447 | 46.015 | 82.351
| 28.2639 | 311.029 | 51.347 | 67.446 | 46.014 | 82.348
| 28.2708 | 311.085 | 51.382 | 67.467 | 46.038 | 82.369
| 28.2778 | 309.915 | 51.362 | 67.455 | 46.024 | 82.358
| 28.2847 | 309.381 | 51.324 | 67.42 | 45.99 | 82.311
| 28.2917 | 311.078 | 51.36 | 67.442 | 46.012 | 82.343
| 28.2986 | 311.818 | 51.399 | 67.471 | 46.053 | 82.391
| 28.3056 | 311.205 | 51.43 | 67.503 | 46.07 | 82.417
| 28.3125 | 310.474 | 51.425 | 67.496 | 46.072 | 82.43
| 28.3194 | 310.007 | 51.422 | 67.507 | 46.065 | 82.439
| 28.3264 | 310.365 | 51.403 | 67.493 | 46.049 | 82.42
| 28.3333 | 312.778 | 51.484 | 67.554 | 46.109 | 82.504
| 28.3403 | 308.886 | 51.416 | 67.527 | 46.07 | 82.462
| 28.3472 | 309.721 | 51.348 | 67.468 | 46.001 | 82.385
| 28.3542 | 309.391 | 51.311 | 67.427 | 45.974 | 82.332
| 28.3611 | 309.125 | 51.296 | 67.408 | 45.959 | 82.308
| 28.3681 | 308.146 | 51.232 | 67.357 | 45.911 | 82.232
| 28.375 | 308.778 | 51.17 | 67.292 | 45.854 | 82.149
| 28.3819 | 308.391 | 51.148 | 67.261 | 45.838 | 82.103
| 28.3889 | 308.136 | 51.104 | 67.216 | 45.806 | 82.043
| 28.3958 | 307.068 | 51.079 | 67.175 | 45.786 | 81.993
| 28.4028 | 307 | 51.017 | 67.113 | 45.725 | 81.912
| 28.4097 | 310.375 | 51.03 | 67.085 | 45.726 | 81.893
| 28.4167 | 310.027 | 51.15 | 67.178 | 45.829 | 82.006
| 28.4236 | 309.815 | 51.208 | 67.222 | 45.876 | 82.069
| 28.4306 | 310.514 | 51.239 | 67.246 | 45.902 | 82.109
| 28.4375 | 309.883 | 51.229 | 67.246 | 45.886 | 82.108
| 28.4444 | 308.692 | 51.183 | 67.213 | 45.851 | 82.066
| 28.4514 | 308.41 | 51.121 | 67.151 | 45.798 | 81.998
| 28.4583 | 307.798 | 51.08 | 67.116 | 45.763 | 81.951
| 28.4653 | 308.287 | 51.042 | 67.074 | 45.729 | 81.893
| 28.4722 | 306.979 | 50.994 | 67.023 | 45.684 | 81.831
| 28.4792 | 308.193 | 50.975 | 66.99 | 45.669 | 81.789
| 28.4861 | 307.999 | 50.93 | 66.956 | 45.643 | 81.74
| 28.4931 | 307.989 | 50.955 | 66.948 | 45.65 | 81.746
| 28.5 | 308.747 | 50.942 | 66.923 | 45.645 | 81.721
| 28.5069 | 307.69 | 50.944 | 66.916 | 45.639 | 81.709
| 28.5139 | 307.571 | 50.922 | 66.887 | 45.624 | 81.677
| 28.5208 | 308.955 | 50.939 | 66.889 | 45.628 | 81.692
| 28.5278 | 309.168 | 50.966 | 66.905 | 45.653 | 81.711
| 28.5347 | 309.686 | 50.995 | 66.913 | 45.667 | 81.738
| 28.5417 | 309.607 | 51.03 | 66.945 | 45.695 | 81.779
| 28.5486 | 310.19 | 51.061 | 66.967 | 45.717 | 81.819
| 28.5556 | 309.979 | 51.075 | 66.978 | 45.727 | 81.845
| 28.5625 | 309.627 | 51.073 | 66.981 | 45.724 | 81.854
| 28.5694 | 309.276 | 51.056 | 66.969 | 45.708 | 81.847
| 28.5764 | 309.228 | 51.043 | 66.962 | 45.689 | 81.837
| 28.5833 | 309.179 | 51.038 | 66.951 | 45.686 | 81.836
| 28.5903 | 310.124 | 51.075 | 66.971 | 45.708 | 81.872
| 28.5972 | 310.045 | 51.108 | 67.002 | 45.727 | 81.922
| 28.6042 | 310.373 | 51.133 | 67.024 | 45.751 | 81.96
| 28.6111 | 310.744 | 51.163 | 67.056 | 45.772 | 82.008
| 28.6181 | 311.007 | 51.174 | 67.07 | 45.777 | 82.038
| 28.625 | 310.618 | 51.197 | 67.086 | 45.792 | 82.074
| 28.6319 | 310.468 | 51.21 | 67.104 | 45.8 | 82.108
| 28.6389 | 311.482 | 51.229 | 67.132 | 45.815 | 82.151
| 28.7292 | 306.257 | 51.068 | 67.053 | 45.67 | 82.11
| 28.7361 | 310.2 | 51.041 | 67.016 | 45.64 | 82.068
| 28.7431 | 309.227 | 51.025 | 66.993 | 45.624 | 82.035
| 28.75 | 309.585 | 50.987 | 66.951 | 45.589 | 81.993
| 28.7569 | 309.108 | 50.951 | 66.914 | 45.561 | 81.942
| 28.7639 | 308.476 | 50.914 | 66.874 | 45.529 | 81.891
| 28.7708 | 309.469 | 50.902 | 66.848 | 45.516 | 81.862
| 28.7778 | 310.717 | 50.931 | 66.852 | 45.538 | 81.873
| 28.7847 | 310.32 | 50.992 | 66.897 | 45.588 | 81.934
| 28.7917 | 310.752 | 51.022 | 66.913 | 45.608 | 81.968
| 28.7986 | 310.668 | 51.049 | 66.939 | 45.628 | 82.005
| 28.8056 | 310.674 | 51.071 | 66.956 | 45.638 | 82.032
| 28.8125 | 311.675 | 51.106 | 66.983 | 45.668 | 82.077
| 28.8194 | 312.065 | 51.126 | 67.013 | 45.69 | 82.115
| 28.8264 | 311.495 | 51.165 | 67.045 | 45.713 | 82.172
| 28.8333 | 311.535 | 51.187 | 67.069 | 45.728 | 82.207
| 28.8403 | 312.349 | 51.212 | 67.102 | 45.746 | 82.253
| 28.8472 | 312.228 | 51.243 | 67.136 | 45.77 | 82.307
| 28.8542 | 309.307 | 51.237 | 67.151 | 45.772 | 82.314
| 28.8611 | 310.084 | 51.09 | 67.042 | 45.65 | 82.172
| 28.8681 | 310.72 | 51.088 | 67.032 | 45.639 | 82.165
| 28.875 | 311.334 | 51.097 | 67.04 | 45.651 | 82.171
| 28.8819 | 311.103 | 51.121 | 67.059 | 45.67 | 82.199
| 28.8889 | 311.842 | 51.134 | 67.07 | 45.677 | 82.218
| 28.8958 | 311.291 | 51.171 | 67.103 | 45.707 | 82.257
| 28.9028 | 312.564 | 51.19 | 67.123 | 45.724 | 82.287
| 28.9097 | 312.28 | 51.237 | 67.163 | 45.754 | 82.344
| 28.9167 | 312.081 | 51.27 | 67.197 | 45.784 | 82.394
| 28.9236 | 309.738 | 51.123 | 67.109 | 45.674 | 82.271
| 28.9306 | 308.94 | 51.033 | 67.034 | 45.593 | 82.168
| 28.9375 | 308.965 | 50.989 | 66.984 | 45.56 | 82.102
| 28.9444 | 306.663 | 50.917 | 66.929 | 45.509 | 82.016
| 28.9514 | 306.927 | 50.774 | 66.799 | 45.384 | 81.838
| 28.9583 | 308.248 | 50.723 | 66.731 | 45.338 | 81.752
| 28.9653 | 310.51 | 50.71 | 66.693 | 45.332 | 81.705
| 28.9722 | 310.017 | 50.815 | 66.76 | 45.419 | 81.787
| 28.9792 | 310.342 | 50.878 | 66.798 | 45.467 | 81.838
| 28.9861 | 311.416 | 50.925 | 66.821 | 45.496 | 81.887
| 28.9931 | 311.664 | 51.002 | 66.888 | 45.559 | 81.978
| 29 | 311.952 | 51.052 | 66.932 | 45.593 | 82.04
| 29.0069 | 311.672 | 51.094 | 66.972 | 45.628 | 82.104
| 29.0139 | 312.139 | 51.139 | 67.014 | 45.662 | 82.169
| 29.0208 | 312.988 | 51.188 | 67.071 | 45.696 | 82.237
| 29.0278 | 309.912 | 51.048 | 66.988 | 45.594 | 82.118
| 29.0347 | 309.534 | 50.988 | 66.941 | 45.537 | 82.063
| 29.0417 | 310.264 | 50.965 | 66.916 | 45.519 | 82.024
| 29.0486 | 309.543 | 50.95 | 66.903 | 45.51 | 82.004
| 29.0556 | 309.004 | 50.916 | 66.868 | 45.484 | 81.957
| 29.0625 | 309.529 | 50.884 | 66.84 | 45.456 | 81.919
| 29.0694 | 309.163 | 50.875 | 66.826 | 45.445 | 81.895
| 29.0764 | 309.777 | 50.875 | 66.817 | 45.445 | 81.889
| 29.0833 | 309.384 | 50.882 | 66.814 | 45.456 | 81.887
| 29.0903 | 309.509 | 50.88 | 66.811 | 45.447 | 81.873
| 29.0972 | 309.963 | 50.89 | 66.811 | 45.452 | 81.878
| 29.1042 | 310.121 | 50.902 | 66.828 | 45.465 | 81.893
| 29.1111 | 311.25 | 50.916 | 66.831 | 45.474 | 81.901
| 29.1181 | 310.801 | 50.982 | 66.883 | 45.527 | 81.974
| 29.125 | 310.687 | 51.004 | 66.904 | 45.539 | 82.007
| 29.1319 | 310.895 | 51.025 | 66.927 | 45.557 | 82.04
| 29.1389 | 311.587 | 51.049 | 66.961 | 45.574 | 82.082
| 29.1458 | 311.761 | 51.075 | 66.984 | 45.591 | 82.115
| 29.1528 | 311.187 | 51.078 | 66.999 | 45.595 | 82.131
| 29.1597 | 311.299 | 51.096 | 67.022 | 45.614 | 82.163
| 29.1667 | 311.146 | 51.108 | 67.041 | 45.622 | 82.189
| 29.1736 | 312.28 | 51.132 | 67.072 | 45.64 | 82.232
| 29.1806 | 311.554 | 51.145 | 67.094 | 45.651 | 82.262
| 29.1875 | 312.048 | 51.157 | 67.106 | 45.654 | 82.284
| 29.1944 | 311.938 | 51.16 | 67.119 | 45.655 | 82.295
| 29.2014 | 311.869 | 51.173 | 67.139 | 45.669 | 82.324
| 29.2083 | 312.157 | 51.191 | 67.161 | 45.681 | 82.355
| 29.2153 | 312.444 | 51.201 | 67.173 | 45.684 | 82.374
| 29.2222 | 311.59 | 51.184 | 67.177 | 45.677 | 82.375
| 29.2292 | 312.168 | 51.177 | 67.176 | 45.669 | 82.378
| 29.2361 | 312.925 | 51.194 | 67.194 | 45.685 | 82.398
| 29.2431 | 311.906 | 51.213 | 67.215 | 45.696 | 82.423
| 29.25 | 311.49 | 51.196 | 67.217 | 45.683 | 82.419
| 29.2569 | 311.294 | 51.185 | 67.212 | 45.677 | 82.415
| 29.2639 | 311.652 | 51.175 | 67.207 | 45.664 | 82.408
| 29.2708 | 311.169 | 51.147 | 67.193 | 45.642 | 82.387
| 29.2778 | 310.256 | 51.11 | 67.168 | 45.618 | 82.351
| 29.2847 | 309.029 | 51.02 | 67.093 | 45.543 | 82.248
| 29.2917 | 309.089 | 50.958 | 67.035 | 45.495 | 82.164
| 29.2986 | 309.557 | 50.903 | 66.981 | 45.444 | 82.088
| 29.3056 | 308.761 | 50.861 | 66.934 | 45.414 | 82.017
| 29.3125 | 307.969 | 50.795 | 66.871 | 45.366 | 81.927
| 29.3194 | 307.872 | 50.763 | 66.821 | 45.335 | 81.856
| 29.3264 | 306.988 | 50.686 | 66.75 | 45.274 | 81.754
| 29.3333 | 307.524 | 50.635 | 66.686 | 45.227 | 81.664
| 29.3403 | 307.443 | 50.613 | 66.645 | 45.215 | 81.612
| 29.3472 | 309.487 | 50.706 | 66.694 | 45.284 | 81.679
| 29.3542 | 310.198 | 50.746 | 66.711 | 45.309 | 81.709
| 29.3611 | 309.342 | 50.753 | 66.714 | 45.318 | 81.717
| 29.3681 | 309.048 | 50.718 | 66.687 | 45.29 | 81.678
| 29.375 | 308.441 | 50.708 | 66.667 | 45.278 | 81.657
| 29.3819 | 308.434 | 50.678 | 66.637 | 45.25 | 81.615
| 29.3889 | 307.981 | 50.649 | 66.602 | 45.232 | 81.58
| 29.3958 | 308.576 | 50.612 | 66.564 | 45.199 | 81.523
| 29.4028 | 306.779 | 50.55 | 66.509 | 45.146 | 81.442
| 29.4097 | 306.349 | 50.467 | 66.434 | 45.085 | 81.341
| 29.4167 | 310.013 | 50.608 | 66.516 | 45.186 | 81.455
| 29.4236 | 310.057 | 50.653 | 66.547 | 45.234 | 81.5
| 29.4306 | 308.814 | 50.656 | 66.55 | 45.229 | 81.505
| 29.4375 | 308.979 | 50.648 | 66.536 | 45.214 | 81.495
| 29.4444 | 307.029 | 50.582 | 66.489 | 45.171 | 81.434
| 29.4514 | 306.521 | 50.476 | 66.397 | 45.085 | 81.314
| 29.4583 | 309.763 | 50.543 | 66.426 | 45.127 | 81.359
| 29.4653 | 309.598 | 50.596 | 66.459 | 45.171 | 81.401
| 29.4722 | 309.1 | 50.626 | 66.479 | 45.191 | 81.436
| 29.4792 | 309.481 | 50.664 | 66.509 | 45.223 | 81.483
| 29.4861 | 309.273 | 50.646 | 66.5 | 45.207 | 81.47
| 29.4931 | 308.159 | 50.586 | 66.456 | 45.159 | 81.421
| 29.5 | 308.499 | 50.561 | 66.433 | 45.134 | 81.377
| 29.5069 | 308.384 | 50.54 | 66.411 | 45.121 | 81.35
| 29.5139 | 308.13 | 50.527 | 66.395 | 45.113 | 81.329
| 29.5208 | 308.222 | 50.528 | 66.386 | 45.107 | 81.319
| 29.5278 | 309.085 | 50.555 | 66.395 | 45.134 | 81.339
| 29.5347 | 309.408 | 50.592 | 66.425 | 45.16 | 81.375
| 29.5417 | 309.007 | 50.611 | 66.442 | 45.175 | 81.403
| 29.5486 | 309.281 | 50.59 | 66.429 | 45.158 | 81.388
| 29.5556 | 309.71 | 50.605 | 66.437 | 45.167 | 81.402
| 29.5625 | 309.726 | 50.62 | 66.456 | 45.18 | 81.428
| 29.5694 | 309.71 | 50.636 | 66.464 | 45.189 | 81.452
| 29.5764 | 311.155 | 50.707 | 66.521 | 45.243 | 81.532
| 29.5833 | 311.532 | 50.769 | 66.58 | 45.29 | 81.612
| 29.5903 | 310.65 | 50.799 | 66.617 | 45.316 | 81.669
| 29.5972 | 311.637 | 50.836 | 66.653 | 45.342 | 81.727
| 29.6042 | 312.695 | 50.881 | 66.701 | 45.373 | 81.795
| 29.6111 | 312.267 | 50.908 | 66.738 | 45.396 | 81.846
| 29.6181 | 313.057 | 50.97 | 66.8 | 45.444 | 81.943
| 29.625 | 312.392 | 51.003 | 66.844 | 45.468 | 81.999
| 29.6319 | 312.677 | 51.022 | 66.875 | 45.476 | 82.045
| 29.6389 | 308.884 | 50.936 | 66.844 | 45.422 | 81.99
| 29.6458 | 309.303 | 50.836 | 66.762 | 45.327 | 81.89
| 29.6528 | 309.143 | 50.778 | 66.714 | 45.284 | 81.821
| 29.6597 | 308.527 | 50.701 | 66.652 | 45.229 | 81.733
| 29.6667 | 308.691 | 50.653 | 66.607 | 45.19 | 81.665
| 29.6736 | 308.683 | 50.628 | 66.567 | 45.166 | 81.618
| 29.6806 | 308.841 | 50.602 | 66.544 | 45.155 | 81.571
| 29.6875 | 309.195 | 50.574 | 66.507 | 45.132 | 81.525
| 29.6944 | 308.061 | 50.552 | 66.471 | 45.108 | 81.477
| 29.7014 | 308.071 | 50.497 | 66.418 | 45.06 | 81.4
| 29.7083 | 307.916 | 50.467 | 66.381 | 45.037 | 81.353
| 29.7153 | 307.643 | 50.411 | 66.325 | 44.999 | 81.269
| 29.7222 | 307.398 | 50.38 | 66.278 | 44.97 | 81.212
| 29.7292 | 306.853 | 50.33 | 66.223 | 44.931 | 81.141
| 29.7361 | 306.279 | 50.337 | 66.209 | 44.931 | 81.12
| 29.7431 | 308.934 | 50.401 | 66.239 | 44.983 | 81.165
| 29.75 | 308.871 | 50.423 | 66.25 | 45.002 | 81.183
| 29.7569 | 308.971 | 50.431 | 66.249 | 45.004 | 81.186
| 29.7639 | 308.8 | 50.442 | 66.258 | 45.018 | 81.201
| 29.7708 | 309.558 | 50.458 | 66.265 | 45.029 | 81.216
| 29.7778 | 308.876 | 50.457 | 66.263 | 45.031 | 81.214
| 29.7847 | 308.426 | 50.445 | 66.253 | 45.02 | 81.202
| 29.7917 | 309.446 | 50.451 | 66.254 | 45.023 | 81.21
| 29.7986 | 311.481 | 50.551 | 66.326 | 45.101 | 81.313
| 29.8056 | 311.592 | 50.659 | 66.412 | 45.188 | 81.44
| 29.8125 | 311.505 | 50.738 | 66.491 | 45.248 | 81.544
| 29.8194 | 312.451 | 50.786 | 66.546 | 45.281 | 81.622
| 29.8264 | 312.784 | 50.848 | 66.612 | 45.334 | 81.722
| 29.8333 | 309.299 | 50.711 | 66.541 | 45.232 | 81.621
| 29.8403 | 309.675 | 50.647 | 66.488 | 45.179 | 81.548
| 29.8472 | 309.497 | 50.616 | 66.465 | 45.148 | 81.518
| 29.8542 | 309.919 | 50.62 | 66.468 | 45.156 | 81.526
| 29.8611 | 310.145 | 50.63 | 66.476 | 45.164 | 81.533
| 29.8681 | 310.953 | 50.665 | 66.5 | 45.196 | 81.574
| 29.875 | 310.534 | 50.7 | 66.534 | 45.225 | 81.618
| 29.8819 | 311.047 | 50.72 | 66.556 | 45.243 | 81.648
| 29.8889 | 310.953 | 50.745 | 66.587 | 45.261 | 81.689
| 29.8958 | 311.736 | 50.772 | 66.617 | 45.285 | 81.726
| 29.9028 | 311.904 | 50.801 | 66.646 | 45.307 | 81.768
| 29.9097 | 311.246 | 50.81 | 66.67 | 45.316 | 81.805
| 29.9167 | 311.441 | 50.803 | 66.669 | 45.308 | 81.804
| 29.9236 | 312.57 | 50.808 | 66.683 | 45.315 | 81.825
| 29.9306 | 307.711 | 50.749 | 66.654 | 45.27 | 81.775
| 29.9375 | 308.65 | 50.631 | 66.556 | 45.176 | 81.648
| 29.9444 | 308.69 | 50.559 | 66.497 | 45.122 | 81.562
| 29.9514 | 307.663 | 50.466 | 66.41 | 45.049 | 81.436
| 29.9583 | 308.508 | 50.427 | 66.356 | 45.014 | 81.361
| 29.9653 | 307.994 | 50.387 | 66.315 | 44.992 | 81.304
| 29.9722 | 309.154 | 50.419 | 66.325 | 45.017 | 81.308
| 29.9792 | 309.992 | 50.466 | 66.339 | 45.052 | 81.334
| 29.9861 | 309.418 | 50.474 | 66.344 | 45.066 | 81.339
| 29.9931 | 310.609 | 50.524 | 66.373 | 45.096 | 81.381
| 30 | 309.994 | 50.556 | 66.399 | 45.125 | 81.416
| 30.0069 | 309.794 | 50.56 | 66.406 | 45.133 | 81.421
| 30.0139 | 309.871 | 50.575 | 66.42 | 45.139 | 81.439
| 30.0208 | 310.165 | 50.596 | 66.44 | 45.155 | 81.465
| 30.0278 | 311.138 | 50.569 | 66.42 | 45.137 | 81.445
| 30.0347 | 309.218 | 50.578 | 66.435 | 45.143 | 81.458
| 30.0417 | 309.922 | 50.566 | 66.421 | 45.136 | 81.443
| 30.0486 | 308.335 | 50.528 | 66.395 | 45.102 | 81.397
| 30.0556 | 308.966 | 50.501 | 66.373 | 45.089 | 81.371
| 30.0625 | 308.999 | 50.482 | 66.346 | 45.069 | 81.332
| 30.0694 | 309.008 | 50.48 | 66.341 | 45.067 | 81.322
| 30.0764 | 309.573 | 50.475 | 66.337 | 45.064 | 81.311
| 30.0833 | 309.381 | 50.474 | 66.333 | 45.061 | 81.303
| 30.0903 | 308.559 | 50.469 | 66.322 | 45.063 | 81.285
| 30.0972 | 308.947 | 50.462 | 66.313 | 45.051 | 81.27
| 30.1042 | 308.415 | 50.44 | 66.29 | 45.034 | 81.236
| 30.1111 | 310.538 | 50.469 | 66.3 | 45.053 | 81.253
| 30.1181 | 310.76 | 50.529 | 66.354 | 45.111 | 81.32
| 30.125 | 310.833 | 50.574 | 66.387 | 45.144 | 81.371
| 30.1319 | 310.924 | 50.62 | 66.428 | 45.179 | 81.426
| 30.1389 | 310.104 | 50.614 | 66.431 | 45.178 | 81.432
| 30.1458 | 310.109 | 50.611 | 66.446 | 45.181 | 81.445
| 30.1528 | 310.621 | 50.59 | 66.43 | 45.155 | 81.43
| 30.1597 | 311.05 | 50.623 | 66.451 | 45.174 | 81.466
| 30.1667 | 310.388 | 50.648 | 66.483 | 45.202 | 81.499
| 30.1736 | 310.225 | 50.66 | 66.497 | 45.216 | 81.522
| 30.1806 | 311.01 | 50.673 | 66.511 | 45.222 | 81.546
| 30.1875 | 310.508 | 50.672 | 66.515 | 45.22 | 81.552
| 30.1944 | 310.231 | 50.672 | 66.524 | 45.225 | 81.565
| 30.2014 | 310.125 | 50.636 | 66.505 | 45.2 | 81.534
| 30.2083 | 309.5 | 50.63 | 66.503 | 45.188 | 81.525
| 30.2153 | 309.641 | 50.617 | 66.492 | 45.189 | 81.512
| 30.2222 | 309.473 | 50.629 | 66.5 | 45.192 | 81.519
| 30.2292 | 310.02 | 50.627 | 66.5 | 45.192 | 81.511
| 30.2361 | 308.61 | 50.59 | 66.481 | 45.164 | 81.485
| 30.2431 | 306.232 | 50.449 | 66.368 | 45.055 | 81.335
| 30.25 | 308.01 | 50.397 | 66.301 | 45.001 | 81.245
| 30.2569 | 307.267 | 50.373 | 66.277 | 44.992 | 81.202
| 30.2639 | 306.534 | 50.334 | 66.231 | 44.962 | 81.139
| 30.2708 | 305.959 | 50.269 | 66.171 | 44.919 | 81.05
| 30.2778 | 307.242 | 50.282 | 66.156 | 44.92 | 81.036
| 30.2847 | 307.026 | 50.255 | 66.121 | 44.901 | 80.989
| 30.2917 | 309.214 | 50.271 | 66.114 | 44.906 | 80.983
| 30.2986 | 308.288 | 50.298 | 66.124 | 44.935 | 80.996
| 30.3056 | 306.601 | 50.229 | 66.059 | 44.874 | 80.912
| 30.3125 | 309.206 | 50.325 | 66.119 | 44.948 | 80.997
| 30.3194 | 307.984 | 50.352 | 66.14 | 44.977 | 81.032
| 30.3264 | 308.749 | 50.355 | 66.135 | 44.966 | 81.025
| 30.3333 | 308.703 | 50.323 | 66.112 | 44.938 | 80.992
| 30.3403 | 308.792 | 50.401 | 66.161 | 45.005 | 81.071
| 30.3472 | 309.125 | 50.415 | 66.181 | 45.018 | 81.087
| 30.3542 | 309.486 | 50.414 | 66.186 | 45.017 | 81.097
| 30.3611 | 308.706 | 50.422 | 66.193 | 45.022 | 81.105
| 30.3681 | 309.394 | 50.421 | 66.191 | 45.015 | 81.105
| 30.375 | 308.379 | 50.409 | 66.186 | 45.013 | 81.1
| 30.3819 | 309.265 | 50.393 | 66.179 | 44.996 | 81.088
| 30.3889 | 309.434 | 50.447 | 66.22 | 45.038 | 81.141
| 30.3958 | 310.865 | 50.482 | 66.246 | 45.065 | 81.188
| 30.4028 | 311.087 | 50.537 | 66.29 | 45.112 | 81.254
| 30.4097 | 311.606 | 50.634 | 66.375 | 45.186 | 81.366
| 30.4167 | 311.026 | 50.673 | 66.428 | 45.224 | 81.436
| 30.4236 | 309.249 | 50.715 | 66.472 | 45.251 | 81.5
| 30.4306 | 308.642 | 50.584 | 66.393 | 45.155 | 81.389
| 30.4375 | 309.209 | 50.534 | 66.357 | 45.109 | 81.342
| 30.4444 | 308.205 | 50.489 | 66.322 | 45.074 | 81.293
| 30.4514 | 307.095 | 50.419 | 66.262 | 45.015 | 81.21
| 30.4583 | 307.541 | 50.357 | 66.2 | 44.966 | 81.126
| 30.4653 | 306.603 | 50.32 | 66.172 | 44.941 | 81.072
| 30.4722 | 310.585 | 50.453 | 66.244 | 45.039 | 81.185
| 30.4792 | 311.017 | 50.511 | 66.3 | 45.094 | 81.243
| 30.4861 | 312.957 | 50.678 | 66.421 | 45.217 | 81.427
| 30.4931 | 313.361 | 50.783 | 66.525 | 45.306 | 81.567
| 30.5 | 313.07 | 50.871 | 66.625 | 45.376 | 81.701
| 30.5069 | 313.519 | 50.928 | 66.69 | 45.409 | 81.795
| 30.5139 | 308.854 | 50.756 | 66.586 | 45.278 | 81.658
| 30.5208 | 309.356 | 50.689 | 66.548 | 45.221 | 81.596
| 30.5278 | 309.929 | 50.656 | 66.517 | 45.192 | 81.562
| 30.5347 | 310.28 | 50.676 | 66.537 | 45.216 | 81.587
| 30.5417 | 308.474 | 50.604 | 66.486 | 45.155 | 81.505
| 30.5486 | 307.813 | 50.522 | 66.417 | 45.092 | 81.412
| 30.5556 | 308.141 | 50.485 | 66.381 | 45.057 | 81.353
| 30.5625 | 308.672 | 50.447 | 66.337 | 45.031 | 81.305
| 30.5694 | 308.062 | 50.407 | 66.292 | 44.996 | 81.24
| 30.5764 | 306.772 | 50.348 | 66.232 | 44.953 | 81.161
| 30.5833 | 306.912 | 50.306 | 66.179 | 44.91 | 81.093
| 30.5903 | 306.32 | 50.257 | 66.125 | 44.873 | 81.018
| 30.5972 | 306.389 | 50.214 | 66.074 | 44.843 | 80.948
| 30.6042 | 307.19 | 50.212 | 66.051 | 44.837 | 80.921
| 30.6111 | 307.09 | 50.192 | 66.017 | 44.818 | 80.874
| 30.6181 | 307.214 | 50.19 | 65.998 | 44.813 | 80.85
| 30.625 | 307.157 | 50.189 | 65.979 | 44.812 | 80.829
| 30.6319 | 308.394 | 50.201 | 65.976 | 44.817 | 80.827
| 30.6389 | 307.071 | 50.197 | 65.964 | 44.814 | 80.818
| 30.6458 | 306.989 | 50.168 | 65.931 | 44.788 | 80.777
| 30.6528 | 307.08 | 50.156 | 65.907 | 44.776 | 80.748
| 30.6597 | 307.039 | 50.133 | 65.881 | 44.758 | 80.713
| 30.6667 | 307.548 | 50.146 | 65.873 | 44.767 | 80.713
| 30.6736 | 307.078 | 50.129 | 65.854 | 44.749 | 80.693
| 30.6806 | 307.205 | 50.131 | 65.85 | 44.745 | 80.678
| 30.6875 | 307.753 | 50.111 | 65.823 | 44.729 | 80.656
| 30.6944 | 306.733 | 50.104 | 65.805 | 44.723 | 80.643
| 30.7014 | 307.202 | 50.087 | 65.779 | 44.702 | 80.611
| 30.7083 | 307.359 | 50.106 | 65.788 | 44.723 | 80.629
| 30.7153 | 306.515 | 50.076 | 65.754 | 44.69 | 80.589
| 30.7222 | 308.241 | 50.186 | 65.833 | 44.776 | 80.702
| 30.7292 | 308.242 | 50.188 | 65.837 | 44.781 | 80.714
| 30.7361 | 309.787 | 50.18 | 65.823 | 44.764 | 80.714
| 30.7431 | 310.776 | 50.313 | 65.931 | 44.871 | 80.857
| 30.75 | 310.041 | 50.334 | 65.961 | 44.894 | 80.903
| 30.7569 | 309.478 | 50.344 | 65.983 | 44.899 | 80.935
| 30.7639 | 309.74 | 50.342 | 65.986 | 44.892 | 80.953
| 30.7708 | 310.404 | 50.365 | 66.01 | 44.907 | 80.983
| 30.7778 | 311.595 | 50.415 | 66.057 | 44.946 | 81.053
| 30.7847 | 311.407 | 50.501 | 66.134 | 45.017 | 81.163
| 30.7917 | 311.932 | 50.565 | 66.205 | 45.069 | 81.267
| 30.7986 | 311.041 | 50.515 | 66.186 | 45.033 | 81.241
| 30.8056 | 310.871 | 50.524 | 66.207 | 45.031 | 81.266
| 30.8125 | 310.236 | 50.53 | 66.22 | 45.033 | 81.29
| 30.8194 | 311.601 | 50.55 | 66.25 | 45.052 | 81.326
| 30.8264 | 311.628 | 50.621 | 66.316 | 45.112 | 81.418
| 30.8333 | 312.371 | 50.671 | 66.373 | 45.154 | 81.492
| 30.8403 | 311.993 | 50.711 | 66.419 | 45.18 | 81.56
| 30.8472 | 309.382 | 50.603 | 66.368 | 45.102 | 81.482
| 30.8542 | 309.738 | 50.546 | 66.323 | 45.047 | 81.425
| 30.8611 | 309.446 | 50.52 | 66.31 | 45.031 | 81.394
| 30.8681 | 311.108 | 50.52 | 66.309 | 45.031 | 81.402
| 30.875 | 309.466 | 50.532 | 66.32 | 45.04 | 81.408
| 30.8819 | 309.895 | 50.511 | 66.299 | 45.022 | 81.384
| 30.8889 | 310.275 | 50.537 | 66.319 | 45.043 | 81.41
| 30.8958 | 312.247 | 50.595 | 66.37 | 45.09 | 81.475
| 30.9028 | 307.942 | 50.468 | 66.292 | 44.995 | 81.367
| 30.9097 | 308.034 | 50.382 | 66.22 | 44.923 | 81.263
| 30.9167 | 308.091 | 50.324 | 66.166 | 44.878 | 81.189
| 30.9236 | 309.019 | 50.299 | 66.127 | 44.85 | 81.142
| 30.9306 | 309.452 | 50.314 | 66.132 | 44.872 | 81.136
| 30.9375 | 309.205 | 50.341 | 66.137 | 44.884 | 81.14
| 30.9444 | 310.189 | 50.352 | 66.139 | 44.894 | 81.144
| 30.9514 | 308.509 | 50.397 | 66.178 | 44.935 | 81.194
| 30.9583 | 308.006 | 50.318 | 66.109 | 44.865 | 81.106
| 30.9653 | 309.377 | 50.297 | 66.083 | 44.842 | 81.074
| 30.9722 | 310.703 | 50.37 | 66.132 | 44.9 | 81.144
| 30.9792 | 311.43 | 50.447 | 66.193 | 44.963 | 81.216
| 30.9861 | 311.807 | 50.503 | 66.246 | 45.01 | 81.288
| 30.9931 | 309.052 | 50.513 | 66.273 | 45.023 | 81.321
| 31 | 308.807 | 50.433 | 66.212 | 44.947 | 81.241
| 31.0069 | 308.884 | 50.38 | 66.172 | 44.909 | 81.192
| 31.0139 | 309.095 | 50.397 | 66.184 | 44.913 | 81.205
| 31.0208 | 308.869 | 50.354 | 66.15 | 44.889 | 81.16
| 31.0278 | 308.917 | 50.346 | 66.135 | 44.88 | 81.138
| 31.0347 | 310.091 | 50.397 | 66.171 | 44.918 | 81.186
| 31.0417 | 311.373 | 50.446 | 66.211 | 44.954 | 81.235
| 31.0486 | 308.797 | 50.423 | 66.203 | 44.939 | 81.219
| 31.0556 | 309.032 | 50.397 | 66.18 | 44.915 | 81.191
| 31.0625 | 309.772 | 50.391 | 66.175 | 44.906 | 81.185
| 31.0694 | 310.278 | 50.405 | 66.184 | 44.921 | 81.197
| 31.0764 | 307.297 | 50.426 | 66.212 | 44.943 | 81.222
| 31.0833 | 308.472 | 50.336 | 66.141 | 44.865 | 81.129
| 31.0903 | 308.789 | 50.316 | 66.118 | 44.847 | 81.102
| 31.0972 | 308.782 | 50.314 | 66.112 | 44.854 | 81.091
| 31.1042 | 308.308 | 50.328 | 66.115 | 44.854 | 81.093
| 31.1111 | 309.994 | 50.34 | 66.118 | 44.862 | 81.097
| 31.1181 | 309.852 | 50.391 | 66.16 | 44.911 | 81.15
| 31.125 | 309.992 | 50.391 | 66.165 | 44.905 | 81.153
| 31.1319 | 309.315 | 50.392 | 66.165 | 44.909 | 81.157
| 31.1389 | 309.181 | 50.356 | 66.145 | 44.879 | 81.123
| 31.1458 | 309.664 | 50.356 | 66.14 | 44.879 | 81.118
| 31.1528 | 310.167 | 50.39 | 66.16 | 44.899 | 81.147
| 31.1597 | 309.962 | 50.407 | 66.185 | 44.925 | 81.174
| 31.1667 | 309.479 | 50.405 | 66.19 | 44.923 | 81.174
| 31.1736 | 309.883 | 50.393 | 66.178 | 44.907 | 81.158
| 31.1806 | 309.151 | 50.384 | 66.17 | 44.897 | 81.151
| 31.1875 | 309.269 | 50.381 | 66.17 | 44.894 | 81.148
| 31.1944 | 310.191 | 50.391 | 66.183 | 44.905 | 81.153
| 31.2014 | 308.983 | 50.366 | 66.164 | 44.884 | 81.129
| 31.2083 | 310.042 | 50.372 | 66.163 | 44.888 | 81.133
| 31.2153 | 309.311 | 50.366 | 66.162 | 44.887 | 81.131
| 31.2222 | 309.761 | 50.36 | 66.159 | 44.879 | 81.128
| 31.2292 | 309.011 | 50.365 | 66.158 | 44.879 | 81.124
| 31.2361 | 309.276 | 50.354 | 66.153 | 44.875 | 81.109
| 31.2431 | 310.137 | 50.322 | 66.127 | 44.85 | 81.084
| 31.25 | 309.56 | 50.333 | 66.132 | 44.856 | 81.078
| 31.2569 | 308.318 | 50.294 | 66.105 | 44.821 | 81.037
| 31.2639 | 308.46 | 50.279 | 66.089 | 44.813 | 81.022
| 31.2708 | 307.427 | 50.237 | 66.047 | 44.784 | 80.957
| 31.2778 | 308.565 | 50.275 | 66.063 | 44.804 | 80.978
| 31.2847 | 313.217 | 50.313 | 66.079 | 44.822 | 81.006
| 31.2917 | 311.983 | 50.485 | 66.222 | 44.975 | 81.187
| 31.2986 | 310.867 | 50.519 | 66.264 | 45.005 | 81.243
| 31.3056 | 310.695 | 50.5 | 66.274 | 44.994 | 81.252
| 31.3125 | 310.101 | 50.523 | 66.301 | 45.004 | 81.291
| 31.3194 | 308.486 | 50.467 | 66.274 | 44.963 | 81.255
| 31.3264 | 308.179 | 50.368 | 66.205 | 44.883 | 81.155
| 31.3333 | 310.88 | 50.348 | 66.176 | 44.862 | 81.124
| 31.3403 | 312.044 | 50.505 | 66.292 | 44.989 | 81.275
| 31.3472 | 311.801 | 50.588 | 66.374 | 45.061 | 81.37
| 31.3542 | 313.826 | 50.712 | 66.478 | 45.154 | 81.516
| 31.3611 | 313.601 | 50.789 | 66.568 | 45.22 | 81.63
| 31.3681 | 312.289 | 50.79 | 66.597 | 45.222 | 81.664
| 31.375 | 312.259 | 50.79 | 66.624 | 45.219 | 81.687
| 31.3819 | 313.006 | 50.821 | 66.66 | 45.239 | 81.737
| 31.3889 | 313.454 | 50.852 | 66.709 | 45.272 | 81.797
| 31.3958 | 312.934 | 50.865 | 66.742 | 45.275 | 81.832
| 31.4028 | 311.982 | 50.812 | 66.724 | 45.246 | 81.803
| 31.4097 | 311.263 | 50.813 | 66.729 | 45.233 | 81.807
| 31.4167 | 311.695 | 50.788 | 66.728 | 45.225 | 81.802
| 31.4236 | 310.654 | 50.738 | 66.689 | 45.187 | 81.752
| 31.4306 | 310.554 | 50.701 | 66.666 | 45.152 | 81.714
| 31.4375 | 310.206 | 50.664 | 66.641 | 45.129 | 81.675
| 31.4444 | 310.411 | 50.618 | 66.603 | 45.089 | 81.619
| 31.4514 | 311.256 | 50.678 | 66.642 | 45.141 | 81.665
| 31.4583 | 311.25 | 50.7 | 66.661 | 45.155 | 81.68
| 31.4653 | 311.055 | 50.675 | 66.644 | 45.137 | 81.657
| 31.4722 | 310.636 | 50.633 | 66.62 | 45.11 | 81.62
| 31.4792 | 310.313 | 50.616 | 66.604 | 45.094 | 81.593
| 31.4861 | 310.934 | 50.604 | 66.586 | 45.083 | 81.559
| 31.4931 | 311.138 | 50.607 | 66.582 | 45.082 | 81.562
| 31.5 | 311.144 | 50.615 | 66.591 | 45.09 | 81.567
| 31.5069 | 311.485 | 50.625 | 66.594 | 45.09 | 81.574
| 31.5139 | 310.053 | 50.616 | 66.587 | 45.09 | 81.555
| 31.5208 | 310.083 | 50.58 | 66.557 | 45.06 | 81.518
| 31.5278 | 311.548 | 50.587 | 66.56 | 45.067 | 81.523
| 31.5347 | 311.809 | 50.642 | 66.601 | 45.11 | 81.577
| 31.5417 | 311.839 | 50.672 | 66.628 | 45.138 | 81.615
| 31.5486 | 312.279 | 50.724 | 66.674 | 45.175 | 81.678
| 31.5556 | 312.216 | 50.773 | 66.72 | 45.219 | 81.74
| 31.5625 | 312.329 | 50.764 | 66.726 | 45.21 | 81.752
| 31.5694 | 311.967 | 50.781 | 66.749 | 45.226 | 81.785
| 31.5764 | 312.503 | 50.824 | 66.796 | 45.256 | 81.84
| 31.5833 | 312.762 | 50.847 | 66.824 | 45.279 | 81.881
| 31.5903 | 312.663 | 50.854 | 66.84 | 45.284 | 81.904
| 31.5972 | 312.096 | 50.857 | 66.859 | 45.29 | 81.92
| 31.6042 | 312.757 | 50.848 | 66.858 | 45.28 | 81.919
| 31.6111 | 312.56 | 50.845 | 66.867 | 45.277 | 81.935
| 31.6181 | 313.188 | 50.879 | 66.894 | 45.301 | 81.972
| 31.625 | 312.711 | 50.881 | 66.909 | 45.31 | 81.987
| 31.6319 | 312.248 | 50.842 | 66.892 | 45.279 | 81.969
| 31.6389 | 313.742 | 50.899 | 66.937 | 45.319 | 82.027
| 31.6458 | 313.432 | 50.923 | 66.966 | 45.346 | 82.066
| 31.6528 | 313.836 | 50.942 | 66.983 | 45.352 | 82.089
| 31.6597 | 312.616 | 50.909 | 66.974 | 45.335 | 82.077
| 31.6667 | 313.798 | 50.9 | 66.971 | 45.328 | 82.072
| 31.6736 | 312.965 | 50.939 | 67.008 | 45.358 | 82.117
| 31.6806 | 314.332 | 50.973 | 67.038 | 45.381 | 82.16
| 31.6875 | 313.889 | 51.002 | 67.075 | 45.411 | 82.204
| 31.6944 | 310.097 | 50.817 | 66.943 | 45.26 | 82.017
| 31.7014 | 310.497 | 50.745 | 66.881 | 45.207 | 81.936
| 31.7083 | 309.625 | 50.704 | 66.836 | 45.176 | 81.868
| 31.7153 | 310.093 | 50.644 | 66.781 | 45.132 | 81.781
| 31.7222 | 309.566 | 50.566 | 66.704 | 45.072 | 81.676
| 31.7292 | 307.499 | 50.414 | 66.569 | 44.948 | 81.484
| 31.7361 | 308.36 | 50.336 | 66.479 | 44.885 | 81.36
| 31.7431 | 307.849 | 50.292 | 66.409 | 44.843 | 81.26
| 31.75 | 307.3 | 50.255 | 66.353 | 44.823 | 81.187
| 31.7569 | 307.005 | 50.21 | 66.286 | 44.781 | 81.09
| 31.7639 | 307.642 | 50.185 | 66.237 | 44.766 | 81.025
| 31.7708 | 307.888 | 50.2 | 66.22 | 44.777 | 81.003
| 31.7778 | 309.104 | 50.254 | 66.239 | 44.814 | 81.026
| 31.7847 | 307.327 | 50.19 | 66.175 | 44.763 | 80.94
| 31.7917 | 307.352 | 50.153 | 66.13 | 44.732 | 80.884
| 31.7986 | 308.329 | 50.171 | 66.118 | 44.742 | 80.881
| 31.8056 | 307.462 | 50.182 | 66.113 | 44.754 | 80.864
| 31.8125 | 308.583 | 50.185 | 66.096 | 44.754 | 80.849
| 31.8194 | 308.161 | 50.146 | 66.058 | 44.724 | 80.801
| 31.8264 | 309.119 | 50.184 | 66.074 | 44.752 | 80.824
| 31.8333 | 307.604 | 50.201 | 66.077 | 44.766 | 80.835
| 31.8403 | 307.21 | 50.175 | 66.044 | 44.74 | 80.795
| 31.8472 | 306.794 | 50.133 | 66.001 | 44.708 | 80.736
| 31.8542 | 306.014 | 50.065 | 65.95 | 44.658 | 80.657
| 31.8611 | 307.456 | 50.057 | 65.919 | 44.645 | 80.618
| 31.8681 | 308.909 | 50.123 | 65.953 | 44.7 | 80.669
| 31.875 | 309.089 | 50.152 | 65.967 | 44.723 | 80.689
| 31.8819 | 309.559 | 50.216 | 66.009 | 44.769 | 80.747
| 31.8889 | 308.805 | 50.261 | 66.052 | 44.81 | 80.809
| 31.8958 | 309.671 | 50.266 | 66.059 | 44.819 | 80.828
| 31.9028 | 310.645 | 50.314 | 66.096 | 44.849 | 80.882
| 31.9097 | 312.211 | 50.434 | 66.198 | 44.947 | 81.023
| 31.9167 | 311.536 | 50.524 | 66.279 | 45.017 | 81.128
| 31.9236 | 312.695 | 50.574 | 66.337 | 45.056 | 81.218
| 31.9306 | 308.416 | 50.539 | 66.343 | 45.036 | 81.217
| 31.9375 | 309.754 | 50.467 | 66.292 | 44.967 | 81.155
| 31.9444 | 311.867 | 50.455 | 66.286 | 44.956 | 81.153
| 31.9514 | 311.84 | 50.556 | 66.37 | 45.049 | 81.263
| 31.9583 | 309.496 | 50.491 | 66.341 | 44.997 | 81.214
| 31.9653 | 310.033 | 50.447 | 66.302 | 44.963 | 81.172
| 31.9722 | 310.49 | 50.48 | 66.332 | 44.988 | 81.199
| 31.9792 | 311.799 | 50.527 | 66.372 | 45.029 | 81.251
| 31.9861 | 312.301 | 50.576 | 66.423 | 45.067 | 81.314
| 31.9931 | 306.312 | 50.514 | 66.399 | 45.032 | 81.271
| 32 | 306.998 | 50.326 | 66.25 | 44.87 | 81.071
| 32.0069 | 307.788 | 50.226 | 66.156 | 44.795 | 80.944
| 32.0139 | 307.504 | 50.174 | 66.097 | 44.75 | 80.855
| 32.0208 | 306.873 | 50.15 | 66.066 | 44.743 | 80.804
| 32.0278 | 308.282 | 50.122 | 66.021 | 44.721 | 80.747
| 32.0347 | 308.205 | 50.173 | 66.044 | 44.765 | 80.774
| 32.0417 | 307.865 | 50.179 | 66.042 | 44.774 | 80.76
| 32.0486 | 308.264 | 50.168 | 66.022 | 44.764 | 80.737
| 32.0556 | 308.122 | 50.148 | 66.002 | 44.749 | 80.7
| 32.0625 | 308.052 | 50.121 | 65.969 | 44.723 | 80.654
| 32.0694 | 308.032 | 50.149 | 65.981 | 44.748 | 80.673
| 32.0764 | 308.798 | 50.158 | 65.977 | 44.754 | 80.669
| 32.0833 | 308.811 | 50.18 | 65.985 | 44.768 | 80.688
| 32.0903 | 308.518 | 50.19 | 65.99 | 44.783 | 80.699
| 32.0972 | 308.856 | 50.192 | 65.99 | 44.779 | 80.699
| 32.1042 | 309.136 | 50.231 | 66.015 | 44.812 | 80.745
| 32.1111 | 309.57 | 50.266 | 66.05 | 44.843 | 80.789
| 32.1181 | 309.443 | 50.288 | 66.069 | 44.864 | 80.833
| 32.125 | 309.331 | 50.294 | 66.074 | 44.859 | 80.842
| 32.1319 | 309.504 | 50.309 | 66.091 | 44.879 | 80.867
| 32.1389 | 309.281 | 50.312 | 66.094 | 44.879 | 80.877
| 32.1458 | 309.464 | 50.306 | 66.096 | 44.875 | 80.883
| 32.1528 | 309.678 | 50.309 | 66.096 | 44.876 | 80.89
| 32.1597 | 309.893 | 50.325 | 66.117 | 44.895 | 80.922
| 32.1667 | 309.605 | 50.353 | 66.139 | 44.919 | 80.953
| 32.1736 | 309.613 | 50.366 | 66.148 | 44.923 | 80.97
| 32.1806 | 309.259 | 50.343 | 66.14 | 44.915 | 80.961
| 32.1875 | 309.339 | 50.345 | 66.143 | 44.914 | 80.967
| 32.1944 | 309.391 | 50.348 | 66.153 | 44.921 | 80.972
| 32.2014 | 309.076 | 50.339 | 66.148 | 44.916 | 80.972
| 32.2083 | 308.652 | 50.321 | 66.14 | 44.907 | 80.956
| 32.2153 | 309.283 | 50.294 | 66.121 | 44.886 | 80.931
| 32.2222 | 308.639 | 50.264 | 66.1 | 44.873 | 80.896
| 32.2292 | 309.031 | 50.255 | 66.084 | 44.858 | 80.88
| 32.2361 | 307.157 | 50.221 | 66.048 | 44.834 | 80.832
| 32.2431 | 306.079 | 50.128 | 65.978 | 44.764 | 80.726
| 32.25 | 309.099 | 50.171 | 65.995 | 44.799 | 80.751
| 32.2569 | 309.146 | 50.209 | 66.019 | 44.831 | 80.781
| 32.2639 | 307.955 | 50.184 | 65.996 | 44.807 | 80.74
| 32.2708 | 307.374 | 50.145 | 65.952 | 44.781 | 80.689
| 32.2778 | 308.107 | 50.095 | 65.909 | 44.742 | 80.627
| 32.2847 | 308.33 | 50.142 | 65.924 | 44.772 | 80.656
| 32.2917 | 311.354 | 50.312 | 66.048 | 44.907 | 80.823
| 32.2986 | 311.385 | 50.443 | 66.163 | 45.016 | 80.98
| 32.3056 | 310.479 | 50.448 | 66.186 | 45.022 | 81.013
| 32.3125 | 309.328 | 50.411 | 66.176 | 44.994 | 81.004
| 32.3194 | 307.461 | 50.341 | 66.128 | 44.935 | 80.941
| 32.3264 | 311.803 | 50.406 | 66.169 | 44.979 | 81.001
| 32.3333 | 311.383 | 50.516 | 66.268 | 45.08 | 81.126
| 32.3403 | 310.574 | 50.573 | 66.332 | 45.131 | 81.205
| 32.3472 | 310.034 | 50.522 | 66.307 | 45.082 | 81.172
| 32.3542 | 310.035 | 50.498 | 66.298 | 45.06 | 81.157
| 32.3611 | 308.699 | 50.451 | 66.275 | 45.037 | 81.123
| 32.3681 | 308.012 | 50.396 | 66.234 | 44.987 | 81.061
| 32.375 | 308.745 | 50.347 | 66.192 | 44.953 | 80.998
| 32.3819 | 307.498 | 50.296 | 66.145 | 44.91 | 80.925
| 32.3889 | 307.711 | 50.297 | 66.135 | 44.914 | 80.909
| 32.3958 | 309.485 | 50.326 | 66.145 | 44.934 | 80.917
| 32.4028 | 308.768 | 50.332 | 66.149 | 44.944 | 80.92
| 32.4097 | 309.911 | 50.372 | 66.169 | 44.969 | 80.954
| 32.4167 | 308.639 | 50.399 | 66.201 | 45.003 | 80.985
| 32.4236 | 308.612 | 50.37 | 66.179 | 44.977 | 80.956
| 32.4306 | 308.14 | 50.342 | 66.157 | 44.958 | 80.928
| 32.4375 | 308.499 | 50.317 | 66.138 | 44.937 | 80.898
| 32.4444 | 307.76 | 50.293 | 66.114 | 44.915 | 80.86
| 32.4514 | 307.787 | 50.265 | 66.081 | 44.894 | 80.821
| 32.4583 | 308.924 | 50.299 | 66.092 | 44.921 | 80.833
| 32.4653 | 308.63 | 50.336 | 66.12 | 44.952 | 80.87
| 32.4722 | 309.083 | 50.353 | 66.133 | 44.966 | 80.892
| 32.4792 | 308.599 | 50.339 | 66.123 | 44.963 | 80.886
| 32.4861 | 307.911 | 50.315 | 66.1 | 44.933 | 80.855
| 32.4931 | 308.014 | 50.284 | 66.075 | 44.911 | 80.822
| 32.5 | 308.19 | 50.27 | 66.057 | 44.895 | 80.799
| 32.5069 | 308.567 | 50.284 | 66.061 | 44.912 | 80.799
| 32.5139 | 309.048 | 50.309 | 66.08 | 44.936 | 80.829
| 32.5208 | 308.199 | 50.312 | 66.077 | 44.936 | 80.829
| 32.5278 | 310.197 | 50.342 | 66.093 | 44.96 | 80.862
| 32.5347 | 310.517 | 50.428 | 66.163 | 45.03 | 80.954
| 32.5417 | 310.651 | 50.496 | 66.23 | 45.092 | 81.046
| 32.5486 | 309.975 | 50.495 | 66.239 | 45.084 | 81.06
| 32.5556 | 310.202 | 50.523 | 66.264 | 45.107 | 81.107
| 32.5625 | 310.487 | 50.557 | 66.303 | 45.132 | 81.164
| 32.5694 | 310.453 | 50.527 | 66.293 | 45.112 | 81.148
| 32.5764 | 309.916 | 50.518 | 66.294 | 45.109 | 81.15
| 32.5833 | 309.55 | 50.503 | 66.289 | 45.098 | 81.149
| 32.5903 | 309.907 | 50.505 | 66.3 | 45.104 | 81.157
| 32.5972 | 310.112 | 50.526 | 66.317 | 45.123 | 81.192
| 32.6042 | 310.816 | 50.573 | 66.355 | 45.162 | 81.235
| 32.6111 | 312.505 | 50.647 | 66.417 | 45.216 | 81.329
| 32.6181 | 308.451 | 50.557 | 66.367 | 45.157 | 81.261
| 32.625 | 309.056 | 50.54 | 66.358 | 45.137 | 81.243
| 32.6319 | 308.554 | 50.492 | 66.323 | 45.103 | 81.194
| 32.6389 | 309.313 | 50.48 | 66.31 | 45.092 | 81.179
| 32.6458 | 308.838 | 50.449 | 66.285 | 45.073 | 81.14
| 32.6528 | 308.538 | 50.436 | 66.273 | 45.059 | 81.118
| 32.6597 | 307.99 | 50.4 | 66.235 | 45.036 | 81.07
| 32.6667 | 308.618 | 50.382 | 66.217 | 45.024 | 81.044
| 32.6736 | 308.712 | 50.362 | 66.192 | 45.007 | 81.021
| 32.6806 | 309.589 | 50.406 | 66.213 | 45.033 | 81.046
| 32.6875 | 309.983 | 50.43 | 66.226 | 45.055 | 81.065
| 32.6944 | 308.806 | 50.439 | 66.233 | 45.068 | 81.074
| 32.7014 | 309.082 | 50.416 | 66.21 | 45.044 | 81.05
| 32.7083 | 308.921 | 50.434 | 66.221 | 45.06 | 81.061
| 32.7153 | 309.098 | 50.427 | 66.214 | 45.058 | 81.044
| 32.7222 | 308.882 | 50.401 | 66.189 | 45.033 | 81.016
| 32.7292 | 306.886 | 50.35 | 66.153 | 44.998 | 80.961
| 32.7361 | 306.917 | 50.367 | 66.159 | 45.011 | 80.96
| 32.7431 | 309.585 | 50.447 | 66.213 | 45.072 | 81.037
| 32.75 | 309.952 | 50.492 | 66.247 | 45.115 | 81.087
| 32.7569 | 309.865 | 50.497 | 66.258 | 45.111 | 81.1
| 32.7639 | 309.628 | 50.46 | 66.231 | 45.084 | 81.072
| 32.7708 | 309.829 | 50.48 | 66.243 | 45.099 | 81.085
| 32.7778 | 310.625 | 50.54 | 66.288 | 45.146 | 81.148
| 32.7847 | 310.498 | 50.592 | 66.336 | 45.193 | 81.218
| 32.7917 | 310.968 | 50.629 | 66.381 | 45.226 | 81.282
| 32.7986 | 311.165 | 50.638 | 66.395 | 45.231 | 81.305
| 32.8056 | 310.958 | 50.639 | 66.403 | 45.233 | 81.318
| 32.8125 | 310.751 | 50.643 | 66.411 | 45.235 | 81.34
| 32.8194 | 310.999 | 50.664 | 66.434 | 45.255 | 81.369
| 32.8264 | 312.169 | 50.747 | 66.505 | 45.319 | 81.465
| 32.8333 | 309.064 | 50.803 | 66.572 | 45.37 | 81.546
| 32.8403 | 308.388 | 50.614 | 66.439 | 45.218 | 81.376
| 32.8472 | 309.106 | 50.581 | 66.415 | 45.196 | 81.334
| 32.8542 | 309.927 | 50.568 | 66.401 | 45.185 | 81.305
| 32.8611 | 309.896 | 50.602 | 66.423 | 45.215 | 81.335
| 32.8681 | 310.762 | 50.645 | 66.455 | 45.255 | 81.372
| 32.875 | 310.841 | 50.697 | 66.501 | 45.298 | 81.43
| 32.8819 | 311.674 | 50.724 | 66.524 | 45.32 | 81.461
| 32.8889 | 309.521 | 50.735 | 66.551 | 45.339 | 81.488
| 32.8958 | 309.7 | 50.689 | 66.519 | 45.289 | 81.444
| 32.9028 | 307.912 | 50.585 | 66.443 | 45.209 | 81.334
| 32.9097 | 307.722 | 50.533 | 66.399 | 45.174 | 81.272
| 32.9167 | 309.022 | 50.52 | 66.38 | 45.163 | 81.243
| 32.9236 | 310.247 | 50.528 | 66.377 | 45.178 | 81.231
| 32.9306 | 309.86 | 50.583 | 66.411 | 45.221 | 81.269
| 32.9375 | 311.289 | 50.646 | 66.461 | 45.275 | 81.331
| 32.9444 | 312.671 | 50.715 | 66.513 | 45.325 | 81.409
| 32.9514 | 309.952 | 50.696 | 66.515 | 45.313 | 81.392
| 32.9583 | 309.872 | 50.663 | 66.494 | 45.286 | 81.373
| 32.9653 | 310.156 | 50.655 | 66.498 | 45.286 | 81.368
| 32.9722 | 311.768 | 50.731 | 66.556 | 45.348 | 81.445
| 32.9792 | 311.247 | 50.742 | 66.574 | 45.361 | 81.461
| 32.9861 | 310.832 | 50.749 | 66.587 | 45.361 | 81.481
| 32.9931 | 311.78 | 50.805 | 66.634 | 45.406 | 81.548
| 33 | 312.471 | 50.858 | 66.688 | 45.456 | 81.619
| 33.0069 | 311.716 | 50.867 | 66.711 | 45.463 | 81.652
| 33.0139 | 312.439 | 50.889 | 66.737 | 45.477 | 81.686
| 33.0208 | 309.716 | 50.796 | 66.684 | 45.408 | 81.609
| 33.0278 | 309.176 | 50.73 | 66.631 | 45.355 | 81.543
| 33.0347 | 306.737 | 50.555 | 66.499 | 45.221 | 81.351
| 33.0417 | 306.868 | 50.433 | 66.381 | 45.123 | 81.194
| 33.0486 | 306.192 | 50.355 | 66.296 | 45.059 | 81.081
| 33.0556 | 308.526 | 50.419 | 66.314 | 45.113 | 81.098
| 33.0625 | 309.701 | 50.473 | 66.338 | 45.158 | 81.14
| 33.0694 | 308.789 | 50.498 | 66.351 | 45.177 | 81.153
| 33.0764 | 310.058 | 50.545 | 66.377 | 45.213 | 81.189
| 33.0833 | 310.045 | 50.564 | 66.392 | 45.228 | 81.216
| 33.0903 | 310.363 | 50.583 | 66.404 | 45.246 | 81.241
| 33.0972 | 309.915 | 50.602 | 66.42 | 45.262 | 81.263
| 33.1042 | 310.513 | 50.648 | 66.453 | 45.29 | 81.313
| 33.1111 | 310.583 | 50.698 | 66.495 | 45.334 | 81.374
| 33.1181 | 310.39 | 50.706 | 66.516 | 45.339 | 81.4
| 33.125 | 310.901 | 50.739 | 66.547 | 45.372 | 81.445
| 33.1319 | 311.127 | 50.785 | 66.589 | 45.405 | 81.509
| 33.1389 | 311.046 | 50.794 | 66.61 | 45.413 | 81.539
| 33.1458 | 311.413 | 50.805 | 66.626 | 45.416 | 81.566
| 33.1528 | 307.741 | 50.709 | 66.57 | 45.355 | 81.482
| 33.1597 | 307.93 | 50.575 | 66.464 | 45.242 | 81.343
| 33.1667 | 307.13 | 50.505 | 66.401 | 45.188 | 81.254
| 33.1736 | 307.844 | 50.454 | 66.337 | 45.145 | 81.174
| 33.1806 | 307.818 | 50.415 | 66.288 | 45.116 | 81.104
| 33.1875 | 307.744 | 50.393 | 66.25 | 45.097 | 81.053
| 33.1944 | 307.66 | 50.367 | 66.214 | 45.075 | 81.005
| 33.2014 | 307.575 | 50.327 | 66.169 | 45.048 | 80.946
| 33.2083 | 307.348 | 50.303 | 66.132 | 45.026 | 80.895
| 33.2153 | 307.691 | 50.293 | 66.107 | 45.021 | 80.866
| 33.2222 | 306.806 | 50.257 | 66.069 | 44.995 | 80.808
| 33.2292 | 306.868 | 50.214 | 66.014 | 44.958 | 80.739
| 33.2361 | 309.122 | 50.196 | 65.973 | 44.936 | 80.693
| 33.2431 | 309.784 | 50.338 | 66.062 | 45.052 | 80.817
| 33.25 | 310.826 | 50.448 | 66.143 | 45.139 | 80.934
| 33.2569 | 311.159 | 50.539 | 66.222 | 45.208 | 81.047
| 33.2639 | 309.776 | 50.573 | 66.259 | 45.24 | 81.108
| 33.2708 | 309.972 | 50.571 | 66.273 | 45.236 | 81.132
| 33.2778 | 306.72 | 50.481 | 66.219 | 45.166 | 81.056
| 33.2847 | 310.263 | 50.461 | 66.182 | 45.138 | 81.028
| 33.2917 | 311.976 | 50.616 | 66.31 | 45.27 | 81.192
| 33.2986 | 308.651 | 50.573 | 66.302 | 45.242 | 81.174
| 33.3056 | 308.699 | 50.488 | 66.237 | 45.169 | 81.1
| 33.3125 | 308.144 | 50.457 | 66.205 | 45.145 | 81.066
| 33.3194 | 306.035 | 50.374 | 66.139 | 45.089 | 80.972
| 33.3264 | 308.638 | 50.38 | 66.125 | 45.079 | 80.952
| 33.3333 | 307.087 | 50.374 | 66.114 | 45.076 | 80.938
| 33.3403 | 308.091 | 50.345 | 66.079 | 45.053 | 80.902
| 33.3472 | 308.979 | 50.379 | 66.094 | 45.08 | 80.921
| 33.3542 | 308.876 | 50.408 | 66.113 | 45.108 | 80.955
| 33.3611 | 307.349 | 50.375 | 66.09 | 45.078 | 80.916
| 33.3681 | 307.134 | 50.317 | 66.037 | 45.031 | 80.854
| 33.375 | 307.988 | 50.307 | 66.018 | 45.028 | 80.833
| 33.3819 | 308.007 | 50.307 | 66.011 | 45.025 | 80.824
| 33.3889 | 307.626 | 50.323 | 66.01 | 45.035 | 80.828
| 33.3958 | 307.321 | 50.294 | 65.98 | 45.019 | 80.793
| 33.4028 | 308.642 | 50.303 | 65.982 | 45.021 | 80.799
| 33.4097 | 307.351 | 50.307 | 65.983 | 45.021 | 80.794
| 33.4167 | 307.968 | 50.3 | 65.979 | 45.024 | 80.79
| 33.4236 | 307.394 | 50.276 | 65.957 | 45.002 | 80.765
| 33.4306 | 309.578 | 50.354 | 65.996 | 45.057 | 80.833
| 33.4375 | 310.199 | 50.468 | 66.089 | 45.155 | 80.963
| 33.4444 | 311.507 | 50.547 | 66.154 | 45.208 | 81.065
| 33.4514 | 311.592 | 50.611 | 66.227 | 45.266 | 81.168
| 33.4583 | 311.685 | 50.665 | 66.284 | 45.306 | 81.254
| 33.4653 | 310.481 | 50.675 | 66.314 | 45.318 | 81.295
| 33.4722 | 310.36 | 50.657 | 66.312 | 45.292 | 81.288
| 33.4792 | 312.439 | 50.709 | 66.362 | 45.335 | 81.366
| 33.4861 | 313.23 | 50.82 | 66.466 | 45.426 | 81.503
| 33.4931 | 309.339 | 50.786 | 66.47 | 45.411 | 81.504
| 33.5 | 309.688 | 50.707 | 66.423 | 45.339 | 81.448
| 33.5069 | 310.78 | 50.703 | 66.421 | 45.332 | 81.449
| 33.5139 | 310.21 | 50.725 | 66.451 | 45.356 | 81.478
| 33.5208 | 311.083 | 50.733 | 66.464 | 45.363 | 81.498
| 33.5278 | 312.002 | 50.781 | 66.501 | 45.398 | 81.553
| 33.5347 | 310.972 | 50.805 | 66.54 | 45.429 | 81.6
| 33.5417 | 310.684 | 50.777 | 66.533 | 45.404 | 81.585
| 33.5486 | 311.232 | 50.767 | 66.521 | 45.391 | 81.583
| 33.5556 | 310.774 | 50.797 | 66.555 | 45.414 | 81.617
| 33.5625 | 307.424 | 50.669 | 66.471 | 45.327 | 81.503
| 33.5694 | 306.916 | 50.522 | 66.354 | 45.202 | 81.338
| 33.5764 | 309.828 | 50.574 | 66.373 | 45.244 | 81.374
| 33.5833 | 309.581 | 50.577 | 66.37 | 45.253 | 81.361
| 33.5903 | 309.778 | 50.564 | 66.358 | 45.245 | 81.346
| 33.5972 | 310.05 | 50.564 | 66.357 | 45.246 | 81.343
| 33.6042 | 310.544 | 50.592 | 66.369 | 45.269 | 81.366
| 33.6111 | 311.169 | 50.637 | 66.4 | 45.302 | 81.406
| 33.6181 | 309.628 | 50.643 | 66.412 | 45.312 | 81.425
| 33.625 | 311.114 | 50.665 | 66.426 | 45.325 | 81.45
| 33.6319 | 310.631 | 50.678 | 66.449 | 45.344 | 81.479
| 33.6389 | 311.358 | 50.685 | 66.461 | 45.345 | 81.495
| 33.6458 | 311.403 | 50.718 | 66.491 | 45.377 | 81.537
| 33.6528 | 311 | 50.735 | 66.507 | 45.39 | 81.565
| 33.6597 | 311.004 | 50.766 | 66.534 | 45.408 | 81.606
| 33.6667 | 311.571 | 50.808 | 66.583 | 45.448 | 81.66
| 33.6736 | 312.259 | 50.836 | 66.619 | 45.471 | 81.71
| 33.6806 | 311.876 | 50.879 | 66.655 | 45.505 | 81.776
| 33.6875 | 313.017 | 50.939 | 66.723 | 45.558 | 81.859
| 33.6944 | 312.238 | 50.941 | 66.742 | 45.56 | 81.879
| 33.7014 | 312.898 | 50.96 | 66.767 | 45.569 | 81.92
| 33.7083 | 312.557 | 50.99 | 66.81 | 45.599 | 81.974
| 33.7153 | 312.608 | 51.023 | 66.851 | 45.625 | 82.031
| 33.7222 | 311.05 | 51.017 | 66.868 | 45.626 | 82.044
| 33.7292 | 308.803 | 50.868 | 66.765 | 45.511 | 81.906
| 33.7361 | 310.807 | 50.844 | 66.731 | 45.476 | 81.869
| 33.7431 | 310.709 | 50.808 | 66.704 | 45.456 | 81.822
| 33.75 | 309.995 | 50.766 | 66.673 | 45.423 | 81.779
| 33.7569 | 310.356 | 50.753 | 66.649 | 45.412 | 81.751
| 33.7639 | 311.113 | 50.763 | 66.648 | 45.417 | 81.744
| 33.7708 | 310.822 | 50.794 | 66.669 | 45.447 | 81.767
| 33.7778 | 311.665 | 50.838 | 66.701 | 45.481 | 81.815
| 33.7847 | 312.265 | 50.882 | 66.74 | 45.524 | 81.858
| 33.7917 | 312.14 | 50.913 | 66.767 | 45.547 | 81.904
| 33.7986 | 313.179 | 50.947 | 66.803 | 45.566 | 81.954
| 33.8056 | 312.52 | 50.981 | 66.836 | 45.596 | 81.994
| 33.8125 | 313.672 | 51.044 | 66.896 | 45.646 | 82.081
| 33.8194 | 313.673 | 51.082 | 66.945 | 45.675 | 82.141
| 33.8264 | 310.363 | 50.921 | 66.837 | 45.555 | 81.99
| 33.8333 | 310.361 | 50.863 | 66.791 | 45.508 | 81.93
| 33.8403 | 310.735 | 50.859 | 66.782 | 45.503 | 81.904
| 33.8472 | 311.053 | 50.849 | 66.765 | 45.494 | 81.881
| 33.8542 | 309.255 | 50.838 | 66.761 | 45.502 | 81.867
| 33.8611 | 307.47 | 50.707 | 66.654 | 45.397 | 81.711
| 33.8681 | 308.025 | 50.64 | 66.587 | 45.336 | 81.615
| 33.875 | 308.094 | 50.592 | 66.538 | 45.306 | 81.537
| 33.8819 | 309.391 | 50.581 | 66.508 | 45.296 | 81.493
| 33.8889 | 309.278 | 50.599 | 66.501 | 45.31 | 81.48
| 33.8958 | 310.608 | 50.636 | 66.525 | 45.34 | 81.502
| 33.9028 | 310.231 | 50.692 | 66.552 | 45.388 | 81.544
| 33.9097 | 310.318 | 50.735 | 66.587 | 45.413 | 81.58
| 33.9167 | 311.554 | 50.773 | 66.618 | 45.453 | 81.626
| 33.9236 | 309.817 | 50.806 | 66.652 | 45.475 | 81.662
| 33.9306 | 311.515 | 50.788 | 66.635 | 45.456 | 81.651
| 33.9375 | 312.613 | 50.851 | 66.692 | 45.51 | 81.726
| 33.9444 | 308.062 | 50.718 | 66.604 | 45.414 | 81.603
| 33.9514 | 307.642 | 50.601 | 66.505 | 45.315 | 81.468
| 33.9583 | 307.871 | 50.538 | 66.442 | 45.27 | 81.382
| 33.9653 | 309.094 | 50.544 | 66.428 | 45.27 | 81.358
| 33.9722 | 309.731 | 50.596 | 66.453 | 45.311 | 81.39
| 33.9792 | 311.242 | 50.649 | 66.489 | 45.359 | 81.447
| 33.9861 | 310.689 | 50.709 | 66.537 | 45.411 | 81.509
| 33.9931 | 312.016 | 50.777 | 66.594 | 45.47 | 81.592
| 34 | 312.216 | 50.854 | 66.658 | 45.526 | 81.686
| 34.0069 | 313.187 | 50.905 | 66.709 | 45.564 | 81.757
| 34.0139 | 309.811 | 50.926 | 66.75 | 45.592 | 81.81
| 34.0208 | 307.373 | 50.799 | 66.671 | 45.489 | 81.704
| 34.0278 | 307.374 | 50.614 | 66.518 | 45.329 | 81.505
| 34.0347 | 307.345 | 50.523 | 66.439 | 45.264 | 81.397
| 34.0417 | 311.39 | 50.65 | 66.511 | 45.37 | 81.499
| 34.0486 | 309.954 | 50.681 | 66.527 | 45.39 | 81.524
| 34.0556 | 309.703 | 50.687 | 66.534 | 45.398 | 81.529
| 34.0625 | 309.617 | 50.67 | 66.515 | 45.383 | 81.51
| 34.0694 | 311.463 | 50.67 | 66.508 | 45.373 | 81.507
| 34.0764 | 310.468 | 50.725 | 66.545 | 45.416 | 81.56
| 34.0833 | 310.645 | 50.725 | 66.548 | 45.425 | 81.568
| 34.0903 | 311.535 | 50.742 | 66.564 | 45.434 | 81.597
| 34.0972 | 310.352 | 50.753 | 66.569 | 45.439 | 81.611
| 34.1042 | 310.179 | 50.725 | 66.561 | 45.423 | 81.59
| 34.1111 | 312.246 | 50.764 | 66.587 | 45.453 | 81.632
| 34.1181 | 312.889 | 50.858 | 66.657 | 45.526 | 81.734
| 34.125 | 312.158 | 50.895 | 66.699 | 45.559 | 81.793
| 34.1319 | 313.121 | 50.932 | 66.74 | 45.587 | 81.85
| 34.1389 | 311.958 | 50.945 | 66.76 | 45.598 | 81.879
| 34.1458 | 311.99 | 50.942 | 66.77 | 45.595 | 81.901
| 34.1528 | 311.796 | 50.948 | 66.788 | 45.599 | 81.918
| 34.1597 | 310.913 | 50.901 | 66.761 | 45.562 | 81.883
| 34.1667 | 311.136 | 50.91 | 66.772 | 45.571 | 81.901
| 34.1736 | 311.749 | 50.93 | 66.79 | 45.581 | 81.918
| 34.1806 | 312.109 | 50.932 | 66.801 | 45.591 | 81.937
| 34.1875 | 312.015 | 50.941 | 66.81 | 45.594 | 81.949
| 34.1944 | 311.45 | 50.961 | 66.834 | 45.612 | 81.98
| 34.2014 | 310.982 | 50.926 | 66.813 | 45.582 | 81.95
| 34.2083 | 311.584 | 50.9 | 66.793 | 45.561 | 81.924
| 34.2153 | 311.652 | 50.919 | 66.806 | 45.57 | 81.942
| 34.2222 | 311.381 | 50.898 | 66.795 | 45.56 | 81.922
| 34.2292 | 310.659 | 50.867 | 66.77 | 45.532 | 81.89
| 34.2361 | 308.842 | 50.789 | 66.716 | 45.478 | 81.809
| 34.2431 | 308.79 | 50.712 | 66.643 | 45.409 | 81.708
| 34.25 | 308.514 | 50.661 | 66.585 | 45.37 | 81.634
| 34.2569 | 308.426 | 50.609 | 66.533 | 45.333 | 81.553
| 34.2639 | 310.784 | 50.693 | 66.577 | 45.39 | 81.618
| 34.2708 | 309.754 | 50.723 | 66.59 | 45.415 | 81.634
| 34.2778 | 308.557 | 50.685 | 66.559 | 45.391 | 81.602
| 34.2847 | 308.838 | 50.626 | 66.508 | 45.332 | 81.524
| 34.2917 | 307.678 | 50.567 | 66.452 | 45.295 | 81.453
| 34.2986 | 307.606 | 50.541 | 66.409 | 45.269 | 81.398
| 34.3056 | 307.416 | 50.474 | 66.35 | 45.214 | 81.312
| 34.3125 | 309.656 | 50.583 | 66.415 | 45.304 | 81.409
| 34.3194 | 308.337 | 50.567 | 66.396 | 45.288 | 81.38
| 34.3264 | 312.946 | 50.611 | 66.403 | 45.3 | 81.406
| 34.3333 | 312.63 | 50.783 | 66.552 | 45.462 | 81.593
| 34.3403 | 311.367 | 50.854 | 66.613 | 45.506 | 81.687
| 34.3472 | 313.706 | 50.861 | 66.637 | 45.509 | 81.727
| 34.3542 | 313.05 | 50.949 | 66.709 | 45.576 | 81.834
| 34.3611 | 313.383 | 51.007 | 66.775 | 45.616 | 81.923
| 34.3681 | 312.469 | 51.052 | 66.833 | 45.653 | 81.998
| 34.375 | 311.657 | 51.041 | 66.842 | 45.639 | 82.016
| 34.3819 | 313.216 | 51.045 | 66.859 | 45.642 | 82.046
| 34.3889 | 313.094 | 51.096 | 66.922 | 45.696 | 82.123
| 34.3958 | 312.162 | 51.093 | 66.934 | 45.687 | 82.138
| 34.4028 | 311.907 | 51.066 | 66.931 | 45.668 | 82.135
| 34.4097 | 312.894 | 51.098 | 66.96 | 45.689 | 82.177
| 34.4167 | 309.613 | 51.016 | 66.917 | 45.631 | 82.11
| 34.4236 | 308.939 | 50.888 | 66.815 | 45.515 | 81.978
| 34.4306 | 308.502 | 50.786 | 66.731 | 45.443 | 81.853
| 34.4375 | 307.101 | 50.691 | 66.645 | 45.368 | 81.733
| 34.4444 | 311.61 | 50.839 | 66.736 | 45.488 | 81.865
| 34.4514 | 311.927 | 50.928 | 66.796 | 45.554 | 81.938
| 34.4583 | 311.943 | 50.961 | 66.829 | 45.577 | 81.98
| 34.4653 | 311.63 | 50.999 | 66.862 | 45.603 | 82.029
| 34.4722 | 315.042 | 51.011 | 66.874 | 45.605 | 82.056
| 34.4792 | 310.798 | 50.991 | 66.869 | 45.591 | 82.043
| 34.4861 | 310.361 | 50.965 | 66.858 | 45.571 | 82.028
| 34.4931 | 311.407 | 50.973 | 66.864 | 45.574 | 82.04
| 34.5 | 311.256 | 51.016 | 66.9 | 45.608 | 82.077
| 34.5069 | 311.447 | 51.028 | 66.918 | 45.622 | 82.107
| 34.5139 | 311.721 | 51.042 | 66.932 | 45.63 | 82.129
| 34.5208 | 309.895 | 50.944 | 66.866 | 45.552 | 82.037
| 34.5278 | 310.004 | 50.893 | 66.819 | 45.51 | 81.974
| 34.5347 | 309.671 | 50.857 | 66.78 | 45.475 | 81.92
| 34.5417 | 310.386 | 50.869 | 66.784 | 45.487 | 81.926
| 34.5486 | 310.549 | 50.868 | 66.777 | 45.481 | 81.913
| 34.5556 | 311.374 | 50.919 | 66.809 | 45.525 | 81.962
| 34.5625 | 311.755 | 50.947 | 66.823 | 45.539 | 81.983
| 34.5694 | 310.665 | 50.972 | 66.846 | 45.56 | 82.011
| 34.5764 | 311.911 | 50.996 | 66.867 | 45.578 | 82.049
| 34.5833 | 311.607 | 51.018 | 66.892 | 45.592 | 82.078
| 34.5903 | 312.544 | 51.038 | 66.91 | 45.605 | 82.114
| 34.5972 | 311.888 | 51.031 | 66.91 | 45.605 | 82.116
| 34.6042 | 312.076 | 51.083 | 66.952 | 45.634 | 82.176
| 34.6111 | 312.492 | 51.113 | 66.989 | 45.664 | 82.222
| 34.6181 | 312.417 | 51.159 | 67.033 | 45.695 | 82.281
| 34.625 | 312.286 | 51.127 | 67.025 | 45.674 | 82.274
| 34.6319 | 312.214 | 51.134 | 67.031 | 45.672 | 82.293
| 34.6389 | 311.978 | 51.135 | 67.04 | 45.678 | 82.307
| 34.6458 | 313.069 | 51.14 | 67.048 | 45.677 | 82.313
| 34.6528 | 312.745 | 51.167 | 67.071 | 45.687 | 82.347
| 34.6597 | 312.509 | 51.217 | 67.115 | 45.728 | 82.411
| 34.6667 | 313.746 | 51.246 | 67.145 | 45.749 | 82.457
| 34.6736 | 313.3 | 51.282 | 67.183 | 45.773 | 82.516
| 34.6806 | 312.446 | 51.231 | 67.156 | 45.736 | 82.484
| 34.6875 | 311.451 | 51.174 | 67.124 | 45.691 | 82.438
| 34.6944 | 309.692 | 51.082 | 67.056 | 45.618 | 82.339
| 34.7014 | 309.593 | 50.964 | 66.95 | 45.523 | 82.205
| 34.7083 | 308.582 | 50.891 | 66.875 | 45.46 | 82.101
| 34.7153 | 309.46 | 50.867 | 66.83 | 45.44 | 82.048
| 34.7222 | 311.461 | 50.852 | 66.801 | 45.422 | 82.011
| 34.7292 | 310.538 | 50.877 | 66.804 | 45.45 | 82.016
| 34.7361 | 311.899 | 50.913 | 66.817 | 45.47 | 82.041
| 34.7431 | 312.316 | 50.999 | 66.88 | 45.542 | 82.127
| 34.75 | 313.548 | 51.075 | 66.934 | 45.588 | 82.205
| 34.7569 | 313.256 | 51.166 | 67.007 | 45.658 | 82.32
| 34.7639 | 313.423 | 51.199 | 67.048 | 45.685 | 82.38
| 34.7708 | 314.328 | 51.234 | 67.088 | 45.707 | 82.442
| 34.7778 | 310.361 | 51.12 | 67.015 | 45.618 | 82.348
| 34.7847 | 310.157 | 50.995 | 66.916 | 45.511 | 82.221
| 34.7917 | 311.257 | 50.965 | 66.878 | 45.487 | 82.175
| 34.7986 | 311.048 | 50.963 | 66.867 | 45.486 | 82.167
| 34.8056 | 310.773 | 50.969 | 66.862 | 45.491 | 82.161
| 34.8125 | 311.209 | 50.988 | 66.863 | 45.501 | 82.17
| 34.8194 | 311.184 | 50.994 | 66.864 | 45.51 | 82.176
| 34.8264 | 311.476 | 51.019 | 66.876 | 45.518 | 82.199
| 34.8333 | 310.508 | 51.001 | 66.864 | 45.504 | 82.182
| 34.8403 | 311.663 | 51 | 66.854 | 45.501 | 82.18
| 34.8472 | 311.461 | 50.983 | 66.832 | 45.485 | 82.161
| 34.8542 | 312.679 | 51.012 | 66.849 | 45.504 | 82.197
| 34.8611 | 309.565 | 51.033 | 66.881 | 45.54 | 82.232
| 34.8681 | 309.066 | 50.878 | 66.753 | 45.399 | 82.067
| 34.875 | 308.605 | 50.794 | 66.671 | 45.331 | 81.963
| 34.8819 | 309.422 | 50.763 | 66.62 | 45.296 | 81.902
| 34.8889 | 310.249 | 50.8 | 66.634 | 45.328 | 81.923
| 34.8958 | 307.485 | 50.716 | 66.557 | 45.265 | 81.826
| 34.9028 | 310.519 | 50.763 | 66.566 | 45.292 | 81.852
| 34.9097 | 310.315 | 50.838 | 66.611 | 45.356 | 81.925
| 34.9167 | 311.625 | 50.875 | 66.63 | 45.381 | 81.959
| 34.9236 | 310.111 | 50.901 | 66.65 | 45.393 | 81.989
| 34.9306 | 310.755 | 50.872 | 66.628 | 45.373 | 81.974
| 34.9375 | 311.384 | 50.901 | 66.643 | 45.39 | 82.008
| 34.9444 | 312.022 | 50.941 | 66.669 | 45.416 | 82.049
| 34.9514 | 312.6 | 50.993 | 66.711 | 45.464 | 82.124
| 34.9583 | 313.249 | 51.027 | 66.739 | 45.481 | 82.175
| 34.9653 | 310.602 | 50.941 | 66.681 | 45.416 | 82.11
| 34.9722 | 310.624 | 50.938 | 66.676 | 45.405 | 82.104
| 34.9792 | 312.58 | 50.968 | 66.694 | 45.426 | 82.135
| 34.9861 | 309.95 | 50.934 | 66.673 | 45.408 | 82.116
| 34.9931 | 311.573 | 50.953 | 66.678 | 45.407 | 82.134
| 35 | 309.944 | 50.967 | 66.689 | 45.431 | 82.156
| 35.0069 | 310.99 | 50.915 | 66.639 | 45.378 | 82.107
| 35.0139 | 311.841 | 50.964 | 66.671 | 45.416 | 82.158
| 35.0208 | 311.3 | 50.975 | 66.68 | 45.425 | 82.174
| 35.0278 | 312.343 | 50.952 | 66.664 | 45.403 | 82.162
| 35.0347 | 312.852 | 51.015 | 66.704 | 45.452 | 82.233
| 35.0417 | 310.505 | 51.022 | 66.715 | 45.463 | 82.254
| 35.0486 | 311.028 | 50.994 | 66.697 | 45.43 | 82.243
| 35.0556 | 311.624 | 50.965 | 66.666 | 45.405 | 82.209
| 35.0625 | 311.811 | 50.961 | 66.658 | 45.399 | 82.209
| 35.0694 | 310.76 | 50.969 | 66.657 | 45.406 | 82.214
| 35.0764 | 312.099 | 50.999 | 66.679 | 45.426 | 82.253
| 35.0833 | 311.752 | 51.031 | 66.703 | 45.451 | 82.299
| 35.0903 | 312.466 | 51.048 | 66.714 | 45.458 | 82.325
| 35.0972 | 312.725 | 51.074 | 66.736 | 45.478 | 82.362
| 35.1042 | 313.407 | 51.135 | 66.784 | 45.528 | 82.443
| 35.1111 | 311.822 | 51.102 | 66.776 | 45.5 | 82.431
| 35.1181 | 312.74 | 51.111 | 66.777 | 45.499 | 82.451
| 35.125 | 313.295 | 51.151 | 66.806 | 45.53 | 82.498
| 35.1319 | 311.614 | 51.147 | 66.816 | 45.528 | 82.514
| 35.1389 | 311.414 | 51.112 | 66.79 | 45.499 | 82.491
| 35.1458 | 312.315 | 51.104 | 66.782 | 45.491 | 82.489
| 35.1528 | 313.004 | 51.112 | 66.779 | 45.492 | 82.499
| 35.1597 | 312.582 | 51.133 | 66.802 | 45.511 | 82.534
| 35.1667 | 312.928 | 51.147 | 66.813 | 45.521 | 82.563
| 35.1736 | 312.821 | 51.153 | 66.815 | 45.521 | 82.575
| 35.1806 | 311.966 | 51.143 | 66.809 | 45.51 | 82.581
| 35.1875 | 311.853 | 51.113 | 66.783 | 45.48 | 82.554
| 35.1944 | 311.493 | 51.092 | 66.765 | 45.467 | 82.541
| 35.2014 | 311.728 | 51.089 | 66.756 | 45.463 | 82.535
| 35.2083 | 312.522 | 51.09 | 66.753 | 45.464 | 82.543
| 35.2153 | 312.44 | 51.107 | 66.76 | 45.472 | 82.559
| 35.2222 | 312.342 | 51.101 | 66.751 | 45.461 | 82.563
| 35.2292 | 311.837 | 51.1 | 66.749 | 45.458 | 82.565
| 35.2361 | 311.795 | 51.101 | 66.745 | 45.457 | 82.568
| 35.2431 | 312.165 | 51.072 | 66.722 | 45.44 | 82.552
| 35.25 | 311.24 | 51.054 | 66.699 | 45.418 | 82.532
| 35.2569 | 311.175 | 51.022 | 66.669 | 45.388 | 82.494
| 35.2639 | 311.988 | 51.008 | 66.645 | 45.373 | 82.471
| 35.2708 | 311.242 | 51.009 | 66.633 | 45.373 | 82.474
| 35.2778 | 311.585 | 50.999 | 66.622 | 45.365 | 82.46
| 35.2847 | 309.941 | 50.92 | 66.555 | 45.299 | 82.379
| 35.2917 | 309.098 | 50.84 | 66.476 | 45.228 | 82.283
| 35.2986 | 308.999 | 50.772 | 66.399 | 45.174 | 82.19
| 35.3056 | 308.672 | 50.733 | 66.351 | 45.143 | 82.126
| 35.3125 | 310.927 | 50.817 | 66.38 | 45.203 | 82.19
| 35.3194 | 309.428 | 50.801 | 66.36 | 45.188 | 82.17
| 35.3264 | 311.017 | 50.783 | 66.319 | 45.164 | 82.14
| 35.3333 | 311.89 | 50.841 | 66.355 | 45.212 | 82.193
| 35.3403 | 312.896 | 50.951 | 66.432 | 45.289 | 82.308
| 35.3472 | 312.666 | 50.986 | 66.459 | 45.319 | 82.359
| 35.3542 | 312.959 | 51.013 | 66.484 | 45.336 | 82.413
| 35.3611 | 312.484 | 51.023 | 66.496 | 45.341 | 82.443
| 35.3681 | 312.814 | 51.035 | 66.5 | 45.339 | 82.47
| 35.375 | 312.662 | 51.001 | 66.482 | 45.312 | 82.45
| 35.3819 | 311.047 | 50.978 | 66.46 | 45.289 | 82.442
| 35.3889 | 311.949 | 50.951 | 66.43 | 45.26 | 82.413
| 35.3958 | 310.562 | 50.895 | 66.391 | 45.225 | 82.366
| 35.4028 | 310.355 | 50.829 | 66.328 | 45.166 | 82.285
| 35.4097 | 308.128 | 50.709 | 66.221 | 45.074 | 82.151
| 35.4167 | 310.808 | 50.649 | 66.141 | 45.011 | 82.062
| 35.4236 | 310.429 | 50.706 | 66.165 | 45.057 | 82.095
| 35.4306 | 309.699 | 50.696 | 66.139 | 45.047 | 82.07
| 35.4375 | 310.273 | 50.703 | 66.123 | 45.051 | 82.067
| 35.4444 | 309.226 | 50.665 | 66.083 | 45.016 | 82.019
| 35.4514 | 309.812 | 50.635 | 66.036 | 44.982 | 81.979
| 35.4583 | 310.675 | 50.63 | 66.012 | 44.972 | 81.959
| 35.4653 | 310.514 | 50.636 | 66.004 | 44.981 | 81.958
| 35.4722 | 310.082 | 50.618 | 65.98 | 44.959 | 81.938
| 35.4792 | 310.458 | 50.618 | 65.96 | 44.953 | 81.928
| 35.4861 | 310.146 | 50.593 | 65.929 | 44.934 | 81.899
| 35.4931 | 310.57 | 50.594 | 65.916 | 44.928 | 81.893
| 35.5 | 310.423 | 50.579 | 65.883 | 44.91 | 81.873
| 35.5069 | 310.013 | 50.565 | 65.866 | 44.9 | 81.855
| 35.5139 | 310.71 | 50.57 | 65.843 | 44.89 | 81.847
| 35.5208 | 310.503 | 50.585 | 65.844 | 44.901 | 81.858
| 35.5278 | 311.203 | 50.598 | 65.845 | 44.904 | 81.872
| 35.5347 | 311.632 | 50.616 | 65.85 | 44.916 | 81.899
| 35.5417 | 312.213 | 50.66 | 65.878 | 44.948 | 81.955
| 35.5486 | 312.247 | 50.706 | 65.91 | 44.984 | 82.014
| 35.5556 | 311.751 | 50.7 | 65.907 | 44.977 | 82.026
| 35.5625 | 312.396 | 50.71 | 65.91 | 44.971 | 82.042
| 35.5694 | 312.057 | 50.71 | 65.91 | 44.971 | 82.058
| 35.5764 | 312.037 | 50.701 | 65.898 | 44.959 | 82.066
| 35.5833 | 311.924 | 50.72 | 65.911 | 44.966 | 82.09
| 35.5903 | 311.655 | 50.709 | 65.902 | 44.957 | 82.098
| 35.5972 | 311.434 | 50.695 | 65.89 | 44.943 | 82.096
| 35.6042 | 311.72 | 50.725 | 65.901 | 44.957 | 82.127
| 35.6111 | 312.29 | 50.753 | 65.923 | 44.981 | 82.17
| 35.6181 | 313.455 | 50.81 | 65.968 | 45.019 | 82.243
| 35.625 | 314.001 | 50.861 | 66.012 | 45.06 | 82.32
| 35.6319 | 310.42 | 50.858 | 66.024 | 45.059 | 82.344
| 35.6389 | 311.166 | 50.761 | 65.947 | 44.96 | 82.26
| 35.6458 | 311.047 | 50.697 | 65.898 | 44.918 | 82.203
| 35.6528 | 310.481 | 50.636 | 65.837 | 44.866 | 82.138
| 35.6597 | 310.525 | 50.593 | 65.787 | 44.825 | 82.082
| 35.6667 | 310.064 | 50.567 | 65.753 | 44.803 | 82.048
| 35.6736 | 310.283 | 50.54 | 65.717 | 44.78 | 82.01
| 35.6806 | 310.581 | 50.505 | 65.676 | 44.744 | 81.961
| 35.6875 | 309.545 | 50.464 | 65.619 | 44.707 | 81.905
| 35.6944 | 309.525 | 50.423 | 65.575 | 44.679 | 81.858
| 35.7014 | 309.933 | 50.394 | 65.533 | 44.643 | 81.812
| 35.7083 | 308.965 | 50.349 | 65.477 | 44.61 | 81.752
| 35.7153 | 308.759 | 50.298 | 65.418 | 44.564 | 81.678
| 35.7222 | 309.93 | 50.288 | 65.38 | 44.552 | 81.653
| 35.7292 | 311.589 | 50.399 | 65.444 | 44.632 | 81.749
| 35.7361 | 312.061 | 50.48 | 65.492 | 44.691 | 81.825
| 35.7431 | 312.212 | 50.514 | 65.516 | 44.712 | 81.879
| 35.75 | 311.26 | 50.517 | 65.521 | 44.71 | 81.902
| 35.7569 | 311.137 | 50.489 | 65.499 | 44.678 | 81.889
| 35.7639 | 311.177 | 50.467 | 65.477 | 44.664 | 81.872
| 35.7708 | 311.455 | 50.49 | 65.485 | 44.673 | 81.893
| 35.7778 | 312.276 | 50.513 | 65.505 | 44.692 | 81.938
| 35.7847 | 312.25 | 50.55 | 65.531 | 44.718 | 81.989
| 35.7917 | 313.032 | 50.562 | 65.539 | 44.729 | 82.021
| 35.7986 | 312.787 | 50.577 | 65.556 | 44.736 | 82.047
| 35.8056 | 313.151 | 50.61 | 65.58 | 44.76 | 82.097
| 35.8125 | 313.086 | 50.652 | 65.615 | 44.784 | 82.156
| 35.8194 | 312.726 | 50.681 | 65.646 | 44.804 | 82.211
| 35.8264 | 312.979 | 50.703 | 65.668 | 44.822 | 82.263
| 35.8333 | 312.365 | 50.698 | 65.669 | 44.81 | 82.271
| 35.8403 | 313.099 | 50.719 | 65.686 | 44.819 | 82.312
| 35.8472 | 313.195 | 50.762 | 65.731 | 44.86 | 82.382
| 35.8542 | 308.055 | 50.77 | 65.759 | 44.88 | 82.423
| 35.8611 | 305.352 | 50.342 | 65.429 | 44.523 | 81.986
| 35.8681 | 309.964 | 50.296 | 65.354 | 44.472 | 81.899
| 35.875 | 311.061 | 50.34 | 65.36 | 44.511 | 81.906
| 35.8819 | 311.616 | 50.387 | 65.368 | 44.548 | 81.93
| 35.8889 | 311.68 | 50.411 | 65.375 | 44.563 | 81.95
| 35.8958 | 312.076 | 50.428 | 65.376 | 44.569 | 81.97
| 35.9028 | 312.005 | 50.453 | 65.381 | 44.589 | 81.992
| 35.9097 | 311.415 | 50.454 | 65.382 | 44.589 | 82.001
| 35.9167 | 311.904 | 50.441 | 65.362 | 44.568 | 81.992
| 35.9236 | 311.555 | 50.45 | 65.365 | 44.574 | 82.003
| 35.9306 | 312.422 | 50.471 | 65.376 | 44.588 | 82.031
| 35.9375 | 312.252 | 50.498 | 65.387 | 44.605 | 82.064
| 35.9444 | 313.259 | 50.527 | 65.411 | 44.625 | 82.104
| 35.9514 | 311.256 | 50.517 | 65.41 | 44.622 | 82.115
| 35.9583 | 310.501 | 50.422 | 65.329 | 44.542 | 82.026
| 35.9653 | 310.99 | 50.342 | 65.261 | 44.477 | 81.942
| 35.9722 | 312.032 | 50.363 | 65.263 | 44.489 | 81.958
| 35.9792 | 312.493 | 50.39 | 65.27 | 44.508 | 81.976
| 35.9861 | 311.601 | 50.393 | 65.264 | 44.517 | 81.982
| 35.9931 | 312.629 | 50.407 | 65.271 | 44.52 | 82
| 36 | 311.858 | 50.421 | 65.274 | 44.534 | 82.02
| 36.0069 | 310.946 | 50.382 | 65.24 | 44.496 | 81.988
| 36.0139 | 311.565 | 50.375 | 65.223 | 44.486 | 81.98
| 36.0208 | 312.955 | 50.403 | 65.235 | 44.506 | 82.014
| 36.0278 | 312.776 | 50.423 | 65.247 | 44.521 | 82.039
| 36.0347 | 312.204 | 50.416 | 65.239 | 44.513 | 82.045
| 36.0417 | 312.231 | 50.406 | 65.225 | 44.502 | 82.039
| 36.0486 | 311.86 | 50.405 | 65.223 | 44.502 | 82.048
| 36.0556 | 311.197 | 50.355 | 65.178 | 44.46 | 81.994
| 36.0625 | 312.062 | 50.351 | 65.153 | 44.452 | 81.991
| 36.0694 | 313.052 | 50.356 | 65.156 | 44.454 | 82.009
| 36.0764 | 312.637 | 50.397 | 65.174 | 44.481 | 82.048
| 36.0833 | 312.406 | 50.424 | 65.192 | 44.508 | 82.085
| 36.0903 | 313.113 | 50.429 | 65.186 | 44.499 | 82.101
| 36.0972 | 313.436 | 50.439 | 65.191 | 44.508 | 82.124
| 36.1042 | 313.884 | 50.478 | 65.218 | 44.537 | 82.179
| 36.1111 | 314.7 | 50.505 | 65.241 | 44.558 | 82.224
| 36.1181 | 313.806 | 50.578 | 65.3 | 44.617 | 82.324
| 36.125 | 314.293 | 50.588 | 65.307 | 44.623 | 82.357
| 36.1319 | 313.983 | 50.586 | 65.312 | 44.613 | 82.38
| 36.1389 | 313.927 | 50.568 | 65.303 | 44.597 | 82.381
| 36.1458 | 314.43 | 50.601 | 65.328 | 44.629 | 82.438
| 36.1528 | 311.575 | 50.526 | 65.279 | 44.57 | 82.376
| 36.1597 | 311.071 | 50.43 | 65.19 | 44.48 | 82.279
| 36.1667 | 310.848 | 50.361 | 65.123 | 44.426 | 82.202
| 36.1736 | 311.406 | 50.338 | 65.084 | 44.407 | 82.168
| 36.1806 | 312.284 | 50.335 | 65.064 | 44.409 | 82.152
| 36.1875 | 312.18 | 50.338 | 65.045 | 44.406 | 82.15
| 36.1944 | 312.105 | 50.358 | 65.037 | 44.417 | 82.16
| 36.2014 | 312.774 | 50.384 | 65.042 | 44.437 | 82.187
| 36.2083 | 312.106 | 50.366 | 65.021 | 44.422 | 82.177
| 36.2153 | 311.833 | 50.343 | 64.99 | 44.397 | 82.157
| 36.2222 | 311.74 | 50.326 | 64.964 | 44.384 | 82.142
| 36.2292 | 312.027 | 50.303 | 64.928 | 44.36 | 82.117
| 36.2361 | 311.197 | 50.272 | 64.891 | 44.338 | 82.087
| 36.2431 | 311.059 | 50.244 | 64.849 | 44.309 | 82.052
| 36.25 | 311.323 | 50.201 | 64.8 | 44.282 | 82.008
| 36.2569 | 310.737 | 50.183 | 64.758 | 44.264 | 81.975
| 36.2639 | 311.139 | 50.151 | 64.719 | 44.237 | 81.936
| 36.2708 | 311.1 | 50.122 | 64.667 | 44.211 | 81.896
| 36.2778 | 309.641 | 50.082 | 64.614 | 44.176 | 81.846
| 36.2847 | 309.682 | 50.016 | 64.536 | 44.12 | 81.761
| 36.2917 | 310.064 | 49.983 | 64.479 | 44.09 | 81.713
| 36.2986 | 310.042 | 49.943 | 64.418 | 44.061 | 81.644
| 36.3056 | 309.645 | 49.898 | 64.346 | 44.014 | 81.577
| 36.3125 | 308.957 | 49.843 | 64.276 | 43.98 | 81.499
| 36.3194 | 312.58 | 49.976 | 64.335 | 44.074 | 81.621
| 36.3264 | 309.208 | 49.904 | 64.264 | 44.018 | 81.545
| 36.3333 | 308.427 | 49.829 | 64.179 | 43.953 | 81.46
| 36.3403 | 309.072 | 49.776 | 64.102 | 43.904 | 81.389
| 36.3472 | 305.683 | 49.681 | 64.004 | 43.836 | 81.267
| 36.3542 | 306.262 | 49.559 | 63.864 | 43.728 | 81.104
| 36.3611 | 305.568 | 49.472 | 63.746 | 43.658 | 80.986
| 36.3681 | 306.093 | 49.393 | 63.632 | 43.592 | 80.861
| 36.375 | 306.554 | 49.363 | 63.559 | 43.57 | 80.788
| 36.3819 | 306.344 | 49.32 | 63.475 | 43.532 | 80.701
| 36.3889 | 305.756 | 49.262 | 63.377 | 43.481 | 80.6
| 36.3958 | 306.215 | 49.233 | 63.306 | 43.451 | 80.533
| 36.4028 | 310.743 | 49.248 | 63.257 | 43.441 | 80.514
| 36.4097 | 314.001 | 49.6 | 63.486 | 43.732 | 80.861
| 36.4167 | 313.818 | 49.818 | 63.644 | 43.899 | 81.117
| 36.4236 | 313.08 | 49.909 | 63.724 | 43.97 | 81.267
| 36.4306 | 313.15 | 49.92 | 63.743 | 43.972 | 81.333
| 36.4375 | 312.217 | 49.948 | 63.761 | 43.984 | 81.4
| 36.4444 | 311.526 | 49.919 | 63.747 | 43.961 | 81.413
| 36.4514 | 310.938 | 49.883 | 63.718 | 43.926 | 81.402
| 36.4583 | 311.74 | 49.871 | 63.694 | 43.918 | 81.422
| 36.4653 | 311.265 | 49.87 | 63.683 | 43.912 | 81.433
| 36.4722 | 312.002 | 49.874 | 63.668 | 43.91 | 81.453
| 36.4792 | 310.448 | 49.828 | 63.622 | 43.878 | 81.424
| 36.4861 | 314.423 | 49.776 | 63.564 | 43.83 | 81.38
| 36.4931 | 306.236 | 49.717 | 63.513 | 43.797 | 81.328
| 36.5 | 306.523 | 49.468 | 63.287 | 43.588 | 81.066
| 36.5069 | 306.709 | 49.365 | 63.152 | 43.502 | 80.92
| 36.5139 | 305.912 | 49.271 | 63.022 | 43.422 | 80.769
| 36.5208 | 310.847 | 49.232 | 62.922 | 43.375 | 80.68
| 36.5278 | 309.832 | 49.408 | 63.016 | 43.531 | 80.84
| 36.5347 | 311.207 | 49.527 | 63.072 | 43.618 | 80.951
| 36.5417 | 310.407 | 49.577 | 63.092 | 43.657 | 81.022
| 36.5486 | 310.628 | 49.59 | 63.08 | 43.658 | 81.05
| 36.5556 | 310.763 | 49.588 | 63.061 | 43.652 | 81.068
| 36.5625 | 310.071 | 49.56 | 63.024 | 43.628 | 81.055
| 36.5694 | 309.89 | 49.513 | 62.963 | 43.588 | 81.011
| 36.5764 | 310.799 | 49.538 | 62.947 | 43.591 | 81.033
| 36.5833 | 310.636 | 49.562 | 62.946 | 43.615 | 81.068
| 36.5903 | 310.517 | 49.56 | 62.913 | 43.606 | 81.074
| 36.5972 | 309.937 | 49.554 | 62.892 | 43.597 | 81.073
| 36.6042 | 311.026 | 49.556 | 62.861 | 43.6 | 81.09
| 36.6111 | 312.907 | 49.656 | 62.913 | 43.667 | 81.202
| 36.6181 | 313.648 | 49.76 | 62.975 | 43.746 | 81.32
| 36.625 | 312.87 | 49.795 | 63.003 | 43.784 | 81.401
| 36.6319 | 313.131 | 49.819 | 63.011 | 43.789 | 81.455
| 36.6389 | 313.685 | 49.865 | 63.034 | 43.823 | 81.535
| 36.6458 | 313.719 | 49.881 | 63.044 | 43.838 | 81.59
| 36.6528 | 313.768 | 49.908 | 63.052 | 43.848 | 81.638
| 36.6597 | 313.589 | 49.923 | 63.056 | 43.861 | 81.69
| 36.6667 | 313.964 | 49.94 | 63.06 | 43.872 | 81.737
| 36.6736 | 313.937 | 49.958 | 63.061 | 43.881 | 81.785
| 36.6806 | 315.115 | 49.99 | 63.076 | 43.904 | 81.844
| 36.6875 | 314.711 | 50.014 | 63.08 | 43.921 | 81.896
| 36.6944 | 314.494 | 49.997 | 63.064 | 43.906 | 81.914
| 36.7014 | 312.542 | 49.955 | 63.016 | 43.875 | 81.892
| 36.7083 | 312.708 | 49.928 | 62.976 | 43.848 | 81.879
| 36.7153 | 312.858 | 49.891 | 62.923 | 43.814 | 81.85
| 36.7222 | 311.468 | 49.804 | 62.837 | 43.752 | 81.764
| 36.7292 | 308.599 | 49.687 | 62.712 | 43.658 | 81.644
| 36.7361 | 311.621 | 49.676 | 62.664 | 43.641 | 81.611
| 36.7431 | 311.054 | 49.634 | 62.587 | 43.611 | 81.557
| 36.75 | 309.974 | 49.568 | 62.494 | 43.553 | 81.466
| 36.7569 | 312.829 | 49.66 | 62.514 | 43.62 | 81.545
| 36.7639 | 312.401 | 49.685 | 62.502 | 43.636 | 81.57
| 36.7708 | 312.217 | 49.685 | 62.477 | 43.644 | 81.576
| 36.7778 | 312.517 | 49.684 | 62.444 | 43.632 | 81.581
| 36.7847 | 313.079 | 49.704 | 62.428 | 43.651 | 81.609
| 36.7917 | 312.574 | 49.715 | 62.408 | 43.651 | 81.625
| 36.7986 | 312.432 | 49.69 | 62.362 | 43.631 | 81.613
| 36.8056 | 312.948 | 49.69 | 62.331 | 43.625 | 81.61
| 36.8125 | 313.185 | 49.714 | 62.322 | 43.643 | 81.645
| 36.8194 | 312.764 | 49.719 | 62.306 | 43.654 | 81.659
| 36.8264 | 313.697 | 49.741 | 62.299 | 43.665 | 81.695
| 36.8333 | 314.56 | 49.79 | 62.312 | 43.705 | 81.764
| 36.8403 | 314.628 | 49.839 | 62.324 | 43.742 | 81.83
| 36.8472 | 314.59 | 49.89 | 62.35 | 43.777 | 81.902
| 36.8542 | 314.889 | 49.924 | 62.361 | 43.808 | 81.969
| 36.8611 | 314.295 | 49.951 | 62.366 | 43.822 | 82.014
| 36.8681 | 314.943 | 49.929 | 62.341 | 43.806 | 82.029
| 36.875 | 311.106 | 49.871 | 62.29 | 43.768 | 81.991
| 36.8819 | 311.342 | 49.691 | 62.116 | 43.608 | 81.803
| 36.8889 | 311.538 | 49.66 | 62.054 | 43.584 | 81.763
| 36.8958 | 312.4 | 49.652 | 62.005 | 43.584 | 81.738
| 36.9028 | 313.553 | 49.692 | 61.997 | 43.614 | 81.773
| 36.9097 | 312.378 | 49.709 | 61.987 | 43.631 | 81.79
| 36.9167 | 312.853 | 49.688 | 61.933 | 43.606 | 81.766
| 36.9236 | 312.85 | 49.693 | 61.906 | 43.607 | 81.771
| 36.9306 | 314.193 | 49.729 | 61.901 | 43.631 | 81.811
| 36.9375 | 311.091 | 49.618 | 61.798 | 43.549 | 81.705
| 36.9444 | 311.291 | 49.56 | 61.715 | 43.498 | 81.636
| 36.9514 | 311.625 | 49.558 | 61.673 | 43.497 | 81.621
| 36.9583 | 311.645 | 49.559 | 61.636 | 43.498 | 81.615
| 36.9653 | 312.656 | 49.566 | 61.607 | 43.495 | 81.619
| 36.9722 | 312.423 | 49.61 | 61.603 | 43.538 | 81.656
| 36.9792 | 312.9 | 49.659 | 61.61 | 43.575 | 81.712
| 36.9861 | 313.791 | 49.692 | 61.617 | 43.595 | 81.758
| 36.9931 | 313.364 | 49.73 | 61.621 | 43.623 | 81.811
| 37 | 312.574 | 49.691 | 61.577 | 43.595 | 81.791
| 37.0069 | 311.681 | 49.655 | 61.513 | 43.555 | 81.76
| 37.0139 | 312.391 | 49.618 | 61.458 | 43.525 | 81.719
| 37.0208 | 311.827 | 49.561 | 61.382 | 43.484 | 81.664
| 37.0278 | 312.515 | 49.561 | 61.344 | 43.474 | 81.654
| 37.0347 | 301.912 | 49.535 | 61.321 | 43.491 | 81.64
| 37.0417 | 314.151 | 49.588 | 61.289 | 43.495 | 81.673
| 37.0486 | 314.45 | 49.658 | 61.319 | 43.555 | 81.748
| 37.0556 | 313.005 | 49.658 | 61.297 | 43.556 | 81.766
| 37.0625 | 312.564 | 49.631 | 61.256 | 43.534 | 81.753
| 37.0694 | 312.89 | 49.623 | 61.221 | 43.519 | 81.745
| 37.0764 | 312.629 | 49.592 | 61.17 | 43.497 | 81.724
| 37.0833 | 313.028 | 49.575 | 61.118 | 43.479 | 81.7
| 37.0903 | 312.559 | 49.557 | 61.076 | 43.463 | 81.681
| 37.0972 | 312.667 | 49.554 | 61.037 | 43.461 | 81.673
| 37.1042 | 314.025 | 49.581 | 61.026 | 43.484 | 81.706
| 37.1111 | 312.491 | 49.599 | 61.013 | 43.494 | 81.729
| 37.1181 | 314.036 | 49.643 | 61.021 | 43.521 | 81.779
| 37.125 | 314.106 | 49.667 | 61.015 | 43.542 | 81.814
| 37.1319 | 313.391 | 49.684 | 61.008 | 43.561 | 81.842
| 37.1389 | 313.726 | 49.707 | 61.003 | 43.576 | 81.885
| 37.1458 | 314.204 | 49.709 | 60.984 | 43.576 | 81.9
| 37.1528 | 313.379 | 49.688 | 60.942 | 43.553 | 81.885
| 37.1597 | 314.731 | 49.649 | 60.882 | 43.519 | 81.858
| 37.1667 | 313.614 | 49.67 | 60.869 | 43.538 | 81.877
| 37.1736 | 313.281 | 49.662 | 60.835 | 43.529 | 81.876
| 37.1806 | 313.684 | 49.636 | 60.787 | 43.503 | 81.852
| 37.1875 | 312.572 | 49.597 | 60.734 | 43.476 | 81.817
| 37.1944 | 313.001 | 49.567 | 60.671 | 43.451 | 81.787
| 37.2014 | 312.101 | 49.516 | 60.603 | 43.408 | 81.736
| 37.2083 | 312.336 | 49.487 | 60.54 | 43.381 | 81.693
| 37.2153 | 314.406 | 49.537 | 60.54 | 43.425 | 81.74
| 37.2222 | 313.866 | 49.583 | 60.545 | 43.451 | 81.781
| 37.2292 | 314.294 | 49.602 | 60.531 | 43.466 | 81.813
| 37.2361 | 313.221 | 49.607 | 60.508 | 43.47 | 81.831
| 37.2431 | 313.502 | 49.599 | 60.471 | 43.463 | 81.826
| 37.25 | 313.542 | 49.585 | 60.433 | 43.445 | 81.814
| 37.2569 | 312.361 | 49.556 | 60.384 | 43.419 | 81.788
| 37.2639 | 310.912 | 49.498 | 60.312 | 43.375 | 81.733
| 37.2708 | 311.469 | 49.43 | 60.226 | 43.324 | 81.666
| 37.2778 | 311.297 | 49.377 | 60.139 | 43.278 | 81.591
| 37.2847 | 307.919 | 49.245 | 60.003 | 43.173 | 81.443
| 37.2917 | 307.337 | 49.084 | 59.831 | 43.041 | 81.242
| 37.2986 | 307.992 | 48.973 | 59.676 | 42.952 | 81.081
| 37.3056 | 309.282 | 48.947 | 59.597 | 42.931 | 81.003
| 37.3125 | 309.07 | 48.946 | 59.526 | 42.926 | 80.961
| 37.3194 | 308.452 | 48.894 | 59.436 | 42.885 | 80.873
| 37.3264 | 307.845 | 48.817 | 59.328 | 42.826 | 80.758
| 37.3333 | 306.349 | 48.722 | 59.196 | 42.748 | 80.62
| 37.3403 | 305.516 | 48.614 | 59.05 | 42.656 | 80.462
| 37.3472 | 308.965 | 48.572 | 58.934 | 42.602 | 80.357
| 37.3542 | 310.839 | 48.735 | 59.005 | 42.743 | 80.486
| 37.3611 | 309.438 | 48.783 | 58.995 | 42.78 | 80.515
| 37.3681 | 308.326 | 48.773 | 58.953 | 42.762 | 80.504
| 37.375 | 311.435 | 48.765 | 58.901 | 42.743 | 80.484
| 37.3819 | 312.084 | 48.913 | 58.979 | 42.856 | 80.633
| 37.3889 | 311.153 | 48.971 | 59.001 | 42.909 | 80.713
| 37.3958 | 311.402 | 48.994 | 58.998 | 42.919 | 80.758
| 37.4028 | 310.997 | 49.009 | 58.989 | 42.925 | 80.796
| 37.4097 | 307.345 | 48.954 | 58.948 | 42.899 | 80.765
| 37.4167 | 308.093 | 48.809 | 58.795 | 42.767 | 80.614
| 37.4236 | 307.291 | 48.695 | 58.667 | 42.674 | 80.476
| 37.4306 | 307.186 | 48.614 | 58.553 | 42.612 | 80.367
| 37.4375 | 306.328 | 48.544 | 58.444 | 42.548 | 80.261
| 37.4444 | 305.999 | 48.465 | 58.327 | 42.481 | 80.142
| 37.4514 | 306.873 | 48.408 | 58.233 | 42.437 | 80.051
| 37.4583 | 306.358 | 48.369 | 58.139 | 42.403 | 79.963
| 37.4653 | 306.521 | 48.311 | 58.041 | 42.349 | 79.877
| 37.4722 | 305.887 | 48.28 | 57.964 | 42.327 | 79.812
| 37.4792 | 305.585 | 48.245 | 57.885 | 42.292 | 79.744
| 37.4861 | 306.563 | 48.23 | 57.816 | 42.278 | 79.694
| 37.4931 | 306.524 | 48.218 | 57.763 | 42.267 | 79.664
| 37.5 | 305.06 | 48.203 | 57.702 | 42.252 | 79.63
| 37.5069 | 305.375 | 48.144 | 57.614 | 42.206 | 79.553
| 37.5139 | 305.149 | 48.096 | 57.527 | 42.157 | 79.475
| 37.5208 | 314.502 | 48.439 | 57.719 | 42.405 | 79.798
| 37.5278 | 314.533 | 48.725 | 57.932 | 42.644 | 80.133
| 37.5347 | 309.566 | 48.642 | 57.876 | 42.581 | 80.109
| 37.5417 | 309.963 | 48.632 | 57.858 | 42.562 | 80.144
| 37.5486 | 311.406 | 48.625 | 57.837 | 42.547 | 80.162
| 37.5556 | 310.12 | 48.658 | 57.852 | 42.58 | 80.222
| 37.5625 | 310.127 | 48.64 | 57.82 | 42.558 | 80.221
| 37.5694 | 310.057 | 48.606 | 57.769 | 42.523 | 80.205
| 37.5764 | 309.042 | 48.554 | 57.716 | 42.489 | 80.167
| 37.5833 | 310.997 | 48.574 | 57.69 | 42.498 | 80.187
| 37.5903 | 310.411 | 48.602 | 57.69 | 42.524 | 80.227
| 37.5972 | 309.465 | 48.582 | 57.65 | 42.506 | 80.225
| 37.6042 | 311.226 | 48.607 | 57.637 | 42.517 | 80.25
| 37.6111 | 310.361 | 48.609 | 57.621 | 42.523 | 80.268
| 37.6181 | 311.081 | 48.658 | 57.629 | 42.559 | 80.331
| 37.625 | 311.352 | 48.699 | 57.64 | 42.584 | 80.386
| 37.6319 | 311.631 | 48.718 | 57.634 | 42.598 | 80.433
| 37.6389 | 310.87 | 48.717 | 57.621 | 42.597 | 80.448
| 37.6458 | 310.867 | 48.659 | 57.554 | 42.545 | 80.406
| 37.6528 | 311.276 | 48.671 | 57.532 | 42.552 | 80.422
| 37.6597 | 311.264 | 48.689 | 57.525 | 42.571 | 80.453
| 37.6667 | 311.226 | 48.684 | 57.498 | 42.563 | 80.46
| 37.6736 | 311.273 | 48.663 | 57.46 | 42.546 | 80.449
| 37.6806 | 311.738 | 48.665 | 57.43 | 42.546 | 80.457
| 37.6875 | 311.776 | 48.674 | 57.412 | 42.549 | 80.472
| 37.6944 | 311.825 | 48.68 | 57.394 | 42.555 | 80.487
| 37.7014 | 311.375 | 48.702 | 57.388 | 42.569 | 80.517
| 37.7083 | 310.969 | 48.704 | 57.362 | 42.572 | 80.531
| 37.7153 | 311.437 | 48.692 | 57.325 | 42.552 | 80.528
| 37.7222 | 312.081 | 48.713 | 57.32 | 42.571 | 80.564
| 37.7292 | 311.576 | 48.709 | 57.289 | 42.572 | 80.565
| 37.7361 | 310.059 | 48.577 | 57.17 | 42.463 | 80.436
| 37.7431 | 310.204 | 48.557 | 57.117 | 42.446 | 80.405
| 37.75 | 308.955 | 48.515 | 57.052 | 42.413 | 80.356
| 37.7569 | 309.455 | 48.481 | 56.985 | 42.388 | 80.312
| 37.7639 | 310.556 | 48.464 | 56.934 | 42.368 | 80.282
| 37.7708 | 310.264 | 48.485 | 56.912 | 42.387 | 80.288
| 37.7778 | 311.233 | 48.518 | 56.904 | 42.412 | 80.322
| 37.7847 | 308.876 | 48.58 | 56.934 | 42.471 | 80.389
| 37.7917 | 308.495 | 48.441 | 56.802 | 42.352 | 80.246
| 37.7986 | 309.734 | 48.382 | 56.712 | 42.297 | 80.177
| 37.8056 | 310.69 | 48.398 | 56.684 | 42.306 | 80.176
| 37.8125 | 309.657 | 48.397 | 56.657 | 42.31 | 80.17
| 37.8194 | 310.386 | 48.423 | 56.64 | 42.328 | 80.188
| 37.8264 | 309.37 | 48.403 | 56.595 | 42.308 | 80.171
| 37.8333 | 310.361 | 48.422 | 56.575 | 42.321 | 80.178
| 37.8403 | 309.72 | 48.418 | 56.552 | 42.325 | 80.19
| 37.8472 | 311.654 | 48.473 | 56.561 | 42.365 | 80.24
| 37.8542 | 311.816 | 48.533 | 56.579 | 42.409 | 80.313
| 37.8611 | 307.753 | 48.381 | 56.454 | 42.294 | 80.172
| 37.8681 | 306.275 | 48.25 | 56.32 | 42.184 | 80.026
| 37.875 | 309.944 | 48.332 | 56.333 | 42.247 | 80.094
| 37.8819 | 311.673 | 48.389 | 56.342 | 42.29 | 80.143
| 37.8889 | 314.285 | 48.5 | 56.394 | 42.37 | 80.252
| 37.8958 | 314.748 | 48.7 | 56.531 | 42.545 | 80.486
| 37.9028 | 309.605 | 48.516 | 56.394 | 42.394 | 80.339
| 37.9097 | 310.336 | 48.453 | 56.323 | 42.335 | 80.286
| 37.9167 | 310.755 | 48.45 | 56.293 | 42.33 | 80.277
| 37.9236 | 308.976 | 48.36 | 56.203 | 42.27 | 80.187
| 37.9306 | 308.879 | 48.306 | 56.122 | 42.221 | 80.125
| 37.9375 | 310.196 | 48.323 | 56.093 | 42.231 | 80.122
| 37.9444 | 309.928 | 48.352 | 56.081 | 42.259 | 80.148
| 37.9514 | 311.45 | 48.424 | 56.1 | 42.315 | 80.218
| 37.9583 | 311.161 | 48.466 | 56.116 | 42.351 | 80.282
| 37.9653 | 312.619 | 48.496 | 56.12 | 42.368 | 80.318
| 37.9722 | 309.521 | 48.418 | 56.036 | 42.303 | 80.249
| 37.9792 | 310.984 | 48.409 | 56.008 | 42.299 | 80.244
| 37.9861 | 311.143 | 48.436 | 55.993 | 42.32 | 80.273
| 37.9931 | 311.574 | 48.481 | 56.007 | 42.355 | 80.329
| 38 | 309.901 | 48.441 | 55.954 | 42.328 | 80.308
| 38.0069 | 310.629 | 48.405 | 55.902 | 42.29 | 80.269
| 38.0139 | 310.144 | 48.398 | 55.871 | 42.293 | 80.262
| 38.0208 | 309.639 | 48.379 | 55.828 | 42.278 | 80.239
| 38.0278 | 309.722 | 48.369 | 55.787 | 42.268 | 80.227
| 38.0347 | 309.179 | 48.358 | 55.748 | 42.255 | 80.213
| 38.0417 | 309.814 | 48.324 | 55.694 | 42.228 | 80.177
| 38.0486 | 309.867 | 48.286 | 55.634 | 42.206 | 80.138
| 38.0556 | 309.265 | 48.277 | 55.592 | 42.193 | 80.118
| 38.0625 | 309.843 | 48.262 | 55.551 | 42.188 | 80.092
| 38.0694 | 308.759 | 48.248 | 55.508 | 42.167 | 80.068
| 38.0764 | 309.501 | 48.274 | 55.496 | 42.194 | 80.093
| 38.0833 | 310.126 | 48.292 | 55.475 | 42.204 | 80.108
| 38.0903 | 310.314 | 48.304 | 55.456 | 42.208 | 80.119
| 38.0972 | 309.434 | 48.317 | 55.438 | 42.218 | 80.134
| 38.1042 | 309.978 | 48.287 | 55.389 | 42.193 | 80.108
| 38.1111 | 309.817 | 48.275 | 55.351 | 42.185 | 80.093
| 38.1181 | 310.38 | 48.306 | 55.339 | 42.206 | 80.126
| 38.125 | 311.077 | 48.335 | 55.34 | 42.23 | 80.163
| 38.1319 | 310.412 | 48.366 | 55.338 | 42.254 | 80.202
| 38.1389 | 311.017 | 48.374 | 55.319 | 42.258 | 80.222
| 38.1458 | 311.963 | 48.396 | 55.313 | 42.276 | 80.254
| 38.1528 | 312.045 | 48.44 | 55.32 | 42.305 | 80.312
| 38.1597 | 312.511 | 48.46 | 55.317 | 42.317 | 80.349
| 38.1667 | 312.168 | 48.478 | 55.31 | 42.336 | 80.385
| 38.1736 | 311.564 | 48.479 | 55.289 | 42.334 | 80.403
| 38.1806 | 311.391 | 48.475 | 55.267 | 42.329 | 80.413
| 38.1875 | 311.203 | 48.477 | 55.242 | 42.332 | 80.426
| 38.1944 | 310.264 | 48.435 | 55.189 | 42.301 | 80.394
| 38.2014 | 309.394 | 48.37 | 55.113 | 42.25 | 80.333
| 38.2083 | 309.076 | 48.305 | 55.028 | 42.196 | 80.259
| 38.2153 | 309.222 | 48.27 | 54.967 | 42.163 | 80.211
| 38.2222 | 308.884 | 48.223 | 54.892 | 42.127 | 80.147
| 38.2292 | 310 | 48.221 | 54.847 | 42.121 | 80.123
| 38.2361 | 308.595 | 48.175 | 54.777 | 42.09 | 80.074
| 38.2431 | 310.248 | 48.179 | 54.737 | 42.083 | 80.059
| 38.25 | 309.514 | 48.218 | 54.732 | 42.114 | 80.087
| 38.2569 | 310.352 | 48.235 | 54.712 | 42.132 | 80.102
| 38.2639 | 309.746 | 48.256 | 54.699 | 42.142 | 80.124
| 38.2708 | 308.226 | 48.202 | 54.634 | 42.103 | 80.077
| 38.2778 | 307.767 | 48.102 | 54.524 | 42.02 | 79.972
| 38.2847 | 307.76 | 48.012 | 54.411 | 41.942 | 79.852
| 38.2917 | 307.138 | 47.937 | 54.315 | 41.885 | 79.752
| 38.2986 | 306.579 | 47.9 | 54.239 | 41.853 | 79.691
| 38.3056 | 309.022 | 47.992 | 54.254 | 41.922 | 79.753
| 38.3125 | 308.475 | 48.05 | 54.263 | 41.968 | 79.803
| 38.3194 | 308.255 | 48.028 | 54.221 | 41.947 | 79.784
| 38.3264 | 308.031 | 48.001 | 54.17 | 41.928 | 79.757
| 38.3333 | 310.188 | 47.942 | 54.085 | 41.869 | 79.686
| 38.3403 | 312.175 | 48.094 | 54.165 | 41.988 | 79.832
| 38.3472 | 312.927 | 48.245 | 54.26 | 42.104 | 80.004
| 38.3542 | 312.997 | 48.322 | 54.304 | 42.162 | 80.115
| 38.3611 | 312.204 | 48.368 | 54.328 | 42.194 | 80.195
| 38.3681 | 309.177 | 48.388 | 54.342 | 42.219 | 80.261
| 38.375 | 309.501 | 48.26 | 54.225 | 42.103 | 80.15
| 38.3819 | 309.269 | 48.194 | 54.146 | 42.047 | 80.092
| 38.3889 | 308.446 | 48.142 | 54.079 | 42.01 | 80.043
| 38.3958 | 308.998 | 48.1 | 54.014 | 41.972 | 79.987
| 38.4028 | 308.242 | 48.05 | 53.944 | 41.933 | 79.929
| 38.4097 | 308.598 | 48.024 | 53.89 | 41.909 | 79.883
| 38.4167 | 308.87 | 47.997 | 53.825 | 41.884 | 79.845
| 38.4236 | 308.282 | 47.965 | 53.766 | 41.86 | 79.798
| 38.4306 | 308.349 | 47.928 | 53.693 | 41.824 | 79.742
| 38.4375 | 308.304 | 47.918 | 53.651 | 41.817 | 79.719
| 38.4444 | 308.251 | 47.898 | 53.609 | 41.801 | 79.694
| 38.4514 | 308.484 | 47.91 | 53.572 | 41.802 | 79.692
| 38.4583 | 308.165 | 47.892 | 53.524 | 41.783 | 79.66
| 38.4653 | 308.015 | 47.867 | 53.473 | 41.759 | 79.62
| 38.4722 | 311.177 | 47.928 | 53.471 | 41.804 | 79.682
| 38.4792 | 312.263 | 48.087 | 53.563 | 41.932 | 79.846
| 38.4861 | 312.121 | 48.165 | 53.604 | 41.99 | 79.956
| 38.4931 | 312.13 | 48.237 | 53.642 | 42.045 | 80.063
| 38.5 | 312.342 | 48.276 | 53.659 | 42.067 | 80.134
| 38.5069 | 312.824 | 48.299 | 53.666 | 42.086 | 80.197
| 38.5139 | 312.616 | 48.331 | 53.671 | 42.102 | 80.258
| 38.5208 | 313.081 | 48.344 | 53.665 | 42.114 | 80.303
| 38.5278 | 313.599 | 48.367 | 53.666 | 42.123 | 80.352
| 38.5347 | 309.44 | 48.248 | 53.558 | 42.03 | 80.257
| 38.5417 | 308.012 | 48.132 | 53.441 | 41.935 | 80.141
| 38.5486 | 308.976 | 48.039 | 53.337 | 41.86 | 80.038
| 38.5556 | 309.466 | 47.998 | 53.269 | 41.825 | 79.974
| 38.5625 | 308.605 | 47.942 | 53.183 | 41.784 | 79.903
| 38.5694 | 308.324 | 47.9 | 53.108 | 41.742 | 79.836
| 38.5764 | 306.784 | 47.839 | 53.023 | 41.699 | 79.761
| 38.5833 | 308.43 | 47.794 | 52.944 | 41.655 | 79.684
| 38.5903 | 308.397 | 47.781 | 52.89 | 41.639 | 79.641
| 38.5972 | 308.545 | 47.787 | 52.856 | 41.641 | 79.633
| 38.6042 | 310.052 | 47.833 | 52.85 | 41.675 | 79.665
| 38.6111 | 305.661 | 47.709 | 52.727 | 41.572 | 79.528
| 38.6181 | 306.334 | 47.635 | 52.633 | 41.506 | 79.435
| 38.625 | 310.04 | 47.715 | 52.642 | 41.563 | 79.485
| 38.6319 | 310.615 | 47.804 | 52.674 | 41.629 | 79.567
| 38.6389 | 312.302 | 47.928 | 52.74 | 41.728 | 79.708
| 38.6458 | 312.868 | 48.035 | 52.801 | 41.803 | 79.844
| 38.6528 | 312.23 | 48.098 | 52.837 | 41.849 | 79.94
| 38.6597 | 312.586 | 48.124 | 52.843 | 41.863 | 80.012
| 38.6667 | 312.626 | 48.161 | 52.863 | 41.889 | 80.084
| 38.6736 | 312.719 | 48.192 | 52.875 | 41.914 | 80.149
| 38.6806 | 312.21 | 48.201 | 52.867 | 41.913 | 80.188
| 38.6875 | 312.485 | 48.223 | 52.871 | 41.933 | 80.241
| 38.6944 | 312.549 | 48.205 | 52.847 | 41.916 | 80.248
| 38.7014 | 314.089 | 48.261 | 52.871 | 41.952 | 80.334
| 38.7083 | 312.277 | 48.287 | 52.873 | 41.969 | 80.379
| 38.7153 | 313.45 | 48.272 | 52.852 | 41.957 | 80.398
| 38.7222 | 312.925 | 48.264 | 52.833 | 41.957 | 80.415
| 38.7292 | 310.059 | 48.204 | 52.77 | 41.906 | 80.37
| 38.7361 | 309.745 | 48.111 | 52.673 | 41.826 | 80.28
| 38.7431 | 310.696 | 48.062 | 52.615 | 41.784 | 80.226
| 38.75 | 311.382 | 48.052 | 52.575 | 41.778 | 80.21
| 38.7569 | 311.864 | 48.084 | 52.571 | 41.803 | 80.241
| 38.7639 | 312.695 | 48.139 | 52.587 | 41.849 | 80.297
| 38.8125 | 310.598 | 48.033 | 52.388 | 41.743 | 80.275
| 38.8194 | 267.179 | 46.662 | 51.423 | 40.743 | 78.877
| 38.8264 | 267.654 | 45.163 | 50.146 | 39.473 | 77.086
| 38.8333 | 261.875 | 44.242 | 49.273 | 38.766 | 75.759
| 38.8403 | 263.644 | 43.474 | 48.471 | 38.158 | 74.524
| 38.8472 | 257.882 | 42.81 | 47.753 | 37.64 | 73.396
| 38.8542 | 251.096 | 42.195 | 47.075 | 37.166 | 72.314
| 38.8611 | 250.845 | 41.577 | 46.378 | 36.651 | 71.228
| 38.8681 | 244.779 | 40.955 | 45.689 | 36.148 | 70.142
| 38.875 | 238.668 | 40.39 | 45.048 | 35.69 | 69.109
| 38.8819 | 239.31 | 39.832 | 44.385 | 35.222 | 68.076
| 38.8889 | 232.634 | 39.282 | 43.762 | 34.768 | 67.066
| 38.8958 | 232.554 | 38.816 | 43.18 | 34.379 | 66.14
| 38.9028 | 225.77 | 38.203 | 42.509 | 33.877 | 65.077
| 38.9097 | 218.213 | 37.696 | 41.931 | 33.481 | 64.13
| 38.9167 | 218.029 | 37.163 | 41.298 | 33.008 | 63.116
| 38.9236 | 211.387 | 36.615 | 40.676 | 32.559 | 62.124
| 38.9306 | 212.316 | 36.2 | 40.133 | 32.192 | 61.244
| 38.9375 | 205.956 | 35.683 | 39.537 | 31.761 | 60.282
| 38.9444 | 199.666 | 35.183 | 38.956 | 31.346 | 59.341
| 38.9514 | 194.325 | 34.653 | 38.349 | 30.905 | 58.378
| 38.9583 | 195.167 | 34.239 | 37.822 | 30.545 | 57.513
| 38.9653 | 187.193 | 33.701 | 37.217 | 30.107 | 56.543
| 38.9722 | 180.751 | 33.276 | 36.699 | 29.756 | 55.679
| 38.9792 | 180.72 | 32.799 | 36.137 | 29.351 | 54.772
| 38.9861 | 174.057 | 32.344 | 35.596 | 28.963 | 53.883
| 38.9931 | 173.971 | 31.971 | 35.11 | 28.636 | 53.075

## Experiment - Data - MF_IV_EVU
Electric Load and Cable Temperatures | [6 empty] | Weather Station Data
|  |  | Silt | Sand | Fluidized Backfill | Loam
Parameter | Time | Electrical load (IV) | Conductor Temperature | Conductor Temperature | Conductor Temperature | Conductor Temperature | Parameter | Time | Air Temperature | Soil Temperature [-0.8 m] | Time | Precipitation
Unit | d | A | °C | °C | °C | °C | Unit | d | °C | °C | d | mm/h
| 0 | 194.346 | 25.752 | 28.577 | 26.365 | 49.88 |  | 0 | 4.6 | 6.7 | 0 | 0.2
| 0.0069444 | 183.151 | 25.456 | 28.209 | 26.04 | 48.986 |  | 0.020833 | 3.7 | 6.7 | 0.041667 | 0
| 0.013889 | 183.325 | 25.033 | 27.712 | 25.554 | 47.934 |  | 0.041667 | 3.8 | 6.7 | 0.083333 | 0
| 0.020833 | 183.603 | 24.786 | 27.369 | 25.245 | 47.087 |  | 0.0625 | 3.4 | 6.7 | 0.125 | 0
| 0.027778 | 183.912 | 24.615 | 27.106 | 25.021 | 46.361 |  | 0.083333 | 3.2 | 6.7 | 0.16667 | 0
| 0.034722 | 184.744 | 24.478 | 26.89 | 24.847 | 45.725 |  | 0.10417 | 3.1 | 6.7 | 0.20833 | 0
| 0.041667 | 176.601 | 24.164 | 26.552 | 24.523 | 44.945 |  | 0.125 | 2.8 | 6.7 | 0.25 | 0
| 0.048611 | 175.882 | 23.966 | 26.283 | 24.275 | 44.273 |  | 0.14583 | 3.1 | 6.7 | 0.29167 | 0
| 0.055556 | 176.393 | 23.817 | 26.07 | 24.093 | 43.681 |  | 0.16667 | 3.1 | 6.7 | 0.33333 | 0
| 0.0625 | 167.649 | 23.497 | 25.732 | 23.766 | 42.932 |  | 0.1875 | 3.1 | 6.7 | 0.375 | 0
| 0.069444 | 167.392 | 23.29 | 25.466 | 23.514 | 42.288 |  | 0.20833 | 2.6 | 6.7 | 0.41667 | 0
| 0.076389 | 167.911 | 23.147 | 25.26 | 23.338 | 41.735 |  | 0.22917 | 2.2 | 6.7 | 0.45833 | 0
| 0.083333 | 159.406 | 22.892 | 24.988 | 23.082 | 41.107 |  | 0.25 | 2.7 | 6.7 | 0.5 | 0
| 0.090278 | 160.649 | 22.696 | 24.735 | 22.841 | 40.508 |  | 0.27083 | 2.1 | 6.7 | 0.54167 | 0.4
| 0.097222 | 159.154 | 22.545 | 24.529 | 22.66 | 39.981 |  | 0.29167 | 2.3 | 6.7 | 0.58333 | 0.2
| 0.10417 | 159.296 | 22.409 | 24.352 | 22.504 | 39.502 |  | 0.3125 | 2.9 | 6.7 | 0.625 | 0
| 0.11111 | 159.476 | 22.312 | 24.203 | 22.373 | 39.082 |  | 0.33333 | 2.7 | 6.7 | 0.66667 | 0.2
| 0.11806 | 159.487 | 22.221 | 24.069 | 22.265 | 38.698 |  | 0.35417 | 3.3 | 6.7 | 0.70833 | 0
| 0.125 | 159.858 | 22.133 | 23.945 | 22.156 | 38.348 |  | 0.375 | 2.9 | 6.7 | 0.75 | 0
| 0.13194 | 160.207 | 22.063 | 23.839 | 22.069 | 38.035 |  | 0.39583 | 2.9 | 6.7 | 0.79167 | 0
| 0.13889 | 160.115 | 21.994 | 23.742 | 21.988 | 37.75 |  | 0.41667 | 3.6 | 6.7 | 0.83333 | 0
| 0.14583 | 159.816 | 21.92 | 23.638 | 21.909 | 37.475 |  | 0.4375 | 3.9 | 6.7 | 0.875 | 0
| 0.15278 | 160.215 | 21.86 | 23.551 | 21.828 | 37.228 |  | 0.45833 | 4.3 | 6.7 | 0.91667 | 0
| 0.15972 | 151.306 | 21.661 | 23.363 | 21.645 | 36.857 |  | 0.47917 | 4.4 | 6.7 | 0.95833 | 0.6
| 0.16667 | 151.381 | 21.504 | 23.175 | 21.458 | 36.47 |  | 0.5 | 4.6 | 6.7 | 1 | 0
| 0.17361 | 151.773 | 21.395 | 23.03 | 21.327 | 36.142 |  | 0.52083 | 4.5 | 6.7 | 1.0417 | 0
| 0.18056 | 151.483 | 21.307 | 22.911 | 21.225 | 35.852 |  | 0.54167 | 4.3 | 6.7 | 1.0833 | 0
| 0.1875 | 159.345 | 21.283 | 22.842 | 21.17 | 35.634 |  | 0.5625 | 3.9 | 6.7 | 1.125 | 0
| 0.19444 | 159.472 | 21.359 | 22.875 | 21.235 | 35.577 |  | 0.58333 | 4.1 | 6.7 | 1.1667 | 0
| 0.20139 | 159.354 | 21.353 | 22.857 | 21.23 | 35.473 |  | 0.60417 | 4.1 | 6.7 | 1.2083 | 0
| 0.20833 | 168.951 | 21.397 | 22.857 | 21.248 | 35.42 |  | 0.625 | 4.3 | 6.7 | 1.25 | 0
| 0.21528 | 177.297 | 21.607 | 23.014 | 21.441 | 35.589 |  | 0.64583 | 4.3 | 6.7 | 1.2917 | 0.2
| 0.22222 | 187.824 | 21.976 | 23.317 | 21.784 | 35.989 |  | 0.66667 | 4.4 | 6.7 | 1.3333 | 0
| 0.22917 | 197.771 | 22.412 | 23.718 | 22.228 | 36.586 |  | 0.6875 | 4.6 | 6.7 | 1.375 | 0
| 0.23611 | 208.107 | 22.869 | 24.158 | 22.702 | 37.301 |  | 0.70833 | 4.6 | 6.7 | 1.4167 | 0
| 0.24306 | 217.58 | 23.463 | 24.724 | 23.31 | 38.246 |  | 0.72917 | 4.7 | 6.7 | 1.4583 | 0
| 0.25 | 236.183 | 24.152 | 25.378 | 24.001 | 39.383 |  | 0.75 | 4.4 | 6.7 | 1.5 | 0
| 0.25694 | 247.468 | 24.839 | 26.059 | 24.709 | 40.618 |  | 0.77083 | 4.3 | 6.7 | 1.5417 | 0
| 0.26389 | 256.087 | 25.654 | 26.867 | 25.547 | 42.079 |  | 0.79167 | 4.3 | 6.7 | 1.5833 | 0
| 0.27083 | 265.961 | 26.485 | 27.722 | 26.428 | 43.664 |  | 0.8125 | 4.3 | 6.7 | 1.625 | 0
| 0.27778 | 284.396 | 27.457 | 28.661 | 27.382 | 45.457 |  | 0.83333 | 4.3 | 6.7 | 1.6667 | 0
| 0.28472 | 295.202 | 28.374 | 29.6 | 28.342 | 47.312 |  | 0.85417 | 4.2 | 6.7 | 1.7083 | 0
| 0.29167 | 302.538 | 29.415 | 30.648 | 29.429 | 49.343 |  | 0.875 | 4.2 | 6.7 | 1.75 | 0
| 0.29861 | 312.161 | 30.514 | 31.766 | 30.567 | 51.528 |  | 0.89583 | 3.9 | 6.7 | 1.7917 | 0
| 0.30556 | 331.357 | 31.742 | 32.958 | 31.785 | 53.935 |  | 0.91667 | 3.8 | 6.7 | 1.8333 | 0
| 0.3125 | 338.842 | 33.02 | 34.246 | 33.105 | 56.498 |  | 0.9375 | 4.1 | 6.7 | 1.875 | 0
| 0.31944 | 358.652 | 34.395 | 35.593 | 34.47 | 59.237 |  | 0.95833 | 4.1 | 6.7 | 1.9167 | 0
| 0.32639 | 365.462 | 35.846 | 37.051 | 35.96 | 62.176 |  | 0.97917 | 3.8 | 6.7 | 1.9583 | 0.2
| 0.33333 | 374.063 | 37.273 | 38.494 | 37.422 | 65.192 |  | 1 | 3.8 | 6.7 | 2 | 0
| 0.34028 | 382.314 | 38.679 | 39.931 | 38.861 | 68.274 |  | 1.0208 | 3.8 | 6.7 | 2.0417 | 0.4
| 0.34722 | 381.274 | 39.605 | 40.998 | 39.874 | 70.932 |  | 1.0417 | 3.7 | 6.7 | 2.0833 | 0
| 0.35417 | 380.776 | 40.205 | 41.737 | 40.527 | 73.131 |  | 1.0625 | 3.8 | 6.7 | 2.125 | 0
| 0.36111 | 381.517 | 40.731 | 42.359 | 41.088 | 75.085 |  | 1.0833 | 3.8 | 6.7 | 2.1667 | 0
| 0.36806 | 376.252 | 40.909 | 42.677 | 41.339 | 76.547 |  | 1.1042 | 3.8 | 6.7 | 2.2083 | 0
| 0.375 | 374.931 | 41.1 | 42.924 | 41.519 | 77.784 |  | 1.125 | 3.8 | 6.7 | 2.25 | 0
| 0.38194 | 374.969 | 41.347 | 43.197 | 41.763 | 78.93 |  | 1.1458 | 3.7 | 6.7 | 2.2917 | 0
| 0.38889 | 375.013 | 41.551 | 43.438 | 41.971 | 79.942 |  | 1.1667 | 3.7 | 6.7 | 2.3333 | 0
| 0.39583 | 375.153 | 41.741 | 43.655 | 42.174 | 80.87 |  | 1.1875 | 3.7 | 6.7 | 2.375 | 0
| 0.40278 | 373.964 | 41.931 | 43.856 | 42.353 | 81.69 |  | 1.2083 | 3.5 | 6.7 | 2.4167 | 0
| 0.40972 | 365.009 | 41.62 | 43.682 | 42.12 | 81.92 |  | 1.2292 | 3.7 | 6.7 | 2.4583 | 0
| 0.41667 | 365.92 | 41.603 | 43.649 | 42.059 | 82.256 |  | 1.25 | 3.8 | 6.7 | 2.5 | 0
| 0.42361 | 367.379 | 41.699 | 43.723 | 42.136 | 82.683 |  | 1.2708 | 3.8 | 6.7 | 2.5417 | 0
| 0.43056 | 360.166 | 41.406 | 43.514 | 41.885 | 82.653 |  | 1.2917 | 3.5 | 6.7 | 2.5833 | 0
| 0.4375 | 359.371 | 41.286 | 43.39 | 41.748 | 82.684 |  | 1.3125 | 3.2 | 6.7 | 2.625 | 0
| 0.44444 | 357.181 | 41.21 | 43.302 | 41.66 | 82.718 |  | 1.3333 | 3.3 | 6.7 | 2.6667 | 0
| 0.45139 | 349.799 | 40.721 | 42.903 | 41.213 | 82.253 |  | 1.3542 | 3.6 | 6.7 | 2.7083 | 0
| 0.45833 | 347.964 | 40.523 | 42.675 | 40.973 | 81.967 |  | 1.375 | 4 | 6.7 | 2.75 | 0
| 0.46528 | 340.206 | 40.02 | 42.224 | 40.492 | 81.314 |  | 1.3958 | 4.4 | 6.7 | 2.7917 | 0
| 0.47222 | 340.183 | 39.775 | 41.931 | 40.201 | 80.843 |  | 1.4167 | 4.9 | 6.7 | 2.8333 | 0
| 0.47917 | 330.978 | 39.314 | 41.525 | 39.787 | 80.152 |  | 1.4375 | 4.8 | 6.7 | 2.875 | 0
| 0.48611 | 333.992 | 39.032 | 41.173 | 39.424 | 79.525 |  | 1.4583 | 4.8 | 6.7 | 2.9167 | 0.2
| 0.49306 | 326.441 | 38.598 | 40.768 | 39.017 | 78.757 |  | 1.4792 | 5.3 | 6.7 | 2.9583 | 0
| 0.5 | 326.031 | 38.383 | 40.504 | 38.758 | 78.174 |  | 1.5 | 5.3 | 6.7 | 3 | 0
| 0.50694 | 318.479 | 37.951 | 40.108 | 38.36 | 77.391 |  | 1.5208 | 5.2 | 6.7 | 3.0417 | 0
| 0.51389 | 317.762 | 37.641 | 39.756 | 38.006 | 76.656 |  | 1.5417 | 5.6 | 6.7 | 3.0833 | 0
| 0.52083 | 318.768 | 37.487 | 39.547 | 37.807 | 76.119 |  | 1.5625 | 5.8 | 6.7 | 3.125 | 0
| 0.52778 | 319.027 | 37.397 | 39.416 | 37.7 | 75.692 |  | 1.5833 | 5.8 | 6.7 | 3.1667 | 0
| 0.53472 | 319.35 | 37.329 | 39.31 | 37.611 | 75.338 |  | 1.6042 | 5.7 | 6.7 | 3.2083 | 0
| 0.54167 | 311.742 | 37.021 | 39.057 | 37.341 | 74.777 |  | 1.625 | 6.7 | 6.7 | 3.25 | 0
| 0.54861 | 312.091 | 36.805 | 38.814 | 37.094 | 74.242 |  | 1.6458 | 6.2 | 6.7 | 3.2917 | 0
| 0.55556 | 313.004 | 36.733 | 38.691 | 36.984 | 73.868 |  | 1.6667 | 6.2 | 6.7 | 3.3333 | 0
| 0.5625 | 313.646 | 36.682 | 38.61 | 36.922 | 73.568 |  | 1.6875 | 5.7 | 6.7 | 3.375 | 0
| 0.56944 | 312.821 | 36.609 | 38.524 | 36.84 | 73.282 |  | 1.7083 | 5.1 | 6.7 | 3.4167 | 0
| 0.57639 | 304.981 | 36.399 | 38.351 | 36.672 | 72.876 |  | 1.7292 | 4.6 | 6.7 | 3.4583 | 0
| 0.58333 | 305.01 | 36.049 | 38.013 | 36.292 | 72.239 |  | 1.75 | 4.2 | 6.7 | 3.5 | 0
| 0.59028 | 303.176 | 35.838 | 37.781 | 36.066 | 71.727 |  | 1.7708 | 4.1 | 6.7 | 3.5417 | 0.2
| 0.59722 | 304.793 | 35.742 | 37.64 | 35.933 | 71.341 |  | 1.7917 | 4.1 | 6.7 | 3.5833 | 0.2
| 0.60417 | 305.144 | 35.694 | 37.56 | 35.883 | 71.052 |  | 1.8125 | 3.9 | 6.7 | 3.625 | 0.2
| 0.61111 | 305.484 | 35.663 | 37.503 | 35.829 | 70.806 |  | 1.8333 | 3.7 | 6.7 | 3.6667 | 0.4
| 0.61806 | 305.595 | 35.629 | 37.454 | 35.79 | 70.596 |  | 1.8542 | 3.2 | 6.7 | 3.7083 | 0.2
| 0.625 | 305.862 | 35.609 | 37.417 | 35.759 | 70.421 |  | 1.875 | 2.2 | 6.7 | 3.75 | 0.2
| 0.63194 | 305.624 | 35.589 | 37.385 | 35.732 | 70.27 |  | 1.8958 | 1.8 | 6.7 | 3.7917 | 0.6
| 0.63889 | 314.614 | 35.963 | 37.649 | 36.042 | 70.572 |  | 1.9167 | 2.4 | 6.7 | 3.8333 | 0
| 0.64583 | 314.004 | 36.118 | 37.812 | 36.211 | 70.763 |  | 1.9375 | 2.9 | 6.7 | 3.875 | 0.4
| 0.65278 | 314.268 | 36.196 | 37.903 | 36.304 | 70.899 |  | 1.9583 | 3.2 | 6.7 | 3.9167 | 0.6
| 0.65972 | 314.031 | 36.277 | 37.982 | 36.378 | 71.02 |  | 1.9792 | 3.2 | 6.7 | 3.9583 | 0.4
| 0.66667 | 314.387 | 36.311 | 38.028 | 36.417 | 71.098 |  | 2 | 3.3 | 6.7 | 4 | 0
| 0.67361 | 313.919 | 36.329 | 38.046 | 36.44 | 71.15 |  | 2.0208 | 3.2 | 6.7 | 4.0417 | 0.2
| 0.68056 | 313.66 | 36.339 | 38.055 | 36.442 | 71.179 |  | 2.0417 | 2.8 | 6.7 | 4.0833 | 0.4
| 0.6875 | 314.049 | 36.34 | 38.057 | 36.441 | 71.197 |  | 2.0625 | 2.6 | 6.7 | 4.125 | 0
| 0.69444 | 314.04 | 36.357 | 38.07 | 36.459 | 71.232 |  | 2.0833 | 2.2 | 6.7 | 4.1667 | 0.2
| 0.70139 | 320.458 | 36.577 | 38.227 | 36.636 | 71.47 |  | 2.1042 | 1.9 | 6.7 | 4.2083 | 0
| 0.70833 | 321.049 | 36.775 | 38.418 | 36.835 | 71.773 |  | 2.125 | 1.7 | 6.7 | 4.25 | 0
| 0.71528 | 319.217 | 36.837 | 38.505 | 36.917 | 71.962 |  | 2.1458 | 1.6 | 6.7 | 4.2917 | 0
| 0.72222 | 319.041 | 36.854 | 38.534 | 36.935 | 72.068 |  | 2.1667 | 1.3 | 6.7 | 4.3333 | 0.2
| 0.72917 | 319.398 | 36.877 | 38.566 | 36.967 | 72.168 |  | 2.1875 | 1.3 | 6.7 | 4.375 | 0
| 0.73611 | 318.723 | 36.908 | 38.594 | 36.992 | 72.254 |  | 2.2083 | 0.8 | 6.7 | 4.4167 | 0
| 0.74306 | 319.534 | 36.923 | 38.607 | 37 | 72.327 |  | 2.2292 | 0.1 | 6.7 | 4.4583 | 0
| 0.75 | 319.179 | 36.92 | 38.613 | 36.999 | 72.359 |  | 2.25 | 0.3 | 6.7 | 4.5 | 0
| 0.75694 | 318.877 | 36.963 | 38.641 | 37.025 | 72.437 |  | 2.2708 | 0.1 | 6.7 | 4.5417 | 0
| 0.76389 | 319.555 | 36.992 | 38.673 | 37.059 | 72.518 |  | 2.2917 | -0.3 | 6.7 | 4.5833 | 0
| 0.77083 | 318.944 | 36.987 | 38.67 | 37.055 | 72.545 |  | 2.3125 | -0.1 | 6.7 | 4.625 | 0
| 0.77778 | 317.846 | 36.962 | 38.653 | 37.036 | 72.544 |  | 2.3333 | 0.3 | 6.7 | 4.6667 | 0
| 0.78472 | 315.588 | 36.892 | 38.589 | 36.959 | 72.473 |  | 2.3542 | 0.6 | 6.7 | 4.7083 | 0
| 0.79167 | 320.277 | 36.98 | 38.638 | 37.017 | 72.55 |  | 2.375 | 1.1 | 6.7 | 4.75 | 0
| 0.79861 | 313.47 | 36.77 | 38.484 | 36.847 | 72.328 |  | 2.3958 | 1.8 | 6.7 | 4.7917 | 0
| 0.80556 | 313.734 | 36.693 | 38.4 | 36.764 | 72.194 |  | 2.4167 | 2.6 | 6.7 | 4.8333 | 0
| 0.8125 | 307.164 | 36.543 | 38.272 | 36.623 | 71.979 |  | 2.4375 | 3.6 | 6.7 | 4.875 | 0
| 0.81944 | 304.088 | 36.254 | 38.011 | 36.339 | 71.557 |  | 2.4583 | 3.8 | 6.7 | 4.9167 | 0
| 0.82639 | 304.011 | 36.006 | 37.751 | 36.068 | 71.12 |  | 2.4792 | 5.3 | 6.7 | 4.9583 | 0
| 0.83333 | 305.798 | 35.907 | 37.626 | 35.951 | 70.826 |  | 2.5 | 5.9 | 6.7 | 5 | 0
| 0.84028 | 305.346 | 35.847 | 37.534 | 35.869 | 70.598 |  | 2.5208 | 5.6 | 6.7
| 0.84722 | 297.311 | 35.538 | 37.287 | 35.598 | 70.13 |  | 2.5417 | 6.7 | 6.7
| 0.85417 | 289.381 | 35.174 | 36.958 | 35.254 | 69.542 |  | 2.5625 | 6.6 | 6.7
| 0.86111 | 290.44 | 34.801 | 36.565 | 34.842 | 68.836 |  | 2.5833 | 6.6 | 6.7
| 0.86806 | 278.624 | 34.277 | 36.101 | 34.363 | 67.969 |  | 2.6042 | 7.1 | 6.7
| 0.875 | 279.669 | 33.875 | 35.66 | 33.907 | 67.108 |  | 2.625 | 6.8 | 6.7
| 0.88194 | 272.999 | 33.443 | 35.243 | 33.489 | 66.246 |  | 2.6458 | 7.1 | 6.7
| 0.88889 | 274.314 | 33.157 | 34.912 | 33.156 | 65.483 |  | 2.6667 | 6.8 | 6.7
| 0.89583 | 266.01 | 32.617 | 34.404 | 32.634 | 64.473 |  | 2.6875 | 6.2 | 6.7
| 0.90278 | 260.546 | 32.226 | 33.991 | 32.22 | 63.564 |  | 2.7083 | 5.7 | 6.7
| 0.90972 | 253.809 | 31.7 | 33.488 | 31.705 | 62.51 |  | 2.7292 | 5.1 | 6.7
| 0.91667 | 253.873 | 31.347 | 33.084 | 31.307 | 61.591 |  | 2.75 | 4.4 | 6.7
| 0.92361 | 245.483 | 30.743 | 32.493 | 30.714 | 60.398 |  | 2.7708 | 4 | 6.7
| 0.93056 | 240.339 | 30.347 | 32.066 | 30.306 | 59.412 |  | 2.7917 | 3.6 | 6.7
| 0.9375 | 232.004 | 29.937 | 31.648 | 29.896 | 58.428 |  | 2.8125 | 3.3 | 6.7
| 0.94444 | 233.302 | 29.52 | 31.19 | 29.437 | 57.407 |  | 2.8333 | 3.2 | 6.7
| 0.95139 | 224.19 | 29.054 | 30.727 | 28.979 | 56.361 |  | 2.8542 | 3.1 | 6.7
| 0.95833 | 224.832 | 28.707 | 30.328 | 28.588 | 55.405 |  | 2.875 | 2.8 | 6.7
| 0.96528 | 216.408 | 28.197 | 29.829 | 28.086 | 54.295 |  | 2.8958 | 2.6 | 6.7
| 0.97222 | 216.693 | 27.909 | 29.478 | 27.753 | 53.4 |  | 2.9167 | 2.2 | 6.7
| 0.97917 | 207.987 | 27.426 | 28.997 | 27.272 | 52.326 |  | 2.9375 | 1.9 | 6.7
| 0.98611 | 199.503 | 27.043 | 28.604 | 26.885 | 51.363 |  | 2.9583 | 1.7 | 6.7
| 0.99306 | 197.271 | 26.615 | 28.15 | 26.43 | 50.338 |  | 2.9792 | 1.6 | 6.7
| 1 | 198.385 | 26.32 | 27.804 | 26.095 | 49.461 |  | 3 | 1.4 | 6.7
| 1.0069 | 189.311 | 25.871 | 27.35 | 25.647 | 48.44 |  | 3.0208 | 1.5 | 6.7
| 1.0139 | 189.623 | 25.603 | 27.034 | 25.343 | 47.611 |  | 3.0417 | 1.2 | 6.7
| 1.0208 | 189.247 | 25.404 | 26.785 | 25.114 | 46.895 |  | 3.0625 | 0.7 | 6.7
| 1.0278 | 181.031 | 25.004 | 26.396 | 24.714 | 45.991 |  | 3.0833 | 0.6 | 6.1
| 1.0347 | 181.038 | 24.77 | 26.117 | 24.449 | 45.257 |  | 3.1042 | 0 | 6.1
| 1.0417 | 181.45 | 24.598 | 25.897 | 24.257 | 44.62 |  | 3.125 | -0.3 | 6.1
| 1.0486 | 174.186 | 24.258 | 25.568 | 23.926 | 43.848 |  | 3.1458 | -0.8 | 6.1
| 1.0556 | 172.156 | 24.016 | 25.295 | 23.66 | 43.158 |  | 3.1667 | -1 | 6.1
| 1.0625 | 172.372 | 23.835 | 25.076 | 23.449 | 42.558 |  | 3.1875 | -0.7 | 6.1
| 1.0694 | 171.599 | 23.677 | 24.889 | 23.284 | 42.016 |  | 3.2083 | -0.9 | 6.1
| 1.0764 | 163.127 | 23.34 | 24.565 | 22.953 | 41.31 |  | 3.2292 | -1.4 | 6.1
| 1.0833 | 163.499 | 23.141 | 24.332 | 22.726 | 40.715 |  | 3.25 | -1.7 | 6.1
| 1.0903 | 163.987 | 22.999 | 24.159 | 22.568 | 40.211 |  | 3.2708 | -1.9 | 6.1
| 1.0972 | 164.116 | 22.876 | 24.008 | 22.434 | 39.764 |  | 3.2917 | -1.8 | 6.1
| 1.1042 | 163.892 | 22.768 | 23.868 | 22.316 | 39.352 |  | 3.3125 | -1.7 | 6.1
| 1.1111 | 164.243 | 22.665 | 23.746 | 22.203 | 38.986 |  | 3.3333 | -0.8 | 6.1
| 1.1181 | 155.885 | 22.381 | 23.483 | 21.931 | 38.434 |  | 3.3542 | -0.2 | 6.1
| 1.125 | 155.985 | 22.215 | 23.295 | 21.747 | 37.977 |  | 3.375 | 0.4 | 6.1
| 1.1319 | 156.873 | 22.105 | 23.157 | 21.622 | 37.594 |  | 3.3958 | 1.2 | 6.1
| 1.1389 | 156.934 | 22.012 | 23.037 | 21.517 | 37.256 |  | 3.4167 | 1.4 | 6.1
| 1.1458 | 156.865 | 21.922 | 22.927 | 21.416 | 36.944 |  | 3.4375 | 2.2 | 6.1
| 1.1528 | 156.229 | 21.832 | 22.814 | 21.318 | 36.646 |  | 3.4583 | 2.7 | 6.1
| 1.1597 | 156.545 | 21.751 | 22.719 | 21.227 | 36.37 |  | 3.4792 | 2.9 | 6.1
| 1.1667 | 156.837 | 21.68 | 22.629 | 21.145 | 36.118 |  | 3.5 | 3.4 | 6.1
| 1.1736 | 156.686 | 21.607 | 22.549 | 21.072 | 35.889 |  | 3.5208 | 4.1 | 6.1
| 1.1806 | 156.613 | 21.546 | 22.475 | 21.005 | 35.677 |  | 3.5417 | 4.3 | 6.1
| 1.1875 | 156.549 | 21.485 | 22.397 | 20.935 | 35.475 |  | 3.5625 | 4.1 | 6.1
| 1.1944 | 154.806 | 21.383 | 22.295 | 20.84 | 35.247 |  | 3.5833 | 4.2 | 6.1
| 1.2014 | 163.332 | 21.495 | 22.359 | 20.926 | 35.239 |  | 3.6042 | 4.4 | 6.1
| 1.2083 | 163.429 | 21.507 | 22.362 | 20.941 | 35.185 |  | 3.625 | 4.3 | 6.1
| 1.2153 | 173.153 | 21.663 | 22.47 | 21.063 | 35.291 |  | 3.6458 | 4.4 | 6.1
| 1.2222 | 183.5 | 21.966 | 22.716 | 21.351 | 35.612 |  | 3.6667 | 4.3 | 6.1
| 1.2292 | 193.124 | 22.387 | 23.101 | 21.776 | 36.167 |  | 3.6875 | 4.4 | 6.1
| 1.2361 | 204.755 | 22.905 | 23.569 | 22.285 | 36.918 |  | 3.7083 | 4.7 | 6.1
| 1.2431 | 223.867 | 23.567 | 24.163 | 22.917 | 37.894 |  | 3.7292 | 4.6 | 6.1
| 1.25 | 232.195 | 24.256 | 24.829 | 23.622 | 39.036 |  | 3.75 | 4.4 | 6.1
| 1.2569 | 243.701 | 24.962 | 25.527 | 24.339 | 40.283 |  | 3.7708 | 4.4 | 6.1
| 1.2639 | 259.191 | 25.81 | 26.345 | 25.178 | 41.759 |  | 3.7917 | 4.4 | 6.1
| 1.2708 | 268.202 | 26.687 | 27.213 | 26.068 | 43.365 |  | 3.8125 | 4.7 | 6.1
| 1.2778 | 277.34 | 27.515 | 28.062 | 26.915 | 45.008 |  | 3.8333 | 4.9 | 6.1
| 1.2847 | 295.196 | 28.586 | 29.086 | 27.964 | 46.974 |  | 3.8542 | 5.2 | 6.1
| 1.2917 | 309.263 | 29.575 | 30.085 | 28.973 | 48.949 |  | 3.875 | 5.3 | 6.1
| 1.2986 | 317.522 | 30.736 | 31.229 | 30.153 | 51.167 |  | 3.8958 | 5.4 | 6.1
| 1.3056 | 325.873 | 31.925 | 32.426 | 31.375 | 53.552 |  | 3.9167 | 6.2 | 6.1
| 1.3125 | 334.365 | 33.148 | 33.661 | 32.63 | 56.066 |  | 3.9375 | 6.3 | 6.1
| 1.3194 | 354.608 | 34.56 | 35.015 | 33.987 | 58.768 |  | 3.9583 | 6.6 | 6.1
| 1.3264 | 361.124 | 35.943 | 36.403 | 35.393 | 61.6 |  | 3.9792 | 6.6 | 6.1
| 1.3333 | 376.752 | 37.507 | 37.917 | 36.928 | 64.691 |  | 4 | 6.5 | 6.1
| 1.3403 | 381.929 | 38.839 | 39.302 | 38.287 | 67.676 |  | 4.0208 | 6.5 | 6.1
| 1.3472 | 379.379 | 39.734 | 40.343 | 39.277 | 70.267 |  | 4.0417 | 6.6 | 6.1
| 1.3542 | 381.931 | 40.419 | 41.131 | 39.982 | 72.504 |  | 4.0625 | 6.7 | 6.1
| 1.3611 | 381.992 | 41.014 | 41.817 | 40.61 | 74.53 |  | 4.0833 | 6.7 | 6.1
| 1.3681 | 374.156 | 41.24 | 42.219 | 40.926 | 76.089 |  | 4.1042 | 6.7 | 6.1
| 1.375 | 374.385 | 41.28 | 42.35 | 40.974 | 77.177 |  | 4.125 | 6.7 | 6.1
| 1.3819 | 368.537 | 41.24 | 42.415 | 40.969 | 78.012 |  | 4.1458 | 6.7 | 6.1
| 1.3889 | 370.064 | 41.338 | 42.53 | 41.047 | 78.798 |  | 4.1667 | 6.9 | 6.1
| 1.3958 | 368.965 | 41.459 | 42.678 | 41.173 | 79.545 |  | 4.1875 | 7.1 | 6.1
| 1.4028 | 369.545 | 41.584 | 42.823 | 41.306 | 80.226 |  | 4.2083 | 7 | 6.1
| 1.4097 | 368.863 | 41.721 | 42.976 | 41.439 | 80.868 |  | 4.2292 | 6.9 | 6.1
| 1.4167 | 368.545 | 41.863 | 43.138 | 41.588 | 81.498 |  | 4.25 | 7.1 | 6.1
| 1.4236 | 362.089 | 41.815 | 43.179 | 41.6 | 81.876 |  | 4.2708 | 7.1 | 6.1
| 1.4306 | 362.198 | 41.632 | 43.035 | 41.402 | 81.981 |  | 4.2917 | 6.9 | 6.1
| 1.4375 | 360.96 | 41.566 | 42.978 | 41.327 | 82.129 |  | 4.3125 | 6.8 | 6.1
| 1.4444 | 352.663 | 41.103 | 42.616 | 40.917 | 81.768 |  | 4.3333 | 6.8 | 6.1
| 1.4514 | 351.243 | 40.94 | 42.44 | 40.722 | 81.618 |  | 4.3542 | 6.7 | 6.1
| 1.4583 | 345.002 | 40.536 | 42.105 | 40.363 | 81.178 |  | 4.375 | 6.8 | 6.1
| 1.4653 | 345.5 | 40.307 | 41.851 | 40.1 | 80.817 |  | 4.3958 | 7.3 | 6.1
| 1.4722 | 337.014 | 39.856 | 41.47 | 39.694 | 80.207 |  | 4.4167 | 7.4 | 6.1
| 1.4792 | 336.495 | 39.57 | 41.157 | 39.373 | 79.682 |  | 4.4375 | 8.1 | 6.1
| 1.4861 | 327.914 | 39.042 | 40.692 | 38.889 | 78.88 |  | 4.4583 | 8.3 | 6.1
| 1.4931 | 328.296 | 38.723 | 40.332 | 38.527 | 78.197 |  | 4.4792 | 8 | 6.1
| 1.5 | 320.078 | 38.369 | 40.012 | 38.209 | 77.513 |  | 4.5 | 8.3 | 6.1
| 1.5069 | 319.315 | 37.949 | 39.578 | 37.759 | 76.686 |  | 4.5208 | 8.7 | 6.1
| 1.5139 | 318.55 | 37.714 | 39.306 | 37.495 | 76.046 |  | 4.5417 | 7.8 | 6.1
| 1.5208 | 319.125 | 37.576 | 39.132 | 37.344 | 75.556 |  | 4.5625 | 7.2 | 6.1
| 1.5278 | 319.579 | 37.47 | 38.993 | 37.212 | 75.136 |  | 4.5833 | 6.9 | 6.1
| 1.5347 | 319.393 | 37.393 | 38.898 | 37.135 | 74.79 |  | 4.6042 | 7.1 | 6.1
| 1.5417 | 312.776 | 36.97 | 38.538 | 36.749 | 74.079 |  | 4.625 | 7.2 | 6.1
| 1.5486 | 312.853 | 36.8 | 38.339 | 36.554 | 73.587 |  | 4.6458 | 6.7 | 6.1
| 1.5556 | 313.222 | 36.722 | 38.23 | 36.455 | 73.229 |  | 4.6667 | 6.6 | 6.1
| 1.5625 | 313.113 | 36.631 | 38.124 | 36.359 | 72.888 |  | 4.6875 | 6.4 | 6.1
| 1.5694 | 312.635 | 36.566 | 38.045 | 36.288 | 72.604 |  | 4.7083 | 6.2 | 6.1
| 1.5764 | 304.842 | 36.342 | 37.871 | 36.114 | 72.183 |  | 4.7292 | 5.7 | 6.1
| 1.5833 | 303.663 | 35.993 | 37.543 | 35.753 | 71.564 |  | 4.75 | 5.3 | 6.1
| 1.5903 | 303.211 | 35.803 | 37.327 | 35.541 | 71.07 |  | 4.7708 | 5.2 | 6.1
| 1.5972 | 303.693 | 35.675 | 37.177 | 35.399 | 70.667 |  | 4.7917 | 5.1 | 6.1
| 1.6042 | 304.463 | 35.61 | 37.085 | 35.319 | 70.36 |  | 4.8125 | 5.3 | 6.1
| 1.6111 | 305.186 | 35.578 | 37.031 | 35.279 | 70.113 |  | 4.8333 | 5.3 | 6.1
| 1.6181 | 306.24 | 35.566 | 37.001 | 35.251 | 69.923 |  | 4.8542 | 5.3 | 6.1
| 1.625 | 306.026 | 35.562 | 36.986 | 35.247 | 69.779 |  | 4.875 | 5.4 | 6.1
| 1.6319 | 306.413 | 35.568 | 36.979 | 35.247 | 69.663 |  | 4.8958 | 5.3 | 6.1
| 1.6389 | 314.622 | 35.748 | 37.094 | 35.377 | 69.745 |  | 4.9167 | 4.9 | 6.1
| 1.6458 | 314.513 | 36.012 | 37.338 | 35.644 | 70.022 |  | 4.9375 | 4.8 | 6.1
| 1.6528 | 314.751 | 36.151 | 37.484 | 35.794 | 70.224 |  | 4.9583 | 4.7 | 6.1
| 1.6597 | 315.459 | 36.222 | 37.578 | 35.886 | 70.36 |  | 4.9792 | 4.7 | 6.1
| 1.6667 | 315.002 | 36.254 | 37.618 | 35.917 | 70.443 |  | 5 | 4.4 | 6.1
| 1.6736 | 315.6 | 36.301 | 37.666 | 35.958 | 70.53
| 1.6806 | 315.643 | 36.361 | 37.725 | 36.018 | 70.637
| 1.6875 | 314.954 | 36.391 | 37.769 | 36.055 | 70.715
| 1.6944 | 313.021 | 36.423 | 37.811 | 36.101 | 70.788
| 1.7014 | 321.859 | 36.761 | 38.079 | 36.387 | 71.213
| 1.7083 | 318.46 | 36.79 | 38.148 | 36.445 | 71.361
| 1.7153 | 318.877 | 36.811 | 38.18 | 36.471 | 71.471
| 1.7222 | 322.203 | 36.837 | 38.211 | 36.483 | 71.559
| 1.7292 | 321.275 | 37.039 | 38.382 | 36.674 | 71.865
| 1.7361 | 321.773 | 37.101 | 38.469 | 36.748 | 72.036
| 1.7431 | 321.75 | 37.151 | 38.523 | 36.803 | 72.188
| 1.75 | 321.175 | 37.183 | 38.571 | 36.843 | 72.307
| 1.7569 | 321.488 | 37.205 | 38.602 | 36.865 | 72.403
| 1.7639 | 321.42 | 37.237 | 38.634 | 36.887 | 72.502
| 1.7708 | 320.888 | 37.246 | 38.653 | 36.909 | 72.572
| 1.7778 | 320.009 | 37.207 | 38.63 | 36.875 | 72.573
| 1.7847 | 314.933 | 37.15 | 38.607 | 36.847 | 72.556
| 1.7917 | 312.196 | 36.781 | 38.299 | 36.496 | 72.129
| 1.7986 | 311.905 | 36.629 | 38.128 | 36.323 | 71.853
| 1.8056 | 313.996 | 36.593 | 38.059 | 36.257 | 71.692
| 1.8125 | 313.415 | 36.587 | 38.043 | 36.249 | 71.604
| 1.8194 | 313.957 | 36.58 | 38.027 | 36.235 | 71.53
| 1.8264 | 307.359 | 36.303 | 37.813 | 36.009 | 71.177
| 1.8333 | 307.946 | 36.176 | 37.668 | 35.852 | 70.898
| 1.8403 | 299.395 | 35.896 | 37.446 | 35.623 | 70.48
| 1.8472 | 300.3 | 35.568 | 37.122 | 35.275 | 69.92
| 1.8542 | 291.818 | 35.139 | 36.731 | 34.865 | 69.221
| 1.8611 | 293.316 | 34.896 | 36.455 | 34.587 | 68.645
| 1.8681 | 285.306 | 34.384 | 35.985 | 34.097 | 67.768
| 1.875 | 273.443 | 33.914 | 35.569 | 33.677 | 66.92
| 1.8819 | 273.881 | 33.398 | 35.04 | 33.126 | 65.916
| 1.8889 | 274.149 | 33.128 | 34.723 | 32.819 | 65.158
| 1.8958 | 266.114 | 32.584 | 34.222 | 32.304 | 64.13
| 1.9028 | 257.843 | 32.158 | 33.804 | 31.89 | 63.2
| 1.9097 | 258.882 | 31.748 | 33.368 | 31.457 | 62.256
| 1.9167 | 247.096 | 31.167 | 32.826 | 30.912 | 61.133
| 1.9236 | 246.811 | 30.742 | 32.361 | 30.449 | 60.113
| 1.9306 | 238.72 | 30.335 | 31.945 | 30.051 | 59.141
| 1.9375 | 237.17 | 29.886 | 31.47 | 29.581 | 58.098
| 1.9444 | 228.841 | 29.471 | 31.056 | 29.182 | 57.117
| 1.9514 | 229.402 | 29.076 | 30.622 | 28.753 | 56.125
| 1.9583 | 221.556 | 28.615 | 30.167 | 28.302 | 55.085
| 1.9653 | 222.848 | 28.305 | 29.806 | 27.957 | 54.195
| 1.9722 | 212.74 | 27.769 | 29.289 | 27.435 | 53.069
| 1.9792 | 204.667 | 27.351 | 28.864 | 27.018 | 52.063
| 1.9861 | 205.255 | 26.977 | 28.446 | 26.607 | 51.091
| 1.9931 | 197.13 | 26.522 | 27.996 | 26.157 | 50.058
| 2 | 194.95 | 26.139 | 27.575 | 25.749 | 49.076
| 2.0069 | 194.186 | 25.882 | 27.277 | 25.477 | 48.261
| 2.0139 | 185.235 | 25.417 | 26.819 | 25.013 | 47.252
| 2.0208 | 185.324 | 25.153 | 26.506 | 24.717 | 46.426
| 2.0278 | 185.335 | 24.951 | 26.262 | 24.493 | 45.712
| 2.0347 | 176.991 | 24.679 | 25.988 | 24.233 | 44.988
| 2.0417 | 177.17 | 24.38 | 25.67 | 23.922 | 44.216
| 2.0486 | 177.704 | 24.199 | 25.45 | 23.716 | 43.593
| 2.0556 | 170.295 | 23.959 | 25.207 | 23.484 | 42.95
| 2.0625 | 170.7 | 23.703 | 24.927 | 23.203 | 42.266
| 2.0694 | 169.563 | 23.506 | 24.701 | 22.992 | 41.672
| 2.0764 | 169.691 | 23.353 | 24.519 | 22.826 | 41.141
| 2.0833 | 161.074 | 23.006 | 24.192 | 22.497 | 40.431
| 2.0903 | 161.128 | 22.819 | 23.973 | 22.284 | 39.863
| 2.0972 | 161.525 | 22.677 | 23.799 | 22.124 | 39.365
| 2.1042 | 161.635 | 22.551 | 23.645 | 21.995 | 38.917
| 2.1111 | 161.659 | 22.438 | 23.512 | 21.874 | 38.524
| 2.1181 | 161.826 | 22.345 | 23.395 | 21.773 | 38.162
| 2.125 | 161.926 | 22.261 | 23.29 | 21.672 | 37.841
| 2.1319 | 153.163 | 22.075 | 23.131 | 21.519 | 37.455
| 2.1389 | 153.778 | 21.873 | 22.913 | 21.302 | 37.005
| 2.1458 | 154.022 | 21.745 | 22.758 | 21.152 | 36.618
| 2.1528 | 153.374 | 21.634 | 22.628 | 21.036 | 36.284
| 2.1597 | 154.254 | 21.542 | 22.519 | 20.94 | 35.977
| 2.1667 | 153.783 | 21.465 | 22.418 | 20.851 | 35.702
| 2.1736 | 154.012 | 21.378 | 22.324 | 20.764 | 35.441
| 2.1806 | 153.753 | 21.305 | 22.235 | 20.688 | 35.198
| 2.1875 | 153.992 | 21.24 | 22.161 | 20.617 | 34.98
| 2.1944 | 162.313 | 21.275 | 22.149 | 20.625 | 34.869
| 2.2014 | 162.355 | 21.341 | 22.197 | 20.696 | 34.847
| 2.2083 | 162.343 | 21.341 | 22.195 | 20.704 | 34.792
| 2.2153 | 180.466 | 21.495 | 22.308 | 20.837 | 34.906
| 2.2222 | 190.937 | 21.812 | 22.579 | 21.14 | 35.255
| 2.2292 | 199.957 | 22.364 | 23.035 | 21.636 | 35.917
| 2.2361 | 210.457 | 22.857 | 23.499 | 22.138 | 36.66
| 2.2431 | 228.127 | 23.458 | 24.067 | 22.742 | 37.599
| 2.25 | 237.681 | 24.078 | 24.687 | 23.382 | 38.677
| 2.2569 | 246.353 | 24.892 | 25.443 | 24.165 | 40
| 2.2639 | 257.299 | 25.739 | 26.268 | 25.011 | 41.472
| 2.2708 | 266.797 | 26.568 | 27.112 | 25.86 | 43.033
| 2.2778 | 286.255 | 27.441 | 27.973 | 26.735 | 44.695
| 2.2847 | 296.158 | 28.416 | 28.958 | 27.727 | 46.585
| 2.2917 | 304.29 | 29.575 | 30.063 | 28.848 | 48.688
| 2.2986 | 316.56 | 30.778 | 31.242 | 30.051 | 50.943
| 2.3056 | 325.788 | 31.953 | 32.424 | 31.244 | 53.296
| 2.3125 | 345.037 | 33.127 | 33.608 | 32.426 | 55.708
| 2.3194 | 352.728 | 34.633 | 35.043 | 33.884 | 58.519
| 2.3264 | 367.377 | 35.951 | 36.4 | 35.227 | 61.296
| 2.3333 | 374.675 | 37.531 | 37.916 | 36.761 | 64.372
| 2.3403 | 378.428 | 38.503 | 39.039 | 37.827 | 66.983
| 2.3472 | 382.838 | 39.808 | 40.335 | 39.087 | 69.874
| 2.3542 | 378.054 | 40.469 | 41.16 | 39.838 | 72.147
| 2.3611 | 377.666 | 40.773 | 41.607 | 40.176 | 73.835
| 2.3681 | 376.004 | 41.069 | 41.989 | 40.49 | 75.323
| 2.375 | 373.981 | 41.296 | 42.289 | 40.735 | 76.617
| 2.3819 | 373.863 | 41.51 | 42.557 | 40.957 | 77.733
| 2.3889 | 375.098 | 41.797 | 42.865 | 41.231 | 78.834
| 2.3958 | 375.868 | 42.015 | 43.125 | 41.459 | 79.806
| 2.4028 | 366.836 | 41.948 | 43.182 | 41.469 | 80.413
| 2.4097 | 367.549 | 41.836 | 43.11 | 41.341 | 80.772
| 2.4167 | 367.908 | 41.876 | 43.158 | 41.363 | 81.196
| 2.4236 | 359.27 | 41.994 | 43.275 | 41.486 | 81.695
| 2.4306 | 359.395 | 41.608 | 43.008 | 41.148 | 81.574
| 2.4375 | 359.648 | 41.538 | 42.931 | 41.058 | 81.671
| 2.4444 | 355.287 | 41.277 | 42.727 | 40.827 | 81.523
| 2.4514 | 346.901 | 40.947 | 42.473 | 40.548 | 81.25
| 2.4583 | 346.562 | 40.607 | 42.136 | 40.177 | 80.825
| 2.4653 | 339.345 | 40.24 | 41.813 | 39.842 | 80.34
| 2.4722 | 339.814 | 39.893 | 41.458 | 39.479 | 79.789
| 2.4792 | 331.969 | 39.509 | 41.12 | 39.135 | 79.195
| 2.4861 | 331.539 | 39.152 | 40.745 | 38.747 | 78.531
| 2.4931 | 324.212 | 38.753 | 40.382 | 38.382 | 77.826
| 2.5 | 323.748 | 38.381 | 39.986 | 37.98 | 77.071
| 2.5069 | 323.867 | 38.169 | 39.741 | 37.75 | 76.505
| 2.5139 | 323.854 | 38.05 | 39.589 | 37.612 | 76.067
| 2.5208 | 315.542 | 37.601 | 39.203 | 37.211 | 75.299
| 2.5278 | 316.322 | 37.346 | 38.913 | 36.923 | 74.669
| 2.5347 | 316.316 | 37.198 | 38.738 | 36.757 | 74.174
| 2.5417 | 316.675 | 37.11 | 38.616 | 36.653 | 73.785
| 2.5486 | 316.05 | 37.044 | 38.531 | 36.575 | 73.459
| 2.5556 | 308.696 | 36.79 | 38.328 | 36.372 | 72.986
| 2.5625 | 309.268 | 36.519 | 38.048 | 36.076 | 72.408
| 2.5694 | 309.274 | 36.387 | 37.893 | 35.93 | 71.995
| 2.5764 | 309.778 | 36.299 | 37.781 | 35.83 | 71.649
| 2.5833 | 310.438 | 36.253 | 37.713 | 35.768 | 71.381
| 2.5903 | 309.309 | 36.196 | 37.648 | 35.717 | 71.137
| 2.5972 | 310.07 | 36.155 | 37.594 | 35.663 | 70.92
| 2.6042 | 310.188 | 36.145 | 37.569 | 35.649 | 70.764
| 2.6111 | 310.761 | 36.132 | 37.547 | 35.63 | 70.625
| 2.6181 | 311.763 | 36.144 | 37.548 | 35.634 | 70.529
| 2.625 | 312.452 | 36.182 | 37.57 | 35.669 | 70.482
| 2.6319 | 308.898 | 36.06 | 37.478 | 35.564 | 70.288
| 2.6389 | 309.091 | 35.991 | 37.408 | 35.491 | 70.122
| 2.6458 | 309.029 | 35.961 | 37.372 | 35.457 | 69.997
| 2.6528 | 315.849 | 36.112 | 37.46 | 35.558 | 70.059
| 2.6597 | 315.735 | 36.311 | 37.635 | 35.762 | 70.269
| 2.6667 | 316.103 | 36.405 | 37.737 | 35.861 | 70.402
| 2.6736 | 316.373 | 36.463 | 37.808 | 35.924 | 70.511
| 2.6806 | 316.296 | 36.48 | 37.832 | 35.94 | 70.559
| 2.6875 | 316.046 | 36.505 | 37.864 | 35.968 | 70.612
| 2.6944 | 316.256 | 36.52 | 37.882 | 35.987 | 70.657
| 2.7014 | 315.838 | 36.544 | 37.904 | 36.005 | 70.7
| 2.7083 | 315.446 | 36.549 | 37.915 | 36.013 | 70.727
| 2.7153 | 315.002 | 36.539 | 37.912 | 36.012 | 70.729
| 2.7222 | 314.933 | 36.539 | 37.916 | 36.005 | 70.742
| 2.7292 | 315.556 | 36.563 | 37.934 | 36.025 | 70.775
| 2.7361 | 324.123 | 36.587 | 37.952 | 36.028 | 70.8
| 2.7431 | 323.761 | 36.985 | 38.274 | 36.401 | 71.278
| 2.75 | 323.772 | 37.134 | 38.436 | 36.565 | 71.56
| 2.7569 | 323.558 | 37.237 | 38.563 | 36.685 | 71.805
| 2.7639 | 323.224 | 37.286 | 38.627 | 36.734 | 71.976
| 2.7708 | 322.814 | 37.316 | 38.675 | 36.777 | 72.114
| 2.7778 | 321.174 | 37.291 | 38.675 | 36.759 | 72.168
| 2.7847 | 315.995 | 37.102 | 38.547 | 36.602 | 72.029
| 2.7917 | 320.547 | 37.011 | 38.432 | 36.479 | 71.895
| 2.7986 | 318.3 | 37.024 | 38.439 | 36.494 | 71.896
| 2.8056 | 309.813 | 36.772 | 38.26 | 36.299 | 71.627
| 2.8333 | 310.559 | 36.262 | 37.712 | 35.74 | 70.581
| 2.8403 | 302.013 | 35.914 | 37.433 | 35.438 | 70.102
| 2.8472 | 293.834 | 35.693 | 37.214 | 35.225 | 69.687
| 2.8542 | 294.44 | 35.228 | 36.792 | 34.774 | 68.953
| 2.8611 | 286.44 | 34.639 | 36.303 | 34.249 | 68.066
| 2.8681 | 286.652 | 34.376 | 35.964 | 33.92 | 67.381
| 2.875 | 280.262 | 33.938 | 35.563 | 33.508 | 66.557
| 2.8819 | 271.056 | 33.457 | 35.111 | 33.054 | 65.651
| 2.8889 | 268.363 | 32.972 | 34.631 | 32.562 | 64.678
| 2.8958 | 268.713 | 32.659 | 34.282 | 32.223 | 63.869
| 2.9028 | 260.395 | 32.135 | 33.794 | 31.727 | 62.857
| 2.9097 | 250.968 | 31.796 | 33.429 | 31.38 | 62.003
| 2.9167 | 251.609 | 31.245 | 32.888 | 30.831 | 60.901
| 2.9236 | 243.24 | 30.78 | 32.435 | 30.389 | 59.885
| 2.9306 | 240.998 | 30.322 | 31.957 | 29.912 | 58.851
| 2.9375 | 231.454 | 29.989 | 31.585 | 29.577 | 57.951
| 2.9444 | 232.719 | 29.476 | 31.072 | 29.059 | 56.86
| 2.9514 | 223.936 | 29.022 | 30.632 | 28.627 | 55.843
| 2.9583 | 225.017 | 28.639 | 30.207 | 28.21 | 54.858
| 2.9653 | 215.615 | 28.127 | 29.709 | 27.72 | 53.765
| 2.9722 | 215.96 | 27.802 | 29.336 | 27.365 | 52.838
| 2.9792 | 207.059 | 27.333 | 28.875 | 26.901 | 51.799
| 2.9861 | 198.84 | 26.99 | 28.499 | 26.548 | 50.871
| 2.9931 | 199.025 | 26.533 | 28.034 | 26.082 | 49.832
| 3 | 189.636 | 26.224 | 27.697 | 25.769 | 48.961
| 3.0069 | 190.323 | 25.786 | 27.249 | 25.319 | 47.964
| 3.0139 | 191.034 | 25.534 | 26.947 | 25.043 | 47.166
| 3.0208 | 182.151 | 25.192 | 26.609 | 24.722 | 46.331
| 3.0278 | 182.461 | 24.88 | 26.264 | 24.378 | 45.498
| 3.0347 | 182.65 | 24.675 | 26.019 | 24.153 | 44.8
| 3.0417 | 175.32 | 24.401 | 25.739 | 23.892 | 44.078
| 3.0486 | 173.8 | 24.134 | 25.45 | 23.608 | 43.36
| 3.0556 | 174.451 | 23.925 | 25.212 | 23.387 | 42.722
| 3.0625 | 165.147 | 23.735 | 25.004 | 23.193 | 42.14
| 3.0694 | 165.23 | 23.382 | 24.654 | 22.847 | 41.383
| 3.0764 | 165.085 | 23.179 | 24.416 | 22.617 | 40.768
| 3.0833 | 165.033 | 23.025 | 24.227 | 22.446 | 40.238
| 3.0903 | 165.246 | 22.891 | 24.067 | 22.304 | 39.764
| 3.0972 | 158.116 | 22.669 | 23.858 | 22.106 | 39.241
| 3.1042 | 156.246 | 22.426 | 23.603 | 21.855 | 38.666
| 3.1111 | 156.38 | 22.26 | 23.406 | 21.665 | 38.172
| 3.1181 | 156.514 | 22.133 | 23.259 | 21.527 | 37.747
| 3.125 | 157.027 | 22.029 | 23.12 | 21.413 | 37.361
| 3.1319 | 156.817 | 21.924 | 23.002 | 21.309 | 37.011
| 3.1389 | 156.726 | 21.834 | 22.894 | 21.213 | 36.694
| 3.1458 | 157.009 | 21.759 | 22.795 | 21.127 | 36.406
| 3.1528 | 157.139 | 21.678 | 22.704 | 21.044 | 36.137
| 3.1597 | 157.161 | 21.61 | 22.62 | 20.971 | 35.891
| 3.1667 | 157.336 | 21.545 | 22.542 | 20.909 | 35.662
| 3.1736 | 157.322 | 21.483 | 22.468 | 20.837 | 35.446
| 3.1806 | 157.572 | 21.422 | 22.394 | 20.777 | 35.253
| 3.1875 | 157.33 | 21.36 | 22.327 | 20.717 | 35.066
| 3.1944 | 157.54 | 21.313 | 22.26 | 20.656 | 34.889
| 3.2014 | 157.762 | 21.248 | 22.194 | 20.599 | 34.712
| 3.2083 | 165.128 | 21.359 | 22.254 | 20.676 | 34.726
| 3.2153 | 175.274 | 21.547 | 22.384 | 20.838 | 34.857
| 3.2222 | 186.252 | 21.866 | 22.655 | 21.14 | 35.201
| 3.2292 | 195.283 | 22.319 | 23.055 | 21.585 | 35.789
| 3.2361 | 214.25 | 22.852 | 23.528 | 22.09 | 36.543
| 3.2431 | 224.405 | 23.422 | 24.073 | 22.659 | 37.447
| 3.25 | 233.847 | 24.159 | 24.763 | 23.384 | 38.6
| 3.2569 | 249.269 | 24.934 | 25.506 | 24.151 | 39.901
| 3.2639 | 258.25 | 25.782 | 26.33 | 24.989 | 41.378
| 3.2708 | 268.397 | 26.604 | 27.154 | 25.81 | 42.909
| 3.2778 | 286.084 | 27.577 | 28.104 | 26.768 | 44.681
| 3.2847 | 293.241 | 28.652 | 29.156 | 27.845 | 46.669
| 3.2917 | 303.404 | 29.764 | 30.267 | 28.964 | 48.774
| 3.2986 | 319.815 | 30.856 | 31.349 | 30.045 | 50.917
| 3.3056 | 328.929 | 32.106 | 32.573 | 31.277 | 53.316
| 3.3125 | 337.436 | 33.277 | 33.748 | 32.45 | 55.724
| 3.3194 | 355.356 | 34.649 | 35.085 | 33.785 | 58.375
| 3.3264 | 361.972 | 36.123 | 36.533 | 35.248 | 61.272
| 3.3333 | 378.36 | 37.62 | 38.009 | 36.705 | 64.254
| 3.3403 | 379.274 | 39.041 | 39.468 | 38.157 | 67.323
| 3.3472 | 378.501 | 39.888 | 40.46 | 39.065 | 69.831
| 3.3542 | 380.759 | 40.579 | 41.249 | 39.763 | 72.037
| 3.3611 | 381.2 | 41.134 | 41.905 | 40.355 | 73.994
| 3.3681 | 379.971 | 41.545 | 42.408 | 40.782 | 75.676
| 3.375 | 372.408 | 41.634 | 42.645 | 40.941 | 76.9
| 3.3819 | 371.932 | 41.676 | 42.761 | 40.969 | 77.816
| 3.3889 | 372.276 | 41.814 | 42.934 | 41.109 | 78.712
| 3.3958 | 372.38 | 41.955 | 43.1 | 41.239 | 79.501
| 3.4028 | 371.851 | 42.066 | 43.247 | 41.365 | 80.22
| 3.4097 | 370.402 | 42.19 | 43.395 | 41.485 | 80.864
| 3.4167 | 369.971 | 42.265 | 43.511 | 41.574 | 81.405
| 3.4236 | 362.84 | 42.118 | 43.456 | 41.482 | 81.663
| 3.4306 | 361.58 | 41.934 | 43.31 | 41.289 | 81.74
| 3.4375 | 353.089 | 41.774 | 43.201 | 41.163 | 81.789
| 3.4444 | 353.07 | 41.332 | 42.818 | 40.721 | 81.404
| 3.4514 | 345.9 | 41.166 | 42.654 | 40.567 | 81.247
| 3.4583 | 344.979 | 40.71 | 42.248 | 40.122 | 80.712
| 3.4653 | 337.82 | 40.443 | 41.993 | 39.875 | 80.326
| 3.4722 | 338.594 | 39.996 | 41.565 | 39.418 | 79.66
| 3.4792 | 329.665 | 39.73 | 41.305 | 39.171 | 79.171
| 3.4861 | 329.169 | 39.179 | 40.794 | 38.622 | 78.307
| 3.4931 | 328.564 | 38.92 | 40.495 | 38.342 | 77.708
| 3.5 | 321.277 | 38.397 | 40.027 | 37.854 | 76.828
| 3.5069 | 320.847 | 38.088 | 39.687 | 37.518 | 76.118
| 3.5139 | 317.454 | 37.809 | 39.398 | 37.245 | 75.457
| 3.5208 | 317.657 | 37.59 | 39.141 | 36.999 | 74.863
| 3.5278 | 318.106 | 37.441 | 38.965 | 36.841 | 74.378
| 3.5347 | 318.466 | 37.352 | 38.842 | 36.735 | 73.983
| 3.5417 | 318.097 | 37.297 | 38.763 | 36.667 | 73.676
| 3.5486 | 310.951 | 36.912 | 38.445 | 36.334 | 73.032
| 3.5556 | 310.413 | 36.719 | 38.228 | 36.112 | 72.538
| 3.5625 | 310.437 | 36.575 | 38.069 | 35.965 | 72.112
| 3.5694 | 310.893 | 36.489 | 37.957 | 35.862 | 71.765
| 3.5764 | 310.287 | 36.409 | 37.859 | 35.781 | 71.465
| 3.5833 | 311.458 | 36.357 | 37.789 | 35.717 | 71.212
| 3.5903 | 311.234 | 36.338 | 37.752 | 35.687 | 71.022
| 3.5972 | 311.768 | 36.347 | 37.738 | 35.685 | 70.881
| 3.6042 | 311.894 | 36.34 | 37.733 | 35.678 | 70.76
| 3.6111 | 312.557 | 36.348 | 37.725 | 35.679 | 70.675
| 3.6181 | 312.772 | 36.363 | 37.732 | 35.692 | 70.608
| 3.625 | 313.532 | 36.384 | 37.745 | 35.712 | 70.564
| 3.6319 | 309.985 | 36.396 | 37.763 | 35.731 | 70.536
| 3.6389 | 310.484 | 36.241 | 37.636 | 35.587 | 70.316
| 3.6458 | 310.09 | 36.186 | 37.573 | 35.516 | 70.168
| 3.6528 | 310.262 | 36.152 | 37.52 | 35.473 | 70.042
| 3.6597 | 317.437 | 36.202 | 37.533 | 35.489 | 70.017
| 3.6667 | 316.669 | 36.479 | 37.766 | 35.762 | 70.302
| 3.6736 | 316.682 | 36.583 | 37.875 | 35.867 | 70.452
| 3.6806 | 316.575 | 36.651 | 37.953 | 35.941 | 70.582
| 3.6875 | 317.789 | 36.705 | 38.013 | 35.996 | 70.686
| 3.6944 | 318.206 | 36.751 | 38.06 | 36.036 | 70.786
| 3.7014 | 317.56 | 36.778 | 38.094 | 36.068 | 70.857
| 3.7083 | 316.768 | 36.803 | 38.125 | 36.097 | 70.927
| 3.7153 | 317.153 | 36.767 | 38.1 | 36.066 | 70.922
| 3.7222 | 316.531 | 36.786 | 38.117 | 36.076 | 70.958
| 3.7292 | 316.657 | 36.765 | 38.109 | 36.061 | 70.951
| 3.7361 | 324.356 | 36.816 | 38.131 | 36.073 | 71.011
| 3.7431 | 323.825 | 37.182 | 38.432 | 36.418 | 71.451
| 3.75 | 324.475 | 37.326 | 38.588 | 36.578 | 71.728
| 3.7569 | 323.604 | 37.401 | 38.685 | 36.665 | 71.939
| 3.7639 | 322.976 | 37.439 | 38.74 | 36.708 | 72.09
| 3.7708 | 318.268 | 37.416 | 38.754 | 36.709 | 72.162
| 3.7778 | 320.947 | 37.256 | 38.619 | 36.549 | 72.034
| 3.7847 | 319.289 | 37.311 | 38.66 | 36.586 | 72.111
| 3.7917 | 317.723 | 37.22 | 38.588 | 36.507 | 72.029
| 3.7986 | 318.029 | 37.163 | 38.535 | 36.452 | 71.969
| 3.8056 | 309.897 | 36.877 | 38.327 | 36.224 | 71.656
| 3.8125 | 309.864 | 36.629 | 38.08 | 35.961 | 71.279
| 3.8194 | 310.42 | 36.513 | 37.949 | 35.827 | 71.02
| 3.8264 | 311.033 | 36.439 | 37.855 | 35.744 | 70.817
| 3.8333 | 310.448 | 36.408 | 37.806 | 35.701 | 70.669
| 3.8403 | 302.19 | 36.027 | 37.501 | 35.372 | 70.158
| 3.8472 | 293.791 | 35.737 | 37.24 | 35.105 | 69.673
| 3.8542 | 294.51 | 35.267 | 36.797 | 34.636 | 68.914
| 3.8611 | 287.161 | 34.836 | 36.397 | 34.23 | 68.165
| 3.8681 | 280.257 | 34.447 | 36.014 | 33.837 | 67.401
| 3.875 | 281.817 | 34.015 | 35.58 | 33.394 | 66.555
| 3.8819 | 267.226 | 33.585 | 35.175 | 33.002 | 65.708
| 3.8889 | 268.291 | 32.952 | 34.576 | 32.373 | 64.58
| 3.8958 | 269.049 | 32.641 | 34.216 | 32.028 | 63.748
| 3.9028 | 261.583 | 32.149 | 33.747 | 31.56 | 62.76
| 3.9097 | 252.816 | 31.646 | 33.26 | 31.081 | 61.737
| 3.9167 | 252.67 | 31.241 | 32.821 | 30.648 | 60.771
| 3.9236 | 244.543 | 30.697 | 32.293 | 30.133 | 59.669
| 3.9306 | 237.615 | 30.3 | 31.88 | 29.742 | 58.711
| 3.9375 | 238.116 | 29.836 | 31.398 | 29.266 | 57.663
| 3.9444 | 228.747 | 29.353 | 30.922 | 28.797 | 56.608
| 3.9514 | 228.886 | 28.964 | 30.492 | 28.386 | 55.625
| 3.9583 | 221.004 | 28.518 | 30.055 | 27.963 | 54.611
| 3.9653 | 221.489 | 28.169 | 29.657 | 27.578 | 53.675
| 3.9722 | 210.902 | 27.669 | 29.173 | 27.103 | 52.603
| 3.9792 | 211.197 | 27.31 | 28.772 | 26.714 | 51.654
| 3.9861 | 203.387 | 26.836 | 28.305 | 26.247 | 50.619
| 3.9931 | 194.29 | 26.469 | 27.92 | 25.887 | 49.688
| 4 | 193.42 | 26.018 | 27.456 | 25.426 | 48.663
| 4.0069 | 194.154 | 25.752 | 27.141 | 25.128 | 47.839
| 4.0139 | 187.063 | 25.337 | 26.728 | 24.733 | 46.902
| 4.0208 | 186.828 | 25.081 | 26.419 | 24.445 | 46.104
| 4.0278 | 187.137 | 24.876 | 26.183 | 24.231 | 45.409
| 4.0347 | 178.243 | 24.485 | 25.808 | 23.86 | 44.562
| 4.0417 | 178.464 | 24.248 | 25.531 | 23.601 | 43.84
| 4.0486 | 177.249 | 24.03 | 25.284 | 23.374 | 43.186
| 4.0556 | 168.306 | 23.811 | 25.05 | 23.161 | 42.563
| 4.0625 | 168.387 | 23.475 | 24.717 | 22.82 | 41.817
| 4.0694 | 168.412 | 23.265 | 24.471 | 22.599 | 41.203
| 4.0764 | 168.312 | 23.108 | 24.278 | 22.423 | 40.663
| 4.0833 | 160.508 | 22.847 | 24.025 | 22.182 | 40.06
| 4.0903 | 160.013 | 22.595 | 23.76 | 21.914 | 39.438
| 4.0972 | 160.066 | 22.434 | 23.562 | 21.737 | 38.925
| 4.1042 | 160.216 | 22.3 | 23.397 | 21.593 | 38.464
| 4.1111 | 160.211 | 22.183 | 23.259 | 21.47 | 38.05
| 4.1181 | 160.751 | 22.079 | 23.134 | 21.364 | 37.692
| 4.125 | 160.529 | 21.99 | 23.025 | 21.268 | 37.364
| 4.1319 | 160.701 | 21.895 | 22.918 | 21.175 | 37.058
| 4.1389 | 160.931 | 21.817 | 22.824 | 21.089 | 36.773
| 4.1458 | 160.936 | 21.738 | 22.735 | 21.012 | 36.511
| 4.1528 | 151.864 | 21.476 | 22.498 | 20.771 | 36.068
| 4.1597 | 152.546 | 21.32 | 22.326 | 20.606 | 35.686
| 4.1667 | 152.192 | 21.202 | 22.192 | 20.481 | 35.355
| 4.1736 | 152.419 | 21.113 | 22.077 | 20.38 | 35.063
| 4.1806 | 152.649 | 21.031 | 21.981 | 20.298 | 34.803
| 4.1875 | 153.104 | 20.953 | 21.888 | 20.221 | 34.565
| 4.1944 | 161.355 | 21.064 | 21.944 | 20.302 | 34.534
| 4.2014 | 161.621 | 21.083 | 21.959 | 20.331 | 34.473
| 4.2083 | 161.215 | 21.066 | 21.945 | 20.326 | 34.401
| 4.2153 | 170.829 | 21.239 | 22.074 | 20.478 | 34.53
| 4.2222 | 190.652 | 21.636 | 22.381 | 20.819 | 34.937
| 4.2292 | 200.593 | 22.055 | 22.757 | 21.231 | 35.5
| 4.2361 | 210.579 | 22.635 | 23.287 | 21.806 | 36.316
| 4.2431 | 220.686 | 23.214 | 23.841 | 22.387 | 37.238
| 4.25 | 229.234 | 23.852 | 24.47 | 23.033 | 38.322
| 4.2569 | 248.629 | 24.634 | 25.196 | 23.779 | 39.603
| 4.2639 | 259.991 | 25.386 | 25.957 | 24.543 | 40.983
| 4.2708 | 268.913 | 26.327 | 26.879 | 25.482 | 42.626
| 4.2778 | 278.911 | 27.213 | 27.771 | 26.381 | 44.308
| 4.2847 | 288.156 | 28.191 | 28.756 | 27.379 | 46.182
| 4.2917 | 307.15 | 29.317 | 29.846 | 28.471 | 48.256
| 4.2986 | 315.563 | 30.489 | 31.018 | 29.658 | 50.487
| 4.3056 | 325.938 | 31.594 | 32.145 | 30.778 | 52.738
| 4.3125 | 344.289 | 32.983 | 33.475 | 32.111 | 55.35
| 4.3194 | 352.58 | 34.224 | 34.751 | 33.384 | 57.942
| 4.3264 | 361.757 | 35.692 | 36.199 | 34.836 | 60.813
| 4.3333 | 377.828 | 37.266 | 37.735 | 36.37 | 63.894
| 4.3403 | 377.227 | 38.485 | 39.07 | 37.671 | 66.779
| 4.3472 | 376.289 | 39.244 | 39.981 | 38.487 | 69.145
| 4.3542 | 378.992 | 39.855 | 40.696 | 39.117 | 71.228
| 4.3611 | 378.337 | 40.416 | 41.351 | 39.705 | 73.137
| 4.3681 | 379.115 | 40.838 | 41.862 | 40.15 | 74.764
| 4.375 | 377.192 | 41.163 | 42.269 | 40.501 | 76.206
| 4.3819 | 376.544 | 41.459 | 42.615 | 40.807 | 77.493
| 4.3889 | 376.208 | 41.685 | 42.905 | 41.052 | 78.594
| 4.3958 | 368.603 | 41.546 | 42.918 | 41.002 | 79.213
| 4.4028 | 368.562 | 41.473 | 42.884 | 40.912 | 79.691
| 4.4097 | 367.425 | 41.517 | 42.944 | 40.951 | 80.192
| 4.4167 | 367.542 | 41.557 | 43 | 40.993 | 80.646
| 4.4236 | 366.789 | 41.627 | 43.088 | 41.059 | 81.074
| 4.4306 | 359.015 | 41.375 | 42.951 | 40.885 | 81.141
| 4.4375 | 358.392 | 41.196 | 42.79 | 40.696 | 81.139
| 4.4444 | 350.593 | 41.002 | 42.659 | 40.547 | 81.089
| 4.4514 | 350.986 | 40.634 | 42.32 | 40.171 | 80.723
| 4.4583 | 341.392 | 40.319 | 42.058 | 39.902 | 80.375
| 4.4653 | 344.944 | 40.006 | 41.729 | 39.546 | 79.911
| 4.4722 | 336.546 | 39.577 | 41.363 | 39.173 | 79.324
| 4.4792 | 335.47 | 39.243 | 41.01 | 38.811 | 78.727
| 4.4861 | 328.107 | 38.786 | 40.605 | 38.401 | 78.002
| 4.4931 | 327.345 | 38.433 | 40.229 | 38.024 | 77.3
| 4.5 | 318.405 | 38.078 | 39.903 | 37.7 | 76.612
| 4.5069 | 322.453 | 37.626 | 39.438 | 37.214 | 75.738
| 4.5139 | 322.085 | 37.538 | 39.28 | 37.097 | 75.274
| 4.5208 | 321.537 | 37.438 | 39.155 | 36.986 | 74.865
| 4.5278 | 314.399 | 37.094 | 38.868 | 36.698 | 74.243
| 4.5347 | 314.006 | 36.833 | 38.584 | 36.415 | 73.634
| 4.5417 | 313.4 | 36.663 | 38.394 | 36.227 | 73.126
| 4.5486 | 313.665 | 36.516 | 38.23 | 36.085 | 72.679
| 4.5556 | 312.986 | 36.403 | 38.101 | 35.959 | 72.29
| 4.5625 | 311.698 | 36.288 | 37.983 | 35.853 | 71.928
| 4.5694 | 312.365 | 36.189 | 37.869 | 35.743 | 71.593
| 4.5764 | 312.138 | 36.151 | 37.815 | 35.697 | 71.348
| 4.5833 | 304.043 | 35.752 | 37.482 | 35.346 | 70.723
| 4.5903 | 305.392 | 35.588 | 37.297 | 35.158 | 70.283
| 4.5972 | 306.165 | 35.53 | 37.199 | 35.082 | 69.981
| 4.6042 | 305.757 | 35.485 | 37.142 | 35.035 | 69.728
| 4.6111 | 306.148 | 35.424 | 37.064 | 34.974 | 69.481
| 4.6181 | 306.573 | 35.381 | 37.011 | 34.92 | 69.268
| 4.625 | 306.49 | 35.362 | 36.985 | 34.901 | 69.113
| 4.6319 | 306.326 | 35.337 | 36.957 | 34.879 | 68.965
| 4.6389 | 312.997 | 35.555 | 37.102 | 35.049 | 69.087
| 4.6458 | 313.405 | 35.735 | 37.273 | 35.244 | 69.266
| 4.6528 | 314.785 | 35.85 | 37.392 | 35.359 | 69.414
| 4.6597 | 314.392 | 35.929 | 37.475 | 35.439 | 69.532
| 4.6667 | 314.963 | 35.985 | 37.542 | 35.505 | 69.634
| 4.6736 | 314.667 | 36.017 | 37.58 | 35.538 | 69.699
| 4.6806 | 314.571 | 36.045 | 37.619 | 35.574 | 69.764
| 4.6875 | 314.728 | 36.08 | 37.652 | 35.599 | 69.827
| 4.6944 | 314.6 | 36.103 | 37.678 | 35.625 | 69.868
| 4.7014 | 314.949 | 36.119 | 37.7 | 35.649 | 69.914
| 4.7083 | 314.964 | 36.134 | 37.718 | 35.662 | 69.953
| 4.7153 | 314.745 | 36.167 | 37.743 | 35.689 | 69.997
| 4.7222 | 314.862 | 36.184 | 37.765 | 35.716 | 70.038
| 4.7292 | 311.393 | 36.199 | 37.792 | 35.736 | 70.077
| 4.7361 | 321.74 | 36.532 | 38.047 | 36.018 | 70.454
| 4.7431 | 320.903 | 36.671 | 38.196 | 36.171 | 70.717
| 4.75 | 320.658 | 36.743 | 38.294 | 36.256 | 70.913
| 4.7569 | 321.121 | 36.809 | 38.369 | 36.324 | 71.081
| 4.7639 | 321.269 | 36.859 | 38.428 | 36.381 | 71.222
| 4.7708 | 319.979 | 36.878 | 38.462 | 36.401 | 71.322
| 4.7778 | 319.748 | 36.86 | 38.466 | 36.396 | 71.37
| 4.7847 | 323.237 | 36.842 | 38.449 | 36.374 | 71.392
| 4.7917 | 312.317 | 36.546 | 38.233 | 36.128 | 71.1
| 4.7986 | 315.748 | 36.426 | 38.091 | 35.972 | 70.891
| 4.8056 | 306.66 | 36.379 | 38.053 | 35.961 | 70.789
| 4.8125 | 305.739 | 36.009 | 37.73 | 35.595 | 70.295
| 4.8194 | 307.186 | 35.855 | 37.555 | 35.42 | 69.955
| 4.8264 | 306.584 | 35.758 | 37.442 | 35.317 | 69.7
| 4.8333 | 306.897 | 35.729 | 37.387 | 35.276 | 69.517
| 4.8403 | 298.904 | 35.555 | 37.255 | 35.146 | 69.24
| 4.8472 | 299.07 | 35.225 | 36.946 | 34.813 | 68.711
| 4.8542 | 290.539 | 34.93 | 36.687 | 34.548 | 68.202
| 4.8611 | 290.579 | 34.536 | 36.303 | 34.136 | 67.5
| 4.8681 | 281.623 | 34.041 | 35.861 | 33.688 | 66.682
| 4.875 | 282.778 | 33.718 | 35.505 | 33.329 | 65.958
| 4.8819 | 274.675 | 33.191 | 35.015 | 32.823 | 65
| 4.8889 | 271.934 | 32.803 | 34.611 | 32.426 | 64.158
| 4.8958 | 262.578 | 32.291 | 34.14 | 31.944 | 63.182
| 4.9028 | 263.545 | 31.924 | 33.734 | 31.551 | 62.296
| 4.9097 | 256.718 | 31.43 | 33.246 | 31.065 | 61.275
| 4.9167 | 247.604 | 31.021 | 32.838 | 30.678 | 60.353
| 4.9236 | 246.598 | 30.554 | 32.347 | 30.183 | 59.32
| 4.9306 | 238.351 | 30.161 | 31.943 | 29.801 | 58.385
| 4.9375 | 238.884 | 29.732 | 31.488 | 29.357 | 57.399
| 4.9444 | 229.704 | 29.239 | 31.006 | 28.881 | 56.351
| 4.9514 | 229.91 | 28.889 | 30.605 | 28.495 | 55.408
| 4.9583 | 222.034 | 28.37 | 30.103 | 27.995 | 54.314
| 4.9653 | 213.905 | 27.984 | 29.692 | 27.607 | 53.345
| 4.9722 | 214.158 | 27.554 | 29.233 | 27.155 | 52.321
| 4.9792 | 204.621 | 27.181 | 28.849 | 26.788 | 51.382
| 4.9861 | 204.46 | 26.759 | 28.405 | 26.345 | 50.381
| 4.9931 | 196.799 | 26.328 | 27.961 | 25.916 | 49.385
| 5 | 194.846 | 25.948 | 27.547 | 25.515 | 48.424

## Experiment - Data - MF_IV_PV
Electric Load and Cable Temperatures | [6 empty] | Weather Station Data
|  |  | Silt | Sand | Fluidized Backfill | Loam
Parameter | Time | Electrical load (IV) | Conductor Temperature | Conductor Temperature | Conductor Temperature | Conductor Temperature | Parameter | Time | Air Temperature | Soil Temperature [-0.8 m] | Time | Precipitation
Unit | d | A | °C | °C | °C | °C | Unit | d | °C | °C | d | mm/h
| 0 | 102.274 | 17.724 | 19.362 | 17.459 | 24.46 |  | 0 | 6.9 | 7.2 | 0 | 0
| 0.0069444 | 92.415 | 17.615 | 19.252 | 17.358 | 24.262 |  | 0.020833 | 7.1 | 7.2 | 0.041667 | 0
| 0.013889 | 91.511 | 17.416 | 19.072 | 17.175 | 23.955 |  | 0.041667 | 7.1 | 7.2 | 0.083333 | 0
| 0.020833 | 83.995 | 17.231 | 18.891 | 16.998 | 23.655 |  | 0.0625 | 7.1 | 7.2 | 0.125 | 0
| 0.027778 | 83.674 | 17.072 | 18.726 | 16.842 | 23.358 |  | 0.083333 | 7.2 | 7.2 | 0.16667 | 0.2
| 0.034722 | 83.837 | 16.962 | 18.605 | 16.732 | 23.114 |  | 0.10417 | 7.1 | 7.2 | 0.20833 | 0
| 0.041667 | 83.984 | 16.879 | 18.499 | 16.646 | 22.906 |  | 0.125 | 6.8 | 7.2 | 0.25 | 0.2
| 0.048611 | 84.468 | 16.807 | 18.415 | 16.57 | 22.727 |  | 0.14583 | 6.7 | 7.2 | 0.29167 | 0.2
| 0.055556 | 84.275 | 16.743 | 18.339 | 16.51 | 22.564 |  | 0.16667 | 6.6 | 7.2 | 0.33333 | 0.2
| 0.0625 | 84.448 | 16.686 | 18.265 | 16.447 | 22.421 |  | 0.1875 | 5.7 | 7.2 | 0.375 | 0.2
| 0.069444 | 84.203 | 16.63 | 18.202 | 16.393 | 22.286 |  | 0.20833 | 5.7 | 7.2 | 0.41667 | 0
| 0.076389 | 84.076 | 16.574 | 18.139 | 16.336 | 22.157 |  | 0.22917 | 5.6 | 7.2 | 0.45833 | 0.6
| 0.083333 | 84.267 | 16.523 | 18.08 | 16.284 | 22.046 |  | 0.25 | 5.4 | 7.2 | 0.5 | 1.2
| 0.090278 | 84.453 | 16.475 | 18.024 | 16.242 | 21.937 |  | 0.27083 | 5.3 | 7.2 | 0.54167 | 1.4
| 0.097222 | 84.309 | 16.433 | 17.976 | 16.198 | 21.834 |  | 0.29167 | 5.3 | 7.2 | 0.58333 | 1
| 0.10417 | 84.345 | 16.398 | 17.926 | 16.155 | 21.749 |  | 0.3125 | 5.6 | 7.2 | 0.625 | 0.8
| 0.11111 | 84.316 | 16.354 | 17.879 | 16.115 | 21.659 |  | 0.33333 | 5.7 | 7.2 | 0.66667 | 1.2
| 0.11806 | 84.292 | 16.316 | 17.834 | 16.076 | 21.573 |  | 0.35417 | 6 | 7.2 | 0.70833 | 0.4
| 0.125 | 84.479 | 16.277 | 17.784 | 16.036 | 21.491 |  | 0.375 | 6.3 | 7.2 | 0.75 | 0.2
| 0.13194 | 84.33 | 16.245 | 17.747 | 15.998 | 21.416 |  | 0.39583 | 6.6 | 7.2 | 0.79167 | 0
| 0.13889 | 84.469 | 16.212 | 17.707 | 15.969 | 21.345 |  | 0.41667 | 7.1 | 7.2 | 0.83333 | 0
| 0.14583 | 84.336 | 16.178 | 17.667 | 15.932 | 21.278 |  | 0.4375 | 7.2 | 7.2 | 0.875 | 0
| 0.15278 | 84.122 | 16.144 | 17.625 | 15.898 | 21.206 |  | 0.45833 | 6.8 | 7.2 | 0.91667 | 0
| 0.15972 | 84.263 | 16.11 | 17.587 | 15.863 | 21.137 |  | 0.47917 | 7 | 7.2 | 0.95833 | 0
| 0.16667 | 84.355 | 16.076 | 17.549 | 15.835 | 21.075 |  | 0.5 | 7.2 | 7.2 | 1 | 0
| 0.17361 | 84.742 | 16.05 | 17.52 | 15.806 | 21.02 |  | 0.52083 | 7.1 | 7.2 | 1.0417 | 0
| 0.18056 | 84.792 | 16.024 | 17.488 | 15.78 | 20.963 |  | 0.54167 | 7.1 | 7.2 | 1.0833 | 0
| 0.1875 | 84.974 | 15.997 | 17.455 | 15.755 | 20.917 |  | 0.5625 | 6.9 | 7.2 | 1.125 | 0
| 0.19444 | 84.941 | 15.975 | 17.422 | 15.729 | 20.861 |  | 0.58333 | 7.1 | 7.2 | 1.1667 | 0
| 0.20139 | 85.037 | 15.949 | 17.393 | 15.7 | 20.811 |  | 0.60417 | 7.4 | 7.2 | 1.2083 | 0
| 0.20833 | 85.055 | 15.92 | 17.364 | 15.671 | 20.759 |  | 0.625 | 7.4 | 7.2 | 1.25 | 0
| 0.21528 | 85.019 | 15.897 | 17.337 | 15.651 | 20.713 |  | 0.64583 | 7.3 | 7.2 | 1.2917 | 0
| 0.22222 | 85.218 | 15.877 | 17.305 | 15.632 | 20.67 |  | 0.66667 | 7.2 | 7.2 | 1.3333 | 0
| 0.22917 | 85.334 | 15.855 | 17.278 | 15.602 | 20.623 |  | 0.6875 | 7.1 | 7.2 | 1.375 | 0
| 0.23611 | 85.287 | 15.833 | 17.251 | 15.583 | 20.588 |  | 0.70833 | 7 | 7.2 | 1.4167 | 0
| 0.24306 | 85.114 | 15.808 | 17.222 | 15.556 | 20.538 |  | 0.72917 | 7 | 7.2 | 1.4583 | 0
| 0.25 | 85.35 | 15.784 | 17.195 | 15.533 | 20.496 |  | 0.75 | 6.7 | 7.2 | 1.5 | 0
| 0.25694 | 84.765 | 15.762 | 17.166 | 15.51 | 20.457 |  | 0.77083 | 6.6 | 7.2 | 1.5417 | 0
| 0.26389 | 76.261 | 15.666 | 17.091 | 15.43 | 20.348 |  | 0.79167 | 6.6 | 7.2 | 1.5833 | 0
| 0.27083 | 76.253 | 15.578 | 17.006 | 15.344 | 20.216 |  | 0.8125 | 6.7 | 7.2 | 1.625 | 0
| 0.27778 | 66.48 | 15.429 | 16.877 | 15.208 | 20.023 |  | 0.83333 | 6.7 | 7.2 | 1.6667 | 0
| 0.28472 | 57.11 | 15.281 | 16.74 | 15.073 | 19.809 |  | 0.85417 | 6.8 | 7.2 | 1.7083 | 0
| 0.29167 | 47.294 | 15.114 | 16.582 | 14.915 | 19.565 |  | 0.875 | 6.6 | 7.2 | 1.75 | 0
| 0.29861 | 38.143 | 14.946 | 16.425 | 14.762 | 19.307 |  | 0.89583 | 6 | 7.2 | 1.7917 | 0
| 0.30556 | 30.01 | 14.794 | 16.27 | 14.612 | 19.046 |  | 0.91667 | 5.2 | 7.2 | 1.8333 | 0
| 0.3125 | 13.32 | 14.652 | 16.13 | 14.473 | 18.791 |  | 0.9375 | 4.5 | 7.2 | 1.875 | 0
| 0.31944 | 22.272 | 14.55 | 16.013 | 14.374 | 18.576 |  | 0.95833 | 4.2 | 7.2 | 1.9167 | 0
| 0.32639 | 31.768 | 14.522 | 15.957 | 14.331 | 18.438 |  | 0.97917 | 4.2 | 7.2 | 1.9583 | 0
| 0.33333 | 52.133 | 14.563 | 15.967 | 14.359 | 18.4 |  | 1 | 3.6 | 7.2 | 2 | 0
| 0.34028 | 63.928 | 14.681 | 16.041 | 14.452 | 18.466 |  | 1.0208 | 3.6 | 7.2 | 2.0417 | 0
| 0.34722 | 92.625 | 14.945 | 16.232 | 14.67 | 18.719 |  | 1.0417 | 3.8 | 7.2 | 2.125 | 0
| 0.35417 | 115.826 | 15.382 | 16.582 | 15.057 | 19.214 |  | 1.0625 | 4.2 | 7.2 | 2.1667 | 0
| 0.36111 | 137.805 | 15.965 | 17.066 | 15.578 | 19.928 |  | 1.0833 | 4.4 | 7.2 | 2.2083 | 0
| 0.36806 | 160.528 | 16.724 | 17.71 | 16.263 | 20.918 |  | 1.1042 | 4.7 | 7.2 | 2.25 | 0
| 0.375 | 184.914 | 17.659 | 18.521 | 17.106 | 22.192 |  | 1.125 | 4.8 | 7.2 | 2.2917 | 0
| 0.38194 | 204.099 | 18.738 | 19.484 | 18.095 | 23.714 |  | 1.1458 | 4.8 | 7.2 | 2.3333 | 0
| 0.38889 | 215.881 | 19.805 | 20.469 | 19.097 | 25.345 |  | 1.1667 | 5 | 7.2 | 2.375 | 0
| 0.39583 | 238.144 | 20.992 | 21.553 | 20.168 | 27.159 |  | 1.1875 | 4.9 | 7.2 | 2.4167 | 0
| 0.40278 | 248.723 | 22.23 | 22.71 | 21.326 | 29.133 |  | 1.2083 | 4.9 | 7.2 | 2.4583 | 0
| 0.40972 | 271.686 | 23.609 | 23.978 | 22.58 | 31.311 |  | 1.2292 | 5.1 | 7.2 | 2.5 | 0.2
| 0.41667 | 283.919 | 25.108 | 25.365 | 23.963 | 33.706 |  | 1.25 | 5.1 | 7.2 | 2.5417 | 0
| 0.42361 | 301.563 | 26.616 | 26.77 | 25.341 | 36.204 |  | 1.2708 | 5.2 | 7.2 | 2.5833 | 0
| 0.43056 | 308.437 | 28.095 | 28.175 | 26.714 | 38.711 |  | 1.2917 | 4.8 | 7.2 | 2.625 | 0
| 0.4375 | 324.931 | 29.609 | 29.584 | 28.081 | 41.292 |  | 1.3125 | 5.2 | 7.2 | 2.6667 | 0
| 0.44444 | 333.294 | 30.957 | 30.886 | 29.326 | 43.761 |  | 1.3333 | 5.8 | 7.2 | 2.7083 | 0
| 0.45139 | 330.898 | 32.101 | 32.047 | 30.414 | 46.038 |  | 1.3542 | 6.4 | 7.2 | 2.75 | 0
| 0.45833 | 340.145 | 33.309 | 33.208 | 31.505 | 48.323 |  | 1.375 | 7.8 | 7.2 | 2.7917 | 0
| 0.46528 | 347.432 | 34.526 | 34.387 | 32.614 | 50.604 |  | 1.3958 | 9.1 | 7.2 | 2.8333 | 0
| 0.47222 | 358.116 | 35.911 | 35.677 | 33.863 | 53.047 |  | 1.4167 | 10.1 | 7.2 | 2.875 | 0
| 0.47917 | 374.843 | 37.414 | 37.046 | 35.185 | 55.635 |  | 1.4375 | 10.8 | 7.2 | 2.9167 | 0
| 0.48611 | 373.547 | 38.732 | 38.344 | 36.428 | 58.129 |  | 1.4583 | 11.8 | 7.2 | 2.9583 | 0
| 0.49306 | 381.42 | 39.875 | 39.469 | 37.476 | 60.401 |  | 1.4792 | 12.1 | 7.2 | 3 | 0
| 0.5 | 385 | 41.1 | 40.655 | 38.598 | 62.748 |  | 1.5 | 12.7 | 7.2 | 3.0417 | 0
| 0.50694 | 385.771 | 41.931 | 41.546 | 39.393 | 64.721 |  | 1.5208 | 12.2 | 7.2 | 3.0833 | 0
| 0.51389 | 384.318 | 42.556 | 42.253 | 39.998 | 66.377 |  | 1.5417 | 13.1 | 7.2 | 3.125 | 0
| 0.52083 | 393.75 | 43.551 | 43.188 | 40.887 | 68.322 |  | 1.5625 | 12.7 | 7.2 | 3.1667 | 0
| 0.52778 | 402.346 | 44.459 | 44.051 | 41.686 | 70.161 |  | 1.5833 | 13.1 | 7.2 | 3.2083 | 0
| 0.53472 | 412.423 | 45.687 | 45.171 | 42.797 | 72.336 |  | 1.6042 | 14 | 7.2 | 3.25 | 0
| 0.54167 | 419.694 | 47.062 | 46.431 | 44.036 | 74.752 |  | 1.625 | 14 | 7.2 | 3.2917 | 0
| 0.54861 | 419.572 | 48.373 | 47.682 | 45.257 | 77.207 |  | 1.6458 | 14.4 | 7.2 | 3.3333 | 0
| 0.55556 | 419.312 | 49.205 | 48.582 | 46.052 | 79.221 |  | 1.6667 | 14.8 | 7.2 | 3.375 | 0
| 0.5625 | 418.838 | 49.777 | 49.251 | 46.612 | 80.881 |  | 1.6875 | 14.6 | 7.2 | 3.4167 | 0
| 0.56944 | 416.848 | 50.275 | 49.839 | 47.107 | 82.362 |  | 1.7083 | 14.3 | 7.2 | 3.4583 | 0
| 0.57639 | 414.857 | 50.514 | 50.208 | 47.377 | 83.463 |  | 1.7292 | 13.8 | 7.2 | 3.5 | 0
| 0.58333 | 422.679 | 51.282 | 50.932 | 48.06 | 85.003 |  | 1.75 | 12.9 | 7.2 | 3.5417 | 0
| 0.59028 | 423.949 | 51.884 | 51.553 | 48.633 | 86.379 |  | 1.7708 | 11.8 | 7.2 | 3.5833 | 0
| 0.59722 | 413.801 | 52.127 | 51.953 | 48.961 | 87.373 |  | 1.7917 | 10.7 | 7.2 | 3.625 | 0
| 0.60417 | 415.337 | 52.005 | 51.977 | 48.87 | 87.837 |  | 1.8125 | 9.6 | 7.2 | 3.6667 | 0
| 0.61111 | 398.553 | 51.358 | 51.632 | 48.424 | 87.619 |  | 1.8333 | 9.4 | 7.2 | 3.7083 | 2
| 0.61806 | 390.27 | 50.385 | 50.93 | 47.62 | 86.818 |  | 1.8542 | 9.2 | 7.2 | 3.75 | 1
| 0.625 | 374.985 | 49.156 | 49.995 | 46.615 | 85.516 |  | 1.875 | 9 | 7.2 | 3.7917 | 0
| 0.63194 | 366.646 | 48.071 | 49.088 | 45.685 | 84.134 |  | 1.8958 | 8.7 | 7.2 | 3.8333 | 0
| 0.63889 | 357.133 | 46.979 | 48.153 | 44.752 | 82.599 |  | 1.9167 | 8.2 | 7.2 | 3.875 | 0
| 0.64583 | 349.773 | 45.902 | 47.205 | 43.811 | 80.956 |  | 1.9375 | 8.1 | 7.2 | 3.9167 | 0
| 0.65278 | 339.692 | 44.825 | 46.256 | 42.876 | 79.229 |  | 1.9583 | 7.6 | 7.2 | 3.9583 | 0
| 0.65972 | 331.375 | 43.704 | 45.26 | 41.898 | 77.388 |  | 1.9792 | 7.4 | 7.2 | 4 | 0
| 0.66667 | 322.827 | 42.609 | 44.267 | 40.93 | 75.514 |  | 2 | 7.7 | 7.2 | 4.0417 | 2.4
| 0.67361 | 315.226 | 41.392 | 43.181 | 39.849 | 73.457 |  | 2.0208 | 7.1 | 7.2 | 4.0833 | 0
| 0.68056 | 297.467 | 40.004 | 41.973 | 38.653 | 71.191 |  | 2.0417 | 6.2 | 7.2 | 4.125 | 0
| 0.6875 | 289.857 | 38.667 | 40.741 | 37.436 | 68.875 |  | 2.0625 | 5.3 | 7.2 | 4.1667 | 0
| 0.69444 | 268.23 | 37.172 | 39.42 | 36.13 | 66.367 |  | 2.125 | 4.4 | 7.2 | 4.2083 | 0
| 0.70139 | 256.614 | 35.612 | 37.992 | 34.712 | 63.705 |  | 2.1458 | 3.9 | 7.2 | 4.25 | 0
| 0.70833 | 237.523 | 33.951 | 36.487 | 33.219 | 60.884 |  | 2.1667 | 3.3 | 7.2 | 4.2917 | 0
| 0.71528 | 214.765 | 32.361 | 35.018 | 31.789 | 58.073 |  | 2.1875 | 3.2 | 7.2 | 4.3333 | 0
| 0.72222 | 195.173 | 30.73 | 33.5 | 30.317 | 55.176 |  | 2.2083 | 2.8 | 7.2 | 4.375 | 0
| 0.72917 | 183.054 | 29.266 | 32.08 | 28.946 | 52.397 |  | 2.2292 | 2.7 | 7.2 | 4.4167 | 0
| 0.73611 | 142.177 | 27.559 | 30.511 | 27.405 | 49.389 |  | 2.25 | 2.6 | 7.2 | 4.4583 | 0
| 0.74306 | 105.214 | 25.751 | 28.826 | 25.727 | 46.191 |  | 2.2708 | 2.6 | 7.2 | 4.5 | 0
| 0.75 | 66.602 | 24.121 | 27.248 | 24.176 | 43.097 |  | 2.2917 | 2.9 | 7.2 | 4.5417 | 0
| 0.75694 | 58.457 | 22.886 | 25.958 | 22.952 | 40.38 |  | 2.3125 | 3.4 | 7.2 | 4.5833 | 0
| 0.76389 | 48.714 | 22.005 | 24.971 | 22.07 | 38.115 |  | 2.3333 | 4.3 | 7.2 | 4.625 | 0
| 0.77083 | 39.893 | 21.318 | 24.175 | 21.372 | 36.178 |  | 2.3542 | 4.9 | 7.2 | 4.6667 | 0
| 0.77778 | 48.306 | 20.756 | 23.514 | 20.787 | 34.509 |  | 2.375 | 5.8 | 7.2 | 4.7083 | 0.4
| 0.78472 | 58.382 | 20.376 | 23.014 | 20.379 | 33.153 |  | 2.3958 | 8.7 | 7.2 | 4.75 | 0
| 0.79167 | 68.508 | 20.112 | 22.642 | 20.087 | 32.05 |  | 2.4167 | 8.9 | 7.2 | 4.7917 | 0
| 0.79861 | 68.529 | 19.899 | 22.341 | 19.852 | 31.148 |  | 2.4375 | 9.2 | 7.2 | 4.8333 | 0
| 0.80556 | 60.153 | 19.642 | 22.032 | 19.593 | 30.305 |  | 2.4583 | 9.9 | 7.2 | 4.875 | 0
| 0.8125 | 60.066 | 19.361 | 21.699 | 19.295 | 29.484 |  | 2.4792 | 10.2 | 7.2 | 4.9167 | 0
| 0.81944 | 68.536 | 19.145 | 21.431 | 19.063 | 28.797 |  | 2.5 | 9.7 | 7.2 | 4.9583 | 0
| 0.82639 | 79.106 | 19.081 | 21.286 | 18.975 | 28.313 |  | 2.5208 | 9.3 | 7.2 | 5 | 0
| 0.83333 | 98.806 | 19.153 | 21.257 | 19 | 28.042 |  | 2.5417 | 10.5 | 7.2
| 0.84028 | 98.835 | 19.201 | 21.248 | 19.037 | 27.846 |  | 2.5625 | 11.5 | 7.2
| 0.84722 | 99.395 | 19.168 | 21.171 | 18.986 | 27.613 |  | 2.5833 | 11.7 | 7.2
| 0.85417 | 109.418 | 19.197 | 21.157 | 18.997 | 27.478 |  | 2.6042 | 11.1 | 7.2
| 0.86111 | 109.596 | 19.214 | 21.138 | 19.002 | 27.361 |  | 2.625 | 10.9 | 7.2
| 0.86806 | 109.699 | 19.174 | 21.071 | 18.958 | 27.222 |  | 2.6458 | 11.2 | 7.2
| 0.875 | 110.145 | 19.119 | 21 | 18.895 | 27.064 |  | 2.6667 | 12.4 | 7.2
| 0.88194 | 118.144 | 19.188 | 21.021 | 18.938 | 27.04 |  | 2.6875 | 12.1 | 7.2
| 0.88889 | 118.228 | 19.182 | 20.987 | 18.935 | 26.977 |  | 2.7083 | 12.1 | 7.2
| 0.89583 | 118.238 | 19.152 | 20.943 | 18.894 | 26.893 |  | 2.7292 | 13.2 | 7.2
| 0.90278 | 118.535 | 19.106 | 20.885 | 18.844 | 26.796 |  | 2.75 | 12.1 | 7.2
| 0.90972 | 118.127 | 19.051 | 20.82 | 18.789 | 26.689 |  | 2.7708 | 12.2 | 7.2
| 0.91667 | 127.287 | 19.156 | 20.871 | 18.867 | 26.735 |  | 2.7917 | 12.1 | 7.2
| 0.92361 | 126.931 | 19.176 | 20.877 | 18.875 | 26.743 |  | 2.8125 | 10.7 | 7.2
| 0.93056 | 127.152 | 19.159 | 20.844 | 18.863 | 26.707 |  | 2.8333 | 8.7 | 7.2
| 0.9375 | 127.329 | 19.135 | 20.813 | 18.832 | 26.668 |  | 2.8542 | 7.6 | 7.8
| 0.94444 | 118.079 | 19.044 | 20.739 | 18.762 | 26.56 |  | 2.875 | 7.1 | 7.8
| 0.95139 | 119.135 | 18.878 | 20.578 | 18.597 | 26.352 |  | 2.8958 | 6.4 | 7.8
| 0.95833 | 110.156 | 18.67 | 20.396 | 18.415 | 26.083 |  | 2.9167 | 6.2 | 7.8
| 0.96528 | 110.206 | 18.513 | 20.228 | 18.252 | 25.822 |  | 2.9375 | 6 | 7.8
| 0.97222 | 109.167 | 18.404 | 20.112 | 18.137 | 25.607 |  | 2.9583 | 6.6 | 7.8
| 0.97917 | 109.329 | 18.3 | 19.983 | 18.034 | 25.403 |  | 2.9792 | 6.8 | 7.8
| 0.98611 | 109.87 | 18.219 | 19.895 | 17.954 | 25.222 |  | 3 | 7.3 | 7.8
| 0.99306 | 101.612 | 18.024 | 19.714 | 17.78 | 24.941 |  | 3.0208 | 7.6 | 7.8
| 1 | 101.729 | 17.907 | 19.585 | 17.656 | 24.715 |  | 3.0417 | 7.6 | 7.8
| 1.0069 | 102.014 | 17.817 | 19.481 | 17.561 | 24.515 |  | 3.0625 | 7.2 | 7.8
| 1.0139 | 91.788 | 17.601 | 19.28 | 17.369 | 24.202 |  | 3.0833 | 7.2 | 7.8
| 1.0208 | 83.39 | 17.387 | 19.08 | 17.168 | 23.871 |  | 3.1042 | 6.8 | 7.8
| 1.0278 | 83.429 | 17.225 | 18.905 | 17.005 | 23.569 |  | 3.125 | 6.3 | 7.8
| 1.0347 | 83.672 | 17.114 | 18.769 | 16.89 | 23.316 |  | 3.1458 | 6.6 | 7.8
| 1.0417 | 82.838 | 17.013 | 18.654 | 16.785 | 23.094 |  | 3.1667 | 6.2 | 7.8
| 1.0486 | 83.498 | 16.935 | 18.555 | 16.702 | 22.9 |  | 3.1875 | 5.9 | 7.8
| 1.0556 | 83.315 | 16.865 | 18.466 | 16.629 | 22.733 |  | 3.2083 | 5.2 | 7.8
| 1.0625 | 83.513 | 16.801 | 18.39 | 16.565 | 22.577 |  | 3.2292 | 4.3 | 7.8
| 1.0694 | 83.001 | 16.742 | 18.314 | 16.5 | 22.436 |  | 3.25 | 4.6 | 7.8
| 1.0764 | 83.045 | 16.684 | 18.243 | 16.443 | 22.3 |  | 3.2708 | 4.2 | 7.8
| 1.0833 | 83.189 | 16.632 | 18.181 | 16.387 | 22.182 |  | 3.2917 | 3.3 | 7.8
| 1.0903 | 83.536 | 16.576 | 18.118 | 16.334 | 22.071 |  | 3.3125 | 3.4 | 7.8
| 1.0972 | 83.52 | 16.535 | 18.062 | 16.287 | 21.97 |  | 3.3333 | 4.2 | 7.8
| 1.1042 | 83.382 | 16.492 | 18.001 | 16.24 | 21.868 |  | 3.3542 | 7.9 | 7.8
| 1.1111 | 83.2 | 16.45 | 17.951 | 16.191 | 21.777 |  | 3.375 | 8.2 | 7.8
| 1.1181 | 83.391 | 16.404 | 17.894 | 16.147 | 21.685 |  | 3.3958 | 8.9 | 7.8
| 1.125 | 83.431 | 16.362 | 17.842 | 16.101 | 21.603 |  | 3.4167 | 9.3 | 7.8
| 1.1319 | 83.204 | 16.321 | 17.793 | 16.065 | 21.524 |  | 3.4375 | 9.6 | 7.8
| 1.1389 | 83.347 | 16.283 | 17.744 | 16.026 | 21.439 |  | 3.4583 | 9.4 | 7.8
| 1.1458 | 83.479 | 16.245 | 17.701 | 15.989 | 21.37 |  | 3.4792 | 9.2 | 7.8
| 1.1528 | 83.506 | 16.213 | 17.657 | 15.951 | 21.303 |  | 3.5 | 9.2 | 7.8
| 1.1597 | 83.484 | 16.181 | 17.614 | 15.909 | 21.235 |  | 3.5208 | 9.7 | 7.8
| 1.1667 | 83.721 | 16.148 | 17.574 | 15.882 | 21.168 |  | 3.5417 | 9.3 | 7.8
| 1.1736 | 82.073 | 16.105 | 17.522 | 15.835 | 21.098 |  | 3.5625 | 10.3 | 7.8
| 1.1806 | 82.358 | 16.057 | 17.473 | 15.792 | 21.02 |  | 3.5833 | 11.8 | 7.8
| 1.1875 | 82.232 | 16.024 | 17.429 | 15.752 | 20.949 |  | 3.6042 | 12 | 7.8
| 1.1944 | 82.139 | 15.987 | 17.384 | 15.721 | 20.89 |  | 3.625 | 12.9 | 7.8
| 1.2014 | 81.75 | 15.951 | 17.344 | 15.681 | 20.818 |  | 3.6458 | 12.7 | 7.8
| 1.2083 | 81.782 | 15.925 | 17.304 | 15.646 | 20.761 |  | 3.6667 | 13.2 | 7.8
| 1.2153 | 81.935 | 15.891 | 17.264 | 15.614 | 20.704 |  | 3.6875 | 13.1 | 7.8
| 1.2222 | 90.165 | 15.964 | 17.306 | 15.668 | 20.746 |  | 3.7083 | 12.9 | 7.8
| 1.2292 | 90.003 | 15.985 | 17.313 | 15.681 | 20.763 |  | 3.7292 | 9.4 | 7.8
| 1.2361 | 89.966 | 15.98 | 17.3 | 15.679 | 20.762 |  | 3.75 | 8.8 | 7.8
| 1.2431 | 90.03 | 15.97 | 17.288 | 15.667 | 20.755 |  | 3.7708 | 8.6 | 7.8
| 1.25 | 91.175 | 15.963 | 17.277 | 15.657 | 20.746 |  | 3.7917 | 8.6 | 7.8
| 1.2569 | 81.919 | 15.866 | 17.197 | 15.577 | 20.654 |  | 3.8125 | 8.3 | 7.8
| 1.2639 | 81.709 | 15.785 | 17.114 | 15.492 | 20.546 |  | 3.8333 | 8.4 | 7.8
| 1.2708 | 73.137 | 15.635 | 16.984 | 15.36 | 20.361 |  | 3.8542 | 8.2 | 7.8
| 1.2778 | 63.006 | 15.508 | 16.863 | 15.244 | 20.185 |  | 3.875 | 7.8 | 7.8
| 1.2847 | 53.516 | 15.337 | 16.709 | 15.087 | 19.942 |  | 3.8958 | 7.9 | 7.8
| 1.2917 | 45.277 | 15.165 | 16.54 | 14.919 | 19.681 |  | 3.9167 | 8.2 | 7.8
| 1.2986 | 35.109 | 15.003 | 16.381 | 14.765 | 19.416 |  | 3.9375 | 8.4 | 7.8
| 1.3056 | 25.898 | 14.842 | 16.221 | 14.613 | 19.149 |  | 3.9583 | 8.3 | 7.8
| 1.3125 | 16.492 | 14.699 | 16.072 | 14.473 | 18.894 |  | 3.9792 | 8.3 | 7.8
| 1.3194 | 16.623 | 14.595 | 15.949 | 14.366 | 18.675 |  | 4 | 8.4 | 7.8
| 1.3264 | 36.581 | 14.566 | 15.892 | 14.318 | 18.536 |  | 4.0208 | 8.7 | 7.8
| 1.3333 | 45.654 | 14.597 | 15.885 | 14.339 | 18.485 |  | 4.0417 | 7.7 | 7.8
| 1.3403 | 68.888 | 14.722 | 15.958 | 14.43 | 18.555 |  | 4.0625 | 6.7 | 7.8
| 1.3472 | 90.867 | 14.995 | 16.162 | 14.661 | 18.82 |  | 4.0833 | 5.8 | 7.8
| 1.3542 | 113.367 | 15.412 | 16.49 | 15.026 | 19.295 |  | 4.1042 | 5.2 | 7.8
| 1.3611 | 135.854 | 15.99 | 16.959 | 15.533 | 19.998 |  | 4.125 | 5.8 | 7.8
| 1.3681 | 158.955 | 16.735 | 17.59 | 16.199 | 20.962 |  | 4.1458 | 6.3 | 7.8
| 1.375 | 182.882 | 17.696 | 18.416 | 17.067 | 22.247 |  | 4.1667 | 7 | 7.8
| 1.3819 | 202.928 | 18.789 | 19.381 | 18.063 | 23.788 |  | 4.1875 | 6.4 | 7.8
| 1.3889 | 213.27 | 19.798 | 20.328 | 19.016 | 25.356 |  | 4.2083 | 6.2 | 7.8
| 1.3958 | 237.133 | 21.026 | 21.438 | 20.118 | 27.212 |  | 4.2292 | 5.9 | 7.8
| 1.4028 | 248.429 | 22.24 | 22.571 | 21.25 | 29.152 |  | 4.25 | 5.8 | 7.8
| 1.4097 | 270.973 | 23.637 | 23.84 | 22.506 | 31.333 |  | 4.2708 | 5.1 | 7.8
| 1.4167 | 281.492 | 25.09 | 25.195 | 23.848 | 33.676 |  | 4.2917 | 5.3 | 7.8
| 1.4236 | 300.385 | 26.649 | 26.63 | 25.264 | 36.211 |  | 4.3125 | 5.7 | 7.8
| 1.4306 | 311.507 | 28.038 | 27.947 | 26.532 | 38.605 |  | 4.3333 | 6.2 | 7.8
| 1.4375 | 318.396 | 29.504 | 29.34 | 27.879 | 41.115 |  | 4.3542 | 6.8 | 7.8
| 1.4444 | 325.197 | 30.849 | 30.633 | 29.114 | 43.556 |  | 4.375 | 7.4 | 7.8
| 1.4514 | 335.808 | 32.267 | 31.958 | 30.383 | 46.064 |  | 4.3958 | 7.9 | 7.8
| 1.4583 | 346.512 | 33.379 | 33.052 | 31.384 | 48.272 |  | 4.4167 | 8.4 | 7.8
| 1.4653 | 353.669 | 34.63 | 34.248 | 32.517 | 50.577 |  | 4.4375 | 9.7 | 7.8
| 1.4722 | 362.566 | 35.905 | 35.448 | 33.656 | 52.904 |  | 4.4583 | 10.1 | 7.8
| 1.4792 | 371.207 | 37.416 | 36.843 | 35.021 | 55.485 |  | 4.4792 | 11.2 | 7.8
| 1.4861 | 378.774 | 38.648 | 38.035 | 36.139 | 57.835 |  | 4.5 | 11 | 7.8
| 1.4931 | 377.108 | 39.733 | 39.142 | 37.173 | 60.054 |  | 4.5208 | 10.8 | 7.8
| 1.5 | 383.722 | 40.806 | 40.184 | 38.132 | 62.214 |  | 4.5417 | 10.9 | 7.8
| 1.5069 | 384.451 | 41.634 | 41.053 | 38.913 | 64.094 |  | 4.5625 | 11.6 | 7.8
| 1.5139 | 392.026 | 42.457 | 41.874 | 39.648 | 65.899 |  | 4.5833 | 13.4 | 7.8
| 1.5208 | 390.907 | 43.338 | 42.763 | 40.48 | 67.73 |  | 4.6042 | 13.7 | 7.8
| 1.5278 | 400.103 | 44.348 | 43.704 | 41.379 | 69.668 |  | 4.625 | 13.2 | 7.8
| 1.5347 | 408.413 | 45.624 | 44.86 | 42.512 | 71.881 |  | 4.6458 | 13.6 | 7.8
| 1.5417 | 416.408 | 47.006 | 46.122 | 43.751 | 74.299 |  | 4.6667 | 13.2 | 7.8
| 1.5486 | 416.853 | 48.076 | 47.194 | 44.758 | 76.475 |  | 4.6875 | 12.6 | 7.8
| 1.5556 | 417.904 | 48.823 | 48.007 | 45.473 | 78.341 |  | 4.7083 | 12.1 | 7.8
| 1.5625 | 417.052 | 49.435 | 48.688 | 46.058 | 79.987 |  | 4.7292 | 12.3 | 7.8
| 1.5694 | 417.1 | 49.959 | 49.288 | 46.569 | 81.459 |  | 4.75 | 11.7 | 7.8
| 1.5764 | 417.015 | 50.373 | 49.777 | 46.983 | 82.728 |  | 4.7708 | 11.2 | 7.8
| 1.5833 | 425.075 | 50.973 | 50.37 | 47.509 | 84.107 |  | 4.7917 | 10.4 | 7.8
| 1.5903 | 424.689 | 51.724 | 51.112 | 48.229 | 85.657 |  | 4.8125 | 9.8 | 7.8
| 1.5972 | 417.361 | 51.822 | 51.397 | 48.412 | 86.515 |  | 4.8333 | 9.3 | 7.8
| 1.6042 | 412.217 | 51.623 | 51.387 | 48.293 | 86.888 |  | 4.8542 | 8.9 | 7.8
| 1.6111 | 403.202 | 51.106 | 51.108 | 47.914 | 86.784 |  | 4.875 | 8.6 | 7.8
| 1.6181 | 385.682 | 50.032 | 50.363 | 47.075 | 85.879 |  | 4.8958 | 8.7 | 7.8
| 1.625 | 376.344 | 48.969 | 49.53 | 46.181 | 84.739 |  | 4.9167 | 8.8 | 7.8
| 1.6319 | 369.313 | 47.771 | 48.536 | 45.143 | 83.243 |  | 4.9375 | 8.7 | 7.8
| 1.6389 | 361.208 | 46.696 | 47.609 | 44.219 | 81.717 |  | 4.9583 | 8.8 | 7.8
| 1.6458 | 351.82 | 45.591 | 46.655 | 43.27 | 80.065 |  | 4.9792 | 8.9 | 7.8
| 1.6528 | 343.708 | 44.549 | 45.725 | 42.366 | 78.381 |  | 5 | 8.4 | 7.8
| 1.6597 | 335.537 | 43.479 | 44.771 | 41.433 | 76.6
| 1.6667 | 326.397 | 42.402 | 43.805 | 40.487 | 74.763
| 1.6736 | 316.374 | 41.256 | 42.782 | 39.487 | 72.82
| 1.6806 | 298.042 | 39.822 | 41.543 | 38.249 | 70.524
| 1.6875 | 286.072 | 38.418 | 40.277 | 36.991 | 68.16
| 1.6944 | 275.53 | 37.027 | 39.007 | 35.745 | 65.746
| 1.7014 | 252.269 | 35.412 | 37.576 | 34.321 | 63.061
| 1.7083 | 240.666 | 33.864 | 36.144 | 32.906 | 60.37
| 1.7153 | 215.419 | 32.199 | 34.637 | 31.431 | 57.527
| 1.7222 | 203.768 | 30.687 | 33.194 | 30.054 | 54.767
| 1.7292 | 177.428 | 29.129 | 31.727 | 28.635 | 51.932
| 1.7361 | 144.71 | 27.396 | 30.132 | 27.063 | 48.902
| 1.7431 | 107.582 | 25.61 | 28.464 | 25.417 | 45.744
| 1.75 | 70.518 | 23.999 | 26.898 | 23.89 | 42.685
| 1.7569 | 58.787 | 22.765 | 25.618 | 22.687 | 39.996
| 1.7639 | 49.473 | 21.882 | 24.642 | 21.811 | 37.749
| 1.7708 | 39.585 | 21.194 | 23.847 | 21.114 | 35.832
| 1.7778 | 40.275 | 20.622 | 23.18 | 20.533 | 34.169
| 1.7847 | 51.693 | 20.246 | 22.697 | 20.135 | 32.837
| 1.7917 | 61.918 | 19.993 | 22.329 | 19.853 | 31.762
| 1.7986 | 61.881 | 19.717 | 21.984 | 19.57 | 30.802
| 1.8056 | 61.737 | 19.463 | 21.67 | 19.301 | 29.945
| 1.8125 | 61.506 | 19.224 | 21.373 | 19.056 | 29.182
| 1.8194 | 62.013 | 19.009 | 21.106 | 18.828 | 28.499
| 1.8264 | 83.109 | 18.976 | 20.981 | 18.755 | 28.047
| 1.8333 | 94.666 | 19.037 | 20.957 | 18.783 | 27.779
| 1.8403 | 103.168 | 19.126 | 20.974 | 18.845 | 27.627
| 1.8472 | 102.957 | 19.122 | 20.939 | 18.841 | 27.452
| 1.8542 | 103.143 | 19.075 | 20.868 | 18.787 | 27.252
| 1.8611 | 103.585 | 19.006 | 20.782 | 18.718 | 27.043
| 1.8681 | 112.777 | 19.08 | 20.797 | 18.765 | 26.996
| 1.875 | 112.898 | 19.066 | 20.764 | 18.754 | 26.892
| 1.8819 | 113.609 | 19.032 | 20.716 | 18.713 | 26.778
| 1.8889 | 113.844 | 18.982 | 20.655 | 18.666 | 26.655
| 1.8958 | 113.891 | 18.928 | 20.586 | 18.61 | 26.532
| 1.9028 | 114.25 | 18.873 | 20.517 | 18.554 | 26.406
| 1.9097 | 123.423 | 18.979 | 20.575 | 18.636 | 26.446
| 1.9167 | 123.438 | 18.996 | 20.574 | 18.647 | 26.432
| 1.9236 | 123.647 | 18.988 | 20.555 | 18.642 | 26.396
| 1.9306 | 123.894 | 18.953 | 20.52 | 18.611 | 26.343
| 1.9375 | 124.376 | 18.924 | 20.483 | 18.586 | 26.283
| 1.9444 | 122.898 | 18.889 | 20.448 | 18.551 | 26.22
| 1.9514 | 114.362 | 18.757 | 20.333 | 18.434 | 26.053
| 1.9583 | 113.832 | 18.586 | 20.176 | 18.274 | 25.82
| 1.9653 | 105.598 | 18.423 | 20.024 | 18.131 | 25.578
| 1.9722 | 105.802 | 18.245 | 19.85 | 17.958 | 25.298
| 1.9792 | 105.791 | 18.133 | 19.724 | 17.844 | 25.069
| 1.9861 | 106.377 | 18.048 | 19.627 | 17.767 | 24.879
| 1.9931 | 106.429 | 17.978 | 19.546 | 17.694 | 24.71
| 2 | 106.272 | 17.915 | 19.474 | 17.636 | 24.563
| 2.0069 | 96.825 | 17.747 | 19.323 | 17.488 | 24.317
| 2.0139 | 86.981 | 17.548 | 19.144 | 17.312 | 24.025
| 2.0208 | 86.246 | 17.349 | 18.949 | 17.112 | 23.699
| 2.0278 | 86.35 | 17.222 | 18.814 | 16.988 | 23.438
| 2.0347 | 86.435 | 17.129 | 18.7 | 16.897 | 23.215
| 2.0417 | 86.781 | 17.053 | 18.61 | 16.826 | 23.027
| 2.0486 | 86.669 | 16.989 | 18.533 | 16.758 | 22.859
| 2.0556 | 86.832 | 16.924 | 18.465 | 16.696 | 22.709
| 2.0625 | 86.79 | 16.872 | 18.397 | 16.641 | 22.569
| 2.0694 | 86.742 | 16.818 | 18.338 | 16.593 | 22.448
| 2.0764 | 86.842 | 16.77 | 18.279 | 16.544 | 22.323
| 2.0833 | 86.735 | 16.725 | 18.224 | 16.502 | 22.221
| 2.0903 | 87.119 | 16.686 | 18.176 | 16.461 | 22.122
| 2.0972 | 79.523 | 16.57 | 18.075 | 16.365 | 21.956
| 2.1042 | 79.384 | 16.479 | 17.986 | 16.273 | 21.792
| 2.1111 | 79.491 | 16.415 | 17.912 | 16.213 | 21.662
| 2.1181 | 79.462 | 16.365 | 17.85 | 16.157 | 21.543
| 2.125 | 79.254 | 16.317 | 17.793 | 16.116 | 21.432
| 2.1319 | 79.63 | 16.271 | 17.739 | 16.075 | 21.331
| 2.1389 | 79.312 | 16.23 | 17.692 | 16.034 | 21.239
| 2.1458 | 79.516 | 16.194 | 17.646 | 15.992 | 21.153
| 2.1528 | 79.412 | 16.155 | 17.604 | 15.954 | 21.069
| 2.1597 | 79.659 | 16.127 | 17.566 | 15.924 | 20.993
| 2.1667 | 79.494 | 16.093 | 17.523 | 15.893 | 20.921
| 2.1736 | 79.689 | 16.063 | 17.491 | 15.865 | 20.86
| 2.1806 | 79.701 | 16.033 | 17.457 | 15.834 | 20.792
| 2.1875 | 79.675 | 16.001 | 17.418 | 15.802 | 20.733
| 2.1944 | 79.836 | 15.972 | 17.383 | 15.775 | 20.673
| 2.2014 | 87.055 | 16.025 | 17.407 | 15.815 | 20.687
| 2.2083 | 87.301 | 16.047 | 17.422 | 15.831 | 20.7
| 2.2153 | 87.22 | 16.048 | 17.413 | 15.832 | 20.699
| 2.2222 | 87.071 | 16.041 | 17.405 | 15.83 | 20.683
| 2.2292 | 87.006 | 16.027 | 17.388 | 15.816 | 20.67
| 2.2361 | 87.117 | 16.014 | 17.37 | 15.801 | 20.644
| 2.2431 | 87.326 | 15.993 | 17.351 | 15.787 | 20.62
| 2.25 | 87.091 | 15.979 | 17.332 | 15.768 | 20.589
| 2.2569 | 86.464 | 15.959 | 17.307 | 15.742 | 20.558
| 2.2639 | 78.913 | 15.839 | 17.207 | 15.641 | 20.425
| 2.2708 | 71.322 | 15.735 | 17.112 | 15.55 | 20.291
| 2.2778 | 61.902 | 15.588 | 16.98 | 15.416 | 20.091
| 2.2847 | 61.83 | 15.456 | 16.854 | 15.288 | 19.885
| 2.2917 | 53.551 | 15.299 | 16.702 | 15.143 | 19.654
| 2.2986 | 42.334 | 15.13 | 16.542 | 14.981 | 19.385
| 2.3056 | 32.243 | 14.976 | 16.386 | 14.836 | 19.128
| 2.3125 | 21.203 | 14.833 | 16.243 | 14.7 | 18.873
| 2.3194 | 20.566 | 14.729 | 16.127 | 14.596 | 18.655
| 2.3264 | 32.261 | 14.699 | 16.072 | 14.56 | 18.531
| 2.3333 | 43.554 | 14.721 | 16.061 | 14.57 | 18.465
| 2.3403 | 69.462 | 14.877 | 16.145 | 14.676 | 18.548
| 2.3472 | 89.787 | 15.143 | 16.358 | 14.916 | 18.821
| 2.3542 | 113.24 | 15.581 | 16.699 | 15.289 | 19.304
| 2.3611 | 136.432 | 16.18 | 17.197 | 15.823 | 20.037
| 2.3681 | 159.552 | 16.947 | 17.838 | 16.511 | 21.024
| 2.375 | 182.848 | 17.901 | 18.663 | 17.372 | 22.309
| 2.3819 | 206.314 | 18.853 | 19.538 | 18.258 | 23.721
| 2.3889 | 218.517 | 20.004 | 20.566 | 19.295 | 25.398
| 2.3958 | 241.534 | 21.098 | 21.587 | 20.311 | 27.131
| 2.4028 | 251.901 | 22.469 | 22.822 | 21.537 | 29.197
| 2.4097 | 274.599 | 23.805 | 24.071 | 22.776 | 31.338
| 2.4167 | 285.118 | 25.338 | 25.464 | 24.157 | 33.749
| 2.4236 | 302.542 | 26.852 | 26.883 | 25.546 | 36.218
| 2.4306 | 310.865 | 28.383 | 28.305 | 26.931 | 38.759
| 2.4375 | 319.377 | 29.841 | 29.684 | 28.261 | 41.278
| 2.4444 | 328.515 | 31.225 | 31 | 29.518 | 43.751
| 2.4514 | 336.065 | 32.415 | 32.154 | 30.592 | 46.031
| 2.4583 | 344.522 | 33.649 | 33.334 | 31.695 | 48.318
| 2.4653 | 352.783 | 34.921 | 34.544 | 32.84 | 50.616
| 2.4722 | 365.31 | 36.122 | 35.702 | 33.942 | 52.878
| 2.4792 | 376.262 | 37.561 | 37.047 | 35.238 | 55.39
| 2.4861 | 375.003 | 39.125 | 38.487 | 36.639 | 58.074
| 2.4931 | 383.581 | 40.07 | 39.487 | 37.534 | 60.185
| 2.5 | 383.253 | 41.26 | 40.631 | 38.607 | 62.463
| 2.5069 | 390.831 | 42.016 | 41.442 | 39.311 | 64.287
| 2.5139 | 388.993 | 43.056 | 42.439 | 40.252 | 66.324
| 2.5208 | 388.453 | 43.693 | 43.142 | 40.863 | 67.949
| 2.5278 | 396.763 | 44.678 | 44.055 | 41.732 | 69.814
| 2.5347 | 408.006 | 46.023 | 45.252 | 42.918 | 72.076
| 2.5417 | 415.447 | 47.463 | 46.556 | 44.21 | 74.542
| 2.5486 | 416.033 | 48.513 | 47.623 | 45.198 | 76.712
| 2.5556 | 416.289 | 49.246 | 48.421 | 45.901 | 78.543
| 2.5625 | 415.604 | 49.836 | 49.088 | 46.464 | 80.15
| 2.5694 | 416.993 | 50.338 | 49.665 | 46.949 | 81.577
| 2.5764 | 420.027 | 50.914 | 50.266 | 47.487 | 82.989
| 2.5833 | 419.394 | 51.402 | 50.825 | 47.978 | 84.322
| 2.5903 | 418.975 | 51.817 | 51.307 | 48.389 | 85.475
| 2.5972 | 419.686 | 52.132 | 51.693 | 48.712 | 86.471
| 2.6042 | 412.238 | 52.084 | 51.816 | 48.744 | 87.012
| 2.6111 | 396.116 | 51.624 | 51.585 | 48.427 | 86.979
| 2.6181 | 387.685 | 50.545 | 50.843 | 47.573 | 86.099
| 2.625 | 371.529 | 49.433 | 49.976 | 46.634 | 84.928
| 2.6319 | 363.34 | 48.296 | 49.024 | 45.665 | 83.503
| 2.6389 | 355.835 | 47.27 | 48.138 | 44.785 | 82.041
| 2.6458 | 354.723 | 46.272 | 47.262 | 43.923 | 80.512
| 2.6528 | 344.26 | 45.111 | 46.269 | 42.936 | 78.748
| 2.6597 | 336.964 | 44.026 | 45.302 | 41.99 | 76.969
| 2.6667 | 327.65 | 42.902 | 44.303 | 41.011 | 75.101
| 2.6736 | 308.071 | 41.726 | 43.258 | 39.992 | 73.122
| 2.6806 | 299.715 | 40.294 | 42.011 | 38.746 | 70.824
| 2.6875 | 281.303 | 38.909 | 40.757 | 37.51 | 68.488
| 2.6944 | 270.248 | 37.357 | 39.381 | 36.152 | 65.924
| 2.7014 | 247.631 | 35.883 | 38.023 | 34.812 | 63.358
| 2.7083 | 236.053 | 34.222 | 36.525 | 33.332 | 60.566
| 2.7153 | 211.098 | 32.666 | 35.08 | 31.925 | 57.822
| 2.7222 | 191.909 | 30.999 | 33.529 | 30.424 | 54.908
| 2.7292 | 179.128 | 29.461 | 32.072 | 29.028 | 52.085
| 2.7361 | 135.992 | 27.801 | 30.534 | 27.527 | 49.143
| 2.7431 | 97.037 | 25.981 | 28.841 | 25.85 | 45.957
| 2.75 | 60.422 | 24.325 | 27.249 | 24.296 | 42.873
| 2.7569 | 52.995 | 23.093 | 25.966 | 23.086 | 40.184
| 2.7639 | 52.537 | 22.204 | 24.975 | 22.2 | 37.93
| 2.7708 | 43.093 | 21.491 | 24.166 | 21.486 | 35.998
| 2.7778 | 43.227 | 20.937 | 23.508 | 20.921 | 34.355
| 2.7847 | 52.467 | 20.542 | 23.001 | 20.503 | 33.003
| 2.7917 | 63.04 | 20.273 | 22.628 | 20.208 | 31.911
| 2.7986 | 63.119 | 20.016 | 22.291 | 19.934 | 30.964
| 2.8056 | 62.995 | 19.762 | 21.967 | 19.67 | 30.123
| 2.8125 | 56.092 | 19.519 | 21.675 | 19.42 | 29.368
| 2.8194 | 65.19 | 19.285 | 21.389 | 19.171 | 28.664
| 2.8264 | 86.083 | 19.227 | 21.252 | 19.088 | 28.193
| 2.8333 | 97.02 | 19.312 | 21.234 | 19.123 | 27.946
| 2.8403 | 97.119 | 19.332 | 21.198 | 19.13 | 27.726
| 2.8472 | 107.801 | 19.362 | 21.168 | 19.131 | 27.557
| 2.8542 | 108.118 | 19.401 | 21.168 | 19.163 | 27.455
| 2.8611 | 108.399 | 19.373 | 21.12 | 19.135 | 27.318
| 2.8681 | 108.728 | 19.32 | 21.048 | 19.074 | 27.164
| 2.875 | 118.16 | 19.341 | 21.021 | 19.068 | 27.074
| 2.8819 | 116.435 | 19.352 | 21.006 | 19.076 | 27.015
| 2.8889 | 116.506 | 19.322 | 20.954 | 19.043 | 26.918
| 2.8958 | 116.674 | 19.271 | 20.893 | 18.987 | 26.816
| 2.9028 | 116.786 | 19.215 | 20.828 | 18.934 | 26.699
| 2.9097 | 126.655 | 19.176 | 20.763 | 18.877 | 26.594
| 2.9167 | 126.505 | 19.287 | 20.83 | 18.971 | 26.663
| 2.9236 | 126.339 | 19.304 | 20.825 | 18.984 | 26.664
| 2.9306 | 126.7 | 19.289 | 20.805 | 18.973 | 26.634
| 2.9375 | 126.829 | 19.268 | 20.772 | 18.946 | 26.591
| 2.9444 | 118.277 | 19.226 | 20.731 | 18.911 | 26.531
| 2.9514 | 118.693 | 19.033 | 20.562 | 18.733 | 26.31
| 2.9583 | 109.151 | 18.845 | 20.395 | 18.565 | 26.06
| 2.9653 | 109.71 | 18.663 | 20.217 | 18.387 | 25.784
| 2.9722 | 109.744 | 18.545 | 20.087 | 18.271 | 25.562
| 2.9792 | 110.044 | 18.46 | 19.982 | 18.18 | 25.372
| 2.9861 | 100.532 | 18.376 | 19.89 | 18.102 | 25.201
| 2.9931 | 99.236 | 18.148 | 19.691 | 17.897 | 24.884
| 3 | 99.487 | 18.014 | 19.544 | 17.765 | 24.634
| 3.0069 | 100.157 | 17.923 | 19.438 | 17.668 | 24.432
| 3.0139 | 91.526 | 17.747 | 19.267 | 17.512 | 24.15
| 3.0208 | 82.156 | 17.54 | 19.078 | 17.326 | 23.835
| 3.0278 | 81.946 | 17.359 | 18.893 | 17.145 | 23.522
| 3.0347 | 82.069 | 17.237 | 18.756 | 17.023 | 23.261
| 3.0417 | 82.266 | 17.147 | 18.643 | 16.926 | 23.042
| 3.0486 | 82.329 | 17.064 | 18.55 | 16.847 | 22.847
| 3.0556 | 82.296 | 16.997 | 18.461 | 16.78 | 22.68
| 3.0625 | 82.332 | 16.934 | 18.388 | 16.714 | 22.528
| 3.0694 | 82.374 | 16.871 | 18.316 | 16.652 | 22.389
| 3.0764 | 82.563 | 16.816 | 18.25 | 16.596 | 22.26
| 3.0833 | 82.623 | 16.77 | 18.188 | 16.549 | 22.141
| 3.0903 | 82.83 | 16.719 | 18.131 | 16.494 | 22.03
| 3.0972 | 82.102 | 16.668 | 18.07 | 16.445 | 21.925
| 3.1042 | 82.411 | 16.619 | 18.015 | 16.395 | 21.825
| 3.1111 | 82.273 | 16.574 | 17.962 | 16.355 | 21.725
| 3.1181 | 82.282 | 16.536 | 17.911 | 16.308 | 21.637
| 3.125 | 82.159 | 16.493 | 17.861 | 16.267 | 21.554
| 3.1319 | 82.226 | 16.459 | 17.817 | 16.226 | 21.473
| 3.1389 | 82.085 | 16.417 | 17.767 | 16.193 | 21.394
| 3.1458 | 82.274 | 16.379 | 17.724 | 16.156 | 21.323
| 3.1528 | 82.438 | 16.343 | 17.681 | 16.116 | 21.251
| 3.1597 | 82.48 | 16.31 | 17.64 | 16.088 | 21.185
| 3.1667 | 82.531 | 16.271 | 17.599 | 16.048 | 21.12
| 3.1736 | 82.383 | 16.24 | 17.563 | 16.018 | 21.057
| 3.1806 | 82.347 | 16.211 | 17.522 | 15.984 | 20.994
| 3.1875 | 82.173 | 16.18 | 17.484 | 15.95 | 20.935
| 3.1944 | 82.24 | 16.147 | 17.45 | 15.922 | 20.878
| 3.2014 | 82.231 | 16.117 | 17.412 | 15.889 | 20.824
| 3.2083 | 82.221 | 16.086 | 17.372 | 15.859 | 20.772
| 3.2153 | 82.082 | 16.059 | 17.341 | 15.829 | 20.711
| 3.2222 | 90.408 | 16.117 | 17.369 | 15.868 | 20.751
| 3.2292 | 90.175 | 16.148 | 17.384 | 15.896 | 20.772
| 3.2361 | 90.07 | 16.14 | 17.379 | 15.893 | 20.777
| 3.2431 | 89.95 | 16.141 | 17.368 | 15.887 | 20.775
| 3.25 | 89.841 | 16.12 | 17.348 | 15.871 | 20.757
| 3.2569 | 81.213 | 16.036 | 17.286 | 15.801 | 20.674
| 3.2639 | 81.312 | 15.944 | 17.201 | 15.713 | 20.563
| 3.2708 | 72.443 | 15.807 | 17.077 | 15.585 | 20.383
| 3.2778 | 63.312 | 15.656 | 16.94 | 15.45 | 20.188
| 3.2847 | 56.226 | 15.493 | 16.79 | 15.298 | 19.955
| 3.2917 | 47.908 | 15.338 | 16.634 | 15.146 | 19.711
| 3.2986 | 38.164 | 15.155 | 16.466 | 14.982 | 19.437
| 3.3056 | 23.334 | 14.983 | 16.292 | 14.814 | 19.147
| 3.3125 | 13.881 | 14.844 | 16.151 | 14.681 | 18.896
| 3.3194 | 24.126 | 14.747 | 16.036 | 14.578 | 18.684
| 3.3264 | 35.001 | 14.727 | 15.988 | 14.545 | 18.559
| 3.3333 | 44.488 | 14.756 | 15.981 | 14.56 | 18.509
| 3.3403 | 67.424 | 14.887 | 16.064 | 14.665 | 18.591
| 3.3472 | 94.946 | 15.126 | 16.239 | 14.863 | 18.828
| 3.3542 | 117.019 | 15.57 | 16.586 | 15.243 | 19.307
| 3.3611 | 140.861 | 16.147 | 17.057 | 15.752 | 20.022
| 3.3681 | 163.404 | 16.904 | 17.693 | 16.428 | 20.994
| 3.375 | 186.648 | 17.847 | 18.509 | 17.281 | 22.262
| 3.3819 | 199.236 | 18.884 | 19.435 | 18.225 | 23.736
| 3.3889 | 226.289 | 19.951 | 20.4 | 19.188 | 25.33
| 3.3958 | 233.39 | 21.207 | 21.547 | 20.344 | 27.222
| 3.4028 | 256.799 | 22.458 | 22.699 | 21.479 | 29.187
| 3.4097 | 267.555 | 23.873 | 24 | 22.773 | 31.401
| 3.4167 | 290.005 | 25.32 | 25.337 | 24.076 | 33.733
| 3.4236 | 299.468 | 26.892 | 26.784 | 25.512 | 36.249
| 3.4306 | 310.27 | 28.346 | 28.149 | 26.83 | 38.7
| 3.4375 | 325.486 | 29.816 | 29.515 | 28.149 | 41.205
| 3.4444 | 332.601 | 31.149 | 30.798 | 29.366 | 43.636
| 3.4514 | 331.604 | 32.396 | 32.014 | 30.511 | 45.965
| 3.4583 | 340.981 | 33.656 | 33.21 | 31.626 | 48.268
| 3.4653 | 348.849 | 34.887 | 34.374 | 32.734 | 50.529
| 3.4722 | 358.441 | 36.24 | 35.646 | 33.948 | 52.912
| 3.4792 | 375.29 | 37.691 | 36.967 | 35.211 | 55.423
| 3.4861 | 373.908 | 39.055 | 38.283 | 36.478 | 57.925
| 3.4931 | 384.128 | 40.085 | 39.308 | 37.4 | 60.072
| 3.5 | 382.181 | 41.267 | 40.46 | 38.499 | 62.339
| 3.5069 | 386.06 | 42.131 | 41.35 | 39.289 | 64.257
| 3.5139 | 392.816 | 43.059 | 42.259 | 40.119 | 66.175
| 3.5208 | 391.116 | 43.905 | 43.133 | 40.925 | 68.007
| 3.5278 | 401.714 | 44.884 | 44.045 | 41.779 | 69.909
| 3.5347 | 409.526 | 46.117 | 45.17 | 42.882 | 72.084
| 3.5417 | 415.964 | 47.346 | 46.311 | 43.985 | 74.322
| 3.5486 | 420.257 | 48.491 | 47.423 | 45.036 | 76.531
| 3.5556 | 420.894 | 49.534 | 48.466 | 46.014 | 78.691
| 3.5625 | 419.645 | 50.212 | 49.227 | 46.665 | 80.463
| 3.5694 | 419.752 | 50.744 | 49.849 | 47.186 | 81.989
| 3.5764 | 420.558 | 51.218 | 50.397 | 47.657 | 83.387
| 3.5833 | 420.549 | 51.668 | 50.917 | 48.096 | 84.646
| 3.5903 | 421.763 | 52.073 | 51.387 | 48.504 | 85.811
| 3.5972 | 414.836 | 52.4 | 51.805 | 48.863 | 86.808
| 3.6042 | 415.03 | 52.264 | 51.831 | 48.789 | 87.256
| 3.6111 | 403.497 | 51.634 | 51.476 | 48.332 | 87.02
| 3.6181 | 384.253 | 50.698 | 50.842 | 47.613 | 86.273
| 3.625 | 376.947 | 49.404 | 49.84 | 46.528 | 84.885
| 3.6319 | 368.983 | 48.266 | 48.898 | 45.565 | 83.454
| 3.6389 | 358.946 | 47.151 | 47.947 | 44.613 | 81.888
| 3.6458 | 351.296 | 46.052 | 46.988 | 43.669 | 80.235
| 3.6528 | 343.237 | 44.977 | 46.033 | 42.739 | 78.506
| 3.6597 | 334.925 | 43.888 | 45.067 | 41.797 | 76.723
| 3.6667 | 324.235 | 42.766 | 44.065 | 40.821 | 74.837
| 3.6736 | 315.006 | 41.611 | 43.032 | 39.812 | 72.873
| 3.6806 | 296.477 | 40.251 | 41.845 | 38.635 | 70.655
| 3.6875 | 286.033 | 38.772 | 40.532 | 37.326 | 68.23
| 3.6944 | 266.999 | 37.316 | 39.216 | 36.039 | 65.756
| 3.7014 | 255.538 | 35.754 | 37.802 | 34.63 | 63.103
| 3.7083 | 231.76 | 34.176 | 36.371 | 33.232 | 60.403
| 3.7153 | 201.537 | 32.438 | 34.812 | 31.705 | 57.494
| 3.7222 | 188.734 | 30.724 | 33.2 | 30.134 | 54.507
| 3.7292 | 180.392 | 29.227 | 31.751 | 28.737 | 51.687
| 3.7361 | 138.445 | 27.575 | 30.232 | 27.267 | 48.746
| 3.7431 | 101.021 | 25.777 | 28.56 | 25.617 | 45.584
| 3.75 | 63.996 | 24.153 | 26.99 | 24.088 | 42.531
| 3.7569 | 54.197 | 22.917 | 25.704 | 22.874 | 39.856
| 3.7639 | 46.364 | 22.045 | 24.732 | 22.004 | 37.635
| 3.7708 | 46.369 | 21.351 | 23.932 | 21.3 | 35.727
| 3.7778 | 46.618 | 20.811 | 23.294 | 20.752 | 34.119
| 3.7847 | 55.174 | 20.416 | 22.788 | 20.334 | 32.776
| 3.7917 | 65.134 | 20.142 | 22.405 | 20.029 | 31.696
| 3.7986 | 65.281 | 19.89 | 22.082 | 19.765 | 30.774
| 3.8056 | 64.952 | 19.644 | 21.771 | 19.507 | 29.951
| 3.8125 | 58.035 | 19.372 | 21.455 | 19.238 | 29.172
| 3.8194 | 68.822 | 19.137 | 21.165 | 18.982 | 28.474
| 3.8264 | 80.063 | 19.084 | 21.026 | 18.899 | 28.009
| 3.8333 | 100.149 | 19.16 | 21.003 | 18.929 | 27.758
| 3.8403 | 99.916 | 19.224 | 21.004 | 18.971 | 27.591
| 3.8472 | 99.826 | 19.183 | 20.935 | 18.931 | 27.377
| 3.8542 | 109.724 | 19.146 | 20.861 | 18.877 | 27.176
| 3.8611 | 110.126 | 19.204 | 20.866 | 18.916 | 27.098
| 3.8681 | 110.419 | 19.178 | 20.822 | 18.887 | 26.983
| 3.875 | 110.617 | 19.13 | 20.748 | 18.834 | 26.846
| 3.8819 | 110.369 | 19.076 | 20.676 | 18.767 | 26.698
| 3.8889 | 119.09 | 19.094 | 20.657 | 18.771 | 26.633
| 3.8958 | 119.382 | 19.124 | 20.66 | 18.795 | 26.609
| 3.9028 | 119.707 | 19.102 | 20.626 | 18.772 | 26.553
| 3.9097 | 120.027 | 19.071 | 20.581 | 18.732 | 26.472
| 3.9167 | 129.238 | 19.066 | 20.547 | 18.715 | 26.42
| 3.9236 | 129.701 | 19.179 | 20.617 | 18.81 | 26.511
| 3.9306 | 129.923 | 19.203 | 20.628 | 18.83 | 26.535
| 3.9375 | 129.893 | 19.197 | 20.612 | 18.82 | 26.523
| 3.9444 | 120.927 | 19.064 | 20.515 | 18.71 | 26.4
| 3.9514 | 111.691 | 18.889 | 20.36 | 18.555 | 26.195
| 3.9583 | 110.589 | 18.643 | 20.135 | 18.322 | 25.869
| 3.9653 | 111.213 | 18.501 | 19.983 | 18.182 | 25.626
| 3.9722 | 110.88 | 18.402 | 19.868 | 18.08 | 25.419
| 3.9792 | 110.187 | 18.308 | 19.765 | 17.987 | 25.234
| 3.9861 | 101.829 | 18.197 | 19.65 | 17.885 | 25.037
| 3.9931 | 101.854 | 18.009 | 19.474 | 17.708 | 24.752
| 4 | 102.84 | 17.896 | 19.344 | 17.593 | 24.522
| 4.0069 | 92.379 | 17.783 | 19.231 | 17.496 | 24.314
| 4.0139 | 92.437 | 17.583 | 19.038 | 17.297 | 24.008
| 4.0208 | 84.868 | 17.393 | 18.855 | 17.123 | 23.703
| 4.0278 | 84.849 | 17.235 | 18.689 | 16.966 | 23.414
| 4.0347 | 85.036 | 17.121 | 18.56 | 16.855 | 23.172
| 4.0417 | 85.017 | 17.031 | 18.456 | 16.766 | 22.967
| 4.0486 | 85.146 | 16.958 | 18.364 | 16.688 | 22.781
| 4.0556 | 85.174 | 16.888 | 18.281 | 16.617 | 22.622
| 4.0625 | 85.223 | 16.828 | 18.205 | 16.551 | 22.474
| 4.0694 | 85.315 | 16.766 | 18.138 | 16.491 | 22.335
| 4.0764 | 85.194 | 16.714 | 18.067 | 16.442 | 22.214
| 4.0833 | 85.323 | 16.661 | 18.008 | 16.383 | 22.094
| 4.0903 | 85.707 | 16.614 | 17.951 | 16.337 | 21.994
| 4.0972 | 85.424 | 16.57 | 17.896 | 16.296 | 21.893
| 4.1042 | 85.604 | 16.525 | 17.845 | 16.246 | 21.799
| 4.1111 | 85.589 | 16.488 | 17.794 | 16.205 | 21.71
| 4.1181 | 85.644 | 16.444 | 17.745 | 16.165 | 21.627
| 4.125 | 85.377 | 16.406 | 17.693 | 16.119 | 21.543
| 4.1319 | 85.515 | 16.363 | 17.649 | 16.08 | 21.464
| 4.1389 | 85.471 | 16.328 | 17.601 | 16.036 | 21.39
| 4.1458 | 76.807 | 16.19 | 17.484 | 15.925 | 21.22
| 4.1528 | 76.837 | 16.106 | 17.39 | 15.834 | 21.078
| 4.1597 | 76.864 | 16.046 | 17.323 | 15.776 | 20.954
| 4.1667 | 84.741 | 16.074 | 17.322 | 15.785 | 20.927
| 4.1736 | 84.409 | 16.076 | 17.308 | 15.788 | 20.897
| 4.1806 | 84.619 | 16.052 | 17.283 | 15.767 | 20.857
| 4.1875 | 84.623 | 16.03 | 17.255 | 15.747 | 20.815
| 4.1944 | 84.753 | 16.007 | 17.226 | 15.717 | 20.768
| 4.2014 | 84.689 | 15.982 | 17.19 | 15.69 | 20.719
| 4.2083 | 84.365 | 15.953 | 17.154 | 15.66 | 20.67
| 4.2153 | 83.655 | 15.914 | 17.119 | 15.627 | 20.614
| 4.2222 | 84.677 | 15.895 | 17.087 | 15.602 | 20.567
| 4.2292 | 84.268 | 15.873 | 17.057 | 15.577 | 20.524
| 4.2361 | 84.169 | 15.843 | 17.028 | 15.547 | 20.48
| 4.2431 | 84.122 | 15.815 | 16.991 | 15.516 | 20.42
| 4.25 | 83.653 | 15.785 | 16.955 | 15.486 | 20.371
| 4.2569 | 84.144 | 15.755 | 16.922 | 15.454 | 20.324
| 4.2639 | 76.923 | 15.676 | 16.857 | 15.39 | 20.229
| 4.2708 | 76.021 | 15.59 | 16.774 | 15.307 | 20.111
| 4.2778 | 66.84 | 15.444 | 16.637 | 15.168 | 19.916
| 4.2847 | 59.231 | 15.284 | 16.497 | 15.029 | 19.695
| 4.2917 | 50.089 | 15.117 | 16.335 | 14.87 | 19.449
| 4.2986 | 41.429 | 14.956 | 16.183 | 14.719 | 19.198
| 4.3056 | 30.084 | 14.795 | 16.025 | 14.564 | 18.934
| 4.3125 | 13.457 | 14.651 | 15.875 | 14.431 | 18.688
| 4.3194 | 22.147 | 14.546 | 15.76 | 14.317 | 18.468
| 4.3264 | 31.602 | 14.511 | 15.7 | 14.279 | 18.328
| 4.3333 | 51.382 | 14.554 | 15.706 | 14.301 | 18.288
| 4.3403 | 73.325 | 14.695 | 15.791 | 14.409 | 18.374
| 4.3472 | 86.474 | 14.945 | 15.979 | 14.627 | 18.623
| 4.3542 | 115.629 | 15.351 | 16.294 | 14.973 | 19.074
| 4.3611 | 137.769 | 15.935 | 16.773 | 15.484 | 19.784
| 4.3681 | 161.889 | 16.702 | 17.416 | 16.167 | 20.769
| 4.375 | 184.23 | 17.649 | 18.232 | 17.014 | 22.034
| 4.3819 | 204.982 | 18.754 | 19.203 | 18.018 | 23.571
| 4.3889 | 215.081 | 19.812 | 20.181 | 19.001 | 25.184
| 4.3958 | 233.983 | 21.039 | 21.296 | 20.113 | 27.03
| 4.4236 | 297.234 | 26.423 | 26.294 | 24.995 | 35.722
| 4.4306 | 308.489 | 28.044 | 27.765 | 26.447 | 38.278
| 4.4375 | 320.255 | 29.537 | 29.159 | 27.797 | 40.785
| 4.4444 | 326.897 | 31.016 | 30.553 | 29.133 | 43.351
| 4.4514 | 335.377 | 32.253 | 31.743 | 30.237 | 45.659
| 4.4583 | 342.981 | 33.53 | 32.952 | 31.373 | 47.99
| 4.4653 | 352.461 | 34.707 | 34.084 | 32.408 | 50.192
| 4.4722 | 362.289 | 36.199 | 35.451 | 33.748 | 52.7
| 4.4792 | 369.153 | 37.571 | 36.751 | 34.991 | 55.181
| 4.4861 | 375.953 | 39.047 | 38.138 | 36.318 | 57.782
| 4.4931 | 375.911 | 40.003 | 39.135 | 37.207 | 59.898
| 4.5 | 384.521 | 41.211 | 40.284 | 38.273 | 62.16
| 4.5069 | 390.463 | 42.157 | 41.233 | 39.135 | 64.158
| 4.5139 | 389.648 | 43.079 | 42.17 | 39.99 | 66.116
| 4.5208 | 389.514 | 43.71 | 42.87 | 40.595 | 67.741
| 4.5278 | 396.432 | 44.628 | 43.733 | 41.409 | 69.541
| 4.5347 | 404.849 | 45.903 | 44.892 | 42.545 | 71.733
| 4.5417 | 412.524 | 47.269 | 46.143 | 43.773 | 74.122
| 4.5486 | 422.777 | 48.752 | 47.493 | 45.084 | 76.691
| 4.5556 | 422.676 | 49.718 | 48.496 | 45.999 | 78.813
| 4.5625 | 421.294 | 50.344 | 49.226 | 46.608 | 80.556
| 4.5694 | 420.739 | 50.823 | 49.811 | 47.08 | 82.049
| 4.5764 | 421.689 | 51.292 | 50.346 | 47.536 | 83.416
| 4.5833 | 422.365 | 51.784 | 50.9 | 48.021 | 84.741
| 4.5903 | 424.017 | 52.282 | 51.444 | 48.498 | 86.013
| 4.5972 | 415.966 | 52.463 | 51.769 | 48.747 | 86.876
| 4.6042 | 413.525 | 52.289 | 51.756 | 48.635 | 87.253
| 4.6111 | 402.747 | 51.691 | 51.427 | 48.206 | 87.056
| 4.6181 | 392.125 | 50.799 | 50.799 | 47.497 | 86.335
| 4.625 | 376.272 | 49.464 | 49.794 | 46.412 | 84.919
| 4.6319 | 368.514 | 48.174 | 48.724 | 45.308 | 83.296
| 4.6389 | 358.756 | 47.177 | 47.868 | 44.483 | 81.846
| 4.6458 | 349.575 | 46.084 | 46.927 | 43.555 | 80.208
| 4.6528 | 340.478 | 44.965 | 45.944 | 42.586 | 78.442
| 4.6597 | 328.552 | 43.789 | 44.916 | 41.584 | 76.546
| 4.6667 | 328.723 | 42.718 | 43.907 | 40.599 | 74.668
| 4.6736 | 318.579 | 41.575 | 42.885 | 39.605 | 72.698
| 4.6806 | 299.408 | 40.174 | 41.677 | 38.413 | 70.441
| 4.6875 | 289.685 | 38.771 | 40.415 | 37.161 | 68.092
| 4.6944 | 269.063 | 37.243 | 39.065 | 35.829 | 65.561
| 4.7014 | 257.506 | 35.711 | 37.661 | 34.437 | 62.945
| 4.7083 | 236.16 | 34.062 | 36.186 | 32.985 | 60.174
| 4.7153 | 214.698 | 32.364 | 34.631 | 31.475 | 57.289
| 4.7222 | 202.884 | 30.818 | 33.16 | 30.066 | 54.499
| 4.7292 | 177.34 | 29.262 | 31.704 | 28.671 | 51.673
| 4.7361 | 145.132 | 27.522 | 30.096 | 27.092 | 48.646
| 4.7431 | 108.009 | 25.716 | 28.427 | 25.447 | 45.491
| 4.75 | 70.179 | 24.074 | 26.846 | 23.912 | 42.423
| 4.7569 | 58.368 | 22.826 | 25.554 | 22.698 | 39.73
| 4.7639 | 48.54 | 21.932 | 24.565 | 21.817 | 37.488
| 4.7708 | 40.004 | 21.23 | 23.76 | 21.122 | 35.577
| 4.7778 | 40.191 | 20.653 | 23.095 | 20.539 | 33.922
| 4.7847 | 50.328 | 20.27 | 22.594 | 20.128 | 32.579
| 4.7917 | 61.221 | 20.005 | 22.225 | 19.838 | 31.505
| 4.7986 | 71.241 | 19.827 | 21.95 | 19.638 | 30.657
| 4.8056 | 62.955 | 19.53 | 21.608 | 19.338 | 29.791
| 4.8125 | 62.89 | 19.271 | 21.304 | 19.077 | 29.025
| 4.8194 | 62.885 | 19.053 | 21.029 | 18.846 | 28.348
| 4.8264 | 83.589 | 19.001 | 20.889 | 18.759 | 27.89
| 4.8333 | 92.259 | 19.035 | 20.84 | 18.767 | 27.604
| 4.8403 | 101.917 | 19.159 | 20.874 | 18.857 | 27.481
| 4.8472 | 103.539 | 19.151 | 20.834 | 18.843 | 27.305
| 4.8542 | 103.788 | 19.096 | 20.761 | 18.781 | 27.106
| 4.8611 | 103.707 | 19.027 | 20.667 | 18.709 | 26.901
| 4.8681 | 113.115 | 19.097 | 20.685 | 18.752 | 26.849
| 4.875 | 113.573 | 19.083 | 20.646 | 18.734 | 26.753
| 4.8819 | 113.479 | 19.041 | 20.591 | 18.686 | 26.643
| 4.8889 | 113.382 | 18.987 | 20.52 | 18.63 | 26.511
| 4.8958 | 113.815 | 18.932 | 20.447 | 18.572 | 26.379
| 4.9028 | 122.325 | 18.92 | 20.406 | 18.547 | 26.293
| 4.9097 | 122.633 | 18.979 | 20.435 | 18.601 | 26.302
| 4.9167 | 122.911 | 18.982 | 20.416 | 18.596 | 26.275
| 4.9236 | 123.32 | 18.965 | 20.39 | 18.574 | 26.228
| 4.9306 | 123.819 | 18.933 | 20.353 | 18.544 | 26.172
| 4.9375 | 123.756 | 18.895 | 20.309 | 18.511 | 26.106
| 4.9444 | 123.965 | 18.865 | 20.264 | 18.475 | 26.038
| 4.9514 | 113.912 | 18.729 | 20.157 | 18.367 | 25.881
| 4.9583 | 113.878 | 18.561 | 19.996 | 18.203 | 25.646
| 4.9653 | 105.033 | 18.342 | 19.801 | 18.009 | 25.349
| 4.9722 | 105.13 | 18.177 | 19.632 | 17.845 | 25.082
| 4.9792 | 105.075 | 18.062 | 19.508 | 17.734 | 24.846
| 4.9861 | 105.367 | 17.974 | 19.405 | 17.649 | 24.65
| 4.9931 | 104.646 | 17.89 | 19.31 | 17.568 | 24.473
| 5 | 104.381 | 17.816 | 19.226 | 17.49 | 24.303

## Experiment - Data - SF_V+VI
Electric Load and Cable Temperatures | [7 empty] | Weather Station Data
|  |  |  | Configuration (V) |  | Configuration (VI)
Parameter | Time | Electrical load (V) | Electrical load (VI) | Conductor Temperature | Protection Pipe Temperature | Conductor Temperature | Protection Pipe Temperature | Parameter | Time | Air Temperature | Soil Temperature [-0.8 m] | Time | Precipitation
Unit | d | A | A | °C | °C | °C | °C | Unit | d | °C | °C | d | mm/h
| 0 | 0.148 | 0.116 | 6.387 | 5.914 | 6.943 | 5.222 |  | 0 | 0.2 | 7 | 0 | 0
| 0.0069444 | 0.139 | 0.102 | 6.369 | 5.909 | 6.929 | 5.216 |  | 0.020833 | 0.1 | 7 | 0.041667 | 0
| 0.013889 | 0.15 | 0.017 | 6.355 | 5.898 | 6.92 | 5.206 |  | 0.041667 | 0.2 | 7 | 0.083333 | 0
| 0.020833 | 0.112 | 0.072 | 6.337 | 5.897 | 6.913 | 5.205 |  | 0.0625 | 0.3 | 7 | 0.125 | 0
| 0.027778 | -0.057 | 0.127 | 6.321 | 5.893 | 6.907 | 5.198 |  | 0.083333 | 0.3 | 7 | 0.16667 | 0
| 0.034722 | 0.169 | 0.111 | 6.312 | 5.886 | 6.896 | 5.193 |  | 0.10417 | 0.3 | 7 | 0.20833 | 0
| 0.041655 | 0.149 | 0.028 | 6.295 | 5.884 | 6.89 | 5.183 |  | 0.125 | 0.4 | 7 | 0.25 | 0
| 0.0486 | 0.139 | 0.06 | 6.285 | 5.875 | 6.878 | 5.178 |  | 0.14583 | 0.4 | 7 | 0.29167 | 0
| 0.055544 | 0.051 | 0.12 | 6.271 | 5.874 | 6.875 | 5.176 |  | 0.16667 | 0.3 | 7 | 0.33333 | 0
| 0.062488 | 0.14 | 0.083 | 6.259 | 5.864 | 6.865 | 5.172 |  | 0.1875 | 0.4 | 7 | 0.375 | 0
| 0.069433 | 0.153 | 0.047 | 6.25 | 5.857 | 6.859 | 5.165 |  | 0.20833 | 0.4 | 7 | 0.41667 | 0
| 0.076377 | 0.213 | 0.03 | 6.243 | 5.854 | 6.854 | 5.159 |  | 0.22917 | 0.4 | 6.9 | 0.45833 | 0
| 0.083322 | 0.205 | 0.008 | 6.231 | 5.847 | 6.844 | 5.156 |  | 0.25 | 0.5 | 6.9 | 0.5 | 0
| 0.090266 | 0.193 | 0.022 | 6.224 | 5.842 | 6.839 | 5.151 |  | 0.27083 | 0.6 | 6.9 | 0.54167 | 0
| 0.097211 | 0.165 | 0.11 | 6.215 | 5.837 | 6.836 | 5.143 |  | 0.29167 | 0.6 | 6.9 | 0.58333 | 0
| 0.10416 | 0.191 | 0.077 | 6.21 | 5.834 | 6.826 | 5.142 |  | 0.3125 | 0.7 | 6.9 | 0.625 | 0
| 0.1111 | 0.091 | 0.066 | 6.202 | 5.832 | 6.823 | 5.14 |  | 0.33333 | 0.7 | 6.9 | 0.66667 | 0
| 0.11804 | 0.111 | -0.001 | 6.192 | 5.824 | 6.816 | 5.137 |  | 0.35417 | 0.8 | 6.9 | 0.70833 | 0
| 0.12499 | 0.117 | 0.101 | 6.187 | 5.818 | 6.81 | 5.13 |  | 0.375 | 0.8 | 6.9 | 0.75 | 0
| 0.13193 | 0.268 | 0.095 | 6.18 | 5.82 | 6.805 | 5.127 |  | 0.39583 | 0.8 | 6.9 | 0.79167 | 0
| 0.13888 | 0.13 | -0.04 | 6.174 | 5.813 | 6.796 | 5.119 |  | 0.41667 | 0.8 | 6.9 | 0.83333 | 0
| 0.14582 | 0.25 | 0.133 | 6.167 | 5.807 | 6.79 | 5.117 |  | 0.4375 | 0.9 | 6.9 | 0.875 | 0
| 0.15277 | 0.088 | 0.031 | 6.16 | 5.803 | 6.783 | 5.111 |  | 0.45833 | 1.1 | 6.9 | 0.91667 | 0
| 0.15971 | 0.103 | 0.016 | 6.155 | 5.799 | 6.778 | 5.108 |  | 0.47917 | 1.1 | 6.9 | 0.95833 | 0
| 0.16666 | 0.153 | -0.028 | 6.146 | 5.795 | 6.771 | 5.104 |  | 0.5 | 1.2 | 6.9 | 1 | 0.2
| 0.1736 | 0.176 | 0.042 | 6.14 | 5.788 | 6.766 | 5.097 |  | 0.52083 | 1.2 | 6.9 | 1.0417 | 0
| 0.18054 | 0.212 | 0.147 | 6.138 | 5.788 | 6.761 | 5.097 |  | 0.54167 | 1.3 | 6.9 | 1.0833 | 0
| 0.18749 | 0.142 | 0.12 | 6.133 | 5.784 | 6.757 | 5.092 |  | 0.5625 | 1.4 | 6.9 | 1.125 | 0
| 0.19443 | 0.123 | 0.009 | 6.127 | 5.78 | 6.752 | 5.086 |  | 0.58333 | 1.5 | 6.9 | 1.1667 | 0
| 0.20138 | 0.197 | 0.097 | 6.122 | 5.775 | 6.742 | 5.085 |  | 0.60417 | 1.5 | 6.9 | 1.2083 | 0
| 0.20832 | 0.221 | 0.083 | 6.114 | 5.771 | 6.741 | 5.077 |  | 0.625 | 1.5 | 6.9 | 1.25 | 0
| 0.21527 | 0.178 | 0.183 | 6.109 | 5.767 | 6.734 | 5.075 |  | 0.64583 | 1.5 | 6.9 | 1.2917 | 0
| 0.22221 | 0.17 | 0.145 | 6.108 | 5.762 | 6.731 | 5.071 |  | 0.66667 | 1.4 | 6.9 | 1.3333 | 0
| 0.22916 | 0.161 | 0.164 | 6.104 | 5.761 | 6.725 | 5.065 |  | 0.6875 | 1.3 | 6.9 | 1.375 | 0
| 0.2361 | 0.186 | 0.128 | 6.095 | 5.758 | 6.719 | 5.066 |  | 0.70833 | 1.2 | 6.9 | 1.4167 | 0
| 0.24304 | 0.163 | 0.038 | 6.094 | 5.753 | 6.713 | 5.056 |  | 0.72917 | 1.2 | 6.9 | 1.4583 | 0
| 0.24999 | 0.24 | 0.106 | 6.088 | 5.747 | 6.709 | 5.056 |  | 0.75 | 1.1 | 6.8 | 1.5 | 0
| 0.25693 | 0.24 | 0.141 | 6.082 | 5.749 | 6.709 | 5.051 |  | 0.77083 | 1.1 | 6.8 | 1.5417 | 0
| 0.26388 | 0.207 | 0.146 | 6.08 | 5.746 | 6.705 | 5.052 |  | 0.79167 | 0.9 | 6.8 | 1.5833 | 0
| 0.27082 | 0.178 | 0.122 | 6.075 | 5.731 | 6.698 | 5.045 |  | 0.8125 | 0.9 | 6.8 | 1.625 | 0
| 0.27777 | 0.229 | 0.145 | 6.071 | 5.735 | 6.689 | 5.041 |  | 0.83333 | 0.8 | 6.8 | 1.6667 | 0
| 0.28471 | 0.21 | 0.073 | 6.069 | 5.735 | 6.69 | 5.034 |  | 0.85417 | 0.9 | 6.8 | 1.7083 | 0
| 0.29166 | 0.285 | 0.026 | 6.065 | 5.729 | 6.69 | 5.032 |  | 0.875 | 0.9 | 6.8 | 1.75 | 0
| 0.2986 | 0.305 | 0.083 | 6.066 | 5.716 | 6.679 | 5.033 |  | 0.89583 | 0.9 | 6.8 | 1.7917 | 0
| 0.30554 | 0.192 | 0.093 | 6.062 | 5.709 | 6.68 | 5.028 |  | 0.91667 | 0.9 | 6.8 | 1.8333 | 0
| 0.31249 | 0.17 | 0.079 | 6.062 | 5.698 | 6.671 | 5.021 |  | 0.9375 | 1 | 6.8 | 1.875 | 0
| 0.31943 | 0.104 | 0.05 | 6.055 | 5.692 | 6.665 | 5.023 |  | 0.95833 | 1 | 6.8 | 1.9167 | 0
| 0.32638 | 0.224 | -0.018 | 6.055 | 5.685 | 6.66 | 5.018 |  | 0.97917 | 0.9 | 6.8 | 1.9583 | 0
| 0.33332 | 0.104 | -0.005 | 6.051 | 5.682 | 6.657 | 5.014 |  | 1 | 0.9 | 6.8 | 2 | 0
| 0.34027 | 0.184 | -0.016 | 6.045 | 5.673 | 6.649 | 5.012 |  | 1.0208 | 0.9 | 6.8 | 2.0417 | 0
| 0.34721 | 0.145 | 0.11 | 6.044 | 5.673 | 6.651 | 5.004 |  | 1.0417 | 0.9 | 6.8 | 2.0833 | 0
| 0.35416 | 0.157 | 0.087 | 6.042 | 5.672 | 6.642 | 5 |  | 1.0625 | 0.8 | 6.8 | 2.125 | 0
| 0.3611 | 0.22 | 0.192 | 6.033 | 5.68 | 6.641 | 5.001 |  | 1.0833 | 0.9 | 6.8 | 2.1667 | 0
| 0.36804 | 0.175 | 0.178 | 6.026 | 5.683 | 6.635 | 5.002 |  | 1.1042 | 0.8 | 6.8 | 2.2083 | 0
| 0.37499 | 0.277 | 0.219 | 6.028 | 5.68 | 6.632 | 4.995 |  | 1.125 | 0.9 | 6.8 | 2.25 | 0.4
| 0.38193 | 0.197 | 0.175 | 6.019 | 5.673 | 6.632 | 4.991 |  | 1.1458 | 1 | 6.8 | 2.2917 | 0.2
| 0.38888 | 0.168 | 0.139 | 6.018 | 5.668 | 6.624 | 4.99 |  | 1.1667 | 1 | 6.8 | 2.3333 | 1.6
| 0.39582 | 0.178 | 0.157 | 6.016 | 5.668 | 6.618 | 4.983 |  | 1.1875 | 0.9 | 6.8 | 2.375 | 2.6
| 0.40277 | 0.213 | 0.058 | 6.013 | 5.663 | 6.616 | 4.983 |  | 1.2083 | 0.9 | 6.8 | 2.4167 | 1.8
| 0.40971 | 0.343 | 0.095 | 6.009 | 5.66 | 6.612 | 4.978 |  | 1.2292 | 1 | 6.8 | 2.4583 | 0.2
| 0.41666 | 0.182 | 0.166 | 6.006 | 5.655 | 6.608 | 4.976 |  | 1.25 | 0.8 | 6.7 | 2.5 | 0
| 0.4236 | 0.187 | 0.12 | 6.002 | 5.65 | 6.605 | 4.972 |  | 1.2708 | 0.9 | 6.7 | 2.5417 | 0
| 0.43054 | 0.016 | 0.061 | 6.002 | 5.648 | 6.601 | 4.97 |  | 1.2917 | 0.8 | 6.7 | 2.5833 | 0
| 0.43749 | 0.182 | 0.161 | 6 | 5.646 | 6.592 | 4.963 |  | 1.3125 | 0.8 | 6.7 | 2.625 | 0.2
| 0.44443 | 0.151 | 0.079 | 5.996 | 5.642 | 6.59 | 4.967 |  | 1.3333 | 0.8 | 6.7 | 2.6667 | 0
| 0.45138 | 0.137 | 0.073 | 5.995 | 5.637 | 6.588 | 4.961 |  | 1.3542 | 0.9 | 6.7 | 2.7083 | 0
| 0.45832 | 0.191 | 0.06 | 5.991 | 5.634 | 6.585 | 4.955 |  | 1.375 | 1.1 | 6.7 | 2.75 | 0
| 0.46527 | 0.1 | 0.047 | 5.988 | 5.631 | 6.581 | 4.955 |  | 1.3958 | 1.2 | 6.7 | 2.7917 | 0
| 0.47221 | 0.06 | -0.081 | 5.984 | 5.634 | 6.579 | 4.953 |  | 1.4167 | 1.4 | 6.7 | 2.8333 | 0
| 0.47916 | 0.064 | -0.034 | 5.983 | 5.631 | 6.575 | 4.95 |  | 1.4375 | 1.8 | 6.7 | 2.875 | 0
| 0.4861 | 0.096 | -0.061 | 5.975 | 5.63 | 6.574 | 4.945 |  | 1.4583 | 1.8 | 6.7 | 2.9167 | 0
| 0.49304 | 0.05 | -0.023 | 5.977 | 5.628 | 6.569 | 4.939 |  | 1.4792 | 2.1 | 6.7 | 2.9583 | 0
| 0.49999 | 0.123 | 0.024 | 5.968 | 5.624 | 6.568 | 4.94 |  | 1.5 | 2.2 | 6.7 | 3 | 0
| 0.50693 | 0.176 | -0.003 | 5.968 | 5.624 | 6.558 | 4.936 |  | 1.5208 | 2.4 | 6.7 | 3.0417 | 0
| 0.51388 | 0.098 | -0.061 | 5.968 | 5.62 | 6.56 | 4.936 |  | 1.5417 | 2.6 | 6.7 | 3.0833 | 0
| 0.52082 | 0.043 | -0.062 | 5.962 | 5.617 | 6.557 | 4.931 |  | 1.5625 | 2.7 | 6.7 | 3.125 | 0
| 0.52777 | 0.017 | -0.135 | 5.96 | 5.615 | 6.555 | 4.926 |  | 1.5833 | 2.7 | 6.7 | 3.1667 | 0
| 0.53471 | 0.077 | -0.043 | 5.956 | 5.616 | 6.548 | 4.925 |  | 1.6042 | 2.6 | 6.7 | 3.2083 | 0
| 0.54166 | 0.069 | -0.146 | 5.951 | 5.612 | 6.545 | 4.924 |  | 1.625 | 2.5 | 6.7 | 3.25 | 0
| 0.5486 | 0.139 | -0.136 | 5.948 | 5.605 | 6.542 | 4.92 |  | 1.6458 | 2.4 | 6.7 | 3.2917 | 0
| 0.55554 | 0.196 | -0.111 | 5.948 | 5.602 | 6.534 | 4.92 |  | 1.6667 | 2.4 | 6.7 | 3.3333 | 0
| 0.5625 | 0.018 | -0.119 | 5.946 | 5.601 | 6.533 | 4.916 |  | 1.6875 | 2.3 | 6.7 | 3.375 | 0
| 0.56389 | 0.1 | -0.09 | 5.945 | 5.601 | 6.537 | 4.915 |  | 1.7083 | 2.3 | 6.7 | 3.4167 | 0
| 0.56528 | 0.046 | -0.103 | 5.946 | 5.599 | 6.532 | 4.91 |  | 1.7292 | 2.3 | 6.7 | 3.4583 | 0
| 0.56667 | 292.12 | 281.316 | 7.361 | 5.599 | 7.365 | 4.911 |  | 1.75 | 2.3 | 6.6 | 3.5 | 0.2
| 0.56806 | 291.853 | 300.255 | 9.223 | 5.6 | 8.833 | 4.913 |  | 1.7708 | 2.3 | 6.6 | 3.5417 | 1.4
| 0.56943 | 292.263 | 300.424 | 10.632 | 5.604 | 10.101 | 4.913 |  | 1.7917 | 2.3 | 6.6 | 3.5833 | 0.4
| 0.57083 | 291.866 | 299.956 | 11.858 | 5.613 | 11.123 | 4.912 |  | 1.8125 | 2.3 | 6.6 | 3.625 | 0.2
| 0.57222 | 292.209 | 299.346 | 13 | 5.62 | 11.965 | 4.91 |  | 1.8333 | 2.3 | 6.6 | 3.6667 | 0.2
| 0.57361 | 291.557 | 299.547 | 14.083 | 5.641 | 12.676 | 4.91 |  | 1.8542 | 2.2 | 6.6 | 3.7083 | 0.2
| 0.575 | 291.609 | 299.403 | 15.131 | 5.657 | 13.277 | 4.911 |  | 1.875 | 2.2 | 6.6 | 3.75 | 1.2
| 0.57639 | 290.785 | 299.367 | 16.14 | 5.682 | 13.794 | 4.908 |  | 1.8958 | 2.2 | 6.6 | 3.7917 | 3.4
| 0.57778 | 290.89 | 298.878 | 17.125 | 5.706 | 14.244 | 4.911 |  | 1.9167 | 2.1 | 6.6 | 3.8333 | 1
| 0.57917 | 291.115 | 299.054 | 18.079 | 5.738 | 14.644 | 4.912 |  | 1.9375 | 1.8 | 6.6 | 3.875 | 0.4
| 0.58056 | 290.838 | 299.312 | 19.012 | 5.768 | 14.999 | 4.916 |  | 1.9583 | 1.6 | 6.6 | 3.9167 | 0
| 0.58194 | 291.072 | 298.54 | 19.911 | 5.8 | 15.32 | 4.916 |  | 1.9792 | 1.4 | 6.6 | 3.9583 | 0.2
| 0.58333 | 291.578 | 298.597 | 20.792 | 5.837 | 15.614 | 4.924 |  | 2 | 1.3 | 6.6 | 4 | 0
| 0.58472 | 290.72 | 298.966 | 21.644 | 5.873 | 15.873 | 4.931 |  | 2.0208 | 1.1 | 6.6 | 4.0417 | 0
| 0.58611 | 290.931 | 299.253 | 22.469 | 5.91 | 16.12 | 4.937 |  | 2.0417 | 1.1 | 6.6 | 4.0833 | 0
| 0.5875 | 291.494 | 299.049 | 23.273 | 5.95 | 16.343 | 4.943 |  | 2.0625 | 0.9 | 6.6 | 4.125 | 0.2
| 0.58889 | 291.558 | 298.851 | 24.055 | 5.985 | 16.553 | 4.955 |  | 2.0833 | 0.8 | 6.6 | 4.1667 | 0
| 0.59028 | 291.462 | 299.217 | 24.803 | 6.026 | 16.747 | 4.964 |  | 2.1042 | 0.8 | 6.6 | 4.2083 | 0
| 0.59167 | 291.472 | 298.41 | 25.538 | 6.07 | 16.933 | 4.977 |  | 2.125 | 0.7 | 6.6 | 4.25 | 0
| 0.59306 | 290.925 | 299.481 | 26.251 | 6.106 | 17.102 | 4.989 |  | 2.1458 | 0.7 | 6.6 | 4.2917 | 0
| 0.59444 | 291.004 | 299.532 | 26.937 | 6.149 | 17.267 | 5.002 |  | 2.1667 | 0.7 | 6.6 | 4.3333 | 0.2
| 0.59583 | 291.213 | 298.856 | 27.603 | 6.196 | 17.42 | 5.02 |  | 2.1875 | 0.4 | 6.6 | 4.375 | 0
| 0.59722 | 290.736 | 298.975 | 28.257 | 6.233 | 17.565 | 5.033 |  | 2.2083 | -0.1 | 6.6 | 4.4167 | 0
| 0.59861 | 291.329 | 299.23 | 28.884 | 6.278 | 17.705 | 5.051 |  | 2.2292 | -0.1 | 6.6 | 4.4583 | 0.2
| 0.6 | 291.202 | 298.381 | 29.497 | 6.32 | 17.845 | 5.069 |  | 2.25 | 0.1 | 6.6 | 4.5 | 0.2
| 0.60139 | 291.723 | 299.044 | 30.094 | 6.366 | 17.976 | 5.087 |  | 2.2708 | 0.1 | 6.6 | 4.5417 | 0.2
| 0.60278 | 291.535 | 298.946 | 30.672 | 6.407 | 18.108 | 5.099 |  | 2.2917 | 0.2 | 6.5 | 4.5833 | 0.2
| 0.60417 | 291.023 | 299.463 | 31.231 | 6.45 | 18.224 | 5.128 |  | 2.3125 | 0.3 | 6.5 | 4.625 | 0
| 0.60556 | 290.74 | 299.425 | 31.779 | 6.497 | 18.345 | 5.143 |  | 2.3333 | 0.3 | 6.5 | 4.6667 | 0.2
| 0.60694 | 291.711 | 299.483 | 32.32 | 6.536 | 18.467 | 5.168 |  | 2.3542 | 0.4 | 6.5 | 4.7083 | 0
| 0.60833 | 291.923 | 299.279 | 32.831 | 6.581 | 18.583 | 5.187 |  | 2.375 | 0.4 | 6.5 | 4.75 | 0
| 0.60972 | 291.435 | 299.902 | 33.337 | 6.628 | 18.7 | 5.211 |  | 2.3958 | 0.5 | 6.5 | 4.7917 | 0
| 0.61111 | 292.073 | 299.425 | 33.833 | 6.666 | 18.81 | 5.231 |  | 2.4167 | 0.6 | 6.5 | 4.8333 | 0
| 0.6125 | 291.992 | 299.863 | 34.312 | 6.713 | 18.917 | 5.252 |  | 2.4375 | 0.7 | 6.5 | 4.875 | 0
| 0.61389 | 291.744 | 299.372 | 34.776 | 6.758 | 19.025 | 5.276 |  | 2.4583 | 0.8 | 6.5 | 4.9167 | 0
| 0.61528 | 292.136 | 299.628 | 35.225 | 6.797 | 19.127 | 5.297 |  | 2.4792 | 1.3 | 6.5 | 4.9583 | 0
| 0.61667 | 292.133 | 299.676 | 35.668 | 6.845 | 19.228 | 5.322 |  | 2.5 | 1.4 | 6.5 | 5 | 0
| 0.61806 | 292.348 | 300.78 | 36.099 | 6.888 | 19.325 | 5.348 |  | 2.5208 | 1.6 | 6.5 | 5.0417 | 0
| 0.61944 | 291.571 | 300.536 | 36.516 | 6.929 | 19.431 | 5.369 |  | 2.5417 | 1.7 | 6.5 | 5.0833 | 0
| 0.62083 | 292.471 | 300.104 | 36.93 | 6.973 | 19.528 | 5.396 |  | 2.5625 | 1.9 | 6.5 | 5.125 | 0
| 0.62222 | 292.207 | 300.795 | 37.327 | 7.016 | 19.623 | 5.421 |  | 2.5833 | 2.1 | 6.5 | 5.1667 | 0.2
| 0.62361 | 291.952 | 300.892 | 37.719 | 7.059 | 19.722 | 5.446 |  | 2.6042 | 2.5 | 6.5 | 5.2083 | 0
| 0.625 | 292.45 | 300.481 | 38.101 | 7.1 | 19.813 | 5.474 |  | 2.625 | 3.3 | 6.5 | 5.25 | 0
| 0.62639 | 292.264 | 300.683 | 38.473 | 7.144 | 19.907 | 5.499 |  | 2.6458 | 3.5 | 6.5 | 5.2917 | 0
| 0.62778 | 292.655 | 300.214 | 38.833 | 7.184 | 19.992 | 5.528 |  | 2.6667 | 3.6 | 6.5 | 5.3333 | 0
| 0.62917 | 292.453 | 300.001 | 39.187 | 7.229 | 20.086 | 5.549 |  | 2.6875 | 3.4 | 6.5 | 5.375 | 0
| 0.63056 | 290.94 | 299.295 | 39.514 | 7.267 | 20.164 | 5.576 |  | 2.7083 | 3.4 | 6.5 | 5.4167 | 0
| 0.63194 | 289.919 | 297.727 | 39.82 | 7.31 | 20.22 | 5.6 |  | 2.7292 | 3.6 | 6.5 | 5.4583 | 0
| 0.63333 | 289.914 | 298.457 | 40.119 | 7.349 | 20.28 | 5.631 |  | 2.75 | 3.7 | 6.5 | 5.5 | 0
| 0.63472 | 289.968 | 297.524 | 40.418 | 7.391 | 20.343 | 5.651 |  | 2.7708 | 3.7 | 6.5 | 5.5417 | 0
| 0.63611 | 289.529 | 298.594 | 40.712 | 7.431 | 20.411 | 5.681 |  | 2.7917 | 3.7 | 6.5 | 5.5833 | 0
| 0.6375 | 289.66 | 298.629 | 40.992 | 7.469 | 20.477 | 5.708 |  | 2.8125 | 3.3 | 6.5 | 5.625 | 0
| 0.63889 | 289.932 | 298.346 | 41.27 | 7.514 | 20.543 | 5.735 |  | 2.8333 | 2.7 | 6.5 | 5.6667 | 0
| 0.64028 | 289.912 | 298.363 | 41.545 | 7.553 | 20.615 | 5.762 |  | 2.8542 | 2.6 | 6.4 | 5.7083 | 0
| 0.64167 | 290.387 | 298.148 | 41.814 | 7.587 | 20.68 | 5.79 |  | 2.875 | 1.9 | 6.4 | 5.75 | 0
| 0.64306 | 289.506 | 298.017 | 42.076 | 7.628 | 20.748 | 5.815 |  | 2.8958 | 1.3 | 6.4 | 5.7917 | 0
| 0.64444 | 290.224 | 297.995 | 42.331 | 7.668 | 20.814 | 5.842 |  | 2.9167 | 0.7 | 6.4 | 5.8333 | 0
| 0.64583 | 287.281 | 295.713 | 42.555 | 7.706 | 20.863 | 5.869 |  | 2.9375 | 0.8 | 6.4 | 5.875 | 0
| 0.64722 | 291.301 | 300.449 | 42.805 | 7.742 | 20.935 | 5.893 |  | 2.9583 | 0.8 | 6.4 | 5.9167 | 0
| 0.64861 | 291.886 | 299.682 | 43.074 | 7.78 | 21.023 | 5.926 |  | 2.9792 | 0.9 | 6.4 | 5.9583 | 0
| 0.65 | 291.156 | 300.299 | 43.326 | 7.818 | 21.108 | 5.949 |  | 3 | 1.1 | 6.4 | 6 | 0
| 0.65139 | 291.842 | 299.631 | 43.571 | 7.852 | 21.189 | 5.979 |  | 3.0208 | 1.1 | 6.4 | 6.0417 | 0
| 0.65278 | 291.743 | 299.49 | 43.809 | 7.891 | 21.265 | 6.003 |  | 3.0417 | 0.8 | 6.4 | 6.0833 | 0
| 0.65417 | 290.912 | 299.697 | 44.035 | 7.923 | 21.334 | 6.031 |  | 3.0625 | 1 | 6.4 | 6.125 | 0
| 0.65556 | 291.585 | 299.827 | 44.256 | 7.963 | 21.411 | 6.057 |  | 3.0833 | 0.9 | 6.4 | 6.1667 | 0
| 0.65694 | 291.269 | 299.412 | 44.476 | 7.999 | 21.479 | 6.084 |  | 3.1042 | 0.9 | 6.4 | 6.2083 | 0
| 0.65833 | 291.535 | 299.559 | 44.691 | 8.035 | 21.547 | 6.106 |  | 3.125 | 0.7 | 6.4 | 6.25 | 0
| 0.65972 | 291.546 | 299.216 | 44.894 | 8.066 | 21.614 | 6.137 |  | 3.1458 | 0.5 | 6.4 | 6.2917 | 0
| 0.66111 | 290.939 | 300.122 | 45.102 | 8.103 | 21.679 | 6.162 |  | 3.1667 | 0.8 | 6.4 | 6.3333 | 0
| 0.6625 | 291.808 | 299.737 | 45.305 | 8.137 | 21.743 | 6.193 |  | 3.1875 | 0.8 | 6.4 | 6.375 | 0
| 0.66389 | 290.938 | 299.873 | 45.499 | 8.173 | 21.811 | 6.213 |  | 3.2083 | 1.1 | 6.4 | 6.4167 | 0
| 0.66528 | 291.262 | 299.449 | 45.682 | 8.207 | 21.87 | 6.244 |  | 3.2292 | 1.3 | 6.4 | 6.4583 | 0
| 0.66667 | 291.217 | 299.064 | 45.863 | 8.241 | 21.928 | 6.271 |  | 3.25 | 1.3 | 6.4 | 6.5 | 0
| 0.66806 | 291.687 | 299.424 | 46.047 | 8.274 | 21.988 | 6.298 |  | 3.2708 | 1.4 | 6.4 | 6.5417 | 0
| 0.66944 | 290.854 | 299.903 | 46.225 | 8.308 | 22.047 | 6.324 |  | 3.2917 | 1.4 | 6.4 | 6.5833 | 0
| 0.67083 | 291.217 | 300.214 | 46.401 | 8.344 | 22.113 | 6.35 |  | 3.3125 | 1.6 | 6.4 | 6.625 | 0
| 0.67222 | 291.592 | 299.61 | 46.57 | 8.375 | 22.171 | 6.374 |  | 3.3333 | 1.5 | 6.4 | 6.6667 | 0
| 0.67361 | 291.493 | 299.48 | 46.742 | 8.407 | 22.231 | 6.399 |  | 3.3542 | 1.5 | 6.4 | 6.7083 | 0
| 0.675 | 291.118 | 300.271 | 46.91 | 8.441 | 22.291 | 6.423 |  | 3.375 | 1.8 | 6.4 | 6.75 | 0
| 0.67639 | 291.873 | 299.819 | 47.066 | 8.471 | 22.347 | 6.45 |  | 3.3958 | 2.2 | 6.4 | 6.7917 | 0
| 0.67778 | 291.605 | 299.834 | 47.226 | 8.503 | 22.403 | 6.478 |  | 3.4167 | 2.5 | 6.4 | 6.8333 | 0
| 0.67917 | 290.752 | 299.529 | 47.377 | 8.532 | 22.457 | 6.501 |  | 3.4375 | 2.6 | 6.4 | 6.875 | 0
| 0.68056 | 291.302 | 299.323 | 47.524 | 8.567 | 22.509 | 6.531 |  | 3.4583 | 2.9 | 6.3 | 6.9167 | 0
| 0.68194 | 290.84 | 300.228 | 47.669 | 8.599 | 22.559 | 6.555 |  | 3.4792 | 2.9 | 6.3 | 6.9583 | 0
| 0.68333 | 290.808 | 300.145 | 47.813 | 8.63 | 22.615 | 6.578 |  | 3.5 | 3 | 6.3 | 7 | 0
| 0.68472 | 290.798 | 300.279 | 47.954 | 8.66 | 22.669 | 6.606 |  | 3.5208 | 3.1 | 6.3 | 7.0417 | 0
| 0.68611 | 290.759 | 300.012 | 48.092 | 8.689 | 22.724 | 6.634 |  | 3.5417 | 2.7 | 6.3 | 7.0833 | 0
| 0.6875 | 290.943 | 299.206 | 48.218 | 8.723 | 22.773 | 6.657 |  | 3.5625 | 1.4 | 6.3 | 7.125 | 0
| 0.68889 | 290.812 | 298.887 | 48.347 | 8.749 | 22.822 | 6.684 |  | 3.5833 | 0.3 | 6.3 | 7.1667 | 0
| 0.69028 | 290.674 | 299.505 | 48.474 | 8.778 | 22.87 | 6.708 |  | 3.6042 | 0.2 | 6.3 | 7.2083 | 0.2
| 0.69167 | 290.05 | 299.372 | 48.592 | 8.808 | 22.917 | 6.728 |  | 3.625 | 0.3 | 6.3 | 7.25 | 0
| 0.69306 | 289.895 | 299.326 | 48.716 | 8.838 | 22.963 | 6.754 |  | 3.6458 | 0.3 | 6.3 | 7.2917 | 0.2
| 0.69443 | 290.16 | 299.465 | 48.829 | 8.872 | 23.014 | 6.784 |  | 3.6667 | 0.3 | 6.3 | 7.3333 | 0
| 0.69583 | 290.822 | 298.76 | 48.943 | 8.895 | 23.057 | 6.808 |  | 3.6875 | 0.4 | 6.3 | 7.375 | 0
| 0.69722 | 290.524 | 298.665 | 49.061 | 8.925 | 23.1 | 6.835 |  | 3.7083 | 0.5 | 6.3 | 7.4167 | 0
| 0.69861 | 290.298 | 298.284 | 49.163 | 8.954 | 23.142 | 6.856 |  | 3.7292 | 0.5 | 6.3 | 7.4583 | 0
| 0.7 | 289.744 | 297.673 | 49.258 | 8.979 | 23.184 | 6.881 |  | 3.75 | 0.4 | 6.3 | 7.5 | 0
| 0.70139 | 289.7 | 297.718 | 49.354 | 9.009 | 23.216 | 6.904 |  | 3.7708 | 0.6 | 6.3 | 7.5417 | 0
| 0.70278 | 289.284 | 297.853 | 49.444 | 9.038 | 23.25 | 6.934 |  | 3.7917 | 0.7 | 6.3 | 7.5833 | 0
| 0.70417 | 289.388 | 297.183 | 49.533 | 9.063 | 23.289 | 6.951 |  | 3.8125 | 0.8 | 6.3 | 7.625 | 0
| 0.70556 | 300.208 | 298.22 | 49.746 | 9.091 | 23.328 | 6.978 |  | 3.8333 | 0.8 | 6.3 | 7.6667 | 0
| 0.70694 | 299.315 | 297.342 | 49.988 | 9.116 | 23.361 | 7.005 |  | 3.8542 | 0.7 | 6.3 | 7.7083 | 0
| 0.70833 | 300.008 | 296.979 | 50.185 | 9.142 | 23.401 | 7.028 |  | 3.875 | 0.6 | 6.3 | 7.75 | 0
| 0.70972 | 300.912 | 298.607 | 50.367 | 9.169 | 23.44 | 7.052 |  | 3.8958 | 0.6 | 6.3 | 7.7917 | 0
| 0.71111 | 301.626 | 299.705 | 50.573 | 9.198 | 23.497 | 7.075 |  | 3.9167 | 0.7 | 6.3 | 7.8333 | 0
| 0.7125 | 300.057 | 296.717 | 50.734 | 9.222 | 23.537 | 7.099 |  | 3.9375 | 0.5 | 6.3 | 7.875 | 0
| 0.71389 | 300.448 | 297.902 | 50.894 | 9.252 | 23.576 | 7.118 |  | 3.9583 | 0.3 | 6.3 | 7.9167 | 0
| 0.71528 | 300.041 | 296.736 | 51.047 | 9.278 | 23.612 | 7.144 |  | 3.9792 | 0 | 6.3 | 7.9583 | 0
| 0.71667 | 299.52 | 296.47 | 51.187 | 9.307 | 23.643 | 7.168 |  | 4 | 0.3 | 6.3 | 8 | 0
| 0.71806 | 299.394 | 296.079 | 51.323 | 9.337 | 23.666 | 7.19 |  | 4.0208 | 0.4 | 6.3 | 8.0417 | 0
| 0.71944 | 298.374 | 296.438 | 51.455 | 9.36 | 23.699 | 7.214 |  | 4.0417 | 0.5 | 6.3 | 8.0833 | 0
| 0.72083 | 298.868 | 295.984 | 51.584 | 9.388 | 23.727 | 7.236 |  | 4.0625 | 0.7 | 6.3 | 8.125 | 0
| 0.72222 | 301.888 | 300.02 | 51.742 | 9.417 | 23.773 | 7.258 |  | 4.0833 | 1.1 | 6.3 | 8.1667 | 0
| 0.72361 | 302.7 | 299.887 | 51.925 | 9.442 | 23.852 | 7.285 |  | 4.1042 | 1.1 | 6.2 | 8.2083 | 0
| 0.725 | 302.215 | 300.324 | 52.091 | 9.468 | 23.911 | 7.304 |  | 4.125 | 1.2 | 6.2 | 8.25 | 0
| 0.72639 | 301.686 | 299.755 | 52.242 | 9.497 | 23.97 | 7.33 |  | 4.1458 | 1.5 | 6.2 | 8.2917 | 0.8
| 0.72778 | 301.464 | 299.572 | 52.381 | 9.523 | 24.022 | 7.35 |  | 4.1667 | 1.3 | 6.2 | 8.3333 | 0.8
| 0.72917 | 303.049 | 300.767 | 52.535 | 9.552 | 24.079 | 7.374 |  | 4.1875 | 1.8 | 6.2 | 8.375 | 0.2
| 0.73056 | 303.403 | 301.617 | 52.7 | 9.579 | 24.146 | 7.393 |  | 4.2083 | 1.3 | 6.2 | 8.4167 | 0.6
| 0.73194 | 303.996 | 301.333 | 52.864 | 9.607 | 24.212 | 7.416 |  | 4.2292 | 1.3 | 6.2 | 8.4583 | 0.2
| 0.73333 | 304.747 | 301.712 | 53.021 | 9.633 | 24.279 | 7.44 |  | 4.25 | 0.5 | 6.2 | 8.5 | 0
| 0.73472 | 303.789 | 301.888 | 53.179 | 9.658 | 24.342 | 7.462 |  | 4.2708 | 0.6 | 6.2 | 8.5417 | 0
| 0.73611 | 304.578 | 301.164 | 53.327 | 9.687 | 24.399 | 7.48 |  | 4.2917 | 0.2 | 6.2 | 8.5833 | 0
| 0.7375 | 303.836 | 301.663 | 53.463 | 9.712 | 24.445 | 7.503 |  | 4.3125 | -0.3 | 6.2 | 8.625 | 0.2
| 0.73889 | 303.873 | 301.761 | 53.603 | 9.739 | 24.497 | 7.525 |  | 4.3333 | -0.7 | 6.2 | 8.6667 | 0.6
| 0.74028 | 303.887 | 301.594 | 53.741 | 9.765 | 24.546 | 7.542 |  | 4.3542 | -0.8 | 6.2 | 8.7083 | 0.4
| 0.74167 | 304.556 | 301.412 | 53.87 | 9.793 | 24.595 | 7.569 |  | 4.375 | -0.7 | 6.2 | 8.75 | 0.4
| 0.74306 | 304.086 | 301.495 | 54.003 | 9.819 | 24.643 | 7.591 |  | 4.3958 | -0.4 | 6.2 | 8.7917 | 0
| 0.74444 | 304.666 | 301.516 | 54.129 | 9.843 | 24.685 | 7.612 |  | 4.4167 | 0.4 | 6.2 | 8.8333 | 0.2
| 0.74583 | 304.357 | 301.185 | 54.249 | 9.871 | 24.725 | 7.631 |  | 4.4375 | 1.1 | 6.2 | 8.875 | 0
| 0.74722 | 304.579 | 301.178 | 54.374 | 9.898 | 24.773 | 7.652 |  | 4.4583 | 1.8 | 6.2 | 8.9167 | 0
| 0.74861 | 304.003 | 301.359 | 54.491 | 9.924 | 24.815 | 7.674 |  | 4.4792 | 2.6 | 6.2 | 8.9583 | 0
| 0.75 | 303.889 | 301.053 | 54.606 | 9.952 | 24.853 | 7.697 |  | 4.5 | 3.1 | 6.2 | 9 | 0
| 0.75139 | 303.604 | 301.176 | 54.714 | 9.974 | 24.891 | 7.72 |  | 4.5208 | 3.4 | 6.2 | 9.0417 | 0
| 0.75278 | 303.517 | 301.393 | 54.825 | 10.004 | 24.927 | 7.74 |  | 4.5417 | 3.4 | 6.2 | 9.0833 | 0
| 0.75417 | 303.919 | 300.888 | 54.93 | 10.027 | 24.964 | 7.762 |  | 4.5625 | 3.7 | 6.2 | 9.125 | 0
| 0.75556 | 303.721 | 301.27 | 55.036 | 10.055 | 24.998 | 7.776 |  | 4.5833 | 3.7 | 6.2 | 9.1667 | 0
| 0.75694 | 303.2 | 301.417 | 55.137 | 10.08 | 25.038 | 7.801 |  | 4.6042 | 3.6 | 6.2 | 9.2083 | 0
| 0.75833 | 303.347 | 301.379 | 55.235 | 10.103 | 25.075 | 7.819 |  | 4.625 | 3.7 | 6.2 | 9.25 | 0
| 0.75972 | 303.394 | 301.482 | 55.334 | 10.128 | 25.111 | 7.84 |  | 4.6458 | 3.4 | 6.2 | 9.2917 | 0
| 0.76111 | 304.261 | 300.876 | 55.425 | 10.153 | 25.141 | 7.862 |  | 4.6667 | 3.1 | 6.2 | 9.3333 | 0
| 0.7625 | 303.922 | 301.829 | 55.528 | 10.182 | 25.194 | 7.88 |  | 4.6875 | 2.7 | 6.2 | 9.375 | 0
| 0.76389 | 303.479 | 301.505 | 55.62 | 10.203 | 25.215 | 7.907 |  | 4.7083 | 2.3 | 6.2 | 9.4167 | 0
| 0.76528 | 304.192 | 300.794 | 55.708 | 10.227 | 25.256 | 7.923 |  | 4.7292 | 2.3 | 6.2 | 9.4583 | 0
| 0.76667 | 303.101 | 301.115 | 55.797 | 10.254 | 25.286 | 7.944 |  | 4.75 | 2.3 | 6.2 | 9.5 | 0
| 0.76806 | 306.374 | 303.305 | 55.912 | 10.278 | 25.342 | 7.967 |  | 4.7708 | 1.9 | 6.1 | 9.5417 | 0
| 0.76944 | 302.247 | 300.409 | 56 | 10.299 | 25.379 | 7.986 |  | 4.7917 | 2 | 6.1 | 9.5833 | 0
| 0.77083 | 303.171 | 300.363 | 56.061 | 10.319 | 25.397 | 8.005 |  | 4.8125 | 2.1 | 6.1 | 9.625 | 0
| 0.77222 | 302.877 | 300.484 | 56.135 | 10.348 | 25.428 | 8.027 |  | 4.8333 | 1.7 | 6.1 | 9.6667 | 0
| 0.77361 | 303.309 | 301.129 | 56.214 | 10.37 | 25.455 | 8.045 |  | 4.8542 | 2 | 6.1 | 9.7083 | 0
| 0.775 | 303.413 | 300.337 | 56.291 | 10.395 | 25.484 | 8.065 |  | 4.875 | 1.9 | 6.1 | 9.75 | 0
| 0.77639 | 303.354 | 301.419 | 56.369 | 10.418 | 25.52 | 8.082 |  | 4.8958 | 1.9 | 6.1 | 9.7917 | 1.4
| 0.77778 | 303.853 | 300.489 | 56.445 | 10.439 | 25.54 | 8.105 |  | 4.9167 | 1.8 | 6.1 | 9.8333 | 2.4
| 0.77917 | 303.319 | 301.325 | 56.519 | 10.468 | 25.594 | 8.123 |  | 4.9375 | 1.7 | 6.1 | 9.875 | 1.6
| 0.78056 | 303.549 | 301.026 | 56.591 | 10.488 | 25.62 | 8.143 |  | 4.9583 | 1.7 | 6.1 | 9.9167 | 0.8
| 0.78194 | 303.628 | 300.849 | 56.667 | 10.509 | 25.647 | 8.16 |  | 4.9792 | 1.4 | 6.1 | 9.9583 | 0
| 0.78333 | 303.886 | 301.038 | 56.733 | 10.533 | 25.679 | 8.183 |  | 5 | 1.7 | 6.1 | 10 | 0.2
| 0.78472 | 303.78 | 301.19 | 56.808 | 10.551 | 25.712 | 8.197 |  | 5.0208 | 1.3 | 6.1 | 10.0417 | 0
| 0.78611 | 303.553 | 300.845 | 56.877 | 10.572 | 25.745 | 8.223 |  | 5.0417 | 1.2 | 6.1 | 10.0833 | 0
| 0.7875 | 303.933 | 301.174 | 56.951 | 10.598 | 25.775 | 8.24 |  | 5.0625 | 1.2 | 6.1 | 10.125 | 0
| 0.78889 | 304.181 | 300.992 | 57.015 | 10.618 | 25.81 | 8.259 |  | 5.0833 | 1 | 6.1 | 10.1667 | 0
| 0.79028 | 304.015 | 301.195 | 57.081 | 10.64 | 25.842 | 8.277 |  | 5.1042 | 0.7 | 6.1 | 10.2083 | 0
| 0.79167 | 303.685 | 301.959 | 57.151 | 10.662 | 25.882 | 8.296 |  | 5.125 | 0.5 | 6.1 | 10.25 | 0
| 0.79306 | 303.884 | 301.921 | 57.223 | 10.682 | 25.914 | 8.312 |  | 5.1458 | 0.2 | 6.1 | 10.2917 | 0
| 0.79444 | 304.02 | 301.84 | 57.291 | 10.705 | 25.948 | 8.337 |  | 5.1667 | -0.2 | 6.1 | 10.3333 | 0
| 0.79583 | 304.497 | 301.742 | 57.362 | 10.728 | 25.99 | 8.351 |  | 5.1875 | -0.6 | 6.1 | 10.375 | 0
| 0.79722 | 304.353 | 302.517 | 57.434 | 10.751 | 26.027 | 8.371 |  | 5.2083 | -0.7 | 6.1 | 10.4167 | 0
| 0.79861 | 304.755 | 302.726 | 57.506 | 10.766 | 26.057 | 8.389 |  | 5.2292 | -0.7 | 6.1 | 10.4583 | 0
| 0.8 | 304.936 | 302.009 | 57.576 | 10.784 | 26.101 | 8.408 |  | 5.25 | -0.9 | 6.1 | 10.5 | 0
| 0.80139 | 304.632 | 302.592 | 57.648 | 10.813 | 26.141 | 8.424 |  | 5.2708 | -1.1 | 6.1 | 10.5417 | 0
| 0.80278 | 303.866 | 302.056 | 57.706 | 10.831 | 26.174 | 8.445 |  | 5.2917 | -1.3 | 6.1 | 10.5833 | 0
| 0.80417 | 303.904 | 300.66 | 57.747 | 10.852 | 26.189 | 8.465 |  | 5.3125 | -1.3 | 6.1 | 10.625 | 0
| 0.80556 | 303.17 | 301.276 | 57.792 | 10.872 | 26.201 | 8.48 |  | 5.3333 | -1.9 | 6.1 | 10.6667 | 0
| 0.80694 | 303.353 | 301.357 | 57.846 | 10.891 | 26.227 | 8.499 |  | 5.3542 | -1.9 | 6 | 10.7083 | 0
| 0.80833 | 303.608 | 300.588 | 57.894 | 10.912 | 26.251 | 8.517 |  | 5.375 | -1.7 | 6 | 10.75 | 0
| 0.80972 | 302.833 | 300.86 | 57.94 | 10.933 | 26.276 | 8.537 |  | 5.3958 | -0.8 | 6 | 10.7917 | 0.6
| 0.81111 | 303.152 | 301.401 | 57.987 | 10.952 | 26.299 | 8.552 |  | 5.4167 | 0.2 | 6 | 10.8333 | 2.2
| 0.8125 | 303.894 | 301.168 | 58.036 | 10.972 | 26.324 | 8.569 |  | 5.4375 | 0.6 | 6 | 10.875 | 0
| 0.81389 | 303.421 | 301.729 | 58.088 | 10.991 | 26.349 | 8.59 |  | 5.4583 | 1.2 | 6 | 10.9167 | 0
| 0.81528 | 304.319 | 301.351 | 58.135 | 11.012 | 26.379 | 8.605 |  | 5.4792 | 1.6 | 6 | 10.9583 | 0
| 0.81667 | 303.342 | 301.353 | 58.185 | 11.028 | 26.412 | 8.625 |  | 5.5 | 2.3 | 6 | 11 | 0
| 0.81806 | 304.097 | 301.032 | 58.231 | 11.051 | 26.438 | 8.64 |  | 5.5208 | 3.2 | 6 | 11.0417 | 0
| 0.81943 | 303.934 | 300.899 | 58.275 | 11.073 | 26.463 | 8.659 |  | 5.5417 | 3.9 | 6 | 11.0833 | 0
| 0.82083 | 304.001 | 300.694 | 58.326 | 11.088 | 26.488 | 8.68 |  | 5.5625 | 4.2 | 6 | 11.125 | 0
| 0.82222 | 304.084 | 301.696 | 58.375 | 11.107 | 26.521 | 8.693 |  | 5.5833 | 4.7 | 6 | 11.1667 | 0
| 0.82361 | 304.363 | 301.3 | 58.427 | 11.123 | 26.547 | 8.712 |  | 5.6042 | 4.8 | 6 | 11.2083 | 0
| 0.825 | 304.491 | 301.899 | 58.475 | 11.144 | 26.585 | 8.724 |  | 5.625 | 4.8 | 6 | 11.25 | 0
| 0.82639 | 304.335 | 301.447 | 58.526 | 11.163 | 26.611 | 8.743 |  | 5.6458 | 4.1 | 6 | 11.2917 | 0
| 0.82778 | 304.091 | 301.453 | 58.576 | 11.184 | 26.639 | 8.761 |  | 5.6667 | 3.7 | 6 | 11.3333 | 0
| 0.82917 | 304.651 | 301.374 | 58.615 | 11.201 | 26.666 | 8.775 |  | 5.6875 | 2.4 | 6 | 11.375 | 0
| 0.83056 | 304.131 | 301.935 | 58.664 | 11.216 | 26.693 | 8.792 |  | 5.7083 | 1.3 | 6 | 11.4167 | 0
| 0.83194 | 304.581 | 302.295 | 58.717 | 11.24 | 26.73 | 8.815 |  | 5.7292 | 0.4 | 6 | 11.4583 | 0
| 0.83333 | 304.264 | 302.508 | 58.765 | 11.256 | 26.763 | 8.83 |  | 5.75 | -0.1 | 6 | 11.5 | 0
| 0.83472 | 304.914 | 301.839 | 58.814 | 11.268 | 26.79 | 8.842 |  | 5.7708 | -0.4 | 6 | 11.5417 | 0
| 0.83611 | 304.397 | 302.534 | 58.863 | 11.292 | 26.828 | 8.864 |  | 5.7917 | -0.7 | 6 | 11.5833 | 0
| 0.8375 | 304.632 | 302.58 | 58.911 | 11.311 | 26.86 | 8.881 |  | 5.8125 | -0.7 | 6 | 11.625 | 0
| 0.83889 | 303.762 | 301.299 | 58.956 | 11.324 | 26.885 | 8.897 |  | 5.8333 | -1.1 | 6 | 11.6667 | 0
| 0.84028 | 302.052 | 300.202 | 58.968 | 11.346 | 26.886 | 8.915 |  | 5.8542 | -1.4 | 6 | 11.7083 | 0
| 0.84167 | 302.798 | 300.016 | 58.982 | 11.364 | 26.896 | 8.931 |  | 5.875 | -1.6 | 6 | 11.75 | 0
| 0.84306 | 302.703 | 299.557 | 59.005 | 11.382 | 26.905 | 8.947 |  | 5.8958 | -2.3 | 6 | 11.7917 | 0
| 0.84444 | 302.753 | 300.795 | 59.029 | 11.401 | 26.922 | 8.965 |  | 5.9167 | -2.6 | 5.9 | 11.8333 | 0
| 0.84583 | 303.183 | 301.489 | 59.067 | 11.416 | 26.944 | 8.975 |  | 5.9375 | -2.7 | 5.9 | 11.875 | 0
| 0.84722 | 304.017 | 300.904 | 59.108 | 11.433 | 26.97 | 8.996 |  | 5.9583 | -2.8 | 5.9 | 11.9167 | 0
| 0.84861 | 303.931 | 301.449 | 59.147 | 11.452 | 26.997 | 9.011 |  | 5.9792 | -2.8 | 5.9 | 11.9583 | 0
| 0.85 | 303.909 | 301.952 | 59.193 | 11.468 | 27.031 | 9.028 |  | 6 | -3.1 | 5.9 | 12 | 0
| 0.85139 | 304.417 | 302.148 | 59.24 | 11.489 | 27.065 | 9.043 |  | 6.0208 | -3.3 | 5.9 | 12.0417 | 0
| 0.85278 | 304.547 | 302.128 | 59.283 | 11.503 | 27.093 | 9.059 |  | 6.0417 | -3.7 | 5.9 | 12.0833 | 0
| 0.85417 | 304.96 | 301.664 | 59.324 | 11.515 | 27.126 | 9.073 |  | 6.0625 | -3.8 | 5.9 | 12.125 | 0
| 0.85556 | 304.771 | 302.03 | 59.371 | 11.535 | 27.155 | 9.088 |  | 6.0833 | -4.2 | 5.9 | 12.1667 | 0
| 0.85694 | 304.607 | 302.367 | 59.411 | 11.551 | 27.189 | 9.107 |  | 6.1042 | -4.7 | 5.9 | 12.2083 | 0
| 0.85833 | 304.782 | 301.722 | 59.45 | 11.565 | 27.215 | 9.123 |  | 6.125 | -4.8 | 5.9 | 12.25 | 0
| 0.85972 | 303.869 | 302.056 | 59.485 | 11.585 | 27.24 | 9.14 |  | 6.1458 | -4.8 | 5.9 | 12.2917 | 0
| 0.86111 | 304.345 | 301.781 | 59.517 | 11.597 | 27.269 | 9.15 |  | 6.1667 | -5.2 | 5.9 | 12.3333 | 0
| 0.8625 | 304.544 | 301.776 | 59.556 | 11.616 | 27.295 | 9.168 |  | 6.1875 | -5.4 | 5.9 | 12.375 | 0
| 0.86389 | 303.782 | 301.953 | 59.589 | 11.634 | 27.316 | 9.182 |  | 6.2083 | -5.7 | 5.9 | 12.4167 | 0
| 0.86528 | 304.962 | 301.817 | 59.623 | 11.645 | 27.334 | 9.201 |  | 6.2292 | -5.8 | 5.9 | 12.4583 | 0
| 0.86667 | 304.568 | 301.46 | 59.662 | 11.661 | 27.358 | 9.216 |  | 6.25 | -5.9 | 5.9 | 12.5 | 0
| 0.86806 | 304.487 | 302.828 | 59.698 | 11.678 | 27.381 | 9.227 |  | 6.2708 | -6.2 | 5.9 | 12.5417 | 0
| 0.86944 | 305.729 | 302.567 | 59.741 | 11.698 | 27.414 | 9.246 |  | 6.2917 | -6.6 | 5.9 | 12.5833 | 0
| 0.87083 | 301.82 | 298.738 | 59.77 | 11.713 | 27.443 | 9.261 |  | 6.3125 | -6.5 | 5.9 | 12.625 | 0
| 0.87222 | 301.449 | 299.35 | 59.752 | 11.731 | 27.427 | 9.278 |  | 6.3333 | -6.4 | 5.9 | 12.6667 | 0
| 0.87361 | 301.746 | 298.72 | 59.748 | 11.747 | 27.423 | 9.29 |  | 6.3542 | -6.7 | 5.9 | 12.7083 | 0
| 0.875 | 301.612 | 298.902 | 59.747 | 11.761 | 27.413 | 9.307 |  | 6.375 | -6.3 | 5.9 | 12.75 | 0
| 0.87639 | 301.182 | 299.117 | 59.754 | 11.772 | 27.423 | 9.322 |  | 6.3958 | -5.5 | 5.9 | 12.7917 | 0
| 0.87778 | 301.568 | 298.759 | 59.76 | 11.79 | 27.428 | 9.335 |  | 6.4167 | -4.4 | 5.9 | 12.8333 | 0
| 0.87917 | 301.73 | 298.602 | 59.769 | 11.801 | 27.437 | 9.352 |  | 6.4375 | -4.1 | 5.8 | 12.875 | 0
| 0.88056 | 301.314 | 299.353 | 59.775 | 11.822 | 27.449 | 9.365 |  | 6.4583 | -3.8 | 5.8 | 12.9167 | 0
| 0.88194 | 301.191 | 299.249 | 59.787 | 11.835 | 27.458 | 9.38 |  | 6.4792 | -3.7 | 5.8 | 12.9583 | 0
| 0.88333 | 301.851 | 298.555 | 59.793 | 11.848 | 27.468 | 9.395 |  | 6.5 | -3.5 | 5.8 | 13 | 0
| 0.88472 | 301.257 | 299.641 | 59.812 | 11.864 | 27.486 | 9.415 |  | 6.5208 | -3.2 | 5.8 | 13.0417 | 0
| 0.88611 | 301.681 | 298.853 | 59.82 | 11.874 | 27.502 | 9.423 |  | 6.5417 | -3.3 | 5.8 | 13.0833 | 0
| 0.8875 | 302.423 | 299.48 | 59.834 | 11.894 | 27.518 | 9.441 |  | 6.5625 | -3.2 | 5.8 | 13.125 | 0
| 0.88889 | 301.641 | 299.43 | 59.852 | 11.91 | 27.543 | 9.453 |  | 6.5833 | -2.7 | 5.8 | 13.1667 | 0
| 0.89028 | 301.126 | 298.856 | 59.861 | 11.924 | 27.558 | 9.47 |  | 6.6042 | -2.5 | 5.8 | 13.2083 | 0
| 0.89167 | 301.212 | 299.393 | 59.874 | 11.932 | 27.579 | 9.485 |  | 6.625 | -2.5 | 5.8 | 13.25 | 0
| 0.89306 | 301.289 | 298.13 | 59.877 | 11.945 | 27.587 | 9.494 |  | 6.6458 | -2.6 | 5.8 | 13.2917 | 0
| 0.89444 | 300.893 | 298.402 | 59.885 | 11.963 | 27.601 | 9.511 |  | 6.6667 | -2.5 | 5.8 | 13.3333 | 0
| 0.89583 | 301.024 | 298.412 | 59.884 | 11.975 | 27.605 | 9.521 |  | 6.6875 | -2.4 | 5.8 | 13.375 | 0
| 0.89722 | 300.767 | 298.726 | 59.892 | 11.993 | 27.623 | 9.54 |  | 6.7083 | -2.4 | 5.8 | 13.4167 | 0
| 0.89861 | 300.37 | 298.57 | 59.896 | 12.006 | 27.631 | 9.549 |  | 6.7292 | -2.4 | 5.8 | 13.4583 | 0
| 0.9 | 300.126 | 298.383 | 59.895 | 12.021 | 27.64 | 9.566 |  | 6.75 | -2.3 | 5.8 | 13.5 | 0
| 0.90139 | 300.608 | 297.313 | 59.894 | 12.033 | 27.644 | 9.58 |  | 6.7708 | -2.2 | 5.8 | 13.5417 | 0
| 0.90278 | 299.351 | 297.512 | 59.883 | 12.045 | 27.65 | 9.589 |  | 6.7917 | -2.1 | 5.8 | 13.5833 | 0
| 0.90417 | 299.979 | 297.1 | 59.883 | 12.055 | 27.655 | 9.607 |  | 6.8125 | -1.9 | 5.8 | 13.625 | 0
| 0.90556 | 300.003 | 296.763 | 59.881 | 12.072 | 27.664 | 9.62 |  | 6.8333 | -1.7 | 5.8 | 13.6667 | 0
| 0.90694 | 299.655 | 297.349 | 59.871 | 12.084 | 27.672 | 9.636 |  | 6.8542 | -1.8 | 5.8 | 13.7083 | 0
| 0.90833 | 299.842 | 297.268 | 59.871 | 12.098 | 27.689 | 9.651 |  | 6.875 | -1.8 | 5.8 | 13.75 | 0
| 0.90972 | 299.27 | 297.713 | 59.872 | 12.109 | 27.7 | 9.666 |  | 6.8958 | -2 | 5.8 | 13.7917 | 0
| 0.91111 | 300.047 | 297.659 | 59.878 | 12.122 | 27.701 | 9.673 |  | 6.9167 | -2.2 | 5.8 | 13.8333 | 0
| 0.9125 | 299.339 | 297.677 | 59.881 | 12.132 | 27.722 | 9.689 |  | 6.9375 | -2.1 | 5.8 | 13.875 | 0
| 0.91389 | 299.602 | 297.754 | 59.885 | 12.146 | 27.74 | 9.706 |  | 6.9583 | -2 | 5.8 | 13.9167 | 0
| 0.91528 | 300.333 | 297.24 | 59.884 | 12.155 | 27.75 | 9.713 |  | 6.9792 | -2 | 5.8 | 13.9583 | 0
| 0.91667 | 299.838 | 298.167 | 59.892 | 12.169 | 27.766 | 9.727 |  | 7 | -1.8 | 5.8 | 14 | 0
| 0.91806 | 300.111 | 298.348 | 59.902 | 12.182 | 27.786 | 9.737 |  | 7.0208 | -1.5 | 5.8 | 14.0417 | 2
| 0.91944 | 300.898 | 298.009 | 59.916 | 12.195 | 27.811 | 9.751 |  | 7.0417 | -1 | 5.7 | 14.0833 | 0.4
| 0.92083 | 300.241 | 298.298 | 59.917 | 12.204 | 27.821 | 9.765 |  | 7.0625 | -0.4 | 5.7 | 14.125 | 0
| 0.92222 | 299.99 | 298.379 | 59.929 | 12.216 | 27.837 | 9.777 |  | 7.0833 | -0.1 | 5.7 | 14.1667 | 0
| 0.92361 | 300.544 | 297.935 | 59.939 | 12.23 | 27.857 | 9.789 |  | 7.1042 | 0.2 | 5.7 | 14.2083 | 0
| 0.925 | 300.321 | 297.994 | 59.95 | 12.242 | 27.877 | 9.801 |  | 7.125 | 0.2 | 5.7 | 14.25 | 0.4
| 0.92639 | 300.57 | 297.557 | 59.949 | 12.254 | 27.89 | 9.816 |  | 7.1458 | 0.4 | 5.7 | 14.2917 | 0
| 0.92778 | 300.223 | 298.278 | 59.961 | 12.267 | 27.902 | 9.828 |  | 7.1667 | 0.7 | 5.7 | 14.3333 | 0
| 0.92917 | 301.077 | 298.315 | 59.977 | 12.277 | 27.925 | 9.838 |  | 7.1875 | 0.8 | 5.7 | 14.375 | 0
| 0.93056 | 301.219 | 298.16 | 59.995 | 12.288 | 27.947 | 9.851 |  | 7.2083 | 0.8 | 5.7 | 14.4167 | 0
| 0.93194 | 301.057 | 297.904 | 60.009 | 12.303 | 27.969 | 9.865 |  | 7.2292 | 0.9 | 5.7 | 14.4583 | 0
| 0.93333 | 301.047 | 298.834 | 60.023 | 12.312 | 27.99 | 9.88 |  | 7.25 | 0.9 | 5.7 | 14.5 | 0
| 0.93472 | 300.655 | 298.685 | 60.039 | 12.325 | 28.014 | 9.891 |  | 7.2708 | 1.1 | 5.7 | 14.5417 | 0
| 0.93611 | 300.883 | 298.204 | 60.05 | 12.331 | 28.02 | 9.902 |  | 7.2917 | 1.2 | 5.7 | 14.5833 | 0
| 0.9375 | 300.818 | 298.78 | 60.063 | 12.347 | 28.042 | 9.911 |  | 7.3125 | 1.2 | 5.7 | 14.625 | 0
| 0.93889 | 301.277 | 298.704 | 60.088 | 12.356 | 28.064 | 9.925 |  | 7.3333 | 1.2 | 5.7 | 14.6667 | 0.4
| 0.94028 | 301.247 | 299.12 | 60.109 | 12.369 | 28.09 | 9.94 |  | 7.3542 | 1.3 | 5.7 | 14.7083 | 0
| 0.94167 | 300.798 | 298.87 | 60.126 | 12.38 | 28.108 | 9.95 |  | 7.375 | 1.5 | 5.7 | 14.75 | 0
| 0.94306 | 300.885 | 299.184 | 60.143 | 12.388 | 28.128 | 9.964 |  | 7.3958 | 1.6 | 5.7 | 14.7917 | 0
| 0.94443 | 301.151 | 298.834 | 60.164 | 12.405 | 28.151 | 9.97 |  | 7.4167 | 1.8 | 5.7 | 14.8333 | 0
| 0.94583 | 300.684 | 299.078 | 60.178 | 12.42 | 28.169 | 9.985 |  | 7.4375 | 1.9 | 5.7 | 14.875 | 0
| 0.94722 | 301.675 | 298.441 | 60.195 | 12.428 | 28.186 | 9.999 |  | 7.4583 | 2.3 | 5.7 | 14.9167 | 0
| 0.94861 | 301.412 | 298.414 | 60.209 | 12.436 | 28.201 | 10.01 |  | 7.4792 | 2.6 | 5.7 | 14.9583 | 0
| 0.95 | 301.461 | 299.47 | 60.233 | 12.45 | 28.222 | 10.019 |  | 7.5 | 2.3 | 5.7 | 15 | 0
| 0.95139 | 301.186 | 299.205 | 60.252 | 12.458 | 28.245 | 10.033 |  | 7.5208 | 2.8 | 5.7 | 15.0417 | 0
| 0.95278 | 300.788 | 299.264 | 60.275 | 12.473 | 28.267 | 10.042 |  | 7.5417 | 2.6 | 5.7 | 15.0833 | 0
| 0.95417 | 301.329 | 299.471 | 60.287 | 12.483 | 28.284 | 10.056 |  | 7.5625 | 3.1 | 5.7 | 15.125 | 0
| 0.95556 | 301.472 | 299.808 | 60.304 | 12.489 | 28.304 | 10.066 |  | 7.5833 | 3.2 | 5.7 | 15.1667 | 0
| 0.95694 | 302.135 | 298.97 | 60.331 | 12.507 | 28.322 | 10.079 |  | 7.6042 | 3.7 | 5.7 | 15.2083 | 0
| 0.95833 | 302.194 | 299.299 | 60.35 | 12.52 | 28.344 | 10.087 |  | 7.625 | 3.1 | 5.7 | 15.25 | 0
| 0.95972 | 302.108 | 299.198 | 60.376 | 12.53 | 28.365 | 10.102 |  | 7.6458 | 2.9 | 5.7 | 15.2917 | 0
| 0.96111 | 301.605 | 299.737 | 60.391 | 12.543 | 28.383 | 10.113 |  | 7.6667 | 2.7 | 5.7 | 15.3333 | 0
| 0.9625 | 302.221 | 299.29 | 60.411 | 12.554 | 28.399 | 10.124 |  | 7.6875 | 2.4 | 5.6 | 15.375 | 0
| 0.96389 | 301.833 | 299.158 | 60.433 | 12.562 | 28.42 | 10.133 |  | 7.7083 | 2.1 | 5.6 | 15.4167 | 0
| 0.96528 | 302.241 | 299.089 | 60.458 | 12.575 | 28.435 | 10.146 |  | 7.7292 | 1.9 | 5.6 | 15.4583 | 0
| 0.96667 | 302.176 | 299.155 | 60.48 | 12.581 | 28.457 | 10.156 |  | 7.75 | 1.8 | 5.6 | 15.5 | 0
| 0.96806 | 302.445 | 299.568 | 60.497 | 12.597 | 28.472 | 10.172 |  | 7.7708 | 1.7 | 5.6 | 15.5417 | 0
| 0.96944 | 301.923 | 299.818 | 60.523 | 12.608 | 28.495 | 10.185 |  | 7.7917 | 1.6 | 5.6 | 15.5833 | 0
| 0.97083 | 302.529 | 300.59 | 60.551 | 12.617 | 28.516 | 10.196 |  | 7.8125 | 1.4 | 5.6 | 15.625 | 0
| 0.97222 | 303.118 | 300.059 | 60.581 | 12.628 | 28.545 | 10.205 |  | 7.8333 | 1.3 | 5.6 | 15.6667 | 0
| 0.97361 | 302.73 | 300.47 | 60.613 | 12.639 | 28.566 | 10.214 |  | 7.8542 | 1.3 | 5.6 | 15.7083 | 0
| 0.975 | 302.827 | 301.07 | 60.646 | 12.647 | 28.589 | 10.224 |  | 7.875 | 1.3 | 5.6 | 15.75 | 0
| 0.97639 | 303.036 | 300.723 | 60.676 | 12.663 | 28.618 | 10.236 |  | 7.8958 | 1.4 | 5.6 | 15.7917 | 0
| 0.97778 | 302.806 | 300.916 | 60.704 | 12.673 | 28.638 | 10.249 |  | 7.9167 | 1.4 | 5.6 | 15.8333 | 0
| 0.97917 | 303.652 | 300.416 | 60.732 | 12.685 | 28.659 | 10.258 |  | 7.9375 | 1.4 | 5.6 | 15.875 | 0
| 0.98056 | 303.109 | 301.275 | 60.761 | 12.694 | 28.683 | 10.271 |  | 7.9583 | 1.4 | 5.6 | 15.9167 | 0
| 0.98194 | 303.617 | 300.276 | 60.792 | 12.705 | 28.706 | 10.283 |  | 7.9792 | 1.3 | 5.6 | 15.9583 | 0
| 0.98333 | 302.967 | 301.045 | 60.817 | 12.72 | 28.724 | 10.298 |  | 8 | 0.8 | 5.6 | 16 | 0
| 0.98472 | 303.492 | 300.33 | 60.84 | 12.728 | 28.744 | 10.305 |  | 8.0208 | 1.1 | 5.6 | 16.0417 | 0
| 0.98611 | 303.288 | 300.275 | 60.864 | 12.739 | 28.759 | 10.317 |  | 8.0417 | 1.3 | 5.6 | 16.0833 | 0
| 0.9875 | 303.088 | 300.553 | 60.892 | 12.754 | 28.776 | 10.328 |  | 8.0625 | 1.8 | 5.6 | 16.125 | 0
| 0.98889 | 303.186 | 300.672 | 60.915 | 12.76 | 28.799 | 10.338 |  | 8.0833 | 2.3 | 5.6 | 16.1667 | 0
| 0.99028 | 302.81 | 300.88 | 60.941 | 12.772 | 28.812 | 10.351 |  | 8.1042 | 2.4 | 5.6 | 16.2083 | 0
| 0.99167 | 303.42 | 301 | 60.961 | 12.785 | 28.832 | 10.361 |  | 8.125 | 2.4 | 5.6 | 16.25 | 0.2
| 0.99306 | 302.798 | 301.102 | 60.985 | 12.793 | 28.844 | 10.37 |  | 8.1458 | 2.5 | 5.6 | 16.2917 | 0.2
| 0.99444 | 302.716 | 300.341 | 61.012 | 12.807 | 28.858 | 10.381 |  | 8.1667 | 2.7 | 5.6 | 16.3333 | 0.2
| 0.99583 | 303.319 | 300.961 | 61.034 | 12.817 | 28.876 | 10.393 |  | 8.1875 | 2.9 | 5.6 | 16.375 | 0
| 0.99722 | 303.051 | 301.178 | 61.058 | 12.828 | 28.892 | 10.406 |  | 8.2083 | 3.3 | 5.6 | 16.4167 | 0.2
| 0.99861 | 303.524 | 300.785 | 61.084 | 12.84 | 28.91 | 10.414 |  | 8.2292 | 3.4 | 5.6 | 16.4583 | 1
| 1 | 303.178 | 301.052 | 61.106 | 12.849 | 28.93 | 10.428 |  | 8.25 | 3.6 | 5.6 | 16.5 | 1.2
| 1.0014 | 303.674 | 300.978 | 61.135 | 12.861 | 28.953 | 10.439 |  | 8.2708 | 3.7 | 5.6 | 16.5417 | 0.6
| 1.0028 | 303.537 | 301.532 | 61.16 | 12.869 | 28.967 | 10.443 |  | 8.2917 | 3.8 | 5.6 | 16.5833 | 0.2
| 1.0042 | 303.774 | 301.521 | 61.192 | 12.882 | 28.989 | 10.456 |  | 8.3125 | 4 | 5.6 | 16.625 | 0.2
| 1.0056 | 302.726 | 300.138 | 61.213 | 12.891 | 29.006 | 10.471 |  | 8.3333 | 4.2 | 5.5 | 16.6667 | 0.2
| 1.0069 | 303.11 | 300.189 | 61.224 | 12.904 | 29.013 | 10.479 |  | 8.3542 | 4.5 | 5.5 | 16.7083 | 0
| 1.0083 | 303.157 | 300.196 | 61.24 | 12.912 | 29.026 | 10.49 |  | 8.375 | 4.8 | 5.5 | 16.75 | 0
| 1.0097 | 302.903 | 300.79 | 61.252 | 12.923 | 29.038 | 10.5 |  | 8.3958 | 5.2 | 5.5 | 16.7917 | 0.6
| 1.0111 | 303.012 | 300.937 | 61.273 | 12.935 | 29.048 | 10.512 |  | 8.4167 | 5.4 | 5.5 | 16.8333 | 0.6
| 1.0125 | 303.135 | 301.354 | 61.301 | 12.943 | 29.067 | 10.521 |  | 8.4375 | 5.6 | 5.5 | 16.875 | 0.8
| 1.0139 | 303.883 | 301.392 | 61.325 | 12.957 | 29.09 | 10.537 |  | 8.4583 | 5.9 | 5.5 | 16.9167 | 0.6
| 1.0153 | 304.63 | 301.618 | 61.355 | 12.968 | 29.111 | 10.544 |  | 8.4792 | 5.9 | 5.5 | 16.9583 | 0.4
| 1.0167 | 301.823 | 299.621 | 61.365 | 12.979 | 29.124 | 10.554 |  | 8.5 | 6 | 5.5 | 17 | 0.2
| 1.0181 | 302.506 | 299.229 | 61.364 | 12.988 | 29.122 | 10.568 |  | 8.5208 | 6.2 | 5.5 | 17.0417 | 0
| 1.0194 | 302.062 | 299.307 | 61.365 | 12.997 | 29.121 | 10.575 |  | 8.5417 | 6.3 | 5.5 | 17.0833 | 0
| 1.0208 | 302.174 | 299.579 | 61.374 | 13.01 | 29.126 | 10.585 |  | 8.5625 | 6.3 | 5.5 | 17.125 | 0
| 1.0222 | 302.546 | 299.477 | 61.385 | 13.023 | 29.132 | 10.593 |  | 8.5833 | 6.7 | 5.5 | 17.1667 | 0
| 1.0236 | 302.543 | 299.433 | 61.39 | 13.03 | 29.144 | 10.602 |  | 8.6042 | 6.9 | 5.5 | 17.2083 | 0
| 1.025 | 302.127 | 299.682 | 61.405 | 13.037 | 29.156 | 10.622 |  | 8.625 | 7.2 | 5.5 | 17.25 | 0
| 1.0264 | 302.037 | 299.087 | 61.41 | 13.05 | 29.16 | 10.629 |  | 8.6458 | 7.7 | 5.5 | 17.2917 | 0
| 1.0278 | 301.209 | 299.639 | 61.416 | 13.06 | 29.166 | 10.637 |  | 8.6667 | 7.8 | 5.5 | 17.3333 | 0
| 1.0292 | 301.748 | 299.251 | 61.416 | 13.07 | 29.175 | 10.644 |  | 8.6875 | 8.3 | 5.5 | 17.375 | 0.2
| 1.0306 | 301.488 | 299.65 | 61.424 | 13.081 | 29.177 | 10.655 |  | 8.7083 | 7.8 | 5.5 | 17.4167 | 0
| 1.0319 | 302.041 | 299.381 | 61.435 | 13.088 | 29.196 | 10.667 |  | 8.7292 | 8.4 | 5.5 | 17.4583 | 0
| 1.0333 | 301.682 | 299.226 | 61.443 | 13.099 | 29.202 | 10.679 |  | 8.75 | 8.7 | 5.5 | 17.5 | 0
| 1.0347 | 301.153 | 299.524 | 61.445 | 13.112 | 29.214 | 10.687 |  | 8.7708 | 8.5 | 5.5 | 17.5417 | 0
| 1.0361 | 301.405 | 298.731 | 61.448 | 13.12 | 29.219 | 10.7 |  | 8.7917 | 8.8 | 5.5 | 17.5833 | 0
| 1.0375 | 301.132 | 299.253 | 61.452 | 13.132 | 29.225 | 10.711 |  | 8.8125 | 8.9 | 5.5 | 17.625 | 0
| 1.0389 | 301.481 | 298.198 | 61.45 | 13.138 | 29.232 | 10.722 |  | 8.8333 | 8.8 | 5.5 | 17.6667 | 0
| 1.0403 | 301.494 | 298.371 | 61.451 | 13.152 | 29.239 | 10.728 |  | 8.8542 | 9.6 | 5.5 | 17.7083 | 0.2
| 1.0417 | 300.837 | 298.346 | 61.449 | 13.161 | 29.243 | 10.738 |  | 8.875 | 9.1 | 5.5 | 17.75 | 0
| 1.0431 | 301.341 | 298.193 | 61.449 | 13.166 | 29.248 | 10.75 |  | 8.8958 | 8.3 | 5.5 | 17.7917 | 0
| 1.0444 | 301.834 | 298.69 | 61.461 | 13.18 | 29.26 | 10.761 |  | 8.9167 | 8.1 | 5.5 | 17.8333 | 0
| 1.0458 | 301.298 | 299.391 | 61.469 | 13.189 | 29.273 | 10.772 |  | 8.9375 | 7.8 | 5.5 | 17.875 | 0
| 1.0472 | 301.793 | 298.749 | 61.477 | 13.199 | 29.288 | 10.78 |  | 8.9583 | 7.7 | 5.5 | 17.9167 | 0
| 1.0486 | 301.76 | 299.074 | 61.485 | 13.207 | 29.297 | 10.789 |  | 8.9792 | 7.4 | 5.5 | 17.9583 | 0
| 1.05 | 301.561 | 298.718 | 61.501 | 13.212 | 29.314 | 10.8 |  | 9 | 6.9 | 5.5 | 18 | 0
| 1.0514 | 301.322 | 299.442 | 61.504 | 13.219 | 29.329 | 10.809 |  | 9.0208 | 6.7 | 5.4 | 18.0417 | 0
| 1.0528 | 301.335 | 299.134 | 61.512 | 13.232 | 29.343 | 10.823 |  | 9.0417 | 6.6 | 5.4 | 18.0833 | 0
| 1.0542 | 301.651 | 299.69 | 61.521 | 13.239 | 29.348 | 10.828 |  | 9.0625 | 6 | 5.4 | 18.125 | 0
| 1.0556 | 302.135 | 298.924 | 61.532 | 13.249 | 29.366 | 10.841 |  | 9.0833 | 5.3 | 5.4 | 18.1667 | 0
| 1.0569 | 301.655 | 299.365 | 61.538 | 13.26 | 29.373 | 10.847 |  | 9.1042 | 5.2 | 5.4 | 18.2083 | 0
| 1.0583 | 301.756 | 299.817 | 61.557 | 13.27 | 29.393 | 10.86 |  | 9.125 | 5.1 | 5.4 | 18.25 | 0
| 1.0597 | 302.445 | 299.641 | 61.573 | 13.279 | 29.413 | 10.868 |  | 9.1458 | 5.5 | 5.4 | 18.2917 | 0
| 1.0611 | 302.028 | 299.733 | 61.587 | 13.291 | 29.431 | 10.875 |  | 9.1667 | 6.1 | 5.4 | 18.3333 | 0
| 1.0625 | 301.84 | 299.99 | 61.596 | 13.297 | 29.448 | 10.884 |  | 9.1875 | 6.4 | 5.4 | 18.375 | 0
| 1.0639 | 301.964 | 299.521 | 61.606 | 13.302 | 29.456 | 10.895 |  | 9.2083 | 6.4 | 5.4 | 18.4167 | 0
| 1.0653 | 301.892 | 299.645 | 61.617 | 13.312 | 29.468 | 10.904 |  | 9.2292 | 6.8 | 5.4 | 18.4583 | 0
| 1.0667 | 302.316 | 299.155 | 61.627 | 13.322 | 29.484 | 10.916 |  | 9.25 | 7.3 | 5.4 | 18.5 | 0
| 1.0681 | 301.599 | 299.887 | 61.642 | 13.329 | 29.501 | 10.926 |  | 9.2708 | 7.3 | 5.4 | 18.5417 | 0
| 1.0694 | 301.594 | 299.492 | 61.645 | 13.34 | 29.508 | 10.935 |  | 9.2917 | 7.4 | 5.4 | 18.5833 | 0
| 1.0708 | 302.042 | 299.2 | 61.654 | 13.352 | 29.515 | 10.943 |  | 9.3125 | 7.6 | 5.4 | 18.625 | 0
| 1.0722 | 301.163 | 299.052 | 61.663 | 13.359 | 29.524 | 10.953 |  | 9.3333 | 7.8 | 5.4 | 18.6667 | 0
| 1.0736 | 301.423 | 299.631 | 61.669 | 13.369 | 29.534 | 10.964 |  | 9.3542 | 8.1 | 5.4 | 18.7083 | 0
| 1.075 | 301.891 | 298.955 | 61.675 | 13.373 | 29.543 | 10.97 |  | 9.375 | 8.2 | 5.4 | 18.75 | 0
| 1.0764 | 301.085 | 299.365 | 61.684 | 13.385 | 29.56 | 10.977 |  | 9.3958 | 8.3 | 5.4 | 18.7917 | 0
| 1.0778 | 301.607 | 299.802 | 61.698 | 13.39 | 29.563 | 10.99 |  | 9.4167 | 8.5 | 5.4 | 18.8333 | 0
| 1.0792 | 301.898 | 299.947 | 61.705 | 13.402 | 29.582 | 11 |  | 9.4375 | 8.5 | 5.4 | 18.875 | 0
| 1.0806 | 302.288 | 299.576 | 61.726 | 13.412 | 29.603 | 11.012 |  | 9.4583 | 8.3 | 5.4 | 18.9167 | 0
| 1.0819 | 302.082 | 300.081 | 61.741 | 13.418 | 29.606 | 11.017 |  | 9.4792 | 8.2 | 5.4 | 18.9583 | 0
| 1.0833 | 302.28 | 299.177 | 61.748 | 13.427 | 29.62 | 11.026 |  | 9.5 | 8.2 | 5.4 | 19 | 0
| 1.0847 | 302.478 | 299.612 | 61.762 | 13.437 | 29.635 | 11.035 |  | 9.5208 | 8.4 | 5.4 | 19.0417 | 0
| 1.0861 | 302.444 | 299.762 | 61.782 | 13.448 | 29.648 | 11.041 |  | 9.5417 | 8.6 | 5.4 | 19.0833 | 0
| 1.0875 | 302.677 | 299.791 | 61.793 | 13.453 | 29.662 | 11.055 |  | 9.5625 | 8.8 | 5.4 | 19.125 | 0
| 1.0889 | 302.712 | 299.67 | 61.806 | 13.46 | 29.681 | 11.062 |  | 9.5833 | 8.9 | 5.4 | 19.1667 | 0
| 1.0903 | 302.851 | 299.873 | 61.82 | 13.47 | 29.692 | 11.07 |  | 9.6042 | 9.2 | 5.4 | 19.2083 | 0
| 1.0917 | 302.183 | 300.493 | 61.836 | 13.477 | 29.713 | 11.079 |  | 9.625 | 9.4 | 5.4 | 19.25 | 0
| 1.0931 | 302.839 | 299.614 | 61.851 | 13.486 | 29.728 | 11.09 |  | 9.6458 | 9.6 | 5.4 | 19.2917 | 0
| 1.0944 | 302.873 | 299.963 | 61.868 | 13.494 | 29.739 | 11.095 |  | 9.6667 | 9.7 | 5.4 | 19.3333 | 0
| 1.0958 | 302.671 | 300.449 | 61.884 | 13.511 | 29.757 | 11.107 |  | 9.6875 | 10 | 5.4 | 19.375 | 0
| 1.0972 | 302.627 | 300.009 | 61.901 | 13.512 | 29.763 | 11.116 |  | 9.7083 | 10.1 | 5.4 | 19.4167 | 0
| 1.0986 | 302.901 | 300.413 | 61.919 | 13.52 | 29.779 | 11.126 |  | 9.7292 | 10.2 | 5.4 | 19.4583 | 0.2
| 1.1 | 303.214 | 300.468 | 61.932 | 13.532 | 29.803 | 11.136 |  | 9.75 | 10.3 | 5.4 | 19.5 | 0
| 1.1014 | 302.71 | 300.798 | 61.956 | 13.539 | 29.813 | 11.138 |  | 9.7708 | 10.4 | 5.3 | 19.5417 | 0
| 1.1028 | 303.224 | 300.741 | 61.969 | 13.548 | 29.829 | 11.151 |  | 9.7917 | 9.7 | 5.4 | 19.5833 | 0
| 1.1042 | 302.713 | 300.971 | 61.997 | 13.557 | 29.852 | 11.156 |  | 9.8125 | 9.4 | 5.3 | 19.625 | 0
| 1.1056 | 302.76 | 300.96 | 62.015 | 13.559 | 29.862 | 11.167 |  | 9.8333 | 9.3 | 5.3 | 19.6667 | 0
| 1.1069 | 303.391 | 300.456 | 62.032 | 13.572 | 29.877 | 11.176 |  | 9.8542 | 9.3 | 5.3 | 19.7083 | 0
| 1.1083 | 302.845 | 301.086 | 62.049 | 13.584 | 29.897 | 11.187 |  | 9.875 | 9.4 | 5.3 | 19.75 | 0
| 1.1097 | 303.241 | 300.149 | 62.066 | 13.585 | 29.901 | 11.193 |  | 9.8958 | 9.8 | 5.3 | 19.7917 | 0
| 1.1111 | 303.278 | 300.377 | 62.083 | 13.598 | 29.919 | 11.202 |  | 9.9167 | 10.2 | 5.3 | 19.8333 | 0
| 1.1125 | 303.302 | 300.368 | 62.096 | 13.606 | 29.931 | 11.212 |  | 9.9375 | 10.6 | 5.3 | 19.875 | 0
| 1.1139 | 303.319 | 300.793 | 62.118 | 13.616 | 29.947 | 11.217 |  | 9.9583 | 11.7 | 5.3 | 19.9167 | 0
| 1.1153 | 302.94 | 301.23 | 62.134 | 13.622 | 29.957 | 11.225 |  | 9.9792 | 12 | 5.3 | 19.9583 | 0
| 1.1167 | 303.474 | 300.741 | 62.153 | 13.631 | 29.976 | 11.239 |  | 10 | 12.4 | 5.3 | 20 | 0
| 1.1181 | 302.984 | 301.224 | 62.173 | 13.641 | 29.984 | 11.245 |  | 10.0208 | 12.9 | 5.3 | 20.0417 | 0
| 1.1194 | 303.221 | 301.044 | 62.188 | 13.646 | 29.993 | 11.259 |  | 10.0417 | 12.8 | 5.3 | 20.0833 | 0
| 1.1208 | 303.527 | 300.717 | 62.2 | 13.66 | 30.018 | 11.263 |  | 10.0625 | 12.9 | 5.3 | 20.125 | 0
| 1.1222 | 303.505 | 300.768 | 62.224 | 13.666 | 30.024 | 11.272 |  | 10.0833 | 13 | 5.3 | 20.1667 | 0
| 1.1236 | 303.45 | 300.461 | 62.242 | 13.673 | 30.036 | 11.277 |  | 10.1042 | 13.1 | 5.3 | 20.2083 | 0
| 1.125 | 303.435 | 300.199 | 62.252 | 13.686 | 30.051 | 11.285 |  | 10.125 | 13.6 | 5.3 | 20.25 | 0
| 1.1264 | 302.735 | 301.22 | 62.267 | 13.692 | 30.06 | 11.295 |  | 10.1458 | 14.4 | 5.3 | 20.2917 | 0
| 1.1278 | 303.278 | 300.727 | 62.285 | 13.699 | 30.076 | 11.308 |  | 10.1667 | 14.6 | 5.3 | 20.3333 | 0
| 1.1292 | 302.988 | 300.672 | 62.299 | 13.713 | 30.088 | 11.317 |  | 10.1875 | 14.6 | 5.3 | 20.375 | 0
| 1.1306 | 303.319 | 300.805 | 62.321 | 13.718 | 30.098 | 11.326 |  | 10.2083 | 14.6 | 5.3 | 20.4167 | 0
| 1.1319 | 303 | 301.331 | 62.333 | 13.725 | 30.11 | 11.33 |  | 10.2292 | 14.5 | 5.3 | 20.4583 | 0
| 1.1333 | 303.574 | 301.588 | 62.353 | 13.736 | 30.131 | 11.342 |  | 10.25 | 14.2 | 5.3 | 20.5 | 0.2
| 1.1347 | 304.41 | 301.244 | 62.38 | 13.744 | 30.146 | 11.347 |  | 10.2708 | 13.8 | 5.3 | 20.5417 | 0.2
| 1.1361 | 304.171 | 301.249 | 62.403 | 13.751 | 30.171 | 11.359 |  | 10.2917 | 13.8 | 5.3 | 20.5833 | 0
| 1.1375 | 304.086 | 301.396 | 62.426 | 13.756 | 30.177 | 11.364 |  | 10.3125 | 13.9 | 5.3 | 20.625 | 0
| 1.1389 | 304.158 | 301.394 | 62.445 | 13.766 | 30.193 | 11.374 |  | 10.3333 | 13.9 | 5.3 | 20.6667 | 0
| 1.1403 | 303.915 | 301.566 | 62.473 | 13.781 | 30.222 | 11.385 |  | 10.3542 | 14 | 5.3 | 20.7083 | 0
| 1.1417 | 303.723 | 301.856 | 62.494 | 13.782 | 30.226 | 11.392 |  | 10.375 | 13.9 | 5.3 | 20.75 | 0
| 1.1431 | 304.762 | 301.575 | 62.517 | 13.793 | 30.253 | 11.4 |  | 10.3958 | 13.8 | 5.3 | 20.7917 | 0
| 1.1444 | 303.591 | 302 | 62.535 | 13.801 | 30.262 | 11.407 |  | 10.4167 | 13.7 | 5.3 | 20.8333 | 0
| 1.1458 | 300.817 | 297.775 | 62.526 | 13.806 | 30.258 | 11.417 |  | 10.4375 | 13.6 | 5.3 | 20.875 | 0
| 1.1472 | 300.709 | 297.878 | 62.489 | 13.813 | 30.223 | 11.427 |  | 10.4583 | 13.9 | 5.3 | 20.9167 | 0
| 1.1486 | 300.25 | 298.033 | 62.467 | 13.821 | 30.21 | 11.43 |  | 10.4792 | 13.5 | 5.3 | 20.9583 | 0
| 1.15 | 300.476 | 298.232 | 62.449 | 13.833 | 30.194 | 11.443 |  | 10.5 | 13.5 | 5.3 | 21 | 0
| 1.1514 | 300.312 | 298.507 | 62.44 | 13.838 | 30.18 | 11.448 |  | 10.5208 | 13.4 | 5.3 | 21.0417 | 0
| 1.1528 | 300.578 | 298.506 | 62.432 | 13.845 | 30.18 | 11.46 |  | 10.5417 | 13.1 | 5.3 | 21.0833 | 0
| 1.1542 | 301.309 | 298.3 | 62.429 | 13.857 | 30.184 | 11.464 |  | 10.5625 | 13 | 5.3 | 21.125 | 0
| 1.1556 | 300.546 | 298.961 | 62.426 | 13.863 | 30.193 | 11.473 |  | 10.5833 | 12.8 | 5.3 | 21.1667 | 0
| 1.1569 | 301.012 | 298.704 | 62.423 | 13.87 | 30.192 | 11.482 |  | 10.6042 | 12.9 | 5.3 | 21.2083 | 0
| 1.1583 | 299.086 | 297.348 | 62.397 | 13.881 | 30.181 | 11.49 |  | 10.625 | 13.1 | 5.3 | 21.25 | 0
| 1.1597 | 299.416 | 296.48 | 62.372 | 13.888 | 30.166 | 11.496 |  | 10.6458 | 12.6 | 5.3 | 21.2917 | 0
| 1.1611 | 299.289 | 296.534 | 62.355 | 13.893 | 30.159 | 11.509 |  | 10.6667 | 12.3 | 5.3 | 21.3333 | 0
| 1.1625 | 299.555 | 296.585 | 62.327 | 13.9 | 30.152 | 11.515 |  | 10.6875 | 12 | 5.3 | 21.375 | 0
| 1.1639 | 299.633 | 296.621 | 62.311 | 13.912 | 30.152 | 11.524 |  | 10.7083 | 11.7 | 5.3 | 21.4167 | 0
| 1.1653 | 299.304 | 296.83 | 62.292 | 13.916 | 30.146 | 11.533 |  | 10.7292 | 11.7 | 5.3 | 21.4583 | 0
| 1.1667 | 298.882 | 297.378 | 62.281 | 13.921 | 30.145 | 11.542 |  | 10.75 | 11.8 | 5.3 | 21.5 | 0
| 1.1681 | 299.422 | 297.096 | 62.269 | 13.927 | 30.15 | 11.549 |  | 10.7708 | 11.7 | 5.3 | 21.5417 | 0
| 1.1694 | 299.245 | 297.37 | 62.259 | 13.933 | 30.151 | 11.556 |  | 10.7917 | 11.2 | 5.3 | 21.5833 | 0
| 1.1708 | 299.465 | 297.177 | 62.252 | 13.943 | 30.153 | 11.559 |  | 10.8125 | 11.1 | 5.3 | 21.625 | 0
| 1.1722 | 299.327 | 297.527 | 62.244 | 13.951 | 30.165 | 11.573 |  | 10.8333 | 8.6 | 5.3 | 21.6667 | 0
| 1.1736 | 299.408 | 297.779 | 62.233 | 13.956 | 30.167 | 11.581 |  | 10.8542 | 7.7 | 5.3 | 21.7083 | 0
| 1.175 | 299.479 | 297.052 | 62.224 | 13.964 | 30.174 | 11.588 |  | 10.875 | 7.7 | 5.3 | 21.75 | 0
| 1.1764 | 299.734 | 296.717 | 62.221 | 13.973 | 30.182 | 11.599 |  | 10.8958 | 7.5 | 5.3 | 21.7917 | 0
| 1.1778 | 299.302 | 297.44 | 62.213 | 13.982 | 30.188 | 11.601 |  | 10.9167 | 7.6 | 5.3 | 21.8333 | 0
| 1.1792 | 299.903 | 296.826 | 62.204 | 13.98 | 30.194 | 11.611 |  | 10.9375 | 7.6 | 5.3 | 21.875 | 0
| 1.1806 | 299.333 | 297.741 | 62.199 | 13.984 | 30.198 | 11.619 |  | 10.9583 | 7.2 | 5.3 | 21.9167 | 0
| 1.1819 | 299.489 | 297.601 | 62.187 | 13.994 | 30.203 | 11.626 |  | 10.9792 | 6.7 | 5.3 | 21.9583 | 0
| 1.1833 | 298.98 | 297.312 | 62.183 | 14.001 | 30.209 | 11.632 |  | 11 | 6.3 | 5.3 | 22 | 0
| 1.1847 | 299.238 | 297.531 | 62.178 | 14.007 | 30.219 | 11.64 |  | 11.0208 | 6.7 | 5.3 | 22.0417 | 0
| 1.1861 | 299.442 | 297.414 | 62.175 | 14.012 | 30.221 | 11.644 |  | 11.0417 | 6.7 | 5.3 | 22.0833 | 0
| 1.1875 | 299.279 | 297.613 | 62.169 | 14.022 | 30.227 | 11.656 |  | 11.0625 | 6.3 | 5.3 | 22.125 | 0
| 1.1889 | 299.064 | 297.321 | 62.167 | 14.027 | 30.237 | 11.666 |  | 11.0833 | 6.1 | 5.3 | 22.1667 | 0
| 1.1903 | 299.724 | 296.878 | 62.16 | 14.034 | 30.245 | 11.667 |  | 11.1042 | 5.9 | 5.3 | 22.2083 | 0
| 1.1917 | 299.167 | 297.458 | 62.152 | 14.04 | 30.248 | 11.678 |  | 11.125 | 5.8 | 5.3 | 22.25 | 0
| 1.1931 | 299.973 | 297.068 | 62.15 | 14.043 | 30.262 | 11.684 |  | 11.1458 | 5.3 | 5.3 | 22.2917 | 0
| 1.1944 | 299.3 | 297.406 | 62.151 | 14.052 | 30.268 | 11.692 |  | 11.1667 | 4.9 | 5.3 | 22.3333 | 0
| 1.1958 | 299.91 | 296.843 | 62.146 | 14.057 | 30.269 | 11.698 |  | 11.1875 | 4.2 | 5.3 | 22.375 | 0
| 1.1972 | 299.219 | 297.548 | 62.146 | 14.062 | 30.28 | 11.706 |  | 11.2083 | 4.4 | 5.3 | 22.4167 | 0
| 1.1986 | 299.118 | 297.599 | 62.141 | 14.07 | 30.288 | 11.711 |  | 11.2292 | 4.6 | 5.3 | 22.4583 | 0
| 1.2 | 299.41 | 297.456 | 62.14 | 14.075 | 30.302 | 11.72 |  | 11.25 | 4.4 | 5.3 | 22.5 | 0
| 1.2014 | 299.334 | 297.468 | 62.141 | 14.082 | 30.301 | 11.727 |  | 11.2708 | 3.8 | 5.3 | 22.5417 | 0
| 1.2028 | 299.939 | 296.923 | 62.146 | 14.09 | 30.309 | 11.735 |  | 11.2917 | 3.2 | 5.3 | 22.5833 | 0
| 1.2042 | 299.091 | 297.499 | 62.139 | 14.096 | 30.313 | 11.739 |  | 11.3125 | 3.4 | 5.3 | 22.625 | 0
| 1.2056 | 300.007 | 297.047 | 62.139 | 14.1 | 30.326 | 11.746 |  | 11.3333 | 2.9 | 5.3 | 22.6667 | 0
| 1.2069 | 299.036 | 297.258 | 62.138 | 14.106 | 30.332 | 11.755 |  | 11.3542 | 3.1 | 5.3 | 22.7083 | 0
| 1.2083 | 299.098 | 297.523 | 62.134 | 14.112 | 30.338 | 11.762 |  | 11.375 | 2.7 | 5.3 | 22.75 | 0
| 1.2097 | 299.439 | 297.27 | 62.138 | 14.12 | 30.346 | 11.763 |  | 11.3958 | 3.3 | 5.3 | 22.7917 | 0
| 1.2111 | 299.285 | 297.066 | 62.137 | 14.125 | 30.348 | 11.775 |  | 11.4167 | 4 | 5.3 | 22.8333 | 0
| 1.2125 | 299.604 | 297.044 | 62.137 | 14.132 | 30.361 | 11.782 |  | 11.4375 | 4.4 | 5.3 | 22.875 | 0
| 1.2139 | 299.455 | 297.031 | 62.136 | 14.139 | 30.367 | 11.787 |  | 11.4583 | 5.4 | 5.3 | 22.9167 | 0
| 1.2153 | 299.229 | 297.355 | 62.134 | 14.141 | 30.37 | 11.796 |  | 11.4792 | 5.4 | 5.3 | 22.9583 | 0
| 1.2167 | 298.957 | 297.337 | 62.125 | 14.148 | 30.377 | 11.803 |  | 11.5 | 5.9 | 5.3 | 23 | 0
| 1.2181 | 299.47 | 296.871 | 62.125 | 14.153 | 30.382 | 11.807 |  | 11.5208 | 5.9 | 5.3 | 23.0417 | 0
| 1.2194 | 299.068 | 297.045 | 62.123 | 14.158 | 30.385 | 11.814 |  | 11.5417 | 6.2 | 5.3 | 23.0833 | 0
| 1.2208 | 299.568 | 296.646 | 62.12 | 14.164 | 30.387 | 11.825 |  | 11.5625 | 6.6 | 5.3 | 23.125 | 0
| 1.2222 | 299.167 | 296.185 | 62.116 | 14.17 | 30.388 | 11.83 |  | 11.5833 | 6.3 | 5.3 | 23.1667 | 0
| 1.2236 | 299.131 | 296.259 | 62.108 | 14.179 | 30.389 | 11.837 |  | 11.6042 | 6.6 | 5.3 | 23.2083 | 0
| 1.225 | 298.36 | 296.556 | 62.101 | 14.187 | 30.391 | 11.839 |  | 11.625 | 6.5 | 5.3 | 23.25 | 0
| 1.2264 | 298.838 | 295.909 | 62.097 | 14.187 | 30.395 | 11.849 |  | 11.6458 | 6.1 | 5.3 | 23.2917 | 0
| 1.2278 | 298.703 | 295.551 | 62.086 | 14.194 | 30.391 | 11.854 |  | 11.6667 | 5.6 | 5.3 | 23.3333 | 0
| 1.2292 | 298.014 | 296.561 | 62.075 | 14.2 | 30.39 | 11.866 |  | 11.6875 | 5.3 | 5.3 | 23.375 | 0
| 1.2306 | 298.693 | 295.946 | 62.076 | 14.206 | 30.397 | 11.871 |  | 11.7083 | 5 | 5.3 | 23.4167 | 0
| 1.2319 | 298.405 | 295.952 | 62.067 | 14.21 | 30.398 | 11.875 |  | 11.7292 | 4.9 | 5.3 | 23.4583 | 0.2
| 1.2333 | 297.796 | 295.998 | 62.054 | 14.217 | 30.403 | 11.881 |  | 11.75 | 4.8 | 5.3 | 23.5 | 0
| 1.2347 | 298.665 | 295.91 | 62.053 | 14.225 | 30.407 | 11.891 |  | 11.7708 | 4.6 | 5.3 | 23.5417 | 0
| 1.2361 | 297.861 | 296.31 | 62.046 | 14.227 | 30.405 | 11.892 |  | 11.7917 | 4.4 | 5.3 | 23.5833 | 0
| 1.2375 | 298.714 | 295.597 | 62.04 | 14.232 | 30.417 | 11.906 |  | 11.8125 | 3.9 | 5.3 | 23.625 | 0
| 1.2389 | 298.358 | 296.239 | 62.036 | 14.24 | 30.416 | 11.909 |  | 11.8333 | 3.7 | 5.3 | 23.6667 | 0
| 1.2403 | 298.006 | 296.49 | 62.032 | 14.245 | 30.424 | 11.917 |  | 11.8542 | 4.1 | 5.3 | 23.7083 | 0
| 1.2417 | 298.015 | 296.203 | 62.028 | 14.253 | 30.426 | 11.918 |  | 11.875 | 4.2 | 5.3 | 23.75 | 0
| 1.2431 | 298.325 | 296.725 | 62.028 | 14.255 | 30.438 | 11.929 |  | 11.8958 | 4.4 | 5.3 | 23.7917 | 0
| 1.2444 | 298.169 | 296.739 | 62.028 | 14.264 | 30.441 | 11.937 |  | 11.9167 | 4.6 | 5.3 | 23.8333 | 0
| 1.2458 | 298.475 | 296.127 | 62.029 | 14.269 | 30.45 | 11.942 |  | 11.9375 | 4.5 | 5.3 | 23.875 | 0
| 1.2472 | 297.962 | 296.433 | 62.027 | 14.268 | 30.451 | 11.947 |  | 11.9583 | 4.9 | 5.3 | 23.9167 | 0
| 1.2486 | 298.902 | 296.245 | 62.022 | 14.279 | 30.46 | 11.955 |  | 11.9792 | 5.1 | 5.3 | 23.9583 | 0
| 1.25 | 298.908 | 295.992 | 62.021 | 14.282 | 30.466 | 11.961 |  | 12 | 4.9 | 5.3 | 24 | 0
| 1.2514 | 298.643 | 296.194 | 62.02 | 14.288 | 30.472 | 11.968 |  | 12.0208 | 5 | 5.3 | 24.0417 | 0
| 1.2528 | 298.498 | 296.437 | 62.016 | 14.293 | 30.479 | 11.973 |  | 12.0417 | 4.9 | 5.3 | 24.0833 | 0
| 1.2542 | 298.596 | 296.343 | 62.015 | 14.3 | 30.483 | 11.977 |  | 12.0625 | 5.3 | 5.4 | 24.125 | 0
| 1.2556 | 298.128 | 296.578 | 62.017 | 14.303 | 30.495 | 11.989 |  | 12.0833 | 5.3 | 5.4 | 24.1667 | 0
| 1.2569 | 298.488 | 295.582 | 62.016 | 14.309 | 30.499 | 11.992 |  | 12.1042 | 5.3 | 5.4 | 24.2083 | 0
| 1.2583 | 298.455 | 295.632 | 62.01 | 14.314 | 30.504 | 11.998 |  | 12.125 | 5.3 | 5.4 | 24.25 | 0
| 1.2597 | 298.373 | 296.336 | 62.017 | 14.319 | 30.51 | 12.005 |  | 12.1458 | 6.1 | 5.4 | 24.2917 | 0
| 1.2611 | 298.593 | 295.964 | 62.014 | 14.327 | 30.515 | 12.012 |  | 12.1667 | 5.1 | 5.4 | 24.3333 | 0
| 1.2625 | 298.054 | 296.362 | 62.012 | 14.33 | 30.526 | 12.018 |  | 12.1875 | 5.2 | 5.4 | 24.375 | 0
| 1.2639 | 298.23 | 295.927 | 62.008 | 14.336 | 30.527 | 12.023 |  | 12.2083 | 5.6 | 5.4 | 24.4167 | 0
| 1.2653 | 301.826 | 299.641 | 62.058 | 14.34 | 30.565 | 12.028 |  | 12.2292 | 5.7 | 5.4 | 24.4583 | 0
| 1.2667 | 302.03 | 299.789 | 62.112 | 14.348 | 30.613 | 12.037 |  | 12.25 | 5.7 | 5.4 | 24.5 | 0
| 1.2681 | 301.869 | 300.136 | 62.158 | 14.355 | 30.649 | 12.041 |  | 12.2708 | 5.6 | 5.4 | 24.5417 | 0
| 1.2694 | 302.211 | 299.682 | 62.189 | 14.358 | 30.677 | 12.048 |  | 12.2917 | 5.6 | 5.4 | 24.5833 | 0
| 1.2708 | 302.361 | 299.665 | 62.219 | 14.364 | 30.707 | 12.051 |  | 12.3125 | 5.6 | 5.4 | 24.625 | 0
| 1.2722 | 301.703 | 299.605 | 62.252 | 14.365 | 30.726 | 12.059 |  | 12.3333 | 5.6 | 5.4 | 24.6667 | 0
| 1.2736 | 301.525 | 299.442 | 62.273 | 14.376 | 30.746 | 12.067 |  | 12.3542 | 5.5 | 5.4 | 24.7083 | 0
| 1.275 | 302.027 | 298.806 | 62.292 | 14.386 | 30.759 | 12.074 |  | 12.375 | 5.7 | 5.4 | 24.75 | 0
| 1.2764 | 301.357 | 299.433 | 62.319 | 14.39 | 30.769 | 12.078 |  | 12.3958 | 5.9 | 5.4 | 24.7917 | 0
| 1.2778 | 301.81 | 299.043 | 62.338 | 14.394 | 30.783 | 12.082 |  | 12.4167 | 5.8 | 5.4 | 24.8333 | 0
| 1.2792 | 301.809 | 299.228 | 62.36 | 14.4 | 30.796 | 12.088 |  | 12.4375 | 5.8 | 5.4 | 24.875 | 0
| 1.2806 | 301.42 | 299.805 | 62.381 | 14.409 | 30.811 | 12.099 |  | 12.4583 | 5.8 | 5.4 | 24.9167 | 0
| 1.2819 | 300.846 | 299.197 | 62.401 | 14.408 | 30.821 | 12.101 |  | 12.4792 | 6.1 | 5.4 | 24.9583 | 0
| 1.2833 | 301.213 | 299.083 | 62.416 | 14.42 | 30.833 | 12.113 |  | 12.5 | 6.3 | 5.4 | 25 | 0
| 1.2847 | 300.976 | 299.305 | 62.44 | 14.425 | 30.837 | 12.116 |  | 12.5208 | 6.7 | 5.4 | 25.0417 | 0
| 1.2861 | 300.971 | 299.112 | 62.452 | 14.43 | 30.846 | 12.125 |  | 12.5417 | 6.9 | 5.4 | 25.0833 | 0
| 1.2875 | 301.583 | 298.415 | 62.47 | 14.439 | 30.859 | 12.127 |  | 12.5625 | 6.5 | 5.4 | 25.125 | 0
| 1.2889 | 301.227 | 299.392 | 62.491 | 14.448 | 30.862 | 12.135 |  | 12.5833 | 6.6 | 5.4 | 25.1667 | 0
| 1.2903 | 301.25 | 298.703 | 62.506 | 14.45 | 30.874 | 12.139 |  | 12.6042 | 6.7 | 5.4 | 25.2083 | 0
| 1.2917 | 301.71 | 298.73 | 62.521 | 14.456 | 30.88 | 12.145 |  | 12.625 | 7 | 5.4 | 25.25 | 0
| 1.2931 | 301.137 | 299.263 | 62.537 | 14.463 | 30.889 | 12.154 |  | 12.6458 | 7 | 5.4 | 25.2917 | 0
| 1.2944 | 302.057 | 298.793 | 62.552 | 14.467 | 30.899 | 12.159 |  | 12.6667 | 6.9 | 5.4 | 25.3333 | 0
| 1.2958 | 301.169 | 298.957 | 62.573 | 14.479 | 30.911 | 12.168 |  | 12.6875 | 6.9 | 5.4 | 25.375 | 0
| 1.2972 | 301.859 | 299.046 | 62.589 | 14.48 | 30.922 | 12.173 |  | 12.7083 | 7 | 5.4 | 25.4167 | 0
| 1.2986 | 301.881 | 299.225 | 62.614 | 14.489 | 30.93 | 12.175 |  | 12.7292 | 7 | 5.4 | 25.4583 | 0.2
| 1.3 | 301.773 | 299.215 | 62.63 | 14.496 | 30.94 | 12.183 |  | 12.75 | 6.9 | 5.4 | 25.5 | 0.4
| 1.3014 | 301.84 | 299.036 | 62.65 | 14.5 | 30.956 | 12.189 |  | 12.7708 | 7.1 | 5.4 | 25.5417 | 0.6
| 1.3028 | 301.682 | 299.107 | 62.662 | 14.507 | 30.967 | 12.194 |  | 12.7917 | 7.3 | 5.4 | 25.5833 | 0.2
| 1.3042 | 301.279 | 299.48 | 62.681 | 14.515 | 30.974 | 12.204 |  | 12.8125 | 7.3 | 5.4 | 25.625 | 0
| 1.3056 | 301.486 | 299.882 | 62.698 | 14.52 | 30.987 | 12.208 |  | 12.8333 | 7.3 | 5.4 | 25.6667 | 0
| 1.3069 | 302.193 | 299.442 | 62.716 | 14.529 | 31.002 | 12.217 |  | 12.8542 | 7.4 | 5.4 | 25.7083 | 0
| 1.3083 | 301.801 | 299.799 | 62.733 | 14.53 | 31.013 | 12.222 |  | 12.875 | 7.4 | 5.4 | 25.75 | 0
| 1.3097 | 301.358 | 299.687 | 62.753 | 14.54 | 31.023 | 12.228 |  | 12.8958 | 7.3 | 5.5 | 25.7917 | 0
| 1.3111 | 301.946 | 298.885 | 62.764 | 14.546 | 31.033 | 12.238 |  | 12.9167 | 7.7 | 5.4 | 25.8333 | 0
| 1.3125 | 301.579 | 299.71 | 62.783 | 14.554 | 31.041 | 12.241 |  | 12.9375 | 7.7 | 5.5 | 25.875 | 0
| 1.3139 | 301.809 | 299.541 | 62.797 | 14.559 | 31.051 | 12.248 |  | 12.9583 | 8.3 | 5.5 | 25.9167 | 0
| 1.3153 | 301.339 | 299.643 | 62.814 | 14.564 | 31.055 | 12.255 |  | 12.9792 | 7.9 | 5.5 | 25.9583 | 0.2
| 1.3167 | 301.359 | 299.832 | 62.825 | 14.571 | 31.063 | 12.263 |  | 13 | 7.3 | 5.5 | 26 | 0
| 1.3181 | 301.724 | 299.156 | 62.842 | 14.577 | 31.069 | 12.262 |  | 13.0208 | 6.8 | 5.5 | 26.0417 | 0.2
| 1.3194 | 301.912 | 299.258 | 62.854 | 14.582 | 31.078 | 12.274 |  | 13.0417 | 6.2 | 5.5 | 26.0833 | 0.2
| 1.3208 | 301.918 | 299.097 | 62.865 | 14.591 | 31.085 | 12.279 |  | 13.0625 | 6.3 | 5.5 | 26.125 | 0.2
| 1.3222 | 301.567 | 299.716 | 62.879 | 14.596 | 31.091 | 12.288 |  | 13.0833 | 6.3 | 5.5 | 26.1667 | 0
| 1.3236 | 301.557 | 299.681 | 62.891 | 14.605 | 31.104 | 12.292 |  | 13.1042 | 6.1 | 5.5 | 26.2083 | 0.2
| 1.325 | 301.915 | 299.137 | 62.906 | 14.609 | 31.111 | 12.297 |  | 13.125 | 5 | 5.5 | 26.25 | 0
| 1.3264 | 301.949 | 299.312 | 62.918 | 14.612 | 31.118 | 12.301 |  | 13.1458 | 4.6 | 5.5 | 26.2917 | 0
| 1.3278 | 301.677 | 298.967 | 62.931 | 14.62 | 31.124 | 12.313 |  | 13.1667 | 4.4 | 5.5 | 26.3333 | 0
| 1.3292 | 301.258 | 299.782 | 62.942 | 14.626 | 31.127 | 12.318 |  | 13.1875 | 4.3 | 5.5 | 26.375 | 0
| 1.3306 | 301.86 | 298.925 | 62.949 | 14.629 | 31.137 | 12.323 |  | 13.2083 | 4.1 | 5.5 | 26.4167 | 0.2
| 1.3319 | 301.633 | 299.118 | 62.958 | 14.638 | 31.146 | 12.329 |  | 13.2292 | 5.6 | 5.5 | 26.4583 | 0
| 1.3333 | 301.896 | 299.003 | 62.973 | 14.643 | 31.152 | 12.335 |  | 13.25 | 6.1 | 5.5 | 26.5 | 0.2
| 1.3347 | 301.478 | 299.47 | 62.982 | 14.655 | 31.162 | 12.343 |  | 13.2708 | 7.1 | 5.5 | 26.5417 | 0
| 1.3361 | 302.107 | 299.249 | 62.999 | 14.658 | 31.167 | 12.346 |  | 13.2917 | 6.8 | 5.5 | 26.5833 | 0.6
| 1.3375 | 301.685 | 300.079 | 63.012 | 14.665 | 31.179 | 12.352 |  | 13.3125 | 6.7 | 5.5 | 26.625 | 0.4
| 1.3389 | 302.066 | 299.54 | 63.026 | 14.668 | 31.191 | 12.359 |  | 13.3333 | 6.7 | 5.5 | 26.6667 | 0.4
| 1.3403 | 302.081 | 299.146 | 63.042 | 14.676 | 31.2 | 12.368 |  | 13.3542 | 6.5 | 5.5 | 26.7083 | 0
| 1.3417 | 302.353 | 299.33 | 63.055 | 14.681 | 31.208 | 12.372 |  | 13.375 | 7.1 | 5.5 | 26.75 | 0.2
| 1.3431 | 301.627 | 299.858 | 63.067 | 14.688 | 31.22 | 12.38 |  | 13.3958 | 6.3 | 5.5 | 26.7917 | 0.4
| 1.3444 | 301.565 | 299.91 | 63.079 | 14.695 | 31.225 | 12.387 |  | 13.4167 | 7.7 | 5.5 | 26.8333 | 0.2
| 1.3458 | 302.368 | 299.609 | 63.088 | 14.694 | 31.238 | 12.391 |  | 13.4375 | 8.6 | 5.5 | 26.875 | 0
| 1.3472 | 302.454 | 299.744 | 63.107 | 14.704 | 31.247 | 12.398 |  | 13.4583 | 9.2 | 5.5 | 26.9167 | 0
| 1.3486 | 302.666 | 300.391 | 63.128 | 14.71 | 31.263 | 12.403 |  | 13.4792 | 10.2 | 5.5 | 26.9583 | 0
| 1.35 | 302.277 | 300.498 | 63.153 | 14.716 | 31.278 | 12.411 |  | 13.5 | 11.1 | 5.5 | 27 | 0
| 1.3514 | 302.603 | 300.451 | 63.17 | 14.721 | 31.294 | 12.418 |  | 13.5208 | 11.9 | 5.5 | 27.0417 | 0
| 1.3528 | 303.628 | 301.559 | 63.188 | 14.728 | 31.306 | 12.421 |  | 13.5417 | 12.1 | 5.5 | 27.0833 | 0
| 1.3542 | 304.817 | 301.943 | 63.238 | 14.735 | 31.337 | 12.428 |  | 13.5625 | 12.1 | 5.5 | 27.125 | 0
| 1.3556 | 304.734 | 301.676 | 63.276 | 14.742 | 31.37 | 12.431 |  | 13.5833 | 13.2 | 5.5 | 27.1667 | 0
| 1.3569 | 304.266 | 302.647 | 63.314 | 14.745 | 31.394 | 12.443 |  | 13.6042 | 12.4 | 5.5 | 27.2083 | 0.2
| 1.3583 | 304.076 | 302.396 | 63.348 | 14.754 | 31.416 | 12.447 |  | 13.625 | 13.7 | 5.5 | 27.25 | 0
| 1.3597 | 304.697 | 302.011 | 63.382 | 14.764 | 31.434 | 12.452 |  | 13.6458 | 13.2 | 5.5 | 27.2917 | 0
| 1.3611 | 304.776 | 301.585 | 63.411 | 14.765 | 31.455 | 12.461 |  | 13.6667 | 13.6 | 5.5 | 27.3333 | 0
| 1.3625 | 304.493 | 302.373 | 63.439 | 14.776 | 31.472 | 12.466 |  | 13.6875 | 13.2 | 5.5 | 27.375 | 0
| 1.3639 | 304.547 | 302.181 | 63.471 | 14.781 | 31.489 | 12.468 |  | 13.7083 | 12.4 | 5.5 | 27.4167 | 0
| 1.3653 | 304.571 | 302.34 | 63.502 | 14.789 | 31.507 | 12.48 |  | 13.7292 | 12 | 5.5 | 27.4583 | 0
| 1.3667 | 300.816 | 298.776 | 63.504 | 14.792 | 31.513 | 12.484 |  | 13.75 | 12 | 5.5 | 27.5 | 0
| 1.3681 | 301.224 | 298.207 | 63.474 | 14.8 | 31.48 | 12.489 |  | 13.7708 | 11.9 | 5.5 | 27.5417 | 0
| 1.3694 | 301.004 | 298.35 | 63.459 | 14.804 | 31.455 | 12.495 |  | 13.7917 | 11.7 | 5.5 | 27.5833 | 0
| 1.3708 | 300.434 | 298.805 | 63.447 | 14.816 | 31.439 | 12.501 |  | 13.8125 | 11.3 | 5.5 | 27.625 | 0
| 1.3722 | 300.702 | 299.113 | 63.443 | 14.82 | 31.427 | 12.509 |  | 13.8333 | 11.2 | 5.5 | 27.6667 | 0
| 1.3736 | 300.844 | 299.243 | 63.442 | 14.823 | 31.426 | 12.517 |  | 13.8542 | 11.6 | 5.5 | 27.7083 | 0
| 1.375 | 301.543 | 298.336 | 63.441 | 14.829 | 31.426 | 12.519 |  | 13.875 | 11.3 | 5.5 | 27.75 | 0
| 1.3764 | 300.875 | 299.05 | 63.436 | 14.837 | 31.423 | 12.532 |  | 13.8958 | 11.3 | 5.5 | 27.7917 | 0
| 1.3778 | 300.789 | 299.047 | 63.437 | 14.845 | 31.423 | 12.533 |  | 13.9167 | 10.7 | 5.5 | 27.8333 | 0
| 1.3792 | 300.954 | 298.908 | 63.438 | 14.852 | 31.422 | 12.541 |  | 13.9375 | 9.9 | 5.5 | 27.875 | 0.2
| 1.3806 | 300.999 | 299.404 | 63.436 | 14.857 | 31.424 | 12.544 |  | 13.9583 | 9.8 | 5.5 | 27.9167 | 0
| 1.3819 | 301.034 | 298.875 | 63.437 | 14.862 | 31.427 | 12.55 |  | 13.9792 | 9.7 | 5.5 | 27.9583 | 0
| 1.3833 | 300.701 | 299.171 | 63.439 | 14.869 | 31.43 | 12.556 |  | 14 | 9.4 | 5.5 | 28 | 0
| 1.3847 | 301.318 | 298.343 | 63.443 | 14.875 | 31.437 | 12.561 |  | 14.0208 | 9.3 | 5.5 | 28.0417 | 0
| 1.3861 | 300.843 | 298.641 | 63.431 | 14.878 | 31.44 | 12.571 |  | 14.0417 | 8.1 | 5.5 | 28.0833 | 0
| 1.3875 | 300.474 | 298.457 | 63.427 | 14.884 | 31.434 | 12.58 |  | 14.0625 | 7.7 | 5.5 | 28.125 | 0
| 1.3889 | 300.704 | 297.578 | 63.422 | 14.89 | 31.433 | 12.584 |  | 14.0833 | 7.3 | 5.5 | 28.1667 | 0
| 1.3903 | 300.874 | 298.141 | 63.416 | 14.895 | 31.433 | 12.589 |  | 14.1042 | 7.7 | 5.5 | 28.2083 | 0
| 1.3917 | 300.742 | 297.85 | 63.41 | 14.898 | 31.433 | 12.599 |  | 14.125 | 7.3 | 5.5 | 28.25 | 0
| 1.3931 | 300.614 | 298.334 | 63.405 | 14.909 | 31.435 | 12.599 |  | 14.1458 | 7.2 | 5.5 | 28.2917 | 0
| 1.3944 | 300.062 | 298.609 | 63.396 | 14.915 | 31.435 | 12.607 |  | 14.1667 | 7.2 | 5.5 | 28.3333 | 0
| 1.3958 | 300.175 | 298.552 | 63.397 | 14.913 | 31.436 | 12.615 |  | 14.1875 | 7.2 | 5.5 | 28.375 | 0
| 1.3972 | 300.564 | 297.582 | 63.394 | 14.923 | 31.436 | 12.615 |  | 14.2083 | 7.5 | 5.5 | 28.4167 | 0
| 1.3986 | 300.325 | 297.416 | 63.381 | 14.93 | 31.443 | 12.626 |  | 14.2292 | 7.7 | 5.5 | 28.4583 | 0
| 1.4 | 300.485 | 297.727 | 63.38 | 14.934 | 31.443 | 12.629 |  | 14.25 | 7.6 | 5.5 | 28.5 | 0
| 1.4014 | 299.869 | 297.669 | 63.373 | 14.937 | 31.443 | 12.641 |  | 14.2708 | 6.3 | 5.5 | 28.5417 | 0
| 1.4028 | 300.375 | 297.461 | 63.371 | 14.947 | 31.446 | 12.645 |  | 14.2917 | 6.7 | 5.5 | 28.5833 | 0
| 1.4042 | 299.638 | 297.937 | 63.363 | 14.951 | 31.448 | 12.645 |  | 14.3125 | --- | 5.5 | 28.625 | 0
| 1.4056 | 299.81 | 297.773 | 63.344 | 14.952 | 31.449 | 12.654 |  | 14.3333 | 6.4 | 5.5 | 28.6667 | 0
| 1.4069 | 300.168 | 297.265 | 63.343 | 14.957 | 31.447 | 12.66 |  | 14.3542 | 6.3 | 5.5 | 28.7083 | 0
| 1.4083 | 300.015 | 296.95 | 63.338 | 14.966 | 31.447 | 12.661 |  | 14.375 | 6.3 | 5.5 | 28.75 | 0
| 1.4097 | 299.967 | 297.072 | 63.329 | 14.968 | 31.45 | 12.671 |  | 14.3958 | 6.3 | 5.6 | 28.7917 | 0
| 1.4111 | 299.724 | 297.724 | 63.318 | 14.973 | 31.451 | 12.676 |  | 14.4167 | 6.6 | 5.6 | 28.8333 | 0
| 1.4125 | 299.454 | 297.833 | 63.316 | 14.982 | 31.454 | 12.681 |  | 14.4375 | 7 | 5.6 | 28.875 | 0.2
| 1.4139 | 300.132 | 297.221 | 63.311 | 14.983 | 31.459 | 12.692 |  | 14.4583 | 7.3 | 5.6 | 28.9167 | 2
| 1.4153 | 299.525 | 297.978 | 63.313 | 14.99 | 31.461 | 12.696 |  | 14.4792 | 7.6 | 5.5 | 28.9583 | 0.2
| 1.4167 | 299.667 | 298.069 | 63.308 | 14.996 | 31.468 | 12.696 |  | 14.5 | 8.1 | 5.6 | 29 | 0
| 1.4181 | 300.15 | 297.383 | 63.304 | 15.001 | 31.474 | 12.705 |  | 14.5208 | 7.7 | 5.6 | 29.0417 | 0
| 1.4194 | 300.075 | 297.15 | 63.302 | 15.004 | 31.484 | 12.71 |  | 14.5417 | 8 | 5.6 | 29.0833 | 0
| 1.4208 | 299.629 | 297.089 | 63.294 | 15.009 | 31.481 | 12.715 |  | 14.5625 | 8 | 5.6 | 29.125 | 0
| 1.4222 | 299.844 | 296.827 | 63.291 | 15.011 | 31.485 | 12.72 |  | 14.5833 | 7.5 | 5.6 | 29.1667 | 0
| 1.4236 | 299.565 | 296.573 | 63.282 | 15.015 | 31.48 | 12.73 |  | 14.6042 | 7.3 | 5.6 | 29.2083 | 0
| 1.425 | 299.665 | 297.048 | 63.271 | 15.022 | 31.482 | 12.732 |  | 14.625 | 6.9 | 5.6 | 29.25 | 0
| 1.4264 | 298.492 | 297.106 | 63.264 | 15.026 | 31.484 | 12.738 |  | 14.6458 | 7.1 | 5.6 | 29.2917 | 0
| 1.4278 | 298.581 | 296.839 | 63.249 | 15.033 | 31.484 | 12.746 |  | 14.6667 | 4.3 | 5.6 | 29.3333 | 0
| 1.4292 | 299.13 | 296.356 | 63.239 | 15.034 | 31.476 | 12.753 |  | 14.6875 | 4.1 | 5.6 | 29.375 | 0
| 1.4306 | 298.301 | 296.791 | 63.22 | 15.04 | 31.475 | 12.754 |  | 14.7083 | 4.2 | 5.6 | 29.4167 | 0
| 1.4319 | 298.794 | 295.872 | 63.21 | 15.046 | 31.472 | 12.761 |  | 14.7292 | 4.1 | 5.6 | 29.4583 | 0.6
| 1.4333 | 298.897 | 296.058 | 63.198 | 15.052 | 31.471 | 12.764 |  | 14.75 | 3.4 | 5.6 | 29.5 | 0.2
| 1.4347 | 298.402 | 295.925 | 63.186 | 15.055 | 31.464 | 12.772 |  | 14.7708 | 2.3 | 5.6 | 29.5417 | 0
| 1.4361 | 298.968 | 296.15 | 63.175 | 15.063 | 31.468 | 12.774 |  | 14.7917 | 3.1 | 5.6 | 29.5833 | 0
| 1.4375 | 298.304 | 296.682 | 63.165 | 15.065 | 31.468 | 12.778 |  | 14.8125 | 2.1 | 5.6 | 29.625 | 0
| 1.4389 | 298.345 | 296.559 | 63.156 | 15.071 | 31.471 | 12.788 |  | 14.8333 | 1.2 | 5.6 | 29.6667 | 0
| 1.4403 | 298.805 | 296.037 | 63.142 | 15.073 | 31.469 | 12.788 |  | 14.8542 | 1.2 | 5.6 | 29.7083 | 0
| 1.4417 | 298.065 | 296.569 | 63.135 | 15.076 | 31.47 | 12.798 |  | 14.875 | 0.8 | 5.6 | 29.75 | 0
| 1.4431 | 298.176 | 296.555 | 63.125 | 15.077 | 31.471 | 12.801 |  | 14.8958 | 1.7 | 5.6 | 29.7917 | 0.2
| 1.4444 | 298.32 | 296.512 | 63.121 | 15.088 | 31.475 | 12.808 |  | 14.9167 | 2.3 | 5.6 | 29.8333 | 0.8
| 1.4458 | 298.228 | 296.665 | 63.109 | 15.088 | 31.481 | 12.81 |  | 14.9375 | 2.6 | 5.6 | 29.875 | 0.4
| 1.4472 | 298.63 | 295.627 | 63.1 | 15.098 | 31.482 | 12.817 |  | 14.9583 | 2.9 | 5.6 | 29.9167 | 0.8
| 1.4486 | 297.962 | 295.823 | 63.089 | 15.098 | 31.478 | 12.82 |  | 14.9792 | 2.6 | 5.6 | 29.9583 | 0.4
| 1.45 | 298.222 | 295.468 | 63.078 | 15.104 | 31.483 | 12.828 |  | 15 | 2.9 | 5.6 | 30 | 0.2
| 1.4514 | 298.181 | 295.895 | 63.066 | 15.107 | 31.478 | 12.833 |  | 15.0208 | 3.6 | 5.6 | 30.0417 | 0.2
| 1.4528 | 298.273 | 295.814 | 63.059 | 15.109 | 31.481 | 12.836 |  | 15.0417 | 3.9 | 5.6 | 30.0833 | 0
| 1.4542 | 298.452 | 296.049 | 63.053 | 15.109 | 31.487 | 12.841 |  | 15.0625 | 4.5 | 5.6 | 30.125 | 0
| 1.4556 | 298.069 | 296.563 | 63.047 | 15.12 | 31.489 | 12.85 |  | 15.0833 | 5.1 | 5.6 | 30.1667 | 0
| 1.4569 | 297.647 | 296.236 | 63.039 | 15.124 | 31.493 | 12.855 |  | 15.1042 | 5.3 | 5.6 | 30.2083 | 0
| 1.4583 | 302.193 | 299.161 | 63.095 | 15.128 | 31.538 | 12.856 |  | 15.125 | 5.6 | 5.6 | 30.25 | 0
| 1.4597 | 301.438 | 299.756 | 63.139 | 15.131 | 31.575 | 12.862 |  | 15.1458 | 5.8 | 5.6 | 30.2917 | 0
| 1.4611 | 301.5 | 299.757 | 63.168 | 15.135 | 31.612 | 12.87 |  | 15.1667 | 5.4 | 5.6 | 30.3333 | 0
| 1.4625 | 301.479 | 299.941 | 63.196 | 15.138 | 31.636 | 12.873 |  | 15.1875 | 5.9 | 5.6 | 30.375 | 0
| 1.4639 | 301.313 | 299.798 | 63.223 | 15.141 | 31.658 | 12.876 |  | 15.2083 | 6.2 | 5.6 | 30.4167 | 0
| 1.4653 | 301.279 | 299.371 | 63.241 | 15.147 | 31.68 | 12.883 |  | 15.2292 | 6.4 | 5.6 | 30.4583 | 0
| 1.4667 | 301.187 | 299.682 | 63.261 | 15.154 | 31.693 | 12.884 |  | 15.25 | 6.4 | 5.6 | 30.5 | 0
| 1.4681 | 301.76 | 298.973 | 63.274 | 15.16 | 31.707 | 12.893 |  | 15.2708 | 6.3 | 5.6 | 30.5417 | 0
| 1.4694 | 301.282 | 298.93 | 63.291 | 15.16 | 31.72 | 12.897 |  | 15.2917 | 7.3 | 5.6 | 30.5833 | 0
| 1.4708 | 301.548 | 298.555 | 63.308 | 15.167 | 31.728 | 12.901 |  | 15.3125 | 7.2 | 5.6 | 30.625 | 0
| 1.4722 | 300.606 | 299.138 | 63.322 | 15.169 | 31.736 | 12.905 |  | 15.3333 | 7.2 | 5.6 | 30.6667 | 0.2
| 1.4736 | 301.332 | 298.764 | 63.335 | 15.177 | 31.744 | 12.909 |  | 15.3542 | 7.3 | 5.6 | 30.7083 | 0
| 1.475 | 301.041 | 298.701 | 63.348 | 15.182 | 31.75 | 12.914 |  | 15.375 | 8.1 | 5.6 | 30.75 | 0
| 1.4764 | 300.771 | 299.235 | 63.357 | 15.186 | 31.758 | 12.919 |  | 15.3958 | 8.4 | 5.6 | 30.7917 | 0
| 1.4778 | 301.204 | 298.8 | 63.372 | 15.196 | 31.766 | 12.925 |  | 15.4167 | 7.9 | 5.6 | 30.8333 | 0
| 1.4792 | 301.077 | 298.271 | 63.385 | 15.193 | 31.774 | 12.93 |  | 15.4375 | 8 | 5.6 | 30.875 | 0
| 1.4806 | 300.737 | 299.076 | 63.396 | 15.2 | 31.775 | 12.934 |  | 15.4583 | 8.2 | 5.6 | 30.9167 | 0
| 1.4819 | 301.129 | 298.291 | 63.405 | 15.205 | 31.785 | 12.939 |  | 15.4792 | 8.9 | 5.6 | 30.9583 | 0
| 1.4833 | 301.381 | 298.475 | 63.42 | 15.212 | 31.787 | 12.944 |  | 15.5 | 9.4 | 5.6 | 31 | 0
| 1.4847 | 300.815 | 299 | 63.436 | 15.215 | 31.8 | 12.952 |  | 15.5208 | 9.9 | 5.6 | 31.0417 | 0
| 1.4861 | 301.042 | 298.034 | 63.44 | 15.224 | 31.802 | 12.957 |  | 15.5417 | 9.5 | 5.6 | 31.0833 | 0
| 1.4875 | 300.882 | 298.259 | 63.448 | 15.228 | 31.807 | 12.961 |  | 15.5625 | 9.3 | 5.6 | 31.125 | 0
| 1.4889 | 300.353 | 298.629 | 63.454 | 15.229 | 31.813 | 12.969 |  | 15.5833 | 9.5 | 5.6 | 31.1667 | 0
| 1.4903 | 300.626 | 298.331 | 63.46 | 15.234 | 31.813 | 12.969 |  | 15.6042 | 9.8 | 5.6 | 31.2083 | 0
| 1.4917 | 300.687 | 297.806 | 63.461 | 15.244 | 31.812 | 12.976 |  | 15.625 | 9.9 | 5.6 | 31.25 | 0
| 1.4931 | 300.256 | 298.187 | 63.463 | 15.245 | 31.811 | 12.975 |  | 15.6458 | 9.9 | 5.6 | 31.2917 | 0
| 1.4944 | 300.234 | 297.319 | 63.469 | 15.251 | 31.818 | 12.987 |  | 15.6667 | 9.7 | 5.6 | 31.3333 | 0
| 1.4958 | 300.465 | 298.208 | 63.472 | 15.255 | 31.817 | 12.994 |  | 15.6875 | 9.4 | 5.6 | 31.375 | 0
| 1.4972 | 300.069 | 298.243 | 63.48 | 15.263 | 31.828 | 13.003 |  | 15.7083 | 9.7 | 5.6 | 31.4167 | 0
| 1.4986 | 300.741 | 297.822 | 63.488 | 15.265 | 31.83 | 13.002 |  | 15.7292 | 10.1 | 5.6 | 31.4583 | 0
| 1.5 | 299.864 | 298.379 | 63.495 | 15.268 | 31.832 | 13.006 |  | 15.75 | 10.4 | 5.6 | 31.5 | 0
| 1.5014 | 299.697 | 298.238 | 63.498 | 15.276 | 31.838 | 13.009 |  | 15.7708 | 10.2 | 5.6 | 31.5417 | 0
| 1.5028 | 299.68 | 297.953 | 63.499 | 15.28 | 31.84 | 13.013 |  | 15.7917 | 9.9 | 5.6 | 31.5833 | 0
| 1.5042 | 299.591 | 297.933 | 63.495 | 15.285 | 31.844 | 13.023 |  | 15.8125 | 9.5 | 5.6 | 31.625 | 0
| 1.5056 | 300.358 | 297.803 | 63.497 | 15.289 | 31.844 | 13.026 |  | 15.8333 | 9.7 | 5.6 | 31.6667 | 0
| 1.5069 | 299.853 | 296.957 | 63.495 | 15.295 | 31.842 | 13.036 |  | 15.8542 | 9.6 | 5.6 | 31.7083 | 0.6
| 1.5083 | 299.619 | 296.877 | 63.492 | 15.301 | 31.845 | 13.037 |  | 15.875 | 9.7 | 5.6 | 31.75 | 1.6
| 1.5097 | 298.583 | 297.009 | 63.481 | 15.304 | 31.838 | 13.043 |  | 15.8958 | 9.6 | 5.6 | 31.7917 | 0.2
| 1.5111 | 299.432 | 296.53 | 63.475 | 15.308 | 31.834 | 13.044 |  | 15.9167 | 9.7 | 5.6 | 31.8333 | 0.2
| 1.5125 | 299.802 | 297.102 | 63.479 | 15.314 | 31.834 | 13.05 |  | 15.9375 | 9.8 | 5.6 | 31.875 | 0
| 1.5139 | 299.449 | 297.411 | 63.483 | 15.316 | 31.844 | 13.056 |  | 15.9583 | 9.8 | 5.6 | 31.9167 | 0.2
| 1.5153 | 299.019 | 297.369 | 63.48 | 15.322 | 31.845 | 13.062 |  | 15.9792 | 10.1 | 5.6 | 31.9583 | 0
| 1.5167 | 299.698 | 296.714 | 63.473 | 15.326 | 31.847 | 13.066 |  | 16 | 9.8 | 5.6 | 32 | 0
| 1.5181 | 299.338 | 296.335 | 63.465 | 15.33 | 31.843 | 13.072 |  | 16.0208 | 9.2 | 5.6 | 32.0417 | 0
| 1.5194 | 298.269 | 296.663 | 63.456 | 15.335 | 31.843 | 13.076 |  | 16.0417 | 8.8 | 5.6 | 32.0833 | 0
| 1.5208 | 299.288 | 296.31 | 63.45 | 15.339 | 31.837 | 13.082 |  | 16.0625 | 8.8 | 5.6 | 32.125 | 0
| 1.5222 | 298.909 | 296.868 | 63.45 | 15.342 | 31.841 | 13.086 |  | 16.0833 | 8.8 | 5.6 | 32.1667 | 0.2
| 1.5236 | 298.792 | 297.101 | 63.449 | 15.35 | 31.842 | 13.09 |  | 16.1042 | 8.5 | 5.6 | 32.2083 | 0
| 1.525 | 299.103 | 296.097 | 63.438 | 15.353 | 31.844 | 13.097 |  | 16.125 | 8.2 | 5.6 | 32.25 | 0.2
| 1.5264 | 298.297 | 296.669 | 63.428 | 15.358 | 31.841 | 13.101 |  | 16.1458 | 7.8 | 5.6 | 32.2917 | 0
| 1.5278 | 298.651 | 295.896 | 63.427 | 15.359 | 31.842 | 13.105 |  | 16.1667 | 7.4 | 5.6 | 32.3333 | 0
| 1.5292 | 298.144 | 296.274 | 63.413 | 15.365 | 31.836 | 13.109 |  | 16.1875 | 7.2 | 5.6 | 32.375 | 0
| 1.5306 | 301.948 | 300.409 | 63.433 | 15.367 | 31.846 | 13.115 |  | 16.2083 | 6.9 | 5.6 | 32.4167 | 0.2
| 1.5319 | 301.594 | 299.778 | 63.486 | 15.371 | 31.893 | 13.123 |  | 16.2292 | 6.7 | 5.6 | 32.4583 | 1.6
| 1.5333 | 301.697 | 299.904 | 63.518 | 15.378 | 31.927 | 13.125 |  | 16.25 | 5.9 | 5.6 | 32.5 | 1.6
| 1.5347 | 301.702 | 300.008 | 63.551 | 15.382 | 31.959 | 13.129 |  | 16.2708 | 6.8 | 5.6 | 32.5417 | 1
| 1.5361 | 302.07 | 300.415 | 63.575 | 15.385 | 31.982 | 13.134 |  | 16.2917 | 6.7 | 5.6 | 32.5833 | 0.4
| 1.5375 | 302.361 | 300.266 | 63.608 | 15.389 | 32.004 | 13.139 |  | 16.3125 | 6.6 | 5.6 | 32.625 | 0
| 1.5389 | 301.742 | 299.87 | 63.633 | 15.391 | 32.026 | 13.148 |  | 16.3333 | 6.6 | 5.6 | 32.6667 | 0.2
| 1.5403 | 302.885 | 299.732 | 63.653 | 15.398 | 32.041 | 13.149 |  | 16.3542 | 6.3 | 5.6 | 32.7083 | 0
| 1.5417 | 302.886 | 299.758 | 63.684 | 15.405 | 32.064 | 13.158 |  | 16.375 | 6.1 | 5.6 | 32.75 | 0.2
| 1.5431 | 302.196 | 299.851 | 63.71 | 15.411 | 32.08 | 13.159 |  | 16.3958 | 6.1 | 5.6 | 32.7917 | 0.2
| 1.5444 | 302.272 | 300.107 | 63.731 | 15.415 | 32.09 | 13.163 |  | 16.4167 | 6.2 | 5.6 | 32.8333 | 0.4
| 1.5458 | 302.513 | 299.448 | 63.755 | 15.42 | 32.104 | 13.168 |  | 16.4375 | 6.3 | 5.6 | 32.875 | 0.6
| 1.5472 | 302.17 | 300.041 | 63.772 | 15.424 | 32.114 | 13.172 |  | 16.4583 | 6.3 | 5.6 | 32.9167 | 0.4
| 1.5486 | 303.195 | 300.194 | 63.8 | 15.426 | 32.127 | 13.181 |  | 16.4792 | 5.3 | 5.6 | 32.9583 | 0.2
| 1.55 | 302.757 | 301.055 | 63.831 | 15.432 | 32.143 | 13.185 |  | 16.5 | 5.3 | 5.6 | 33 | 0
| 1.5514 | 303.434 | 300.178 | 63.858 | 15.442 | 32.157 | 13.191 |  | 16.5208 | 5.3 | 5.6 | 33.0417 | 0
| 1.5528 | 303.418 | 301.136 | 63.889 | 15.442 | 32.172 | 13.191 |  | 16.5417 | 5.2 | 5.6 | 33.0833 | 0.2
| 1.5542 | 303.411 | 300.597 | 63.916 | 15.45 | 32.187 | 13.199 |  | 16.5625 | 5.3 | 5.6 | 33.125 | 0
| 1.5556 | 303.337 | 301.151 | 63.945 | 15.454 | 32.204 | 13.201 |  | 16.5833 | 5.5 | 5.6 | 33.1667 | 0
| 1.5569 | 303.19 | 301.559 | 63.971 | 15.459 | 32.223 | 13.21 |  | 16.6042 | 5.5 | 5.6 | 33.2083 | 0
| 1.5583 | 303.201 | 301.595 | 63.999 | 15.463 | 32.236 | 13.211 |  | 16.625 | 5.3 | 5.6 | 33.25 | 0
| 1.5597 | 303.194 | 301.427 | 64.026 | 15.469 | 32.249 | 13.217 |  | 16.6458 | 5.4 | 5.6 | 33.2917 | 0
| 1.5611 | 303.947 | 300.732 | 64.047 | 15.475 | 32.258 | 13.224 |  | 16.6667 | 5.4 | 5.6 | 33.3333 | 0
| 1.5625 | 303.411 | 300.391 | 64.069 | 15.481 | 32.27 | 13.228 |  | 16.6875 | 5.3 | 5.6 | 33.375 | 0
| 1.5639 | 302.873 | 301.311 | 64.093 | 15.486 | 32.28 | 13.233 |  | 16.7083 | 5.3 | 5.6 | 33.4167 | 0
| 1.5653 | 303.616 | 300.556 | 64.121 | 15.493 | 32.293 | 13.238 |  | 16.7292 | 5.2 | 5.6 | 33.4583 | 0.2
| 1.5667 | 303.206 | 300.125 | 64.137 | 15.499 | 32.299 | 13.245 |  | 16.75 | 5.2 | 5.6 | 33.5 | 0.2
| 1.5681 | 302.778 | 300.732 | 64.157 | 15.503 | 32.304 | 13.246 |  | 16.7708 | 5.2 | 5.6 | 33.5417 | 0.2
| 1.5694 | 303.006 | 301.239 | 64.174 | 15.51 | 32.316 | 13.25 |  | 16.7917 | 5.1 | 5.6 | 33.5833 | 0
| 1.5708 | 303.494 | 300.786 | 64.2 | 15.511 | 32.318 | 13.258 |  | 16.8125 | 4.9 | 5.6 | 33.625 | 0
| 1.5722 | 303.167 | 301.091 | 64.214 | 15.519 | 32.328 | 13.263 |  | 16.8333 | 4.9 | 5.6 | 33.6667 | 0
| 1.5736 | 302.657 | 300.593 | 64.228 | 15.524 | 32.338 | 13.27 |  | 16.8542 | 4.9 | 5.6
| 1.575 | 303.161 | 300.47 | 64.247 | 15.532 | 32.347 | 13.271 |  | 16.875 | 4.8 | 5.6
| 1.5764 | 302.621 | 301.077 | 64.264 | 15.535 | 32.348 | 13.279 |  | 16.8958 | 4.8 | 5.6
| 1.5778 | 302.626 | 300.847 | 64.285 | 15.541 | 32.358 | 13.287 |  | 16.9167 | 4.7 | 5.6
| 1.5792 | 302.692 | 301.033 | 64.299 | 15.546 | 32.364 | 13.29 |  | 16.9375 | 4.6 | 5.6
| 1.5806 | 303.3 | 300.393 | 64.314 | 15.552 | 32.375 | 13.292 |  | 16.9583 | 4.4 | 5.6
| 1.5819 | 303.133 | 300.114 | 64.327 | 15.557 | 32.374 | 13.302 |  | 16.9792 | 4.4 | 5.6
| 1.5833 | 303.328 | 300.362 | 64.34 | 15.564 | 32.384 | 13.302 |  | 17 | 4.3 | 5.6
| 1.5847 | 303.59 | 300.828 | 64.357 | 15.567 | 32.389 | 13.308 |  | 17.0208 | 4.2 | 5.6
| 1.5861 | 303.074 | 300.903 | 64.376 | 15.572 | 32.402 | 13.311 |  | 17.0417 | 4 | 5.6
| 1.5875 | 303.3 | 300.24 | 64.402 | 15.578 | 32.408 | 13.322 |  | 17.0625 | 4.1 | 5.6
| 1.5889 | 302.981 | 301.283 | 64.416 | 15.584 | 32.418 | 13.326 |  | 17.0833 | 4.1 | 5.6
| 1.5903 | 303.039 | 301.417 | 64.431 | 15.588 | 32.427 | 13.331 |  | 17.1042 | 4.1 | 5.6
| 1.5917 | 303.266 | 300.804 | 64.456 | 15.596 | 32.443 | 13.339 |  | 17.125 | 3.9 | 5.7
| 1.5931 | 303.978 | 301.313 | 64.47 | 15.6 | 32.45 | 13.341 |  | 17.1458 | 3.4 | 5.7
| 1.5944 | 303.336 | 301.299 | 64.492 | 15.605 | 32.467 | 13.348 |  | 17.1667 | 3 | 5.7
| 1.5958 | 303.682 | 301.828 | 64.515 | 15.608 | 32.478 | 13.354 |  | 17.1875 | 2.3 | 5.6
| 1.5972 | 304.169 | 301.366 | 64.541 | 15.617 | 32.492 | 13.358 |  | 17.2083 | 2.7 | 5.7
| 1.5986 | 304.089 | 301.121 | 64.559 | 15.621 | 32.504 | 13.365 |  | 17.2292 | 2.8 | 5.7
| 1.6 | 303.871 | 302.328 | 64.58 | 15.626 | 32.517 | 13.368 |  | 17.25 | 4.3 | 5.7
| 1.6014 | 303.485 | 301.354 | 64.602 | 15.634 | 32.53 | 13.373 |  | 17.2708 | 4.6 | 5.7
| 1.6028 | 303.603 | 301.293 | 64.612 | 15.638 | 32.539 | 13.38 |  | 17.2917 | 4.6 | 5.7
| 1.6042 | 303.905 | 301.039 | 64.628 | 15.644 | 32.536 | 13.377 |  | 17.3125 | 4.6 | 5.7
| 1.6056 | 303.556 | 301.761 | 64.645 | 15.649 | 32.548 | 13.388 |  | 17.3333 | 4.6 | 5.7
| 1.6069 | 303.352 | 301.426 | 64.663 | 15.654 | 32.557 | 13.394 |  | 17.3542 | 4.6 | 5.7
| 1.6083 | 303.698 | 301.931 | 64.678 | 15.66 | 32.562 | 13.401 |  | 17.375 | 4.6 | 5.7
| 1.6097 | 304.105 | 301.25 | 64.695 | 15.664 | 32.568 | 13.4 |  | 17.3958 | 4.8 | 5.7
| 1.6111 | 304.125 | 301.36 | 64.71 | 15.671 | 32.579 | 13.41 |  | 17.4167 | 4.9 | 5.7
| 1.6125 | 303.69 | 301.986 | 64.73 | 15.676 | 32.592 | 13.413 |  | 17.4375 | 4.3 | 5.7
| 1.6139 | 303.807 | 301.059 | 64.752 | 15.682 | 32.599 | 13.418 |  | 17.4583 | 4.4 | 5.7
| 1.6153 | 303.626 | 301.307 | 64.763 | 15.69 | 32.606 | 13.421 |  | 17.4792 | 4.4 | 5.7
| 1.6167 | 304.007 | 301.928 | 64.781 | 15.688 | 32.614 | 13.426 |  | 17.5 | 4.8 | 5.7
| 1.6181 | 304.357 | 301.555 | 64.801 | 15.698 | 32.629 | 13.439 |  | 17.5208 | 5.1 | 5.7
| 1.6194 | 304.038 | 302.042 | 64.817 | 15.701 | 32.639 | 13.44 |  | 17.5417 | 5.3 | 5.7
| 1.6208 | 304.923 | 301.815 | 64.841 | 15.705 | 32.648 | 13.446 |  | 17.5625 | 5.4 | 5.7
| 1.6222 | 304.233 | 302.405 | 64.864 | 15.71 | 32.659 | 13.453 |  | 17.5833 | 5.6 | 5.7
| 1.6236 | 304.711 | 301.839 | 64.884 | 15.719 | 32.675 | 13.458 |  | 17.6042 | 5.7 | 5.7
| 1.625 | 304.093 | 302.265 | 64.908 | 15.724 | 32.688 | 13.456 |  | 17.625 | 5.6 | 5.7
| 1.6264 | 304.329 | 302.416 | 64.919 | 15.731 | 32.693 | 13.465 |  | 17.6458 | 5.5 | 5.7
| 1.6278 | 305.033 | 302.003 | 64.937 | 15.734 | 32.7 | 13.476 |  | 17.6667 | 4.8 | 5.7
| 1.6292 | 303.94 | 301.812 | 64.955 | 15.74 | 32.713 | 13.48 |  | 17.6875 | 4.2 | 5.7
| 1.6306 | 304.101 | 302.029 | 64.97 | 15.747 | 32.724 | 13.485 |  | 17.7083 | 3.3 | 5.7
| 1.6319 | 304.145 | 302.32 | 64.985 | 15.755 | 32.726 | 13.489 |  | 17.7292 | 2.8 | 5.7
| 1.6333 | 304.069 | 302.21 | 64.997 | 15.756 | 32.734 | 13.494 |  | 17.75 | 2.7 | 5.7
| 1.6347 | 304.797 | 302.379 | 65.015 | 15.763 | 32.743 | 13.5 |  | 17.7708 | 2.4 | 5.7
| 1.6361 | 305.023 | 302.012 | 65.038 | 15.766 | 32.751 | 13.505 |  | 17.7917 | 1.9 | 5.7
| 1.6375 | 304.289 | 302.458 | 65.057 | 15.775 | 32.763 | 13.509 |  | 17.8125 | 1.8 | 5.7
| 1.6389 | 304.627 | 301.826 | 65.064 | 15.779 | 32.769 | 13.515 |  | 17.8333 | 1.6 | 5.7
| 1.6403 | 304.106 | 302.394 | 65.079 | 15.785 | 32.773 | 13.522 |  | 17.8542 | 1.6 | 5.7
| 1.6417 | 303.973 | 301.737 | 65.088 | 15.793 | 32.774 | 13.525 |  | 17.875 | 1.5 | 5.7
| 1.6431 | 304.455 | 301.456 | 65.098 | 15.792 | 32.779 | 13.529 |  | 17.8958 | 1.4 | 5.7
| 1.6444 | 303.602 | 301.616 | 65.103 | 15.8 | 32.777 | 13.535 |  | 17.9167 | 1.6 | 5.7
| 1.6458 | 303.768 | 300.879 | 65.111 | 15.807 | 32.779 | 13.544 |  | 17.9375 | 1.6 | 5.7
| 1.6472 | 303.49 | 301.894 | 65.117 | 15.815 | 32.785 | 13.547 |  | 17.9583 | 0.8 | 5.7
| 1.6486 | 303.846 | 301.474 | 65.127 | 15.821 | 32.793 | 13.549 |  | 17.9792 | 0.2 | 5.7
| 1.65 | 303.324 | 301.619 | 65.134 | 15.822 | 32.791 | 13.56 |  | 18 | -0.1 | 5.7
| 1.6514 | 303.346 | 301.788 | 65.141 | 15.828 | 32.799 | 13.563 |  | 18.0208 | -0.3 | 5.7
| 1.6528 | 303.697 | 301.973 | 65.152 | 15.836 | 32.805 | 13.568 |  | 18.0417 | -0.7 | 5.7
| 1.6542 | 304.261 | 301.191 | 65.158 | 15.84 | 32.808 | 13.573 |  | 18.0625 | -1.1 | 5.7
| 1.6556 | 303.436 | 301.794 | 65.169 | 15.841 | 32.817 | 13.575 |  | 18.0833 | -1.2 | 5.7
| 1.6569 | 304.07 | 301.284 | 65.175 | 15.849 | 32.819 | 13.58 |  | 18.1042 | -0.2 | 5.7
| 1.6583 | 303.816 | 301.342 | 65.182 | 15.857 | 32.818 | 13.591 |  | 18.125 | -0.4 | 5.7
| 1.6597 | 304.061 | 300.867 | 65.188 | 15.863 | 32.825 | 13.591 |  | 18.1458 | -0.8 | 5.7
| 1.6611 | 303.78 | 300.885 | 65.191 | 15.863 | 32.828 | 13.6 |  | 18.1667 | -0.2 | 5.7
| 1.6625 | 303.456 | 301.548 | 65.194 | 15.868 | 32.833 | 13.605 |  | 18.1875 | -0.1 | 5.7
| 1.6639 | 303.783 | 300.902 | 65.196 | 15.878 | 32.832 | 13.612 |  | 18.2083 | -0.3 | 5.7
| 1.6653 | 303.143 | 301.481 | 65.199 | 15.882 | 32.84 | 13.615 |  | 18.2292 | -0.4 | 5.7
| 1.6667 | 303.798 | 301.088 | 65.211 | 15.886 | 32.845 | 13.621 |  | 18.25 | -0.6 | 5.7
| 1.6681 | 303.791 | 300.843 | 65.219 | 15.891 | 32.848 | 13.624 |  | 18.2708 | -0.8 | 5.7
| 1.6694 | 303.704 | 301.556 | 65.22 | 15.891 | 32.852 | 13.631 |  | 18.2917 | 0.4 | 5.7
| 1.6708 | 303.294 | 301.178 | 65.223 | 15.903 | 32.857 | 13.634 |  | 18.3125 | 0.3 | 5.7
| 1.6722 | 303.666 | 301.234 | 65.226 | 15.904 | 32.86 | 13.64 |  | 18.3333 | 0.2 | 5.7
| 1.6736 | 303.075 | 301.401 | 65.236 | 15.911 | 32.864 | 13.646 |  | 18.3542 | 0.4 | 5.7
| 1.675 | 302.563 | 301.025 | 65.231 | 15.916 | 32.867 | 13.651 |  | 18.375 | 0.8 | 5.7
| 1.6764 | 303.171 | 300.345 | 65.229 | 15.923 | 32.863 | 13.656 |  | 18.3958 | 1.1 | 5.7
| 1.6778 | 302.8 | 301.172 | 65.228 | 15.927 | 32.866 | 13.658 |  | 18.4167 | 1.3 | 5.7
| 1.6792 | 302.581 | 300.604 | 65.228 | 15.929 | 32.867 | 13.664 |  | 18.4375 | 1.6 | 5.7
| 1.6806 | 302.91 | 299.973 | 65.22 | 15.934 | 32.867 | 13.674 |  | 18.4583 | 1.8 | 5.7
| 1.6819 | 302.435 | 300.518 | 65.213 | 15.941 | 32.863 | 13.675 |  | 18.4792 | 1.6 | 5.7
| 1.6833 | 302.7 | 299.919 | 65.215 | 15.944 | 32.864 | 13.683 |  | 18.5 | 2.6 | 5.7
| 1.6847 | 302.294 | 300.434 | 65.204 | 15.95 | 32.858 | 13.689 |  | 18.5208 | 3.8 | 5.7
| 1.6861 | 302.595 | 299.549 | 65.198 | 15.953 | 32.857 | 13.694 |  | 18.5417 | 3.5 | 5.7
| 1.6875 | 302.591 | 299.96 | 65.197 | 15.956 | 32.861 | 13.696 |  | 18.5625 | 4.4 | 5.7
| 1.6889 | 302.086 | 300.217 | 65.193 | 15.967 | 32.862 | 13.698 |  | 18.5833 | 4.3 | 5.7
| 1.6903 | 302.784 | 300.31 | 65.188 | 15.969 | 32.862 | 13.707 |  | 18.6042 | 4.2 | 5.7
| 1.6917 | 302.268 | 300.143 | 65.191 | 15.973 | 32.869 | 13.714 |  | 18.625 | 3.4 | 5.7
| 1.6931 | 302.426 | 299.945 | 65.193 | 15.974 | 32.872 | 13.718 |  | 18.6458 | 3.3 | 5.7
| 1.6944 | 302.69 | 299.925 | 65.192 | 15.984 | 32.874 | 13.721 |  | 18.6667 | 2.3 | 5.7
| 1.6958 | 301.481 | 299.898 | 65.187 | 15.987 | 32.878 | 13.726 |  | 18.6875 | 1.7 | 5.7
| 1.6972 | 301.728 | 299.399 | 65.173 | 15.988 | 32.875 | 13.732 |  | 18.7083 | 1.2 | 5.7
| 1.6986 | 302.187 | 299.237 | 65.165 | 15.995 | 32.872 | 13.741 |  | 18.7292 | 0.8 | 5.7
| 1.7 | 301.055 | 299.143 | 65.158 | 16 | 32.869 | 13.741 |  | 18.75 | 0.7 | 5.7
| 1.7014 | 301.021 | 299.268 | 65.144 | 16 | 32.868 | 13.747 |  | 18.7708 | 0.7 | 5.7
| 1.7028 | 300.802 | 299.301 | 65.136 | 16.006 | 32.861 | 13.751 |  | 18.7917 | 0.7 | 5.7
| 1.7042 | 300.668 | 298.755 | 65.119 | 16.012 | 32.854 | 13.757 |  | 18.8125 | 0.7 | 5.7
| 1.7056 | 302.578 | 300.231 | 65.113 | 16.017 | 32.857 | 13.763 |  | 18.8333 | 0.5 | 5.7
| 1.7069 | 302.216 | 300.665 | 65.126 | 16.018 | 32.868 | 13.766 |  | 18.8542 | 0.2 | 5.7
| 1.7083 | 300.987 | 298.041 | 65.113 | 16.024 | 32.875 | 13.769 |  | 18.875 | 0 | 5.7
| 1.7097 | 300.173 | 298.603 | 65.081 | 16.031 | 32.857 | 13.773 |  | 18.8958 | -0.4 | 5.7
| 1.7111 | 300.121 | 298.213 | 65.058 | 16.031 | 32.843 | 13.778 |  | 18.9167 | -0.7 | 5.7
| 1.7125 | 299.339 | 297.921 | 65.035 | 16.034 | 32.834 | 13.786 |  | 18.9375 | -0.8 | 5.7
| 1.7139 | 298.984 | 297.184 | 65.013 | 16.041 | 32.82 | 13.79 |  | 18.9583 | -0.9 | 5.7
| 1.7153 | 299.364 | 296.599 | 64.984 | 16.045 | 32.809 | 13.793 |  | 18.9792 | -1.2 | 5.7
| 1.7167 | 298.474 | 296.849 | 64.948 | 16.048 | 32.787 | 13.801 |  | 19 | -1.6 | 5.7
| 1.7181 | 301.033 | 298.621 | 64.941 | 16.053 | 32.79 | 13.808 |  | 19.0208 | -1.9 | 5.7
| 1.7194 | 300.404 | 298.842 | 64.947 | 16.055 | 32.804 | 13.809 |  | 19.0417 | -2.2 | 5.7
| 1.7208 | 300.692 | 297.905 | 64.948 | 16.062 | 32.813 | 13.815 |  | 19.0625 | -2.7 | 5.7
| 1.7222 | 300.167 | 298.604 | 64.93 | 16.064 | 32.813 | 13.817 |  | 19.0833 | -2.7 | 5.7
| 1.7236 | 300.783 | 298.303 | 64.92 | 16.068 | 32.815 | 13.822 |  | 19.1042 | -3.1 | 5.7
| 1.725 | 300.596 | 297.67 | 64.913 | 16.07 | 32.819 | 13.825 |  | 19.125 | -3.1 | 5.7
| 1.7264 | 299.919 | 298.321 | 64.905 | 16.073 | 32.816 | 13.83 |  | 19.1458 | -2.7 | 5.7
| 1.7278 | 300.431 | 297.658 | 64.889 | 16.075 | 32.817 | 13.833 |  | 19.1667 | -2.6 | 5.7
| 1.7292 | 299.409 | 297.654 | 64.875 | 16.075 | 32.814 | 13.841 |  | 19.1875 | -2.6 | 5.7
| 1.7306 | 299.518 | 297.481 | 64.863 | 16.083 | 32.819 | 13.845 |  | 19.2083 | -2.5 | 5.7
| 1.7319 | 299.818 | 296.972 | 64.843 | 16.087 | 32.814 | 13.849 |  | 19.2292 | -2.5 | 5.7
| 1.7333 | 299.535 | 296.992 | 64.83 | 16.087 | 32.81 | 13.852 |  | 19.25 | -2.8 | 5.7
| 1.7347 | 298.603 | 297.134 | 64.81 | 16.09 | 32.808 | 13.858 |  | 19.2708 | -2.1 | 5.7
| 1.7361 | 299.365 | 297.441 | 64.794 | 16.091 | 32.8 | 13.861 |  | 19.2917 | -2.2 | 5.7
| 1.7375 | 300.189 | 297.184 | 64.786 | 16.101 | 32.801 | 13.861 |  | 19.3125 | -2.1 | 5.7
| 1.7389 | 299.675 | 297.943 | 64.78 | 16.1 | 32.804 | 13.871 |  | 19.3333 | -1.8 | 5.7
| 1.7403 | 300.028 | 297.019 | 64.769 | 16.101 | 32.806 | 13.877 |  | 19.3542 | -1.6 | 5.7
| 1.7417 | 299.919 | 297.928 | 64.764 | 16.108 | 32.81 | 13.879 |  | 19.375 | -1.3 | 5.7
| 1.7431 | 300.105 | 297.258 | 64.756 | 16.112 | 32.814 | 13.883 |  | 19.3958 | -1.2 | 5.7
| 1.7444 | 300.193 | 297.532 | 64.749 | 16.116 | 32.82 | 13.884 |  | 19.4167 | -0.8 | 5.7
| 1.7458 | 300.127 | 297.595 | 64.744 | 16.12 | 32.821 | 13.891 |  | 19.4375 | -0.5 | 5.7
| 1.7472 | 299.928 | 297.336 | 64.738 | 16.121 | 32.826 | 13.897 |  | 19.4583 | -0.4 | 5.7
| 1.7486 | 299.336 | 297.771 | 64.724 | 16.126 | 32.823 | 13.898 |  | 19.4792 | -0.2 | 5.7
| 1.75 | 299.84 | 298.256 | 64.717 | 16.129 | 32.825 | 13.902 |  | 19.5 | 0 | 5.7
| 1.7514 | 300.149 | 297.157 | 64.717 | 16.131 | 32.833 | 13.902 |  | 19.5208 | -0.1 | 5.7
| 1.7528 | 299.862 | 297.667 | 64.71 | 16.133 | 32.833 | 13.913 |  | 19.5417 | 0 | 5.7
| 1.7542 | 299.49 | 298.055 | 64.703 | 16.135 | 32.836 | 13.914 |  | 19.5625 | 0.1 | 5.7
| 1.7556 | 300.203 | 297.538 | 64.705 | 16.141 | 32.843 | 13.918 |  | 19.5833 | 0.2 | 5.7
| 1.7569 | 300.24 | 297.784 | 64.699 | 16.142 | 32.848 | 13.926 |  | 19.6042 | 0.2 | 5.7
| 1.7583 | 300.523 | 297.674 | 64.696 | 16.145 | 32.857 | 13.929 |  | 19.625 | 0.1 | 5.7
| 1.7597 | 300.37 | 297.567 | 64.695 | 16.148 | 32.865 | 13.933 |  | 19.6458 | 0.2 | 5.7
| 1.7611 | 300.561 | 298.144 | 64.7 | 16.15 | 32.869 | 13.934 |  | 19.6667 | -0.6 | 5.7
| 1.7625 | 300.536 | 298.484 | 64.71 | 16.157 | 32.875 | 13.941 |  | 19.6875 | -0.6 | 5.7
| 1.7639 | 300.624 | 298.126 | 64.709 | 16.161 | 32.889 | 13.942 |  | 19.7083 | -0.5 | 5.7
| 1.7653 | 300.117 | 298.293 | 64.711 | 16.163 | 32.894 | 13.945 |  | 19.7292 | -0.5 | 5.7
| 1.7667 | 301.313 | 298.358 | 64.715 | 16.164 | 32.899 | 13.951 |  | 19.75 | -0.5 | 5.7
| 1.7681 | 301.035 | 298.26 | 64.72 | 16.169 | 32.912 | 13.952 |  | 19.7708 | -0.4 | 5.7
| 1.7694 | 300.583 | 298.589 | 64.724 | 16.169 | 32.917 | 13.961 |  | 19.7917 | -0.3 | 5.7
| 1.7708 | 300.735 | 298.882 | 64.73 | 16.173 | 32.924 | 13.965 |  | 19.8125 | -0.3 | 5.7
| 1.7722 | 301.34 | 298.373 | 64.736 | 16.179 | 32.934 | 13.968 |  | 19.8333 | -0.3 | 5.7
| 1.7736 | 300.963 | 298.268 | 64.74 | 16.179 | 32.938 | 13.967 |  | 19.8542 | -0.3 | 5.7
| 1.775 | 300.15 | 298.628 | 64.743 | 16.187 | 32.942 | 13.975 |  | 19.875 | -0.2 | 5.7
| 1.7764 | 300.474 | 298.425 | 64.744 | 16.188 | 32.95 | 13.978 |  | 19.8958 | -0.2 | 5.7
| 1.7778 | 300.149 | 298.103 | 64.745 | 16.19 | 32.95 | 13.984 |  | 19.9167 | -0.2 | 5.7
| 1.7792 | 300.336 | 297.769 | 64.743 | 16.199 | 32.948 | 13.986 |  | 19.9375 | -0.2 | 5.7
| 1.7806 | 300.576 | 298.537 | 64.738 | 16.202 | 32.949 | 13.992 |  | 19.9583 | -0.1 | 5.7
| 1.7819 | 300.529 | 297.588 | 64.74 | 16.205 | 32.957 | 13.999 |  | 19.9792 | -0.1 | 5.7
| 1.7833 | 300.751 | 297.843 | 64.742 | 16.208 | 32.956 | 14 |  | 20 | -0.1 | 5.7
| 1.7847 | 300.337 | 298.082 | 64.741 | 16.208 | 32.957 | 14.004 |  | 20.0208 | -0.1 | 5.7
| 1.7861 | 300.724 | 297.571 | 64.74 | 16.216 | 32.96 | 14.006 |  | 20.0417 | -0.1 | 5.7
| 1.7875 | 300.105 | 298.292 | 64.74 | 16.217 | 32.961 | 14.012 |  | 20.0625 | -0.1 | 5.7
| 1.7889 | 300.64 | 297.467 | 64.739 | 16.222 | 32.968 | 14.019 |  | 20.0833 | -0.1 | 5.7
| 1.7903 | 299.962 | 297.338 | 64.739 | 16.223 | 32.97 | 14.022 |  | 20.1042 | -0.2 | 5.7
| 1.7917 | 299.874 | 298.114 | 64.733 | 16.23 | 32.973 | 14.025 |  | 20.125 | -0.4 | 5.7
| 1.7931 | 300.214 | 297.235 | 64.732 | 16.233 | 32.971 | 14.025 |  | 20.1458 | -0.6 | 5.7
| 1.7944 | 300.156 | 297.717 | 64.727 | 16.235 | 32.972 | 14.035 |  | 20.1667 | -0.6 | 5.7
| 1.7958 | 300.064 | 297.951 | 64.733 | 16.238 | 32.975 | 14.036 |  | 20.1875 | -0.6 | 5.7
| 1.7972 | 300.527 | 297.512 | 64.733 | 16.239 | 32.98 | 14.039 |  | 20.2083 | -0.6 | 5.7
| 1.7986 | 300.279 | 297.991 | 64.735 | 16.242 | 32.981 | 14.045 |  | 20.2292 | -0.5 | 5.7
| 1.8 | 299.974 | 298.099 | 64.731 | 16.249 | 32.985 | 14.048 |  | 20.25 | -0.4 | 5.7
| 1.8014 | 299.981 | 297.96 | 64.735 | 16.247 | 32.99 | 14.052 |  | 20.2708 | 0.5 | 5.7
| 1.8028 | 299.895 | 298.314 | 64.734 | 16.255 | 32.998 | 14.06 |  | 20.2917 | 0.3 | 5.7
| 1.8042 | 300.611 | 298.738 | 64.743 | 16.256 | 32.999 | 14.062 |  | 20.3125 | 0.3 | 5.7
| 1.8056 | 300.763 | 298.049 | 64.75 | 16.262 | 33.01 | 14.069 |  | 20.3333 | 0.2 | 5.7
| 1.8069 | 300.464 | 298.003 | 64.754 | 16.262 | 33.017 | 14.069 |  | 20.3542 | 0.3 | 5.7
| 1.8083 | 300.622 | 298.36 | 64.76 | 16.27 | 33.024 | 14.074 |  | 20.375 | 0.3 | 5.7
| 1.8097 | 300.386 | 298.344 | 64.763 | 16.271 | 33.029 | 14.078 |  | 20.3958 | 0.2 | 5.7
| 1.8111 | 300.147 | 297.726 | 64.761 | 16.275 | 33.031 | 14.082 |  | 20.4167 | 0.3 | 5.7
| 1.8125 | 300.94 | 297.978 | 64.76 | 16.281 | 33.041 | 14.091 |  | 20.4375 | -0.6 | 5.7
| 1.8139 | 301.061 | 298.125 | 64.769 | 16.283 | 33.043 | 14.093 |  | 20.4583 | -0.2 | 5.7
| 1.8153 | 300.787 | 298.849 | 64.782 | 16.286 | 33.049 | 14.094 |  | 20.4792 | 0 | 5.7
| 1.8167 | 300.498 | 298.726 | 64.787 | 16.29 | 33.066 | 14.1 |  | 20.5 | 0.2 | 5.7
| 1.8181 | 300.801 | 298.951 | 64.8 | 16.294 | 33.067 | 14.104 |  | 20.5208 | 0.9 | 5.7
| 1.8194 | 301.112 | 298.188 | 64.804 | 16.298 | 33.074 | 14.107 |  | 20.5417 | 1.4 | 5.7
| 1.8208 | 301.073 | 298.659 | 64.811 | 16.303 | 33.083 | 14.109 |  | 20.5625 | 1.6 | 5.7
| 1.8222 | 300.753 | 299.035 | 64.821 | 16.303 | 33.087 | 14.116 |  | 20.5833 | 1.5 | 5.7
| 1.8236 | 301.411 | 298.654 | 64.829 | 16.306 | 33.092 | 14.118 |  | 20.6042 | 1.3 | 5.7
| 1.825 | 301.229 | 298.527 | 64.832 | 16.315 | 33.105 | 14.124 |  | 20.625 | 1.3 | 5.7
| 1.8264 | 301.07 | 298.576 | 64.843 | 16.316 | 33.109 | 14.13 |  | 20.6458 | 1.3 | 5.7
| 1.8278 | 301.488 | 298.303 | 64.85 | 16.316 | 33.112 | 14.129 |  | 20.6667 | 1.3 | 5.7
| 1.8292 | 301.729 | 298.689 | 64.855 | 16.324 | 33.119 | 14.135 |  | 20.6875 | 1.2 | 5.7
| 1.8306 | 301.136 | 299.146 | 64.869 | 16.325 | 33.129 | 14.139 |  | 20.7083 | 1.1 | 5.7
| 1.8319 | 301.366 | 298.893 | 64.889 | 16.326 | 33.14 | 14.144 |  | 20.7292 | 1 | 5.7
| 1.8333 | 301.856 | 298.683 | 64.892 | 16.335 | 33.151 | 14.146 |  | 20.75 | 0.7 | 5.7
| 1.8347 | 301.587 | 299.653 | 64.909 | 16.34 | 33.163 | 14.152 |  | 20.7708 | 0.6 | 5.7
| 1.8361 | 302.364 | 299.124 | 64.926 | 16.343 | 33.177 | 14.156 |  | 20.7917 | 0.4 | 5.7
| 1.8375 | 301.853 | 299.219 | 64.939 | 16.348 | 33.187 | 14.159 |  | 20.8125 | 0.3 | 5.7
| 1.8389 | 302.007 | 299.159 | 64.953 | 16.348 | 33.196 | 14.165 |  | 20.8333 | 0.3 | 5.7
| 1.8403 | 301.968 | 299.121 | 64.964 | 16.353 | 33.205 | 14.17 |  | 20.8542 | 0.2 | 5.7
| 1.8417 | 301.503 | 299.553 | 64.978 | 16.356 | 33.209 | 14.171 |  | 20.875 | 0.1 | 5.7
| 1.8431 | 302.21 | 299.112 | 64.987 | 16.361 | 33.214 | 14.177 |  | 20.8958 | 0 | 5.7
| 1.8444 | 301.524 | 299.549 | 65.004 | 16.365 | 33.226 | 14.181 |  | 20.9167 | -0.1 | 5.7
| 1.8458 | 302.68 | 300.314 | 65.016 | 16.37 | 33.238 | 14.181 |  | 20.9375 | -0.1 | 5.6
| 1.8472 | 302.52 | 299.618 | 65.038 | 16.369 | 33.245 | 14.186 |  | 20.9583 | -0.2 | 5.7
| 1.8486 | 302.414 | 299.372 | 65.049 | 16.378 | 33.263 | 14.193 |  | 20.9792 | -0.3 | 5.6
| 1.85 | 302.612 | 299.624 | 65.071 | 16.385 | 33.266 | 14.197 |  | 21 | -0.8 | 5.6
| 1.8514 | 301.998 | 300.116 | 65.08 | 16.385 | 33.271 | 14.2 |  | 21.0208 | -1.2 | 5.6
| 1.8528 | 302.146 | 300.403 | 65.103 | 16.388 | 33.284 | 14.209 |  | 21.0417 | -1.8 | 5.6
| 1.8542 | 302.906 | 299.815 | 65.118 | 16.393 | 33.298 | 14.211 |  | 21.0625 | -1.9 | 5.6
| 1.8556 | 302.303 | 300.735 | 65.134 | 16.4 | 33.311 | 14.215 |  | 21.0833 | -1.5 | 5.6
| 1.8569 | 303.1 | 300.434 | 65.162 | 16.401 | 33.312 | 14.217 |  | 21.1042 | -1.3 | 5.6
| 1.8583 | 302.892 | 300.577 | 65.178 | 16.405 | 33.333 | 14.218 |  | 21.125 | -1.4 | 5.6
| 1.8597 | 302.766 | 300.511 | 65.201 | 16.41 | 33.349 | 14.224 |  | 21.1458 | -1.4 | 5.6
| 1.8611 | 303.17 | 300.096 | 65.215 | 16.413 | 33.347 | 14.229 |  | 21.1667 | -1.8 | 5.6
| 1.8625 | 302.817 | 301.021 | 65.232 | 16.427 | 33.37 | 14.237 |  | 21.1875 | -1.7 | 5.6
| 1.8639 | 302.209 | 300.614 | 65.246 | 16.419 | 33.362 | 14.242 |  | 21.2083 | -2 | 5.6
| 1.8653 | 302.751 | 299.557 | 65.265 | 16.424 | 33.371 | 14.243 |  | 21.2292 | -2.3 | 5.6
| 1.8667 | 302.459 | 300.802 | 65.277 | 16.432 | 33.382 | 14.248 |  | 21.25 | -3 | 5.6
| 1.8681 | 303.31 | 300.244 | 65.291 | 16.433 | 33.39 | 14.255 |  | 21.2708 | -1.4 | 5.6
| 1.8694 | 303.086 | 300.821 | 65.308 | 16.444 | 33.398 | 14.257 |  | 21.2917 | -1.9 | 5.6
| 1.8708 | 303.154 | 300.49 | 65.318 | 16.449 | 33.4 | 14.26 |  | 21.3125 | -2.2 | 5.6
| 1.8722 | 303.218 | 300.471 | 65.338 | 16.448 | 33.408 | 14.265 |  | 21.3333 | -1.9 | 5.6
| 1.8736 | 303.466 | 300.298 | 65.359 | 16.459 | 33.425 | 14.271 |  | 21.3542 | -1.8 | 5.6
| 1.875 | 303.085 | 301.04 | 65.368 | 16.455 | 33.43 | 14.275 |  | 21.375 | -1.3 | 5.6
| 1.8764 | 303.006 | 300.904 | 65.389 | 16.463 | 33.442 | 14.277 |  | 21.3958 | -0.8 | 5.6
| 1.8778 | 302.973 | 301.106 | 65.408 | 16.469 | 33.45 | 14.281 |  | 21.4167 | -0.5 | 5.6
| 1.8792 | 303.257 | 300.536 | 65.424 | 16.473 | 33.459 | 14.288 |  | 21.4375 | -0.4 | 5.6
| 1.8806 | 303.391 | 300.46 | 65.433 | 16.478 | 33.468 | 14.296 |  | 21.4583 | 0.3 | 5.6
| 1.8819 | 303.644 | 300.524 | 65.455 | 16.481 | 33.473 | 14.295 |  | 21.4792 | 0.1 | 5.6
| 1.8833 | 303.612 | 300.363 | 65.47 | 16.48 | 33.475 | 14.299 |  | 21.5 | 0.3 | 5.6
| 1.8847 | 303.509 | 300.937 | 65.482 | 16.488 | 33.488 | 14.304 |  | 21.5208 | 0.4 | 5.6
| 1.8861 | 302.999 | 301.099 | 65.5 | 16.491 | 33.486 | 14.311 |  | 21.5417 | 0.6 | 5.6
| 1.8875 | 303.52 | 301.174 | 65.516 | 16.492 | 33.497 | 14.313 |  | 21.5625 | 0.9 | 5.6
| 1.8889 | 303.089 | 301.471 | 65.532 | 16.5 | 33.509 | 14.318 |  | 21.5833 | 1.2 | 5.6
| 1.8903 | 302.552 | 300.914 | 65.551 | 16.51 | 33.521 | 14.323 |  | 21.6042 | 1.3 | 5.6
| 1.8917 | 303.395 | 300.186 | 65.557 | 16.51 | 33.525 | 14.325 |  | 21.625 | 1.4 | 5.6
| 1.8931 | 302.593 | 300.274 | 65.566 | 16.513 | 33.53 | 14.33 |  | 21.6458 | 1.6 | 5.6
| 1.8944 | 302.542 | 300.12 | 65.567 | 16.519 | 33.521 | 14.335 |  | 21.6667 | 1.6 | 5.6
| 1.8958 | 302.434 | 299.995 | 65.567 | 16.524 | 33.516 | 14.344 |  | 21.6875 | 1.6 | 5.6
| 1.8972 | 302.221 | 300.553 | 65.574 | 16.53 | 33.518 | 14.348 |  | 21.7083 | 1.4 | 5.6
| 1.8986 | 302.68 | 299.474 | 65.583 | 16.534 | 33.517 | 14.349 |  | 21.7292 | 1.3 | 5.6
| 1.9 | 302.546 | 299.571 | 65.582 | 16.54 | 33.523 | 14.355 |  | 21.75 | 1.3 | 5.6
| 1.9014 | 302.407 | 300.282 | 65.59 | 16.54 | 33.525 | 14.358 |  | 21.7708 | 1.4 | 5.6
| 1.9028 | 302.203 | 300.604 | 65.596 | 16.546 | 33.528 | 14.365 |  | 21.7917 | 1.6 | 5.6
| 1.9042 | 302.884 | 299.733 | 65.602 | 16.546 | 33.526 | 14.363 |  | 21.8125 | 1.4 | 5.6
| 1.9056 | 302.669 | 300.543 | 65.613 | 16.551 | 33.528 | 14.37 |  | 21.8333 | 1.2 | 5.6
| 1.9069 | 302.192 | 300.386 | 65.616 | 16.557 | 33.545 | 14.375 |  | 21.8542 | 1.3 | 5.6
| 1.9083 | 303.092 | 299.897 | 65.626 | 16.561 | 33.541 | 14.382 |  | 21.875 | 1.6 | 5.6
| 1.9097 | 303.035 | 300.126 | 65.637 | 16.566 | 33.546 | 14.385 |  | 21.8958 | 1.4 | 5.6
| 1.9111 | 302.481 | 300.581 | 65.64 | 16.567 | 33.548 | 14.39 |  | 21.9167 | 1.6 | 5.6
| 1.9125 | 302.888 | 300.186 | 65.648 | 16.575 | 33.556 | 14.396 |  | 21.9375 | 1.5 | 5.6
| 1.9139 | 302.474 | 300.824 | 65.66 | 16.579 | 33.565 | 14.399 |  | 21.9583 | 1.5 | 5.6
| 1.9153 | 302.586 | 300.513 | 65.667 | 16.581 | 33.569 | 14.404 |  | 21.9792 | 1.5 | 5.6
| 1.9167 | 302.789 | 300.268 | 65.671 | 16.587 | 33.576 | 14.409 |  | 22 | 1.4 | 5.5
| 1.9181 | 302.444 | 300.367 | 65.68 | 16.594 | 33.586 | 14.411 |  | 22.0208 | 1.4 | 5.5
| 1.9194 | 303.023 | 300.544 | 65.693 | 16.593 | 33.594 | 14.414 |  | 22.0417 | 1.3 | 5.5
| 1.9208 | 303.231 | 300.514 | 65.704 | 16.599 | 33.594 | 14.42 |  | 22.0625 | 1.3 | 5.5
| 1.9222 | 302.932 | 300.74 | 65.706 | 16.604 | 33.601 | 14.424 |  | 22.0833 | 1.3 | 5.5
| 1.9236 | 302.982 | 300.235 | 65.717 | 16.607 | 33.61 | 14.427 |  | 22.1042 | 1.1 | 5.5
| 1.925 | 302.487 | 300.88 | 65.725 | 16.612 | 33.613 | 14.432 |  | 22.125 | 1 | 5.5
| 1.9264 | 302.697 | 300.041 | 65.736 | 16.615 | 33.62 | 14.437 |  | 22.1458 | 1.1 | 5.5
| 1.9278 | 302.319 | 300.66 | 65.739 | 16.619 | 33.622 | 14.444 |  | 22.1667 | 0.9 | 5.5
| 1.9292 | 304.061 | 301.147 | 65.756 | 16.625 | 33.636 | 14.447 |  | 22.1875 | 0.8 | 5.5
| 1.9306 | 304.023 | 301.884 | 65.777 | 16.629 | 33.653 | 14.449 |  | 22.2083 | 0.7 | 5.5
| 1.9319 | 303.704 | 302.104 | 65.804 | 16.632 | 33.67 | 14.455 |  | 22.2292 | 0.7 | 5.5
| 1.9333 | 303.397 | 301.949 | 65.824 | 16.635 | 33.682 | 14.458 |  | 22.25 | 0.7 | 5.5
| 1.9347 | 303.725 | 302.05 | 65.848 | 16.639 | 33.699 | 14.461 |  | 22.2708 | 0.7 | 5.5
| 1.9361 | 304.65 | 301.38 | 65.863 | 16.646 | 33.71 | 14.472 |  | 22.2917 | 1.7 | 5.5
| 1.9375 | 304.105 | 302.11 | 65.886 | 16.647 | 33.722 | 14.473 |  | 22.3125 | 1.6 | 5.5
| 1.9389 | 304.475 | 301.594 | 65.907 | 16.654 | 33.738 | 14.48 |  | 22.3333 | 1.4 | 5.5
| 1.9403 | 300.574 | 297.303 | 65.848 | 16.66 | 33.704 | 14.482 |  | 22.3542 | 1.3 | 5.5
| 1.9417 | 300.502 | 297.578 | 65.819 | 16.663 | 33.669 | 14.487 |  | 22.375 | 1.2 | 5.5
| 1.9431 | 300.484 | 297.664 | 65.796 | 16.666 | 33.644 | 14.489 |  | 22.3958 | 1.2 | 5.5
| 1.9444 | 300.579 | 297.797 | 65.777 | 16.671 | 33.63 | 14.492 |  | 22.4167 | 1.3 | 5.5
| 1.9458 | 300.059 | 298.271 | 65.758 | 16.671 | 33.617 | 14.499 |  | 22.4375 | 0.6 | 5.5
| 1.9472 | 300.618 | 297.446 | 65.741 | 16.674 | 33.607 | 14.502 |  | 22.4583 | 0.7 | 5.5
| 1.9486 | 300.753 | 297.754 | 65.734 | 16.683 | 33.599 | 14.51 |  | 22.4792 | 0.7 | 5.5
| 1.95 | 300.853 | 297.924 | 65.718 | 16.688 | 33.591 | 14.511 |  | 22.5 | 0.8 | 5.5
| 1.9514 | 301.022 | 298.177 | 65.712 | 16.688 | 33.593 | 14.515 |  | 22.5208 | 1.1 | 5.5
| 1.9528 | 301.17 | 298.108 | 65.706 | 16.686 | 33.596 | 14.523 |  | 22.5417 | 1.2 | 5.5
| 1.9542 | 301.205 | 298.716 | 65.701 | 16.696 | 33.596 | 14.528 |  | 22.5625 | 1.6 | 5.5
| 1.9556 | 301.449 | 298.476 | 65.696 | 16.699 | 33.607 | 14.528 |  | 22.5833 | 1.6 | 5.5
| 1.9569 | 300.927 | 299.001 | 65.695 | 16.705 | 33.611 | 14.54 |  | 22.6042 | 1.8 | 5.5
| 1.9583 | 301.498 | 298.33 | 65.688 | 16.705 | 33.611 | 14.538 |  | 22.625 | 1.9 | 5.5
| 1.9597 | 300.906 | 299.223 | 65.692 | 16.71 | 33.62 | 14.545 |  | 22.6458 | 1.9 | 5.5
| 1.9611 | 300.802 | 299.055 | 65.692 | 16.714 | 33.623 | 14.549 |  | 22.6667 | 1.9 | 5.5
| 1.9625 | 301.508 | 298.536 | 65.683 | 16.718 | 33.627 | 14.554 |  | 22.6875 | 1.9 | 5.5
| 1.9639 | 301.091 | 299.073 | 65.68 | 16.714 | 33.628 | 14.555 |  | 22.7083 | 1.9 | 5.5
| 1.9653 | 301.834 | 298.692 | 65.681 | 16.728 | 33.636 | 14.56 |  | 22.7292 | 1.9 | 5.5
| 1.9667 | 301.404 | 298.662 | 65.685 | 16.73 | 33.636 | 14.564 |  | 22.75 | 1.9 | 5.5
| 1.9681 | 301.53 | 298.466 | 65.683 | 16.735 | 33.647 | 14.57 |  | 22.7708 | 1.7 | 5.5
| 1.9694 | 301.023 | 299.061 | 65.678 | 16.734 | 33.643 | 14.575 |  | 22.7917 | 1.7 | 5.5
| 1.9708 | 301.602 | 299.336 | 65.68 | 16.738 | 33.653 | 14.576 |  | 22.8125 | 1.6 | 5.5
| 1.9722 | 301.541 | 299.784 | 65.689 | 16.741 | 33.66 | 14.581 |  | 22.8333 | 1.6 | 5.5
| 1.9736 | 302.252 | 300.087 | 65.705 | 16.744 | 33.675 | 14.588 |  | 22.8542 | 1.6 | 5.5
| 1.975 | 302.249 | 300.407 | 65.722 | 16.749 | 33.696 | 14.592 |  | 22.875 | 1.6 | 5.5
| 1.9764 | 302.205 | 300.069 | 65.735 | 16.752 | 33.706 | 14.595 |  | 22.8958 | 1.5 | 5.4
| 1.9778 | 302.853 | 299.732 | 65.742 | 16.756 | 33.71 | 14.596 |  | 22.9167 | 1.4 | 5.4
| 1.9792 | 302.306 | 300.376 | 65.749 | 16.757 | 33.722 | 14.6 |  | 22.9375 | 1.5 | 5.4
| 1.9806 | 301.881 | 300.164 | 65.754 | 16.76 | 33.732 | 14.603 |  | 22.9583 | 1.5 | 5.4
| 1.9819 | 302.215 | 299.908 | 65.767 | 16.768 | 33.737 | 14.61 |  | 22.9792 | 1.5 | 5.4
| 1.9833 | 301.93 | 299.826 | 65.773 | 16.766 | 33.739 | 14.611 |  | 23 | 1.4 | 5.4
| 1.9847 | 301.777 | 300.123 | 65.774 | 16.773 | 33.747 | 14.618 |  | 23.0208 | 1.4 | 5.4
| 1.9861 | 301.855 | 300.109 | 65.778 | 16.776 | 33.749 | 14.616 |  | 23.0417 | 1.4 | 5.4
| 1.9875 | 302.192 | 299.432 | 65.786 | 16.78 | 33.759 | 14.624 |  | 23.0625 | 1.4 | 5.4
| 1.9889 | 302.282 | 299.227 | 65.793 | 16.785 | 33.763 | 14.63 |  | 23.0833 | 1.4 | 5.4
| 1.9903 | 302.656 | 299.431 | 65.8 | 16.787 | 33.767 | 14.629 |  | 23.1042 | 1.4 | 5.4
| 1.9917 | 302.551 | 300.312 | 65.813 | 16.795 | 33.771 | 14.638 |  | 23.125 | 1.3 | 5.4
| 1.9931 | 302.693 | 299.724 | 65.819 | 16.796 | 33.78 | 14.64 |  | 23.1458 | 1.3 | 5.4
| 1.9944 | 301.819 | 299.715 | 65.822 | 16.798 | 33.783 | 14.644 |  | 23.1667 | 1.4 | 5.4
| 1.9958 | 301.964 | 299.973 | 65.825 | 16.803 | 33.786 | 14.646 |  | 23.1875 | 1.4 | 5.4
| 1.9972 | 302.189 | 299.647 | 65.828 | 16.805 | 33.791 | 14.652 |  | 23.2083 | 1.4 | 5.4
| 1.9986 | 302.225 | 300.131 | 65.842 | 16.811 | 33.801 | 14.656 |  | 23.2292 | 1.4 | 5.4
| 2 | 302.295 | 300.519 | 65.847 | 16.812 | 33.801 | 14.662 |  | 23.25 | 1.3 | 5.4
| 2.0014 | 302.26 | 300.167 | 65.858 | 16.816 | 33.81 | 14.664 |  | 23.2708 | 2.3 | 5.4
| 2.0028 | 302.974 | 299.952 | 65.869 | 16.818 | 33.818 | 14.665 |  | 23.2917 | 2.3 | 5.4
| 2.0042 | 302.639 | 300.274 | 65.881 | 16.827 | 33.828 | 14.673 |  | 23.3125 | --- | 5.4
| 2.0056 | 303.222 | 300.736 | 65.898 | 16.832 | 33.843 | 14.681 |  | 23.3333 | --- | 5.4
| 2.0069 | 303.708 | 300.387 | 65.92 | 16.833 | 33.851 | 14.681 |  | 23.3542 | --- | 5.4
| 2.0083 | 303.18 | 300.821 | 65.933 | 16.837 | 33.868 | 14.689 |  | 23.375 | --- | 5.4
| 2.0097 | 302.55 | 300.648 | 65.941 | 16.844 | 33.868 | 14.689 |  | 23.3958 | --- | 5.4
| 2.0111 | 303.106 | 301.02 | 65.95 | 16.844 | 33.879 | 14.694 |  | 23.4167 | 1.8 | 5.4
| 2.0125 | 303.23 | 300.819 | 65.97 | 16.845 | 33.887 | 14.697 |  | 23.4375 | 2 | 5.4
| 2.0139 | 303.832 | 301.294 | 65.993 | 16.847 | 33.903 | 14.701 |  | 23.4583 | 2.2 | 5.4
| 2.0153 | 303.909 | 302.042 | 66.018 | 16.857 | 33.919 | 14.707 |  | 23.4792 | 2.6 | 5.4
| 2.0167 | 304.526 | 301.913 | 66.041 | 16.854 | 33.935 | 14.71 |  | 23.5 | 2.7 | 5.4
| 2.0181 | 300.595 | 298.648 | 66.052 | 16.864 | 33.944 | 14.714 |  | 23.5208 | 3 | 5.4
| 2.0194 | 300.864 | 298.703 | 66.013 | 16.865 | 33.915 | 14.716 |  | 23.5417 | 3.4 | 5.4
| 2.0208 | 301.081 | 298.54 | 65.991 | 16.869 | 33.896 | 14.719 |  | 23.5625 | 3.2 | 5.4
| 2.0222 | 301.783 | 298.515 | 65.988 | 16.876 | 33.884 | 14.726 |  | 23.5833 | 3.2 | 5.4
| 2.0236 | 301.365 | 298.855 | 65.978 | 16.877 | 33.882 | 14.729 |  | 23.6042 | 3.2 | 5.4
| 2.025 | 301.102 | 299.101 | 65.971 | 16.88 | 33.877 | 14.733 |  | 23.625 | 2.9 | 5.4
| 2.0264 | 300.831 | 299.068 | 65.966 | 16.882 | 33.873 | 14.738 |  | 23.6458 | 2.8 | 5.4
| 2.0278 | 301.024 | 298.962 | 65.962 | 16.889 | 33.865 | 14.74 |  | 23.6667 | 2.8 | 5.4
| 2.0292 | 301.054 | 299.092 | 65.96 | 16.892 | 33.867 | 14.748 |  | 23.6875 | 2.6 | 5.4
| 2.0306 | 301.027 | 297.569 | 65.954 | 16.894 | 33.864 | 14.749 |  | 23.7083 | 2.3 | 5.4
| 2.0319 | 299.497 | 296.178 | 65.908 | 16.899 | 33.833 | 14.753 |  | 23.7292 | 2.1 | 5.3
| 2.0333 | 298.795 | 296.163 | 65.872 | 16.904 | 33.809 | 14.762 |  | 23.75 | 1.8 | 5.3
| 2.0347 | 298.296 | 296.049 | 65.836 | 16.91 | 33.789 | 14.759 |  | 23.7708 | 1.8 | 5.3
| 2.0361 | 298.047 | 296.096 | 65.806 | 16.908 | 33.771 | 14.767 |  | 23.7917 | 1.8 | 5.3
| 2.0375 | 297.627 | 295.661 | 65.774 | 16.914 | 33.747 | 14.769 |  | 23.8125 | 1.6 | 5.3
| 2.0389 | 298.218 | 295.212 | 65.742 | 16.913 | 33.736 | 14.772 |  | 23.8333 | 1.3 | 5.3
| 2.0403 | 297.736 | 295.453 | 65.709 | 16.918 | 33.717 | 14.777 |  | 23.8542 | 1 | 5.3
| 2.0417 | 298.221 | 295.478 | 65.679 | 16.925 | 33.705 | 14.785 |  | 23.875 | 0.3 | 5.3
| 2.0431 | 297.553 | 295.655 | 65.655 | 16.924 | 33.698 | 14.782 |  | 23.8958 | -0.7 | 5.3
| 2.0444 | 298.136 | 294.811 | 65.626 | 16.925 | 33.685 | 14.787 |  | 23.9167 | -1.3 | 5.3
| 2.0458 | 297.774 | 295.482 | 65.598 | 16.929 | 33.676 | 14.793 |  | 23.9375 | -1.7 | 5.3
| 2.0472 | 297.715 | 295.488 | 65.573 | 16.933 | 33.671 | 14.796 |  | 23.9583 | -2.1 | 5.3
| 2.0486 | 297.916 | 295.33 | 65.548 | 16.934 | 33.66 | 14.801 |  | 23.9792 | -2.6 | 5.3
| 2.05 | 297.515 | 295.66 | 65.523 | 16.939 | 33.657 | 14.804 |  | 24 | -3.2 | 5.3
| 2.0514 | 298.509 | 295.898 | 65.502 | 16.94 | 33.656 | 14.809 |  | 24.0208 | -3.4 | 5.3
| 2.0528 | 298.527 | 296.409 | 65.485 | 16.94 | 33.657 | 14.81 |  | 24.0417 | -3.8 | 5.3
| 2.0542 | 298.999 | 296.583 | 65.482 | 16.943 | 33.657 | 14.816 |  | 24.0625 | -3.8 | 5.3
| 2.0556 | 299.431 | 296.67 | 65.483 | 16.947 | 33.67 | 14.818 |  | 24.0833 | -4.3 | 5.3
| 2.0569 | 300.052 | 296.795 | 65.476 | 16.949 | 33.685 | 14.821 |  | 24.1042 | -4.3 | 5.3
| 2.0583 | 299.396 | 296.759 | 65.476 | 16.95 | 33.696 | 14.825 |  | 24.125 | -4.6 | 5.3
| 2.0597 | 299.364 | 295.998 | 65.461 | 16.954 | 33.702 | 14.833 |  | 24.1458 | -4.9 | 5.3
| 2.0611 | 298.976 | 296.127 | 65.45 | 16.96 | 33.702 | 14.834 |  | 24.1667 | -5.4 | 5.3
| 2.0625 | 298.543 | 296.091 | 65.433 | 16.958 | 33.704 | 14.836 |  | 24.1875 | -5.5 | 5.3
| 2.0639 | 298.433 | 295.652 | 65.419 | 16.963 | 33.697 | 14.842 |  | 24.2083 | -5.8 | 5.3
| 2.0653 | 298.291 | 295.882 | 65.399 | 16.962 | 33.692 | 14.841 |  | 24.2292 | -5.7 | 5.3
| 2.0667 | 298.481 | 296.145 | 65.387 | 16.964 | 33.688 | 14.845 |  | 24.25 | -4.8 | 5.3
| 2.0681 | 298.243 | 296.231 | 65.374 | 16.966 | 33.686 | 14.848 |  | 24.2708 | -2.5 | 5.3
| 2.0694 | 298.178 | 296.35 | 65.362 | 16.968 | 33.686 | 14.855 |  | 24.2917 | -2.1 | 5.3
| 2.0708 | 298.772 | 295.4 | 65.349 | 16.968 | 33.686 | 14.854 |  | 24.3125 | -1 | 5.3
| 2.0722 | 298.409 | 295.609 | 65.34 | 16.973 | 33.684 | 14.858 |  | 24.3333 | -0.7 | 5.3
| 2.0736 | 298.846 | 295.477 | 65.332 | 16.971 | 33.686 | 14.862 |  | 24.3542 | -0.4 | 5.3
| 2.075 | 297.986 | 296.193 | 65.321 | 16.977 | 33.688 | 14.865 |  | 24.375 | -0.2 | 5.3
| 2.0764 | 299.013 | 295.675 | 65.316 | 16.979 | 33.691 | 14.867 |  | 24.3958 | 0.1 | 5.3
| 2.0778 | 299.106 | 295.868 | 65.308 | 16.982 | 33.693 | 14.872 |  | 24.4167 | 0.3 | 5.3
| 2.0792 | 299.035 | 296.165 | 65.3 | 16.982 | 33.697 | 14.875 |  | 24.4375 | 0.6 | 5.3
| 2.0806 | 298.753 | 296.049 | 65.296 | 16.981 | 33.701 | 14.878 |  | 24.4583 | -0.2 | 5.3
| 2.0819 | 298.992 | 295.87 | 65.288 | 16.986 | 33.706 | 14.882 |  | 24.4792 | 0.4 | 5.3
| 2.0833 | 298.962 | 295.917 | 65.281 | 16.993 | 33.707 | 14.886 |  | 24.5 | 0.4 | 5.3
| 2.0847 | 299.357 | 296.316 | 65.282 | 16.99 | 33.712 | 14.89 |  | 24.5208 | 0.6 | 5.2
| 2.0861 | 298.641 | 296.458 | 65.277 | 16.994 | 33.712 | 14.895 |  | 24.5417 | 0.9 | 5.2
| 2.0875 | 298.776 | 296.449 | 65.275 | 16.996 | 33.72 | 14.893 |  | 24.5625 | 1.1 | 5.2
| 2.0889 | 299.071 | 295.989 | 65.269 | 16.999 | 33.726 | 14.897 |  | 24.5833 | 1.1 | 5.2
| 2.0903 | 298.834 | 296.499 | 65.266 | 17.002 | 33.726 | 14.902 |  | 24.6042 | 0.9 | 5.2
| 2.0917 | 299.031 | 296.598 | 65.264 | 17.006 | 33.733 | 14.904 |  | 24.625 | 0.3 | 5.2
| 2.0931 | 299.229 | 296.299 | 65.262 | 17.007 | 33.737 | 14.905 |  | 24.6458 | 0.2 | 5.2
| 2.0944 | 299.166 | 296.695 | 65.263 | 17.01 | 33.742 | 14.909 |  | 24.6667 | 0.1 | 5.2
| 2.0958 | 299.593 | 296.375 | 65.265 | 17.012 | 33.747 | 14.913 |  | 24.6875 | 0.1 | 5.2
| 2.0972 | 299.663 | 296.786 | 65.268 | 17.013 | 33.758 | 14.915 |  | 24.7083 | 0.1 | 5.2
| 2.0986 | 300.551 | 298.349 | 65.286 | 17.019 | 33.776 | 14.92 |  | 24.7292 | 0.1 | 5.2
| 2.1 | 301.141 | 297.771 | 65.312 | 17.019 | 33.792 | 14.921 |  | 24.75 | 0.1 | 5.2
| 2.1014 | 300.049 | 297.943 | 65.322 | 17.019 | 33.803 | 14.926 |  | 24.7708 | 0.1 | 5.2
| 2.1028 | 299.675 | 297.648 | 65.331 | 17.021 | 33.816 | 14.928 |  | 24.7917 | 0.1 | 5.2
| 2.1042 | 299.26 | 297.372 | 65.332 | 17.025 | 33.817 | 14.931 |  | 24.8125 | 0.1 | 5.2
| 2.1056 | 299.111 | 297.266 | 65.324 | 17.029 | 33.823 | 14.937 |  | 24.8333 | 0.1 | 5.2
| 2.1069 | 299.085 | 297.15 | 65.327 | 17.032 | 33.819 | 14.939 |  | 24.8542 | 0 | 5.2
| 2.1083 | 299.436 | 296.355 | 65.327 | 17.037 | 33.817 | 14.941 |  | 24.875 | -0.2 | 5.2
| 2.1097 | 299.684 | 296.835 | 65.323 | 17.036 | 33.816 | 14.942 |  | 24.8958 | -0.2 | 5.2
| 2.1111 | 299.523 | 296.992 | 65.328 | 17.041 | 33.82 | 14.944 |  | 24.9167 | -0.6 | 5.2
| 2.1125 | 299.728 | 297.021 | 65.33 | 17.041 | 33.82 | 14.948 |  | 24.9375 | -1.1 | 5.2
| 2.1139 | 299.785 | 296.826 | 65.337 | 17.048 | 33.825 | 14.952 |  | 24.9583 | -1.7 | 5.2
| 2.1153 | 299.994 | 296.85 | 65.344 | 17.047 | 33.833 | 14.957 |  | 24.9792 | -2.2 | 5.2
| 2.1167 | 299.53 | 297.269 | 65.346 | 17.05 | 33.836 | 14.96 |  | 25 | -2.7 | 5.2
| 2.1181 | 299.524 | 296.815 | 65.346 | 17.05 | 33.835 | 14.96 |  | 25.0208 | -2.8 | 5.2
| 2.1194 | 299.501 | 297.442 | 65.347 | 17.055 | 33.84 | 14.967 |  | 25.0417 | -3 | 5.2
| 2.1208 | 299.175 | 297.011 | 65.35 | 17.058 | 33.845 | 14.971 |  | 25.0625 | -3.3 | 5.2
| 2.1222 | 299.61 | 296.566 | 65.35 | 17.06 | 33.846 | 14.969 |  | 25.0833 | -3.4 | 5.2
| 2.1236 | 299.328 | 297.299 | 65.35 | 17.062 | 33.843 | 14.979 |  | 25.1042 | -3.8 | 5.2
| 2.125 | 299.331 | 297.271 | 65.352 | 17.069 | 33.848 | 14.976 |  | 25.125 | -4.1 | 5.2
| 2.1264 | 299.552 | 296.874 | 65.354 | 17.067 | 33.848 | 14.98 |  | 25.1458 | -4.3 | 5.2
| 2.1278 | 298.961 | 297.079 | 65.353 | 17.072 | 33.85 | 14.981 |  | 25.1667 | -4.6 | 5.2
| 2.1292 | 299.534 | 296.949 | 65.358 | 17.074 | 33.85 | 14.987 |  | 25.1875 | -4.3 | 5.2
| 2.1306 | 299.882 | 296.888 | 65.361 | 17.074 | 33.859 | 14.989 |  | 25.2083 | -3.8 | 5.2
| 2.1319 | 299.681 | 297.114 | 65.362 | 17.078 | 33.859 | 14.994 |  | 25.2292 | -4.4 | 5.2
| 2.1333 | 299.611 | 297.394 | 65.37 | 17.087 | 33.869 | 14.996 |  | 25.25 | -0.8 | 5.2
| 2.1347 | 300.341 | 296.906 | 65.375 | 17.088 | 33.873 | 14.998 |  | 25.2708 | -1.8 | 5.2
| 2.1361 | 300.237 | 297.028 | 65.386 | 17.092 | 33.88 | 15.001 |  | 25.2917 | -1.7 | 5.2
| 2.1375 | 300.137 | 297.209 | 65.39 | 17.087 | 33.888 | 15.005 |  | 25.3125 | -1.1 | 5.2
| 2.1389 | 300.046 | 297.719 | 65.403 | 17.094 | 33.896 | 15.009 |  | 25.3333 | -0.8 | 5.2
| 2.1403 | 300.138 | 297.727 | 65.414 | 17.096 | 33.906 | 15.016 |  | 25.3542 | -0.1 | 5.2
| 2.1417 | 300.393 | 297.934 | 65.425 | 17.099 | 33.918 | 15.017 |  | 25.375 | 0.3 | 5.2
| 2.1431 | 300.717 | 297.652 | 65.436 | 17.102 | 33.921 | 15.015 |  | 25.3958 | 0.6 | 5.2
| 2.1444 | 300.228 | 297.693 | 65.445 | 17.108 | 33.928 | 15.022 |  | 25.4167 | 0.9 | 5.2
| 2.1458 | 300.644 | 297.327 | 65.45 | 17.112 | 33.93 | 15.026 |  | 25.4375 | 0.4 | 5.2
| 2.1472 | 300.168 | 298.382 | 65.456 | 17.111 | 33.943 | 15.029 |  | 25.4583 | 0.6 | 5.1
| 2.1486 | 299.839 | 297.895 | 65.464 | 17.115 | 33.948 | 15.033 |  | 25.4792 | 0.7 | 5.1
| 2.15 | 300.417 | 297.05 | 65.468 | 17.12 | 33.95 | 15.037 |  | 25.5 | 0.8 | 5.1
| 2.1514 | 299.808 | 297.922 | 65.471 | 17.121 | 33.948 | 15.041 |  | 25.5208 | 1.2 | 5.1
| 2.1528 | 300.567 | 296.979 | 65.481 | 17.126 | 33.948 | 15.044 |  | 25.5417 | 1.4 | 5.1
| 2.1542 | 300.447 | 297.144 | 65.484 | 17.127 | 33.953 | 15.046 |  | 25.5625 | 1.9 | 5.1
| 2.1556 | 299.977 | 297.571 | 65.489 | 17.133 | 33.957 | 15.047 |  | 25.5833 | 1.6 | 5.1
| 2.1569 | 299.983 | 297.941 | 65.493 | 17.132 | 33.961 | 15.052 |  | 25.6042 | 1.6 | 5.1
| 2.1583 | 300.111 | 297.47 | 65.495 | 17.136 | 33.966 | 15.055 |  | 25.625 | 1.7 | 5.1
| 2.1597 | 299.687 | 297.736 | 65.505 | 17.136 | 33.966 | 15.057 |  | 25.6458 | 1.8 | 5.1
| 2.1611 | 299.645 | 297.741 | 65.507 | 17.145 | 33.967 | 15.059 |  | 25.6667 | 1.7 | 5.1
| 2.1625 | 300.378 | 296.917 | 65.512 | 17.144 | 33.967 | 15.063 |  | 25.6875 | 1.6 | 5.1
| 2.1639 | 300.134 | 297.103 | 65.515 | 17.15 | 33.972 | 15.064 |  | 25.7083 | 1.6 | 5.1
| 2.1653 | 299.654 | 297.234 | 65.516 | 17.149 | 33.977 | 15.071 |  | 25.7292 | 1.6 | 5.1
| 2.1667 | 299.948 | 296.663 | 65.517 | 17.152 | 33.972 | 15.069 |  | 25.75 | 1.5 | 5.1
| 2.1681 | 299.484 | 297.404 | 65.518 | 17.155 | 33.973 | 15.077 |  | 25.7708 | 1.4 | 5.1
| 2.1694 | 300.085 | 296.739 | 65.515 | 17.159 | 33.978 | 15.078 |  | 25.7917 | 1.4 | 5.1
| 2.1708 | 299.435 | 297.201 | 65.517 | 17.163 | 33.973 | 15.084 |  | 25.8125 | 1.4 | 5.1
| 2.1722 | 299.551 | 297.299 | 65.517 | 17.168 | 33.978 | 15.085 |  | 25.8333 | 1.4 | 5.1
| 2.1736 | 299.707 | 297.311 | 65.518 | 17.168 | 33.977 | 15.09 |  | 25.8542 | 1.4 | 5.1
| 2.175 | 299.796 | 297.077 | 65.525 | 17.173 | 33.981 | 15.093 |  | 25.875 | 1.4 | 5.1
| 2.1764 | 300.181 | 297.03 | 65.527 | 17.173 | 33.98 | 15.096 |  | 25.8958 | 1.5 | 5.1
| 2.1778 | 300.204 | 297.537 | 65.532 | 17.179 | 33.987 | 15.096 |  | 25.9167 | 1.4 | 5.1
| 2.1792 | 299.89 | 296.415 | 65.542 | 17.184 | 33.996 | 15.102 |  | 25.9375 | 1.4 | 5.1
| 2.1806 | 299.521 | 296.509 | 65.533 | 17.189 | 33.997 | 15.104 |  | 25.9583 | 1.4 | 5.1
| 2.1819 | 299.996 | 296.644 | 65.536 | 17.188 | 33.994 | 15.11 |  | 25.9792 | 1.3 | 5.1
| 2.1833 | 299.578 | 297.134 | 65.542 | 17.189 | 33.999 | 15.113 |  | 26 | 1.2 | 5.1
| 2.1847 | 300.235 | 296.864 | 65.535 | 17.191 | 33.997 | 15.115 |  | 26.0208 | 1.1 | 5.1
| 2.1861 | 300.337 | 297.095 | 65.541 | 17.193 | 34.006 | 15.119 |  | 26.0417 | 1 | 5.1
| 2.1875 | 300.151 | 296.733 | 65.547 | 17.198 | 34.006 | 15.121 |  | 26.0625 | 0.9 | 5.1
| 2.1889 | 300.027 | 297.493 | 65.55 | 17.202 | 34.012 | 15.126 |  | 26.0833 | 0.9 | 5.1
| 2.1903 | 299.549 | 297.52 | 65.558 | 17.204 | 34.018 | 15.126 |  | 26.1042 | 0.8 | 5.1
| 2.1917 | 299.215 | 297.375 | 65.556 | 17.208 | 34.022 | 15.131 |  | 26.125 | 0.6 | 5.1
| 2.1931 | 300.328 | 297.12 | 65.565 | 17.211 | 34.024 | 15.134 |  | 26.1458 | 0.3 | 5.1
| 2.1944 | 299.532 | 297.192 | 65.567 | 17.21 | 34.026 | 15.138 |  | 26.1667 | 0.4 | 5.1
| 2.1958 | 299.556 | 297.076 | 65.564 | 17.216 | 34.027 | 15.141 |  | 26.1875 | 0.4 | 5.1
| 2.1972 | 299.911 | 297.039 | 65.567 | 17.22 | 34.026 | 15.146 |  | 26.2083 | 0.6 | 5.1
| 2.1986 | 299.37 | 296.669 | 65.567 | 17.224 | 34.026 | 15.148 |  | 26.2292 | 0.6 | 5.1
| 2.2 | 299.175 | 297.083 | 65.559 | 17.223 | 34.032 | 15.15 |  | 26.25 | 0.3 | 5.1
| 2.2014 | 299.662 | 296.974 | 65.563 | 17.225 | 34.023 | 15.153 |  | 26.2708 | 0.3 | 5.1
| 2.2028 | 299.445 | 297.271 | 65.56 | 17.229 | 34.032 | 15.159 |  | 26.2917 | --- | 5.1
| 2.2042 | 299.749 | 296.992 | 65.564 | 17.234 | 34.031 | 15.157 |  | 26.3125 | --- | 5.1
| 2.2056 | 299.051 | 297.127 | 65.564 | 17.238 | 34.037 | 15.164 |  | 26.3333 | --- | 5.1
| 2.2069 | 299.309 | 297.264 | 65.563 | 17.241 | 34.037 | 15.168 |  | 26.3542 | --- | 5.1
| 2.2083 | 299.158 | 296.789 | 65.563 | 17.243 | 34.04 | 15.171 |  | 26.375 | --- | 5.1
| 2.2097 | 299.857 | 296.522 | 65.559 | 17.243 | 34.04 | 15.175 |  | 26.3958 | --- | 5.1
| 2.2111 | 299.009 | 296.824 | 65.562 | 17.245 | 34.037 | 15.174 |  | 26.4167 | 1.2 | 5.1
| 2.2125 | 298.973 | 296.445 | 65.56 | 17.252 | 34.036 | 15.181 |  | 26.4375 | 1.3 | 5.1
| 2.2139 | 298.915 | 297.065 | 65.557 | 17.254 | 34.041 | 15.182 |  | 26.4583 | 1.4 | 5.1
| 2.2153 | 299.499 | 296.134 | 65.554 | 17.259 | 34.039 | 15.185 |  | 26.4792 | 1.7 | 5
| 2.2167 | 298.796 | 296.901 | 65.554 | 17.258 | 34.04 | 15.19 |  | 26.5 | 1.8 | 5
| 2.2181 | 299.428 | 295.946 | 65.548 | 17.263 | 34.038 | 15.192 |  | 26.5208 | 1.9 | 5
| 2.2194 | 298.638 | 296.515 | 65.545 | 17.262 | 34.04 | 15.193 |  | 26.5417 | 1.9 | 5
| 2.2208 | 298.332 | 295.536 | 65.532 | 17.265 | 34.035 | 15.196 |  | 26.5625 | 1.8 | 5
| 2.2222 | 297.819 | 295.862 | 65.518 | 17.27 | 34.025 | 15.198 |  | 26.5833 | 1.8 | 5
| 2.2236 | 297.986 | 294.716 | 65.499 | 17.277 | 34.016 | 15.204 |  | 26.6042 | 1.6 | 5
| 2.225 | 301.537 | 298.791 | 65.541 | 17.277 | 34.043 | 15.206 |  | 26.625 | 1.3 | 5
| 2.2264 | 301.214 | 298.292 | 65.574 | 17.277 | 34.07 | 15.213 |  | 26.6458 | 1.1 | 5
| 2.2278 | 301.002 | 298.921 | 65.589 | 17.279 | 34.091 | 15.213 |  | 26.6667 | 0.7 | 5
| 2.2292 | 301.536 | 298.344 | 65.615 | 17.285 | 34.111 | 15.214 |  | 26.6875 | 0.5 | 5
| 2.2306 | 301.179 | 298.585 | 65.636 | 17.289 | 34.126 | 15.217 |  | 26.7083 | 0.4 | 5
| 2.2319 | 301.562 | 298.252 | 65.654 | 17.291 | 34.136 | 15.222 |  | 26.7292 | 0.2 | 5
| 2.2333 | 300.929 | 298.427 | 65.666 | 17.292 | 34.15 | 15.228 |  | 26.75 | 0.3 | 5
| 2.2347 | 301.715 | 298.275 | 65.68 | 17.296 | 34.157 | 15.228 |  | 26.7708 | 0.4 | 5
| 2.2361 | 300.536 | 298.557 | 65.691 | 17.297 | 34.168 | 15.23 |  | 26.7917 | 0.5 | 5
| 2.2375 | 301.415 | 298.329 | 65.708 | 17.299 | 34.179 | 15.238 |  | 26.8125 | 0.7 | 5
| 2.2389 | 301.318 | 297.835 | 65.719 | 17.303 | 34.181 | 15.238 |  | 26.8333 | 0.8 | 5
| 2.2403 | 301.168 | 297.803 | 65.731 | 17.305 | 34.188 | 15.24 |  | 26.8542 | 0.9 | 5
| 2.2417 | 301.011 | 297.692 | 65.742 | 17.315 | 34.188 | 15.245 |  | 26.875 | 0.9 | 5
| 2.2431 | 300.766 | 298.248 | 65.745 | 17.316 | 34.196 | 15.244 |  | 26.8958 | 1.2 | 5
| 2.2444 | 301.373 | 297.931 | 65.752 | 17.314 | 34.2 | 15.252 |  | 26.9167 | 1.3 | 5
| 2.2458 | 300.831 | 297.68 | 65.77 | 17.321 | 34.201 | 15.253 |  | 26.9375 | 1.4 | 5
| 2.2472 | 300.469 | 298.404 | 65.777 | 17.324 | 34.201 | 15.256 |  | 26.9583 | 1.4 | 5
| 2.2486 | 300.607 | 297.813 | 65.784 | 17.328 | 34.212 | 15.256 |  | 26.9792 | 1.6 | 5
| 2.25 | 300.833 | 298.346 | 65.788 | 17.326 | 34.212 | 15.265 |  | 27 | 1.4 | 5
| 2.2514 | 300.356 | 298.303 | 65.798 | 17.332 | 34.216 | 15.265 |  | 27.0208 | 1.2 | 5
| 2.2528 | 301.347 | 298.353 | 65.809 | 17.338 | 34.223 | 15.267 |  | 27.0417 | 1.8 | 5
| 2.2542 | 300.36 | 298.379 | 65.824 | 17.34 | 34.235 | 15.271 |  | 27.0625 | 2.3 | 5
| 2.2556 | 301.149 | 297.883 | 65.832 | 17.341 | 34.242 | 15.277 |  | 27.0833 | 2.3 | 5
| 2.2569 | 300.759 | 297.448 | 65.836 | 17.345 | 34.24 | 15.28 |  | 27.1042 | 1.9 | 5
| 2.2583 | 300.342 | 298.339 | 65.846 | 17.353 | 34.243 | 15.282 |  | 27.125 | 1.7 | 5
| 2.2597 | 300.412 | 297.737 | 65.85 | 17.354 | 34.248 | 15.286 |  | 27.1458 | 1.9 | 5
| 2.2611 | 299.539 | 297.53 | 65.85 | 17.356 | 34.243 | 15.286 |  | 27.1667 | 2.3 | 5
| 2.2625 | 298.577 | 296.221 | 65.844 | 17.361 | 34.233 | 15.291 |  | 27.1875 | 1.6 | 5
| 2.2639 | 299.912 | 296.898 | 65.808 | 17.364 | 34.217 | 15.293 |  | 27.2083 | 0.9 | 5
| 2.2653 | 300.585 | 297.528 | 65.825 | 17.364 | 34.221 | 15.298 |  | 27.2292 | 0.6 | 5
| 2.2667 | 300.672 | 298.213 | 65.838 | 17.368 | 34.226 | 15.301 |  | 27.25 | 0.7 | 5
| 2.2681 | 300.884 | 298.03 | 65.851 | 17.372 | 34.236 | 15.304 |  | 27.2708 | 2.7 | 5
| 2.2694 | 301.579 | 297.841 | 65.86 | 17.374 | 34.248 | 15.309 |  | 27.2917 | 2.4 | 5
| 2.2708 | 300.752 | 298.192 | 65.878 | 17.379 | 34.26 | 15.31 |  | 27.3125 | 2.4 | 5
| 2.2722 | 301.635 | 298.564 | 65.894 | 17.379 | 34.267 | 15.313 |  | 27.3333 | 2 | 5
| 2.2736 | 301.449 | 298.672 | 65.91 | 17.384 | 34.274 | 15.318 |  | 27.3542 | 2.2 | 4.9
| 2.275 | 301.648 | 298.316 | 65.924 | 17.392 | 34.289 | 15.318 |  | 27.375 | 1 | 4.9
| 2.2764 | 301.789 | 298.864 | 65.939 | 17.391 | 34.302 | 15.325 |  | 27.3958 | 1.3 | 4.9
| 2.2778 | 301.647 | 299.048 | 65.96 | 17.396 | 34.311 | 15.327 |  | 27.4167 | 1.8 | 4.9
| 2.2792 | 301.186 | 298.656 | 65.967 | 17.394 | 34.323 | 15.333 |  | 27.4375 | 2.3 | 4.9
| 2.2806 | 301.559 | 298.751 | 65.985 | 17.403 | 34.324 | 15.333 |  | 27.4583 | 3.4 | 4.9
| 2.2819 | 301.966 | 298.516 | 65.998 | 17.408 | 34.337 | 15.333 |  | 27.4792 | 3.7 | 4.9
| 2.2833 | 301.644 | 298.437 | 66.012 | 17.41 | 34.342 | 15.337 |  | 27.5 | 4.6 | 4.9
| 2.2847 | 301.301 | 299.201 | 66.016 | 17.411 | 34.344 | 15.345 |  | 27.5208 | 4.1 | 4.9
| 2.2861 | 301.963 | 298.521 | 66.029 | 17.415 | 34.352 | 15.349 |  | 27.5417 | 3.9 | 4.9
| 2.2875 | 300.986 | 298.633 | 66.041 | 17.422 | 34.363 | 15.352 |  | 27.5625 | 4.2 | 4.9
| 2.2889 | 301.213 | 298.64 | 66.055 | 17.42 | 34.364 | 15.354 |  | 27.5833 | 4.3 | 4.9
| 2.2903 | 301.748 | 298.582 | 66.068 | 17.425 | 34.37 | 15.355 |  | 27.6042 | 4.1 | 4.9
| 2.2917 | 301.568 | 299.303 | 66.084 | 17.431 | 34.373 | 15.358 |  | 27.625 | 4.1 | 4.9
| 2.2931 | 301.901 | 299.099 | 66.094 | 17.434 | 34.387 | 15.363 |  | 27.6458 | 3.9 | 4.9
| 2.2944 | 302.387 | 298.868 | 66.109 | 17.436 | 34.397 | 15.367 |  | 27.6667 | 3.9 | 4.9
| 2.2958 | 302.423 | 298.934 | 66.128 | 17.437 | 34.407 | 15.373 |  | 27.6875 | 3.7 | 4.9
| 2.2972 | 301.791 | 299.479 | 66.144 | 17.439 | 34.412 | 15.371 |  | 27.7083 | 3.6 | 4.9
| 2.2986 | 302.023 | 298.579 | 66.154 | 17.446 | 34.417 | 15.375 |  | 27.7292 | 3.2 | 4.9
| 2.3 | 301.181 | 298.784 | 66.153 | 17.452 | 34.417 | 15.38 |  | 27.75 | 3.1 | 4.9
| 2.3014 | 300.914 | 298.789 | 66.164 | 17.454 | 34.422 | 15.383 |  | 27.7708 | 3.2 | 4.9
| 2.3028 | 301.469 | 298.779 | 66.168 | 17.458 | 34.421 | 15.386 |  | 27.7917 | 3.1 | 4.9
| 2.3042 | 301.004 | 298.775 | 66.175 | 17.462 | 34.421 | 15.387 |  | 27.8125 | 3.4 | 4.9
| 2.3056 | 300.359 | 298.206 | 66.171 | 17.465 | 34.421 | 15.391 |  | 27.8333 | 3.2 | 4.9
| 2.3069 | 301.143 | 297.586 | 66.176 | 17.466 | 34.417 | 15.394 |  | 27.8542 | 2.8 | 4.9
| 2.3083 | 300.335 | 298.098 | 66.169 | 17.469 | 34.417 | 15.397 |  | 27.875 | 2.4 | 4.9
| 2.3097 | 300.639 | 297.991 | 66.173 | 17.476 | 34.411 | 15.401 |  | 27.8958 | 2.3 | 4.9
| 2.3111 | 300.543 | 298.046 | 66.169 | 17.48 | 34.414 | 15.406 |  | 27.9167 | 2.4 | 4.9
| 2.3125 | 300.424 | 297.884 | 66.17 | 17.48 | 34.41 | 15.408 |  | 27.9375 | 2.4 | 4.9
| 2.3139 | 300.51 | 297.484 | 66.167 | 17.488 | 34.41 | 15.418 |  | 27.9583 | 2.4 | 4.9
| 2.3153 | 300.633 | 297.472 | 66.168 | 17.485 | 34.403 | 15.413 |  | 27.9792 | 2.4 | 4.9
| 2.3167 | 299.597 | 297.426 | 66.165 | 17.492 | 34.404 | 15.422 |  | 28 | 2.3 | 4.9
| 2.3181 | 299.926 | 297.408 | 66.152 | 17.493 | 34.398 | 15.422 |  | 28.0208 | 2.3 | 4.9
| 2.3194 | 300.011 | 297.683 | 66.147 | 17.499 | 34.389 | 15.425 |  | 28.0417 | 2.4 | 4.9
| 2.3208 | 300.417 | 296.968 | 66.146 | 17.501 | 34.388 | 15.43 |  | 28.0625 | 2.5 | 4.9
| 2.3222 | 299.454 | 297.47 | 66.146 | 17.501 | 34.396 | 15.429 |  | 28.0833 | 2.5 | 4.9
| 2.3236 | 299.859 | 297.029 | 66.139 | 17.503 | 34.386 | 15.436 |  | 28.1042 | 2.4 | 4.9
| 2.325 | 300.154 | 296.743 | 66.13 | 17.511 | 34.381 | 15.439 |  | 28.125 | 2.4 | 4.9
| 2.3264 | 300.337 | 297.14 | 66.129 | 17.512 | 34.385 | 15.439 |  | 28.1458 | 2.4 | 4.9
| 2.3278 | 299.604 | 297.555 | 66.119 | 17.518 | 34.387 | 15.443 |  | 28.1667 | 2.3 | 4.9
| 2.3292 | 299.788 | 297.826 | 66.12 | 17.518 | 34.384 | 15.449 |  | 28.1875 | 2.3 | 4.9
| 2.3306 | 300.28 | 297.204 | 66.116 | 17.519 | 34.385 | 15.454 |  | 28.2083 | 2.2 | 4.9
| 2.3319 | 299.809 | 296.766 | 66.109 | 17.523 | 34.377 | 15.451 |  | 28.2292 | 2.1 | 4.9
| 2.3333 | 299.803 | 296.73 | 66.105 | 17.526 | 34.386 | 15.452 |  | 28.25 | 2 | 4.9
| 2.3347 | 299.715 | 296.701 | 66.096 | 17.533 | 34.381 | 15.46 |  | 28.2708 | 3.1 | 4.9
| 2.3361 | 299.243 | 296.612 | 66.086 | 17.53 | 34.38 | 15.465 |  | 28.2917 | 2.9 | 4.8
| 2.3375 | 299.366 | 295.902 | 66.077 | 17.537 | 34.365 | 15.467 |  | 28.3125 | 3.1 | 4.8
| 2.3389 | 299.117 | 296.56 | 66.069 | 17.54 | 34.367 | 15.468 |  | 28.3333 | 3.2 | 4.8
| 2.3403 | 298.834 | 296.727 | 66.062 | 17.544 | 34.367 | 15.476 |  | 28.3542 | 3.3 | 4.8
| 2.3417 | 299.358 | 295.743 | 66.053 | 17.541 | 34.366 | 15.475 |  | 28.375 | 3.3 | 4.8
| 2.3431 | 298.769 | 296.43 | 66.046 | 17.547 | 34.364 | 15.481 |  | 28.3958 | 3.5 | 4.8
| 2.3444 | 299.246 | 296.156 | 66.036 | 17.546 | 34.368 | 15.481 |  | 28.4167 | 2.9 | 4.8
| 2.3458 | 299.236 | 295.809 | 66.027 | 17.549 | 34.361 | 15.482 |  | 28.4375 | 3.1 | 4.8
| 2.3472 | 298.168 | 295.595 | 66.018 | 17.553 | 34.366 | 15.488 |  | 28.4583 | 3.1 | 4.8
| 2.3486 | 301.895 | 299.827 | 66.014 | 17.557 | 34.359 | 15.491 |  | 28.4792 | 3.2 | 4.8
| 2.35 | 301.801 | 299.799 | 66.071 | 17.555 | 34.403 | 15.496 |  | 28.5 | 3.2 | 4.8
| 2.3514 | 302.205 | 299.166 | 66.101 | 17.558 | 34.433 | 15.496 |  | 28.5208 | 3.7 | 4.8
| 2.3528 | 303.665 | 300.742 | 66.14 | 17.566 | 34.468 | 15.499 |  | 28.5417 | 3.7 | 4.8
| 2.3542 | 303.596 | 300.881 | 66.192 | 17.567 | 34.506 | 15.503 |  | 28.5625 | 3.9 | 4.8
| 2.3556 | 305.956 | 302.313 | 66.255 | 17.568 | 34.555 | 15.506 |  | 28.5833 | 4 | 4.8
| 2.3569 | 305.209 | 303.207 | 66.318 | 17.571 | 34.599 | 15.507 |  | 28.6042 | 4.2 | 4.8
| 2.3583 | 305.339 | 302.849 | 66.368 | 17.576 | 34.637 | 15.506 |  | 28.625 | 4.1 | 4.8
| 2.3597 | 305.719 | 302.541 | 66.419 | 17.578 | 34.681 | 15.516 |  | 28.6458 | 4 | 4.8
| 2.3611 | 306.157 | 302.519 | 66.466 | 17.582 | 34.707 | 15.516 |  | 28.6667 | 4.1 | 4.8
| 2.3625 | 305.435 | 303.266 | 66.514 | 17.583 | 34.735 | 15.52 |  | 28.6875 | 4.2 | 4.8
| 2.3639 | 306.123 | 303.56 | 66.563 | 17.593 | 34.757 | 15.522 |  | 28.7083 | 4.4 | 4.8
| 2.3653 | 301.747 | 299.511 | 66.607 | 17.597 | 34.789 | 15.526 |  | 28.7292 | 4.3 | 4.8
| 2.3667 | 302.567 | 298.834 | 66.576 | 17.596 | 34.759 | 15.53 |  | 28.75 | 4.3 | 4.8
| 2.3681 | 302.33 | 298.567 | 66.564 | 17.604 | 34.732 | 15.534 |  | 28.7708 | 4.5 | 4.8
| 2.3694 | 301.184 | 298.936 | 66.554 | 17.607 | 34.71 | 15.536 |  | 28.7917 | 4.7 | 4.8
| 2.3708 | 300.859 | 298.659 | 66.557 | 17.615 | 34.699 | 15.538 |  | 28.8125 | 4.6 | 4.8
| 2.3722 | 301.05 | 298.816 | 66.552 | 17.619 | 34.68 | 15.538 |  | 28.8333 | 4.3 | 4.8
| 2.3736 | 301.703 | 298.505 | 66.553 | 17.618 | 34.676 | 15.544 |  | 28.8542 | 3.9 | 4.8
| 2.375 | 301.739 | 298.39 | 66.552 | 17.623 | 34.665 | 15.548 |  | 28.875 | 3.7 | 4.8
| 2.3764 | 301.09 | 297.387 | 66.551 | 17.626 | 34.659 | 15.551 |  | 28.8958 | 3.7 | 4.8
| 2.3778 | 300.84 | 298.548 | 66.542 | 17.631 | 34.649 | 15.555 |  | 28.9167 | 4 | 4.8
| 2.3792 | 300.845 | 298.516 | 66.54 | 17.633 | 34.647 | 15.56 |  | 28.9375 | 3.6 | 4.8
| 2.3806 | 301.125 | 297.666 | 66.541 | 17.637 | 34.643 | 15.56 |  | 28.9583 | 2.5 | 4.8
| 2.3819 | 301.239 | 297.556 | 66.531 | 17.641 | 34.636 | 15.565 |  | 28.9792 | 1.9 | 4.8
| 2.3833 | 300.692 | 297.935 | 66.528 | 17.644 | 34.634 | 15.566 |  | 29 | 2.1 | 4.8
| 2.3847 | 300.102 | 297.843 | 66.519 | 17.649 | 34.626 | 15.567 |  | 29.0208 | 1.7 | 4.8
| 2.3861 | 300.141 | 297.922 | 66.516 | 17.652 | 34.614 | 15.575 |  | 29.0417 | 1 | 4.8
| 2.3875 | 299.824 | 297.706 | 66.514 | 17.657 | 34.616 | 15.578 |  | 29.0625 | 0.3 | 4.8
| 2.3889 | 299.933 | 297.229 | 66.494 | 17.655 | 34.607 | 15.581 |  | 29.0833 | 1 | 4.8
| 2.3903 | 299.523 | 297.337 | 66.485 | 17.658 | 34.601 | 15.582 |  | 29.1042 | 1.4 | 4.8
| 2.3917 | 299.782 | 297.74 | 66.477 | 17.665 | 34.599 | 15.588 |  | 29.125 | 1.9 | 4.8
| 2.3931 | 299.553 | 297.33 | 66.466 | 17.664 | 34.593 | 15.591 |  | 29.1458 | 1.8 | 4.8
| 2.3944 | 299.232 | 297.118 | 66.454 | 17.671 | 34.591 | 15.595 |  | 29.1667 | 1.4 | 4.8
| 2.4167 | 302.673 | 299.848 | 66.581 | 17.715 | 34.744 | 15.64 |  | 29.1875 | 0.9 | 4.8
| 2.4181 | 302.496 | 299.532 | 66.595 | 17.715 | 34.754 | 15.642 |  | 29.2083 | 0.7 | 4.8
| 2.4194 | 302.2 | 300.053 | 66.608 | 17.723 | 34.764 | 15.647 |  | 29.2292 | 0.4 | 4.8
| 2.4208 | 302.978 | 299.241 | 66.618 | 17.723 | 34.768 | 15.651 |  | 29.25 | 0 | 4.8
| 2.4222 | 302.148 | 299.305 | 66.627 | 17.73 | 34.77 | 15.653 |  | 29.2708 | --- | 4.8
| 2.4236 | 301.79 | 299.824 | 66.634 | 17.734 | 34.767 | 15.656 |  | 29.2917 | --- | 4.8
| 2.425 | 301.958 | 299.894 | 66.642 | 17.733 | 34.77 | 15.658 |  | 29.3125 | --- | 4.8
| 2.4264 | 301.7 | 299.411 | 66.649 | 17.739 | 34.779 | 15.663 |  | 29.3333 | --- | 4.8
| 2.4278 | 302.393 | 298.754 | 66.653 | 17.742 | 34.776 | 15.666 |  | 29.3542 | --- | 4.8
| 2.4292 | 301.236 | 298.439 | 66.657 | 17.743 | 34.779 | 15.665 |  | 29.375 | 1.2 | 4.8
| 2.4306 | 301.776 | 298.303 | 66.66 | 17.746 | 34.778 | 15.668 |  | 29.3958 | 1.6 | 4.8
| 2.4319 | 302.11 | 298.941 | 66.669 | 17.751 | 34.779 | 15.673 |  | 29.4167 | 1.9 | 4.8
| 2.4333 | 301.399 | 298.976 | 66.671 | 17.753 | 34.783 | 15.676 |  | 29.4375 | 1.9 | 4.8
| 2.4347 | 301.274 | 298.224 | 66.667 | 17.757 | 34.779 | 15.676 |  | 29.4583 | 1.8 | 4.8
| 2.4361 | 301.203 | 298.115 | 66.668 | 17.759 | 34.78 | 15.679 |  | 29.4792 | 1.9 | 4.8
| 2.4375 | 301.665 | 298.015 | 66.671 | 17.762 | 34.775 | 15.686 |  | 29.5 | 2.6 | 4.8
| 2.4389 | 301.321 | 297.866 | 66.67 | 17.768 | 34.778 | 15.69 |  | 29.5208 | 3.3 | 4.8
| 2.4403 | 301.321 | 298.293 | 66.667 | 17.77 | 34.777 | 15.693 |  | 29.5417 | 3.7 | 4.8
| 2.4417 | 301.31 | 298.249 | 66.67 | 17.774 | 34.772 | 15.691 |  | 29.5625 | 3.9 | 4.8
| 2.4431 | 301.139 | 297.904 | 66.666 | 17.778 | 34.774 | 15.698 |  | 29.5833 | 3.1 | 4.8
| 2.4444 | 300.541 | 298.503 | 66.666 | 17.782 | 34.772 | 15.7 |  | 29.6042 | 2.9 | 4.8
| 2.4458 | 300.851 | 297.626 | 66.663 | 17.782 | 34.77 | 15.703 |  | 29.625 | 3 | 4.8
| 2.4472 | 300.827 | 297.098 | 66.653 | 17.787 | 34.764 | 15.705 |  | 29.6458 | 3.2 | 4.8
| 2.4486 | 300.743 | 297.653 | 66.649 | 17.79 | 34.763 | 15.71 |  | 29.6667 | 3.4 | 4.8
| 2.45 | 300.406 | 298.279 | 66.646 | 17.791 | 34.762 | 15.709 |  | 29.6875 | 3.5 | 4.8
| 2.4514 | 300.214 | 297.696 | 66.639 | 17.796 | 34.759 | 15.715 |  | 29.7083 | 3.4 | 4.8
| 2.4528 | 300.944 | 297.648 | 66.641 | 17.798 | 34.761 | 15.715 |  | 29.7292 | 3.3 | 4.8
| 2.4542 | 300.869 | 297.348 | 66.638 | 17.803 | 34.762 | 15.72 |  | 29.75 | 3.4 | 4.8
| 2.4556 | 300.58 | 298.029 | 66.63 | 17.806 | 34.761 | 15.723 |  | 29.7708 | 3.6 | 4.8
| 2.4569 | 300.865 | 297.364 | 66.628 | 17.803 | 34.759 | 15.723 |  | 29.7917 | 3.6 | 4.8
| 2.4583 | 300.72 | 297.295 | 66.625 | 17.812 | 34.761 | 15.726 |  | 29.8125 | 3.4 | 4.8
| 2.4597 | 300.69 | 297.553 | 66.622 | 17.813 | 34.759 | 15.732 |  | 29.8333 | 3.3 | 4.8
| 2.4611 | 299.887 | 297.658 | 66.619 | 17.816 | 34.764 | 15.734 |  | 29.8542 | 3.2 | 4.8
| 2.4625 | 300.248 | 298.068 | 66.614 | 17.819 | 34.761 | 15.74 |  | 29.875 | 3.2 | 4.8
| 2.4639 | 300.626 | 297.311 | 66.611 | 17.823 | 34.759 | 15.741 |  | 29.8958 | 3.3 | 4.8
| 2.4653 | 300.628 | 297.123 | 66.607 | 17.826 | 34.764 | 15.743 |  | 29.9167 | 3.2 | 4.8
| 2.4667 | 300.427 | 297.675 | 66.606 | 17.823 | 34.762 | 15.746 |  | 29.9375 | 3.2 | 4.8
| 2.4681 | 299.626 | 297.6 | 66.596 | 17.83 | 34.762 | 15.752 |  | 29.9583 | 3.1 | 4.8
| 2.4694 | 299.542 | 297.129 | 66.588 | 17.833 | 34.761 | 15.752 |  | 29.9792 | 2.9 | 4.8
| 2.4708 | 300.043 | 296.359 | 66.577 | 17.836 | 34.756 | 15.751 |  | 30 | 3 | 4.8
| 2.4722 | 300.313 | 297.654 | 66.567 | 17.839 | 34.752 | 15.753 |  | 30.0208 | 3 | 4.8
| 2.4736 | 300.095 | 296.863 | 66.569 | 17.841 | 34.751 | 15.757 |  | 30.0417 | 3.1 | 4.8
| 2.475 | 300.32 | 297.542 | 66.566 | 17.843 | 34.752 | 15.765 |  | 30.0625 | 3.1 | 4.8
| 2.4764 | 299.799 | 297.737 | 66.556 | 17.846 | 34.758 | 15.77 |  | 30.0833 | 2.8 | 4.8
| 2.4778 | 299.242 | 297.068 | 66.553 | 17.842 | 34.757 | 15.769 |  | 30.1042 | 2.7 | 4.8
| 2.4792 | 300.614 | 297.281 | 66.554 | 17.848 | 34.762 | 15.773 |  | 30.125 | 2.5 | 4.8
| 2.4806 | 300.734 | 297.72 | 66.557 | 17.853 | 34.766 | 15.771 |  | 30.1458 | 2.6 | 4.8
| 2.4819 | 300.974 | 297.645 | 66.56 | 17.856 | 34.77 | 15.776 |  | 30.1667 | 2.5 | 4.8
| 2.4833 | 300.319 | 297.647 | 66.56 | 17.857 | 34.779 | 15.779 |  | 30.1875 | 2.5 | 4.8
| 2.4847 | 300.916 | 297.487 | 66.558 | 17.863 | 34.779 | 15.779 |  | 30.2083 | 2.2 | 4.8
| 2.4861 | 301.009 | 297.596 | 66.552 | 17.862 | 34.778 | 15.784 |  | 30.2292 | 1.7 | 4.8
| 2.4875 | 300.803 | 297.211 | 66.561 | 17.863 | 34.787 | 15.789 |  | 30.25 | 1.7 | 4.8
| 2.4889 | 300.757 | 297.81 | 66.557 | 17.868 | 34.79 | 15.791 |  | 30.2708 | 2.6 | 4.8
| 2.4903 | 300.209 | 298.233 | 66.56 | 17.872 | 34.794 | 15.795 |  | 30.2917 | 2.3 | 4.8
| 2.4917 | 301.188 | 297.561 | 66.56 | 17.871 | 34.801 | 15.795 |  | 30.3125 | 2.4 | 4.8
| 2.4931 | 300.636 | 298.183 | 66.564 | 17.873 | 34.804 | 15.8 |  | 30.3333 | 2.2 | 4.8
| 2.4944 | 301.314 | 297.634 | 66.569 | 17.876 | 34.807 | 15.801 |  | 30.3542 | 2.4 | 4.8
| 2.4958 | 299.838 | 297.942 | 66.568 | 17.878 | 34.813 | 15.804 |  | 30.375 | 2.2 | 4.8
| 2.4972 | 300.279 | 297.768 | 66.567 | 17.883 | 34.813 | 15.805 |  | 30.3958 | 2.4 | 4.8
| 2.4986 | 300.734 | 297.598 | 66.564 | 17.884 | 34.812 | 15.813 |  | 30.4167 | 2.7 | 4.8
| 2.5 | 300.661 | 297.14 | 66.565 | 17.887 | 34.814 | 15.81 |  | 30.4375 | 2.8 | 4.8
| 2.5014 | 300.1 | 297.335 | 66.558 | 17.89 | 34.814 | 15.815 |  | 30.4583 | 2.9 | 4.8
| 2.5028 | 300.415 | 297.518 | 66.556 | 17.89 | 34.816 | 15.817 |  | 30.4792 | 3 | 4.8
| 2.5042 | 299.893 | 297.709 | 66.559 | 17.896 | 34.816 | 15.814 |  | 30.5 | 2.9 | 4.8
| 2.5056 | 300.989 | 297.476 | 66.557 | 17.896 | 34.818 | 15.818 |  | 30.5208 | 2.8 | 4.8
| 2.5069 | 299.986 | 297.05 | 66.558 | 17.9 | 34.823 | 15.82 |  | 30.5417 | 2.7 | 4.8
| 2.5083 | 300.275 | 297.856 | 66.558 | 17.903 | 34.821 | 15.826 |  | 30.5625 | 2.6 | 4.8
| 2.5097 | 300.257 | 297.553 | 66.553 | 17.906 | 34.825 | 15.831 |  | 30.5833 | 2.7 | 4.8
| 2.5111 | 300.488 | 297.097 | 66.55 | 17.907 | 34.823 | 15.829 |  | 30.6042 | 2.8 | 4.8
| 2.5125 | 299.352 | 297.298 | 66.543 | 17.912 | 34.821 | 15.831 |  | 30.625 | 2.5 | 4.8
| 2.5139 | 299.975 | 297.258 | 66.535 | 17.914 | 34.825 | 15.835 |  | 30.6458 | 1.4 | 4.8
| 2.5153 | 300.094 | 297.069 | 66.539 | 17.915 | 34.827 | 15.839 |  | 30.6667 | 1.8 | 4.8
| 2.5167 | 300.171 | 297.848 | 66.539 | 17.916 | 34.823 | 15.838 |  | 30.6875 | 1.4 | 4.8
| 2.5181 | 300.587 | 297.023 | 66.534 | 17.92 | 34.826 | 15.845 |  | 30.7083 | 1.3 | 4.8
| 2.5194 | 300.453 | 297.539 | 66.542 | 17.924 | 34.831 | 15.844 |  | 30.7292 | 0.8 | 4.7
| 2.5208 | 300.026 | 297.999 | 66.54 | 17.925 | 34.836 | 15.849 |  | 30.75 | 0.8 | 4.7
| 2.5222 | 300.829 | 297.205 | 66.54 | 17.926 | 34.841 | 15.848 |  | 30.7708 | 0.4 | 4.7
| 2.5236 | 300.409 | 297.02 | 66.54 | 17.931 | 34.841 | 15.851 |  | 30.7917 | -0.2 | 4.7
| 2.525 | 299.917 | 297.341 | 66.531 | 17.931 | 34.836 | 15.856 |  | 30.8125 | -0.4 | 4.7
| 2.5264 | 299.859 | 296.986 | 66.532 | 17.938 | 34.836 | 15.853 |  | 30.8333 | 0 | 4.7
| 2.5278 | 299.889 | 297.326 | 66.526 | 17.938 | 34.836 | 15.861 |  | 30.8542 | 0.3 | 4.7
| 2.5292 | 300.089 | 296.82 | 66.526 | 17.941 | 34.838 | 15.863 |  | 30.875 | 0.2 | 4.7
| 2.5306 | 300.399 | 296.848 | 66.519 | 17.943 | 34.834 | 15.87 |  | 30.8958 | -0.1 | 4.7
| 2.5319 | 299.527 | 297.144 | 66.515 | 17.944 | 34.836 | 15.866 |  | 30.9167 | 0.2 | 4.7
| 2.5333 | 300.204 | 297.055 | 66.511 | 17.946 | 34.833 | 15.872 |  | 30.9375 | 0.2 | 4.7
| 2.5347 | 299.9 | 297.266 | 66.514 | 17.951 | 34.836 | 15.87 |  | 30.9583 | 0.2 | 4.7
| 2.5361 | 300.218 | 297.311 | 66.509 | 17.955 | 34.844 | 15.876 |  | 30.9792 | 0.1 | 4.7
| 2.5375 | 299.745 | 297.719 | 66.508 | 17.952 | 34.842 | 15.877 |  | 31 | -0.1 | 4.7
| 2.5389 | 299.692 | 297.564 | 66.509 | 17.955 | 34.844 | 15.88 |  | 31.0208 | -0.1 | 4.7
| 2.5403 | 299.458 | 297.369 | 66.507 | 17.957 | 34.842 | 15.881 |  | 31.0417 | 0 | 4.7
| 2.5417 | 300.351 | 297.014 | 66.505 | 17.961 | 34.846 | 15.883 |  | 31.0625 | 0.3 | 4.7
| 2.5431 | 299.903 | 297.915 | 66.504 | 17.966 | 34.849 | 15.888 |  | 31.0833 | 0.3 | 4.7
| 2.5444 | 300.096 | 297.766 | 66.515 | 17.966 | 34.856 | 15.887 |  | 31.1042 | 0.4 | 4.7
| 2.5458 | 300.506 | 298.082 | 66.514 | 17.968 | 34.858 | 15.894 |  | 31.125 | 0.3 | 4.7
| 2.5472 | 299.995 | 297.902 | 66.523 | 17.973 | 34.869 | 15.893 |  | 31.1458 | 0.1 | 4.7
| 2.5486 | 300.362 | 297.591 | 66.522 | 17.971 | 34.866 | 15.894 |  | 31.1667 | 0.3 | 4.7
| 2.55 | 300.052 | 298.124 | 66.525 | 17.975 | 34.875 | 15.9 |  | 31.1875 | 0.4 | 4.7
| 2.5514 | 300.212 | 298.286 | 66.536 | 17.977 | 34.882 | 15.898 |  | 31.2083 | 0.3 | 4.7
| 2.5528 | 299.634 | 297.619 | 66.529 | 17.979 | 34.882 | 15.9 |  | 31.2292 | 0.1 | 4.7
| 2.5542 | 299.852 | 297.209 | 66.534 | 17.98 | 34.888 | 15.907 |  | 31.25 | 0.1 | 4.7
| 2.5556 | 300.36 | 297.421 | 66.537 | 17.986 | 34.885 | 15.906 |  | 31.2708 | 0.2 | 4.7
| 2.5569 | 299.386 | 297.51 | 66.531 | 17.986 | 34.884 | 15.91 |  | 31.2917 | 1.5 | 4.7
| 2.5583 | 299.969 | 297.983 | 66.536 | 17.99 | 34.889 | 15.913 |  | 31.3125 | 1.6 | 4.7
| 2.5597 | 300.071 | 297.732 | 66.539 | 17.99 | 34.891 | 15.916 |  | 31.3333 | 1.7 | 4.7
| 2.5611 | 300.609 | 297.595 | 66.54 | 17.996 | 34.894 | 15.917 |  | 31.3542 | --- | 4.7
| 2.5625 | 300.525 | 297.559 | 66.542 | 17.997 | 34.898 | 15.917 |  | 31.375 | 2.2 | 4.7
| 2.5639 | 300.037 | 298.034 | 66.542 | 18 | 34.899 | 15.918 |  | 31.3958 | 2.3 | 4.7
| 2.5653 | 300.548 | 297.931 | 66.545 | 18.003 | 34.904 | 15.924 |  | 31.4167 | 2 | 4.7
| 2.5667 | 300.932 | 297.737 | 66.555 | 18.003 | 34.909 | 15.922 |  | 31.4375 | 2.1 | 4.7
| 2.5681 | 300.665 | 297.397 | 66.557 | 18.006 | 34.918 | 15.926 |  | 31.4583 | 2.5 | 4.7
| 2.5694 | 300.672 | 297.38 | 66.564 | 18.009 | 34.919 | 15.929 |  | 31.4792 | 2.9 | 4.7
| 2.5708 | 300.269 | 297.562 | 66.567 | 18.013 | 34.92 | 15.932 |  | 31.5 | 3.2 | 4.7
| 2.5722 | 300.775 | 297.959 | 66.569 | 18.015 | 34.93 | 15.933 |  | 31.5208 | 3.7 | 4.7
| 2.5736 | 300.928 | 297.987 | 66.575 | 18.013 | 34.931 | 15.937 |  | 31.5417 | 4.1 | 4.7
| 2.575 | 301.41 | 298.007 | 66.582 | 18.017 | 34.939 | 15.937 |  | 31.5625 | 4.2 | 4.7
| 2.5764 | 301.161 | 298.667 | 66.6 | 18.02 | 34.948 | 15.938 |  | 31.5833 | 3.9 | 4.7
| 2.5778 | 301.463 | 298.564 | 66.612 | 18.022 | 34.957 | 15.946 |  | 31.6042 | 3.8 | 4.6
| 2.5792 | 301.321 | 298.811 | 66.622 | 18.028 | 34.963 | 15.945 |  | 31.625 | 3.8 | 4.6
| 2.5806 | 301.194 | 299.014 | 66.634 | 18.034 | 34.975 | 15.947 |  | 31.6458 | 3.5 | 4.6
| 2.5819 | 300.83 | 298.88 | 66.643 | 18.029 | 34.983 | 15.949 |  | 31.6667 | 3.5 | 4.6
| 2.5833 | 301.116 | 299.108 | 66.652 | 18.032 | 34.985 | 15.955 |  | 31.6875 | 3.4 | 4.6
| 2.5847 | 301.346 | 297.99 | 66.666 | 18.036 | 34.994 | 15.958 |  | 31.7083 | 3.3 | 4.6
| 2.5861 | 301.685 | 298.626 | 66.671 | 18.04 | 35 | 15.961 |  | 31.7292 | 3.2 | 4.6
| 2.5875 | 301.221 | 298.572 | 66.681 | 18.044 | 35.009 | 15.959 |  | 31.75 | 0.9 | 4.6
| 2.5889 | 300.961 | 299.114 | 66.69 | 18.045 | 35.01 | 15.962 |  | 31.7708 | 0.3 | 4.6
| 2.5903 | 301.712 | 298.389 | 66.701 | 18.05 | 35.022 | 15.964 |  | 31.7917 | 0.2 | 4.6
| 2.5917 | 302.164 | 298.872 | 66.708 | 18.051 | 35.027 | 15.968 |  | 31.8125 | 0.3 | 4.6
| 2.5931 | 301.56 | 299.621 | 66.723 | 18.053 | 35.031 | 15.967 |  | 31.8333 | 0.4 | 4.6
| 2.5944 | 302.251 | 299.264 | 66.741 | 18.056 | 35.04 | 15.97 |  | 31.8542 | 0.4 | 4.6
| 2.5958 | 301.799 | 298.542 | 66.752 | 18.059 | 35.048 | 15.977 |  | 31.875 | 0.4 | 4.6
| 2.5972 | 302.47 | 299.256 | 66.761 | 18.062 | 35.055 | 15.98 |  | 31.8958 | 0.7 | 4.6
| 2.5986 | 302.406 | 299.232 | 66.78 | 18.064 | 35.064 | 15.977 |  | 31.9167 | 0.7 | 4.6
| 2.6 | 302.252 | 299.06 | 66.794 | 18.068 | 35.074 | 15.981 |  | 31.9375 | 0.5 | 4.6
| 2.6014 | 301.731 | 299.954 | 66.81 | 18.072 | 35.085 | 15.982 |  | 31.9583 | 0.4 | 4.6
| 2.6028 | 302.083 | 298.71 | 66.823 | 18.074 | 35.09 | 15.99 |  | 31.9792 | 0.3 | 4.6
| 2.6042 | 302.151 | 299.032 | 66.83 | 18.073 | 35.093 | 15.989 |  | 32 | 0.3 | 4.6
| 2.6056 | 302.252 | 298.988 | 66.843 | 18.08 | 35.1 | 15.99 |  | 32.0208 | 0.4 | 4.6
| 2.6069 | 301.89 | 298.733 | 66.853 | 18.082 | 35.104 | 15.989 |  | 32.0417 | 0.2 | 4.6
| 2.6083 | 302.546 | 299.072 | 66.865 | 18.084 | 35.109 | 15.993 |  | 32.0625 | 0.1 | 4.6
| 2.6097 | 301.592 | 299.643 | 66.875 | 18.088 | 35.112 | 15.998 |  | 32.0833 | 0.2 | 4.6
| 2.6111 | 302.392 | 299.035 | 66.89 | 18.09 | 35.12 | 16.001 |  | 32.1042 | 0.3 | 4.6
| 2.6125 | 302.157 | 299.001 | 66.894 | 18.094 | 35.123 | 16.003 |  | 32.125 | 0.3 | 4.6
| 2.6139 | 302.335 | 299.112 | 66.909 | 18.095 | 35.122 | 16.005 |  | 32.1458 | 0.4 | 4.6
| 2.6153 | 302.208 | 299.935 | 66.921 | 18.097 | 35.14 | 16.006 |  | 32.1667 | 0.5 | 4.6
| 2.6167 | 302.281 | 299.052 | 66.933 | 18.104 | 35.139 | 16.013 |  | 32.1875 | 0.3 | 4.6
| 2.6181 | 302.64 | 299.847 | 66.951 | 18.105 | 35.154 | 16.013 |  | 32.2083 | 0.3 | 4.6
| 2.6194 | 302.631 | 300.689 | 66.97 | 18.112 | 35.164 | 16.018 |  | 32.2292 | 0.3 | 4.6
| 2.6208 | 302.54 | 300.592 | 66.988 | 18.111 | 35.173 | 16.018 |  | 32.25 | 0.2 | 4.6
| 2.6222 | 302.377 | 300.12 | 67.001 | 18.114 | 35.185 | 16.02 |  | 32.2708 | 0.2 | 4.6
| 2.6236 | 302.827 | 299.534 | 67.014 | 18.117 | 35.185 | 16.023 |  | 32.2917 | --- | 4.6
| 2.625 | 302.554 | 299.166 | 67.023 | 18.122 | 35.192 | 16.029 |  | 32.3125 | --- | 4.6
| 2.6264 | 302.902 | 299.532 | 67.035 | 18.124 | 35.198 | 16.028 |  | 32.3333 | --- | 4.6
| 2.6278 | 302.427 | 299.842 | 67.047 | 18.125 | 35.202 | 16.032 |  | 32.3542 | --- | 4.6
| 2.6292 | 301.865 | 299.325 | 67.053 | 18.13 | 35.203 | 16.033 |  | 32.375 | --- | 4.6
| 2.6306 | 302.23 | 298.918 | 67.064 | 18.136 | 35.204 | 16.033 |  | 32.3958 | 0.3 | 4.6
| 2.6319 | 302.679 | 299.532 | 67.07 | 18.132 | 35.196 | 16.039 |  | 32.4167 | 0.3 | 4.6
| 2.6333 | 302.569 | 299.238 | 67.08 | 18.14 | 35.206 | 16.038 |  | 32.4375 | 0.6 | 4.6
| 2.6347 | 302.113 | 299.991 | 67.087 | 18.139 | 35.211 | 16.037 |  | 32.4583 | 0.9 | 4.6
| 2.6361 | 301.966 | 299.373 | 67.104 | 18.147 | 35.214 | 16.042 |  | 32.4792 | 1.2 | 4.6
| 2.6375 | 303.204 | 299.738 | 67.114 | 18.149 | 35.223 | 16.048 |  | 32.5 | 1.3 | 4.6
| 2.6389 | 303.316 | 299.896 | 67.133 | 18.151 | 35.234 | 16.046 |  | 32.5208 | 2 | 4.6
| 2.6403 | 303.129 | 299.89 | 67.149 | 18.154 | 35.241 | 16.053 |  | 32.5417 | 2.2 | 4.6
| 2.6417 | 302.783 | 299.837 | 67.165 | 18.159 | 35.251 | 16.054 |  | 32.5625 | 2 | 4.6
| 2.6431 | 302.937 | 300.943 | 67.179 | 18.161 | 35.26 | 16.056 |  | 32.5833 | 1.8 | 4.6
| 2.6444 | 303.347 | 300.187 | 67.199 | 18.164 | 35.269 | 16.058 |  | 32.6042 | 1.7 | 4.6
| 2.6458 | 302.996 | 300.905 | 67.214 | 18.167 | 35.275 | 16.064 |  | 32.625 | 1.4 | 4.6
| 2.6472 | 303.847 | 300.521 | 67.234 | 18.173 | 35.291 | 16.063 |  | 32.6458 | 1.4 | 4.6
| 2.6486 | 303.458 | 300.273 | 67.25 | 18.174 | 35.299 | 16.07 |  | 32.6667 | 1.6 | 4.6
| 2.65 | 303.362 | 300.561 | 67.26 | 18.178 | 35.307 | 16.066 |  | 32.6875 | 1.5 | 4.6
| 2.6514 | 303.407 | 300.669 | 67.277 | 18.181 | 35.31 | 16.074 |  | 32.7083 | 1.4 | 4.6
| 2.6528 | 302.749 | 300.818 | 67.288 | 18.183 | 35.314 | 16.074 |  | 32.7292 | 1.4 | 4.6
| 2.6542 | 302.968 | 300.854 | 67.303 | 18.188 | 35.323 | 16.075 |  | 32.75 | 1.6 | 4.6
| 2.6556 | 302.683 | 300.889 | 67.308 | 18.19 | 35.324 | 16.081 |  | 32.7708 | 1.7 | 4.6
| 2.6569 | 302.895 | 300.398 | 67.32 | 18.196 | 35.326 | 16.082 |  | 32.7917 | 1.3 | 4.6
| 2.6583 | 302.39 | 300.482 | 67.327 | 18.197 | 35.322 | 16.082 |  | 32.8125 | 0.8 | 4.6
| 2.6597 | 303.115 | 299.734 | 67.34 | 18.2 | 35.33 | 16.086 |  | 32.8333 | 0.6 | 4.6
| 2.6611 | 303.368 | 300.386 | 67.351 | 18.202 | 35.342 | 16.089 |  | 32.8542 | 0.8 | 4.6
| 2.6625 | 302.44 | 300.639 | 67.361 | 18.205 | 35.339 | 16.088 |  | 32.875 | 0.9 | 4.6
| 2.6639 | 302.814 | 300.085 | 67.369 | 18.21 | 35.34 | 16.094 |  | 32.8958 | 1 | 4.6
| 2.6653 | 302.321 | 300.185 | 67.371 | 18.213 | 35.34 | 16.098 |  | 32.9167 | 1.2 | 4.6
| 2.6667 | 302.73 | 299.501 | 67.377 | 18.214 | 35.343 | 16.098 |  | 32.9375 | 1 | 4.6
| 2.6681 | 302.823 | 299.71 | 67.387 | 18.221 | 35.341 | 16.106 |  | 32.9583 | 0.8 | 4.6
| 2.6694 | 302.703 | 300.777 | 67.392 | 18.224 | 35.353 | 16.106 |  | 32.9792 | 0.9 | 4.6
| 2.6708 | 303.144 | 300.484 | 67.405 | 18.227 | 35.357 | 16.108 |  | 33 | 1.1 | 4.6
| 2.6722 | 302.917 | 299.982 | 67.42 | 18.228 | 35.361 | 16.109 |  | 33.0208 | 1.1 | 4.6
| 2.6736 | 302.627 | 300.767 | 67.421 | 18.231 | 35.365 | 16.117 |  | 33.0417 | 1.1 | 4.6
| 2.675 | 302.825 | 300.902 | 67.431 | 18.235 | 35.369 | 16.112 |  | 33.0625 | 0.7 | 4.6
| 2.6764 | 303.694 | 300.371 | 67.442 | 18.24 | 35.372 | 16.115 |  | 33.0833 | 0.2 | 4.6
| 2.6778 | 302.714 | 300.725 | 67.449 | 18.24 | 35.385 | 16.12 |  | 33.1042 | 0.2 | 4.6
| 2.6792 | 301.69 | 299.644 | 67.456 | 18.246 | 35.385 | 16.121 |  | 33.125 | 0.2 | 4.6
| 2.6806 | 301.479 | 298.926 | 67.441 | 18.25 | 35.372 | 16.123 |  | 33.1458 | 0.2 | 4.6
| 2.6819 | 301.527 | 299.525 | 67.429 | 18.25 | 35.361 | 16.13 |  | 33.1667 | 0.1 | 4.6
| 2.6833 | 301.826 | 298.882 | 67.419 | 18.252 | 35.355 | 16.132 |  | 33.1875 | -0.3 | 4.6
| 2.6847 | 300.919 | 299.102 | 67.414 | 18.258 | 35.346 | 16.135 |  | 33.2083 | -1 | 4.6
| 2.6861 | 301.441 | 299.182 | 67.408 | 18.256 | 35.341 | 16.136 |  | 33.2292 | -0.6 | 4.6
| 2.6875 | 301.288 | 299.218 | 67.408 | 18.261 | 35.338 | 16.141 |  | 33.25 | 0.2 | 4.6
| 2.6889 | 301.577 | 299.34 | 67.397 | 18.266 | 35.335 | 16.137 |  | 33.2708 | 0.2 | 4.6
| 2.6903 | 301.954 | 300.203 | 67.402 | 18.27 | 35.339 | 16.143 |  | 33.2917 | --- | 4.6
| 2.6917 | 301.942 | 300.282 | 67.406 | 18.27 | 35.35 | 16.145 |  | 33.3125 | 1.2 | 4.6
| 2.6931 | 301.932 | 299.578 | 67.414 | 18.276 | 35.357 | 16.146 |  | 33.3333 | 1.2 | 4.6
| 2.6944 | 301.756 | 299.94 | 67.419 | 18.274 | 35.358 | 16.152 |  | 33.3542 | 1.2 | 4.6
| 2.6958 | 301.923 | 299.602 | 67.42 | 18.279 | 35.366 | 16.153 |  | 33.375 | 0.2 | 4.6
| 2.6972 | 301.86 | 299.562 | 67.42 | 18.278 | 35.366 | 16.155 |  | 33.3958 | 0.3 | 4.6
| 2.6986 | 302.457 | 299.393 | 67.415 | 18.283 | 35.363 | 16.158 |  | 33.4167 | 0.5 | 4.6
| 2.7 | 300.257 | 297.489 | 67.398 | 18.29 | 35.359 | 16.159 |  | 33.4375 | 0.8 | 4.6
| 2.7014 | 299.881 | 298.25 | 67.373 | 18.291 | 35.34 | 16.16 |  | 33.4583 | 1.1 | 4.6
| 2.7028 | 300.276 | 297.499 | 67.359 | 18.291 | 35.332 | 16.163 |  | 33.4792 | 1.8 | 4.6
| 2.7042 | 300.132 | 298.261 | 67.344 | 18.298 | 35.321 | 16.169 |  | 33.5 | 3.1 | 4.6
| 2.7056 | 300.088 | 297.874 | 67.329 | 18.299 | 35.312 | 16.169 |  | 33.5208 | 3.3 | 4.6
| 2.7069 | 299.793 | 297.953 | 67.307 | 18.296 | 35.307 | 16.171 |  | 33.5417 | 2.8 | 4.6
| 2.7083 | 299.869 | 297.278 | 67.292 | 18.301 | 35.297 | 16.176 |  | 33.5625 | 3.3 | 4.6
| 2.7097 | 299.146 | 297.043 | 67.275 | 18.306 | 35.281 | 16.178 |  | 33.5833 | 3.6 | 4.5
| 2.7111 | 299.925 | 296.6 | 67.256 | 18.307 | 35.271 | 16.178 |  | 33.6042 | 3.2 | 4.5
| 2.7125 | 299.801 | 296.605 | 67.235 | 18.309 | 35.264 | 16.18 |  | 33.625 | 2.9 | 4.5
| 2.7139 | 299.5 | 296.491 | 67.221 | 18.31 | 35.26 | 16.183 |  | 33.6458 | 3.2 | 4.5
| 2.7153 | 299.105 | 297.188 | 67.196 | 18.311 | 35.251 | 16.185 |  | 33.6667 | 3.8 | 4.5
| 2.7167 | 299.891 | 296.518 | 67.178 | 18.316 | 35.243 | 16.187 |  | 33.7083 | 2.7 | 4.5
| 2.7181 | 299.183 | 296.777 | 67.161 | 18.313 | 35.239 | 16.192 |  | 33.7292 | 2.7 | 4.5
| 2.7194 | 299.627 | 296.948 | 67.145 | 18.32 | 35.231 | 16.191 |  | 33.75 | 2.7 | 4.5
| 2.7208 | 299.657 | 296.363 | 67.135 | 18.323 | 35.228 | 16.195 |  | 33.7708 | 2.7 | 4.5
| 2.7222 | 299.2 | 295.953 | 67.12 | 18.324 | 35.227 | 16.193 |  | 33.7917 | 2.8 | 4.5
| 2.7236 | 298.832 | 297.133 | 67.098 | 18.325 | 35.22 | 16.197 |  | 33.8125 | 2.7 | 4.5
| 2.725 | 298.834 | 295.834 | 67.071 | 18.323 | 35.209 | 16.204 |  | 33.8333 | 2.7 | 4.5
| 2.7264 | 298.278 | 296.017 | 67.041 | 18.327 | 35.199 | 16.204 |  | 33.8542 | 2.7 | 4.5
| 2.7278 | 302.111 | 300.396 | 67.073 | 18.327 | 35.225 | 16.203 |  | 33.875 | 2.7 | 4.5
| 2.7292 | 302.284 | 300.439 | 67.111 | 18.334 | 35.262 | 16.205 |  | 33.8958 | 2.7 | 4.5
| 2.7306 | 302.526 | 300.478 | 67.142 | 18.329 | 35.292 | 16.212 |  | 33.9167 | 2.7 | 4.5
| 2.7319 | 301.888 | 300.126 | 67.157 | 18.334 | 35.314 | 16.206 |  | 33.9375 | 2.7 | 4.5
| 2.7333 | 301.981 | 300.348 | 67.172 | 18.331 | 35.33 | 16.214 |  | 33.9583 | 2.6 | 4.5
| 2.7347 | 302.917 | 299.672 | 67.186 | 18.339 | 35.348 | 16.213 |  | 33.9792 | 2.7 | 4.5
| 2.7361 | 301.93 | 299.681 | 67.202 | 18.339 | 35.361 | 16.221 |  | 34 | 2.7 | 4.5
| 2.7375 | 301.925 | 300.079 | 67.208 | 18.339 | 35.373 | 16.217 |  | 34.0208 | 2.7 | 4.5
| 2.7389 | 302.523 | 299.521 | 67.213 | 18.345 | 35.375 | 16.221 |  | 34.0417 | 2.7 | 4.5
| 2.7403 | 302.426 | 299.566 | 67.222 | 18.344 | 35.381 | 16.224 |  | 34.0625 | 2.8 | 4.5
| 2.7417 | 302.063 | 299.99 | 67.235 | 18.348 | 35.391 | 16.224 |  | 34.0833 | 2.8 | 4.5
| 2.7431 | 301.228 | 299.427 | 67.236 | 18.348 | 35.395 | 16.227 |  | 34.1042 | 2.8 | 4.5
| 2.7444 | 301.491 | 298.732 | 67.238 | 18.353 | 35.392 | 16.23 |  | 34.125 | 2.8 | 4.5
| 2.7458 | 301.815 | 298.966 | 67.248 | 18.353 | 35.396 | 16.228 |  | 34.1458 | 2.8 | 4.5
| 2.7472 | 301.146 | 298.784 | 67.249 | 18.355 | 35.394 | 16.228 |  | 34.1667 | 2.8 | 4.5
| 2.7486 | 301.554 | 298.403 | 67.241 | 18.356 | 35.394 | 16.235 |  | 34.1875 | 2.8 | 4.5
| 2.75 | 301.477 | 299.213 | 67.242 | 18.362 | 35.395 | 16.236 |  | 34.2083 | 2.8 | 4.5
| 2.7514 | 301.453 | 299.76 | 67.247 | 18.363 | 35.395 | 16.238 |  | 34.2292 | 2.8 | 4.5
| 2.7528 | 300.966 | 298.717 | 67.259 | 18.363 | 35.4 | 16.242 |  | 34.25 | 2.8 | 4.5
| 2.7542 | 300.858 | 298.884 | 67.254 | 18.366 | 35.396 | 16.243 |  | 34.2708 | 2.8 | 4.5
| 2.7556 | 300.829 | 298.944 | 67.252 | 18.37 | 35.398 | 16.239 |  | 34.2917 | 2.8 | 4.5
| 2.7569 | 300.677 | 298.643 | 67.245 | 18.374 | 35.391 | 16.244 |  | 34.3125 | 2.8 | 4.5
| 2.7583 | 301.746 | 299.115 | 67.244 | 18.373 | 35.394 | 16.247 |  | 34.3333 | 2.8 | 4.5
| 2.7597 | 303.456 | 301.397 | 67.269 | 18.374 | 35.408 | 16.251 |  | 34.3542 | 2.8 | 4.5
| 2.7611 | 304.128 | 301.339 | 67.31 | 18.378 | 35.437 | 16.253 |  | 34.375 | 2.8 | 4.5
| 2.7625 | 303.629 | 301.876 | 67.346 | 18.382 | 35.463 | 16.254 |  | 34.3958 | 2.9 | 4.5
| 2.7639 | 304.214 | 300.953 | 67.373 | 18.385 | 35.495 | 16.256 |  | 34.4167 | 2.8 | 4.5
| 2.7653 | 304.514 | 301.473 | 67.398 | 18.386 | 35.511 | 16.258 |  | 34.4375 | 2.8 | 4.5
| 2.7667 | 304.574 | 301.541 | 67.429 | 18.385 | 35.528 | 16.257 |  | 34.4583 | 2.9 | 4.5
| 2.7681 | 304.352 | 301.354 | 67.455 | 18.391 | 35.545 | 16.258 |  | 34.4792 | 2.9 | 4.5
| 2.7694 | 304.348 | 301.131 | 67.481 | 18.397 | 35.561 | 16.265 |  | 34.5 | 3 | 4.5
| 2.7708 | 304.519 | 301.307 | 67.496 | 18.398 | 35.571 | 16.265 |  | 34.5208 | 3 | 4.5
| 2.7722 | 304.795 | 301.496 | 67.526 | 18.399 | 35.586 | 16.267 |  | 34.5417 | 3 | 4.5
| 2.7736 | 304.346 | 302.528 | 67.554 | 18.406 | 35.598 | 16.271 |  | 34.5625 | 3 | 4.5
| 2.775 | 304.904 | 301.675 | 67.581 | 18.405 | 35.611 | 16.268 |  | 34.5833 | 3 | 4.5
| 2.7764 | 304.728 | 301.481 | 67.605 | 18.408 | 35.622 | 16.273 |  | 34.6042 | 3 | 4.5
| 2.7778 | 304.785 | 301.996 | 67.62 | 18.412 | 35.633 | 16.276 |  | 34.625 | 2.9 | 4.5
| 2.7792 | 304.403 | 301.334 | 67.647 | 18.415 | 35.643 | 16.281 |  | 34.6458 | 2.9 | 4.5
| 2.7806 | 304.487 | 301.512 | 67.666 | 18.416 | 35.647 | 16.277 |  | 34.6667 | 2.9 | 4.5
| 2.7819 | 304.756 | 302.08 | 67.678 | 18.418 | 35.658 | 16.282 |  | 34.6875 | 2.9 | 4.5
| 2.7833 | 304.295 | 302.592 | 67.708 | 18.428 | 35.666 | 16.283 |  | 34.7083 | 2.9 | 4.5
| 2.7847 | 304.251 | 301.656 | 67.733 | 18.429 | 35.68 | 16.284 |  | 34.7292 | 2.9 | 4.5
| 2.7861 | 304.23 | 302.471 | 67.748 | 18.431 | 35.684 | 16.288 |  | 34.75 | 3 | 4.5
| 2.7875 | 304.155 | 302.554 | 67.766 | 18.438 | 35.691 | 16.291 |  | 34.7708 | 3 | 4.5
| 2.7889 | 304.389 | 302.512 | 67.787 | 18.437 | 35.696 | 16.292 |  | 34.7917 | 3 | 4.5
| 2.7903 | 300.922 | 298.141 | 67.769 | 18.443 | 35.682 | 16.293 |  | 34.8125 | 3 | 4.5
| 2.7917 | 301.238 | 298.897 | 67.732 | 18.445 | 35.651 | 16.298 |  | 34.8333 | 2.9 | 4.5
| 2.7931 | 301.507 | 298.686 | 67.716 | 18.447 | 35.629 | 16.301 |  | 34.8542 | 3 | 4.5
| 2.7944 | 301.506 | 298.65 | 67.701 | 18.455 | 35.616 | 16.304 |  | 34.875 | 3 | 4.5
| 2.7958 | 301.506 | 298.246 | 67.692 | 18.457 | 35.598 | 16.304 |  | 34.8958 | 3 | 4.5
| 2.7972 | 301.473 | 298.408 | 67.676 | 18.454 | 35.582 | 16.305 |  | 34.9167 | 3 | 4.5
| 2.7986 | 301.22 | 298.623 | 67.668 | 18.462 | 35.574 | 16.305 |  | 34.9375 | 3 | 4.5
| 2.8 | 301.35 | 298.021 | 67.654 | 18.464 | 35.568 | 16.312 |  | 34.9583 | 3 | 4.5
| 2.8014 | 300.457 | 298.908 | 67.641 | 18.467 | 35.556 | 16.315 |  | 34.9792 | 3 | 4.5
| 2.8028 | 301.225 | 298.31 | 67.627 | 18.468 | 35.547 | 16.318 |  | 35 | 3 | 4.4
| 2.8042 | 301.608 | 298.766 | 67.62 | 18.466 | 35.546 | 16.322 |  | 35.0208 | 2.9 | 4.4
| 2.8056 | 301.302 | 299.485 | 67.623 | 18.471 | 35.549 | 16.323 |  | 35.0417 | 2.9 | 4.4
| 2.8069 | 301.497 | 299.8 | 67.624 | 18.474 | 35.555 | 16.323 |  | 35.0625 | 2.9 | 4.4
| 2.8083 | 300.866 | 299.037 | 67.611 | 18.477 | 35.55 | 16.326 |  | 35.0833 | 2.9 | 4.4
| 2.8097 | 301.474 | 298.603 | 67.609 | 18.477 | 35.554 | 16.326 |  | 35.1042 | 2.9 | 4.4
| 2.8111 | 302.298 | 299.056 | 67.614 | 18.482 | 35.562 | 16.335 |  | 35.125 | 2.9 | 4.4
| 2.8125 | 301.55 | 299.458 | 67.606 | 18.484 | 35.562 | 16.333 |  | 35.1458 | 2.9 | 4.4
| 2.8139 | 301.536 | 299.138 | 67.604 | 18.487 | 35.564 | 16.337 |  | 35.1667 | 2.9 | 4.4
| 2.8153 | 301.721 | 299.279 | 67.598 | 18.489 | 35.566 | 16.337 |  | 35.1875 | 2.8 | 4.4
| 2.8167 | 302.297 | 299.089 | 67.601 | 18.489 | 35.565 | 16.336 |  | 35.2083 | 2.7 | 4.4
| 2.8181 | 302.195 | 299.747 | 67.607 | 18.495 | 35.577 | 16.34 |  | 35.2292 | 2.8 | 4.4
| 2.8194 | 301.841 | 299.928 | 67.606 | 18.497 | 35.586 | 16.346 |  | 35.25 | 2.7 | 4.4
| 2.8208 | 301.681 | 299.804 | 67.61 | 18.498 | 35.586 | 16.352 |  | 35.2708 | 2.7 | 4.4
| 2.8222 | 301.849 | 299.921 | 67.608 | 18.502 | 35.591 | 16.352 |  | 35.2917 | 2.7 | 4.4
| 2.8236 | 302.417 | 299.806 | 67.617 | 18.499 | 35.593 | 16.352 |  | 35.3125 | 2.7 | 4.4
| 2.825 | 302.163 | 299.933 | 67.621 | 18.505 | 35.603 | 16.35 |  | 35.3333 | 2.7 | 4.4
| 2.8264 | 302.393 | 299.385 | 67.621 | 18.507 | 35.603 | 16.352 |  | 35.3542 | 2.7 | 4.4
| 2.8278 | 302.932 | 299.732 | 67.625 | 18.508 | 35.61 | 16.357 |  | 35.375 | 2.6 | 4.4
| 2.8292 | 301.803 | 299.541 | 67.626 | 18.511 | 35.611 | 16.357 |  | 35.3958 | 2.6 | 4.4
| 2.8306 | 302.423 | 299.353 | 67.629 | 18.514 | 35.623 | 16.362 |  | 35.4167 | 2.6 | 4.4
| 2.8319 | 302.277 | 300.349 | 67.635 | 18.517 | 35.629 | 16.363 |  | 35.4375 | 2.6 | 4.4
| 2.8333 | 302.855 | 299.874 | 67.637 | 18.517 | 35.634 | 16.366 |  | 35.4583 | 2.7 | 4.4
| 2.8347 | 302.496 | 299.997 | 67.644 | 18.522 | 35.639 | 16.371 |  | 35.4792 | 2.8 | 4.4
| 2.8361 | 302.485 | 300.539 | 67.647 | 18.525 | 35.642 | 16.371 |  | 35.5 | 2.8 | 4.4
| 2.8375 | 302.367 | 300.638 | 67.657 | 18.52 | 35.645 | 16.374 |  | 35.5208 | 2.8 | 4.4
| 2.8389 | 302.76 | 300.919 | 67.668 | 18.525 | 35.653 | 16.377 |  | 35.5417 | 2.8 | 4.4
| 2.8403 | 302.715 | 301.107 | 67.675 | 18.532 | 35.663 | 16.378 |  | 35.5625 | 2.8 | 4.4
| 2.8417 | 302.678 | 300.959 | 67.688 | 18.533 | 35.679 | 16.378 |  | 35.5833 | 2.8 | 4.4
| 2.8431 | 302.734 | 300.691 | 67.695 | 18.531 | 35.677 | 16.376 |  | 35.6042 | 2.7 | 4.4
| 2.8444 | 303.254 | 300.288 | 67.697 | 18.532 | 35.683 | 16.381 |  | 35.625 | 2.5 | 4.4
| 2.8458 | 303.414 | 301.806 | 67.713 | 18.537 | 35.694 | 16.383 |  | 35.6458 | 2.4 | 4.4
| 2.8472 | 302.975 | 301.451 | 67.731 | 18.54 | 35.713 | 16.386 |  | 35.6667 | 2.2 | 4.4
| 2.8486 | 304.42 | 301.446 | 67.755 | 18.547 | 35.725 | 16.388 |  | 35.6875 | 2.1 | 4.4
| 2.85 | 301.167 | 298.885 | 67.731 | 18.546 | 35.706 | 16.389 |  | 35.7083 | 2 | 4.4
| 2.8514 | 300.74 | 299.077 | 67.705 | 18.545 | 35.69 | 16.389 |  | 35.7292 | 1.9 | 4.4
| 2.8528 | 301.37 | 299.004 | 67.694 | 18.548 | 35.674 | 16.393 |  | 35.75 | 1.8 | 4.4
| 2.8542 | 301.611 | 299.186 | 67.687 | 18.553 | 35.67 | 16.397 |  | 35.7708 | 1.7 | 4.4
| 2.8556 | 302.025 | 299.092 | 67.689 | 18.556 | 35.668 | 16.396 |  | 35.8194 | 1.7 | 4.4
| 2.8569 | 302.043 | 299.16 | 67.682 | 18.558 | 35.67 | 16.402 |  | 35.8403 | 1.7 | 4.4
| 2.8583 | 301.488 | 299.796 | 67.684 | 18.559 | 35.664 | 16.402 |  | 35.8611 | 1.7 | 4.4
| 2.8597 | 301.822 | 298.853 | 67.678 | 18.565 | 35.663 | 16.404 |  | 35.8819 | 1.7 | 4.4
| 2.8611 | 302.204 | 299.075 | 67.68 | 18.561 | 35.659 | 16.406 |  | 35.9028 | 1.5 | 4.4
| 2.8625 | 302.129 | 298.938 | 67.675 | 18.569 | 35.671 | 16.409 |  | 35.9236 | 1.5 | 4.4
| 2.8639 | 301.584 | 299.446 | 67.67 | 18.569 | 35.665 | 16.409 |  | 35.9444 | 1.4 | 4.4
| 2.8653 | 301.823 | 300.069 | 67.677 | 18.576 | 35.679 | 16.411 |  | 35.9653 | 1.4 | 4.4
| 2.8667 | 302.378 | 299.565 | 67.677 | 18.568 | 35.671 | 16.411 |  | 35.9861 | 1.6 | 4.4
| 2.8681 | 302.485 | 299.621 | 67.682 | 18.569 | 35.678 | 16.417 |  | 36.0069 | 1.7 | 4.4
| 2.8694 | 302.043 | 300.18 | 67.686 | 18.585 | 35.698 | 16.419 |  | 36.0278 | 1.8 | 4.4
| 2.8708 | 302.859 | 300.425 | 67.691 | 18.577 | 35.69 | 16.42 |  | 36.0486 | 1.8 | 4.4
| 2.8722 | 302.309 | 300.317 | 67.702 | 18.579 | 35.7 | 16.419 |  | 36.0694 | 1.8 | 4.4
| 2.8736 | 303.205 | 300.314 | 67.704 | 18.581 | 35.709 | 16.426 |  | 36.0903 | 1.8 | 4.4
| 2.875 | 302.187 | 300.633 | 67.719 | 18.58 | 35.715 | 16.424 |  | 36.1111 | 1.7 | 4.4
| 2.8764 | 302.962 | 300.511 | 67.729 | 18.587 | 35.723 | 16.426 |  | 36.1319 | 1.7 | 4.4
| 2.8778 | 303.016 | 300.229 | 67.735 | 18.588 | 35.729 | 16.432 |  | 36.1528 | 1.6 | 4.4
| 2.8792 | 302.883 | 300.186 | 67.739 | 18.59 | 35.733 | 16.434 |  | 36.1736 | 1.6 | 4.4
| 2.8806 | 302.851 | 300.419 | 67.749 | 18.591 | 35.741 | 16.435 |  | 36.1944 | 1.6 | 4.4
| 2.8819 | 303.004 | 300.671 | 67.758 | 18.595 | 35.752 | 16.43 |  | 36.2153 | 1.5 | 4.4
| 2.8833 | 302.958 | 301.322 | 67.77 | 18.598 | 35.756 | 16.435 |  | 36.2361 | 1.5 | 4.3
| 2.8847 | 302.4 | 300.619 | 67.779 | 18.604 | 35.759 | 16.441 |  | 36.2569 | 1.5 | 4.4
| 2.8861 | 302.695 | 300.752 | 67.783 | 18.602 | 35.768 | 16.441 |  | 36.2778 | 1.4 | 4.3
| 2.8875 | 302.683 | 300.536 | 67.79 | 18.603 | 35.77 | 16.444 |  | 36.2986 | 1.4 | 4.3
| 2.8889 | 303.779 | 300.854 | 67.801 | 18.609 | 35.778 | 16.446 |  | 36.3194 | 1.2 | 4.3
| 2.8903 | 302.877 | 301.221 | 67.819 | 18.61 | 35.788 | 16.448 |  | 36.3403 | 1.3 | 4.3
| 2.8917 | 300.832 | 298.109 | 67.803 | 18.614 | 35.787 | 16.45 |  | 36.3611 | 1.4 | 4.3
| 2.8931 | 299.908 | 297.994 | 67.755 | 18.614 | 35.754 | 16.45 |  | 36.3819 | 1.4 | 4.3
| 2.8944 | 300.23 | 298.16 | 67.726 | 18.614 | 35.729 | 16.45 |  | 36.4028 | 1.3 | 4.3
| 2.8958 | 300.652 | 297.523 | 67.706 | 18.617 | 35.708 | 16.46 |  | 36.4236 | 1.3 | 4.3
| 2.8972 | 300.029 | 297.996 | 67.683 | 18.62 | 35.694 | 16.456 |  | 36.4444 | 1.2 | 4.3
| 2.8986 | 300.605 | 297.749 | 67.672 | 18.624 | 35.69 | 16.464 |  | 36.4653 | 1.2 | 4.3
| 2.9 | 300.215 | 298.611 | 67.662 | 18.622 | 35.678 | 16.459 |  | 36.4861 | 1.1 | 4.3
| 2.9014 | 299.985 | 298.283 | 67.649 | 18.628 | 35.67 | 16.462 |  | 36.5069 | 1.1 | 4.3
| 2.9028 | 300.816 | 297.901 | 67.638 | 18.628 | 35.675 | 16.469 |  | 36.5278 | 1.1 | 4.3
| 2.9042 | 300.36 | 298.599 | 67.631 | 18.63 | 35.668 | 16.468 |  | 36.5486 | 1.2 | 4.3
| 2.9056 | 300.882 | 297.567 | 67.616 | 18.632 | 35.662 | 16.472 |  | 36.5694 | 1.1 | 4.3
| 2.9069 | 300.349 | 297.926 | 67.609 | 18.629 | 35.663 | 16.473 |  | 36.5903 | 1.1 | 4.3
| 2.9083 | 300.419 | 298.161 | 67.595 | 18.636 | 35.658 | 16.473 |  | 36.6111 | 1 | 4.3
| 2.9097 | 300.527 | 298.178 | 67.582 | 18.634 | 35.662 | 16.477 |  | 36.6319 | 0.9 | 4.3
| 2.9111 | 299.733 | 298.062 | 67.572 | 18.637 | 35.653 | 16.477 |  | 36.6528 | 0.9 | 4.3
| 2.9125 | 300.449 | 297.808 | 67.563 | 18.639 | 35.651 | 16.481 |  | 36.6736 | 0.8 | 4.3
| 2.9139 | 300.109 | 298.402 | 67.556 | 18.639 | 35.652 | 16.481 |  | 36.6944 | 0.8 | 4.3
| 2.9153 | 300.566 | 298.75 | 67.547 | 18.642 | 35.656 | 16.483 |  | 36.7153 | 0.7 | 4.3
| 2.9167 | 300.618 | 298.578 | 67.54 | 18.646 | 35.658 | 16.491 |  | 36.7361 | 0.7 | 4.3
| 2.9181 | 300.586 | 298.472 | 67.537 | 18.644 | 35.657 | 16.484 |  | 36.7569 | 0.6 | 4.3
| 2.9194 | 300.603 | 298.911 | 67.533 | 18.647 | 35.659 | 16.484 |  | 36.7778 | 0.6 | 4.3
| 2.9208 | 300.8 | 298.747 | 67.528 | 18.648 | 35.663 | 16.493 |  | 36.7986 | 0.6 | 4.3
| 2.9222 | 300.948 | 298.724 | 67.527 | 18.652 | 35.67 | 16.495 |  | 36.8194 | 0.5 | 4.3
| 2.9236 | 300.752 | 298.705 | 67.526 | 18.652 | 35.672 | 16.495 |  | 36.8403 | 0.4 | 4.3
| 2.925 | 301.058 | 298.153 | 67.518 | 18.652 | 35.674 | 16.496 |  | 36.8611 | 0.5 | 4.3
| 2.9264 | 301.219 | 297.791 | 67.508 | 18.652 | 35.673 | 16.498 |  | 36.8819 | 0.4 | 4.3
| 2.9278 | 300.275 | 298.413 | 67.504 | 18.652 | 35.673 | 16.497 |  | 36.9028 | 0.3 | 4.3
| 2.9292 | 301.719 | 299.412 | 67.507 | 18.656 | 35.676 | 16.502 |  | 36.9236 | 0.3 | 4.3
| 2.9306 | 302.325 | 298.997 | 67.52 | 18.659 | 35.692 | 16.506 |  | 36.9444 | 0 | 4.3
| 2.9319 | 301.809 | 299.898 | 67.528 | 18.658 | 35.701 | 16.506 |  | 36.9653 | -0.1 | 4.3
| 2.9333 | 302.136 | 299.516 | 67.538 | 18.662 | 35.712 | 16.505 |  | 36.9861 | -0.1 | 4.3
| 2.9347 | 301.776 | 299.909 | 67.545 | 18.659 | 35.721 | 16.509 |  | 37.0069 | -0.1 | 4.3
| 2.9361 | 302.315 | 299.156 | 67.552 | 18.663 | 35.731 | 16.507 |  | 37.0278 | 0.1 | 4.3
| 2.9375 | 302.379 | 299.569 | 67.561 | 18.664 | 35.739 | 16.509 |  | 37.0486 | 0.2 | 4.3
| 2.9389 | 302.584 | 300.366 | 67.566 | 18.666 | 35.748 | 16.513 |  | 37.0694 | 0.2 | 4.3
| 2.9403 | 302.478 | 300.071 | 67.585 | 18.668 | 35.755 | 16.512 |  | 37.0903 | 0.1 | 4.3
| 2.9417 | 302.726 | 300.062 | 67.592 | 18.673 | 35.766 | 16.518 |  | 37.1111 | 0.1 | 4.3
| 2.9431 | 302.901 | 299.769 | 67.6 | 18.671 | 35.775 | 16.519 |  | 37.1319 | 0 | 4.3
| 2.9444 | 302.609 | 299.947 | 67.611 | 18.672 | 35.776 | 16.523 |  | 37.1528 | 0 | 4.3
| 2.9458 | 302.714 | 299.8 | 67.618 | 18.681 | 35.785 | 16.522 |  | 37.1736 | -0.1 | 4.3
| 2.9472 | 302.807 | 299.67 | 67.625 | 18.679 | 35.791 | 16.522 |  | 37.1944 | 0 | 4.3
| 2.9486 | 302.353 | 300.396 | 67.633 | 18.68 | 35.792 | 16.524 |  | 37.2153 | 0.1 | 4.3
| 2.95 | 303.199 | 300.252 | 67.642 | 18.682 | 35.798 | 16.525 |  | 37.2361 | 0.1 | 4.3
| 2.9514 | 302.305 | 300.917 | 67.65 | 18.684 | 35.804 | 16.527 |  | 37.2569 | 0.1 | 4.3
| 2.9528 | 302.94 | 299.959 | 67.659 | 18.686 | 35.813 | 16.533 |  | 37.2778 | 0.1 | 4.3
| 2.9542 | 302.882 | 301.336 | 67.673 | 18.689 | 35.817 | 16.529 |  | 37.2986 | 0.1 | 4.3
| 2.9556 | 303.783 | 301.571 | 67.694 | 18.691 | 35.838 | 16.536 |  | 37.3194 | 0 | 4.3
| 2.9569 | 303.811 | 301.41 | 67.715 | 18.695 | 35.856 | 16.537 |  | 37.3403 | 0 | 4.3
| 2.9583 | 303.701 | 300.824 | 67.741 | 18.695 | 35.869 | 16.536 |  | 37.3611 | 0 | 4.3
| 2.9597 | 303.58 | 301.155 | 67.749 | 18.695 | 35.874 | 16.534 |  | 37.3819 | 0 | 4.3
| 2.9611 | 303.789 | 300.925 | 67.764 | 18.699 | 35.887 | 16.539 |  | 37.4028 | 0 | 4.3
| 2.9625 | 303.718 | 301.397 | 67.782 | 18.703 | 35.895 | 16.54 |  | 37.4236 | 0 | 4.3
| 2.9639 | 304.007 | 300.765 | 67.795 | 18.706 | 35.899 | 16.544 |  | 37.4444 | 0 | 4.3
| 2.9653 | 303.816 | 300.694 | 67.814 | 18.707 | 35.906 | 16.544 |  | 37.4653 | 0 | 4.3
| 2.9667 | 303.237 | 301.447 | 67.831 | 18.707 | 35.917 | 16.549 |  | 37.4861 | -0.1 | 4.3
| 2.9681 | 303.434 | 300.942 | 67.847 | 18.712 | 35.922 | 16.551 |  | 37.5069 | 0 | 4.3
| 2.9694 | 303.416 | 301.529 | 67.858 | 18.71 | 35.924 | 16.551 |  | 37.5278 | 0 | 4.3
| 2.9708 | 303.827 | 301.734 | 67.875 | 18.713 | 35.939 | 16.552 |  | 37.5486 | 0.1 | 4.2
| 2.9722 | 303.921 | 302.342 | 67.896 | 18.717 | 35.949 | 16.551 |  | 37.5694 | 0 | 4.2
| 2.9736 | 304.099 | 302.52 | 67.916 | 18.716 | 35.962 | 16.557 |  | 37.5903 | 0 | 4.2
| 2.975 | 304.301 | 302.666 | 67.945 | 18.723 | 35.975 | 16.558 |  | 37.6111 | -0.1 | 4.2
| 2.9764 | 301.53 | 298.328 | 67.956 | 18.727 | 35.98 | 16.563 |  | 37.6319 | -0.1 | 4.2
| 2.9778 | 300.94 | 298.885 | 67.91 | 18.726 | 35.948 | 16.56 |  | 37.6528 | 0 | 4.2
| 2.9792 | 300.472 | 297.657 | 67.888 | 18.731 | 35.925 | 16.563 |  | 37.6736 | -0.1 | 4.2
| 2.9806 | 301.793 | 298.691 | 67.878 | 18.734 | 35.91 | 16.564 |  | 37.6944 | -0.1 | 4.2
| 2.9819 | 301.943 | 299.237 | 67.875 | 18.737 | 35.9 | 16.567 |  | 37.7153 | 0 | 4.2
| 2.9833 | 301.131 | 299.009 | 67.869 | 18.737 | 35.892 | 16.571 |  | 37.7361 | 0.1 | 4.2
| 2.9847 | 302.3 | 299.198 | 67.863 | 18.737 | 35.887 | 16.571 |  | 37.7569 | 0.2 | 4.2
| 2.9861 | 302.366 | 299.12 | 67.865 | 18.74 | 35.885 | 16.573 |  | 37.7778 | 0.2 | 4.2
| 2.9875 | 302.607 | 299.442 | 67.873 | 18.741 | 35.891 | 16.576 |  | 37.7986 | 0.3 | 4.2
| 2.9889 | 299.324 | 297.048 | 67.868 | 18.745 | 35.89 | 16.582 |  | 37.8194 | 0.2 | 4.2
| 2.9903 | 299.058 | 297.304 | 67.814 | 18.748 | 35.854 | 16.581 |  | 37.8403 | 0.1 | 4.2
| 2.9917 | 299.228 | 297.381 | 67.779 | 18.751 | 35.83 | 16.582 |  | 37.8611 | 0.1 | 4.2
| 2.9931 | 300.177 | 297.042 | 67.759 | 18.753 | 35.816 | 16.585 |  | 37.8819 | 0.1 | 4.2
| 2.9944 | 299.835 | 297.397 | 67.737 | 18.754 | 35.802 | 16.583 |  | 37.9028 | 0.1 | 4.2
| 2.9958 | 299.692 | 297.21 | 67.718 | 18.759 | 35.794 | 16.589 |  | 37.9236 | 0.1 | 4.2
| 2.9972 | 300.009 | 296.862 | 67.695 | 18.757 | 35.78 | 16.587 |  | 37.9444 | 0 | 4.2
| 2.9986 | 299.651 | 297.97 | 67.677 | 18.762 | 35.779 | 16.592 |  | 37.9653 | 0 | 4.2
| 3 | 300.075 | 297.385 | 67.67 | 18.759 | 35.771 | 16.597 |  | 37.9861 | 0 | 4.2
| 3.0014 | 299.867 | 297.936 | 67.656 | 18.766 | 35.772 | 16.599 |  | 38.0069 | 0 | 4.2
| 3.0028 | 299.7 | 297.735 | 67.644 | 18.765 | 35.77 | 16.6 |  | 38.0278 | -0.1 | 4.2
| 3.0042 | 299.989 | 296.923 | 67.63 | 18.767 | 35.765 | 16.602 |  | 38.0486 | -0.1 | 4.2
| 3.0056 | 299.285 | 297.241 | 67.607 | 18.766 | 35.758 | 16.603 |  | 38.0694 | 0 | 4.2
| 3.0069 | 299.689 | 296.757 | 67.591 | 18.771 | 35.752 | 16.601 |  | 38.0903 | 0 | 4.2
| 3.0083 | 299.221 | 296.133 | 67.569 | 18.769 | 35.739 | 16.605 |  | 38.1111 | -0.1 | 4.2
| 3.0097 | 299.05 | 296.024 | 67.55 | 18.771 | 35.734 | 16.607 |  | 38.1319 | -0.1 | 4.2
| 3.0111 | 299.806 | 296.701 | 67.531 | 18.772 | 35.734 | 16.611 |  | 38.1528 | 0 | 4.2
| 3.0125 | 300.135 | 297.744 | 67.524 | 18.772 | 35.727 | 16.613 |  | 38.1736 | 0.1 | 4.2
| 3.0139 | 300.89 | 297.887 | 67.527 | 18.773 | 35.736 | 16.612 |  | 38.1944 | 0 | 4.2
| 3.0153 | 301.336 | 298.212 | 67.528 | 18.773 | 35.749 | 16.614 |  | 38.2153 | -0.1 | 4.2
| 3.0167 | 300.951 | 298.892 | 67.531 | 18.773 | 35.759 | 16.615 |  | 38.2361 | -0.1 | 4.2
| 3.0181 | 300.887 | 298.893 | 67.542 | 18.777 | 35.774 | 16.621 |  | 38.2569 | -0.2 | 4.2
| 3.0194 | 301.306 | 298.303 | 67.541 | 18.778 | 35.786 | 16.618 |  | 38.2778 | -0.2 | 4.2
| 3.0208 | 301.293 | 299.344 | 67.549 | 18.78 | 35.792 | 16.618 |  | 38.2986 | -0.2 | 4.2
| 3.0222 | 301.539 | 299.089 | 67.555 | 18.779 | 35.811 | 16.621 |  | 38.3194 | -0.2 | 4.2
| 3.0236 | 301.221 | 298.779 | 67.561 | 18.781 | 35.818 | 16.625 |  | 38.3403 | -0.2 | 4.2
| 3.025 | 300.738 | 298.974 | 67.563 | 18.778 | 35.818 | 16.625 |  | 38.3611 | 0.1 | 4.2
| 3.0264 | 300.827 | 298.866 | 67.559 | 18.783 | 35.823 | 16.625 |  | 38.3819 | -0.1 | 4.2
| 3.0278 | 301.096 | 298.563 | 67.547 | 18.782 | 35.821 | 16.631 |  | 38.4028 | 0 | 4.2
| 3.0292 | 301.022 | 298.44 | 67.549 | 18.785 | 35.829 | 16.635 |  | 38.4236 | 0 | 4.2
| 3.0306 | 300.707 | 298.046 | 67.547 | 18.785 | 35.822 | 16.633 |  | 38.4444 | 0 | 4.2
| 3.0319 | 300.148 | 297.186 | 67.531 | 18.785 | 35.811 | 16.631 |  | 38.4653 | 0 | 4.2
| 3.0333 | 300.14 | 297.078 | 67.517 | 18.787 | 35.805 | 16.635 |  | 38.4861 | -0.1 | 4.2
| 3.0347 | 299.586 | 297.968 | 67.501 | 18.787 | 35.797 | 16.637 |  | 38.5069 | -0.1 | 4.2
| 3.0361 | 299.892 | 297.427 | 67.497 | 18.793 | 35.79 | 16.64 |  | 38.5278 | 0 | 4.2
| 3.0375 | 299.384 | 297.497 | 67.485 | 18.791 | 35.786 | 16.641 |  | 38.5486 | -0.1 | 4.2
| 3.0389 | 298.933 | 297.153 | 67.466 | 18.797 | 35.778 | 16.645 |  | 38.5694 | 0 | 4.2
| 3.0403 | 299.152 | 297.173 | 67.454 | 18.795 | 35.775 | 16.642 |  | 38.5903 | 0 | 4.1
| 3.0417 | 299.196 | 297.358 | 67.441 | 18.796 | 35.767 | 16.643 |  | 38.6111 | -0.1 | 4.2
| 3.0431 | 299.599 | 296.327 | 67.432 | 18.8 | 35.764 | 16.643 |  | 38.6319 | 0 | 4.1
| 3.0444 | 299.446 | 296.787 | 67.416 | 18.796 | 35.756 | 16.648 |  | 38.6528 | 0 | 4.1
| 3.0458 | 299.803 | 297.023 | 67.407 | 18.801 | 35.755 | 16.649 |  | 38.6736 | -0.1 | 4.1
| 3.0472 | 299.469 | 297.186 | 67.399 | 18.804 | 35.753 | 16.652 |  | 38.6944 | -0.1 | 4.1
| 3.0486 | 299.506 | 296.846 | 67.387 | 18.803 | 35.749 | 16.652 |  | 38.7153 | -0.1 | 4.1
| 3.05 | 299.334 | 297.39 | 67.377 | 18.806 | 35.743 | 16.655 |  | 38.7361 | -0.1 | 4.1
| 3.0514 | 299.1 | 297.34 | 67.368 | 18.809 | 35.747 | 16.653 |  | 38.7569 | -0.1 | 4.1
| 3.0528 | 299.479 | 297.215 | 67.355 | 18.805 | 35.741 | 16.661 |  | 38.7778 | -0.1 | 4.1
| 3.0542 | 299.462 | 297.369 | 67.347 | 18.808 | 35.746 | 16.66 |  | 38.7986 | -0.1 | 4.1
| 3.0556 | 300.328 | 297.812 | 67.349 | 18.807 | 35.747 | 16.655 |  | 38.8194 | -0.1 | 4.1
| 3.0569 | 300.068 | 298.299 | 67.357 | 18.808 | 35.755 | 16.662 |  | 38.8403 | -0.1 | 4.1
| 3.0583 | 300.985 | 297.914 | 67.368 | 18.812 | 35.774 | 16.666 |  | 38.8611 | -0.1 | 4.1
| 3.0597 | 300.868 | 298.191 | 67.37 | 18.811 | 35.778 | 16.667 |  | 38.8819 | -0.2 | 4.1
| 3.0611 | 300.565 | 298.873 | 67.367 | 18.812 | 35.788 | 16.66 |  | 38.9028 | -0.1 | 4.1
| 3.0625 | 300.656 | 298.586 | 67.379 | 18.816 | 35.797 | 16.668 |  | 38.9236 | -0.2 | 4.1
| 3.0639 | 300.947 | 298.742 | 67.382 | 18.819 | 35.803 | 16.67 |  | 38.9444 | -0.3 | 4.1
| 3.0653 | 301.244 | 298.697 | 67.404 | 18.816 | 35.814 | 16.672 |  | 38.9653 | -0.1 | 4.1
| 3.0667 | 300.909 | 298.649 | 67.405 | 18.818 | 35.826 | 16.677 |  | 38.9861 | -0.2 | 4.1
| 3.0681 | 301.235 | 298.243 | 67.408 | 18.819 | 35.83 | 16.675 |  | 39.0069 | -0.2 | 4.1
| 3.0694 | 300.816 | 298.941 | 67.415 | 18.82 | 35.836 | 16.677 |  | 39.0278 | -0.1 | 4.1
| 3.0708 | 300.782 | 298.588 | 67.417 | 18.821 | 35.836 | 16.675 |  | 39.0486 | -0.2 | 4.1
| 3.0722 | 300.739 | 298.79 | 67.42 | 18.821 | 35.841 | 16.679 |  | 39.0694 | -0.1 | 4.1
| 3.0736 | 301.486 | 298.56 | 67.422 | 18.825 | 35.84 | 16.68 |  | 39.0903 | -0.1 | 4.1
| 3.075 | 301.052 | 299.297 | 67.436 | 18.828 | 35.851 | 16.68 |  | 39.1111 | -0.1 | 4.1
| 3.0764 | 301.817 | 298.545 | 67.448 | 18.828 | 35.861 | 16.682 |  | 39.1319 | -0.1 | 4.1
| 3.0778 | 301.775 | 298.94 | 67.456 | 18.831 | 35.863 | 16.684 |  | 39.1528 | 0 | 4.1
| 3.0792 | 301.657 | 298.836 | 67.47 | 18.83 | 35.877 | 16.685 |  | 39.1736 | 0 | 4.1
| 3.0806 | 301.027 | 298.828 | 67.475 | 18.832 | 35.88 | 16.686 |  | 39.1944 | 0 | 4.1
| 3.0819 | 301.585 | 298.9 | 67.476 | 18.834 | 35.88 | 16.689 |  | 39.2153 | 0 | 4.1
| 3.0833 | 301.054 | 299.085 | 67.486 | 18.838 | 35.882 | 16.69 |  | 39.2361 | 0 | 4.1
| 3.0847 | 301.679 | 298.593 | 67.49 | 18.837 | 35.888 | 16.691 |  | 39.2569 | 0 | 4.1
| 3.0861 | 301.282 | 299.439 | 67.505 | 18.839 | 35.898 | 16.69 |  | 39.2778 | 0 | 4.1
| 3.0875 | 302.034 | 298.72 | 67.513 | 18.838 | 35.908 | 16.696 |  | 39.2986 | 0 | 4.1
| 3.0889 | 302.298 | 299.159 | 67.524 | 18.839 | 35.91 | 16.696 |  | 39.3194 | 0 | 4.1
| 3.0903 | 302.386 | 299.384 | 67.544 | 18.845 | 35.92 | 16.695 |  | 39.3403 | -0.1 | 4.1
| 3.0917 | 301.938 | 299.694 | 67.558 | 18.845 | 35.931 | 16.698 |  | 39.3611 | 0 | 4.1
| 3.0931 | 301.608 | 299.772 | 67.562 | 18.845 | 35.933 | 16.703 |  | 39.3819 | 0 | 4.1
| 3.0944 | 301.6 | 298.6 | 67.57 | 18.85 | 35.936 | 16.7 |  | 39.4028 | 0 | 4.1
| 3.0958 | 301.492 | 299.46 | 67.574 | 18.849 | 35.937 | 16.705 |  | 39.4236 | 0 | 4.1
| 3.0972 | 302.022 | 299.481 | 67.586 | 18.854 | 35.944 | 16.705 |  | 39.4444 | -0.1 | 4.1
| 3.0986 | 302.314 | 299.343 | 67.597 | 18.855 | 35.954 | 16.704 |  | 39.4653 | 0 | 4.1
| 3.1 | 302.106 | 299.35 | 67.605 | 18.856 | 35.955 | 16.707 |  | 39.4861 | 0 | 4.1
| 3.1014 | 301.509 | 299.658 | 67.613 | 18.859 | 35.954 | 16.707 |  | 39.5069 | -0.1 | 4.1
| 3.1028 | 302.162 | 299.743 | 67.626 | 18.863 | 35.96 | 16.71 |  | 39.5278 | 0.1 | 4.1
| 3.1042 | 302.468 | 299.835 | 67.639 | 18.861 | 35.972 | 16.715 |  | 39.5486 | 0.1 | 4.1
| 3.1056 | 302.913 | 299.583 | 67.653 | 18.863 | 35.977 | 16.71 |  | 39.5694 | 0.1 | 4.1
| 3.1069 | 302.057 | 300.238 | 67.665 | 18.865 | 35.98 | 16.714 |  | 39.5903 | 0.1 | 4.1
| 3.1083 | 301.875 | 300.215 | 67.672 | 18.869 | 35.988 | 16.718 |  | 39.6111 | 0.1 | 4
| 3.1097 | 302.705 | 299.492 | 67.685 | 18.87 | 35.993 | 16.72 |  | 39.6319 | 0.1 | 4
| 3.1111 | 302.95 | 299.996 | 67.697 | 18.874 | 36.002 | 16.72 |  | 39.6528 | 0.1 | 4
| 3.1125 | 302.266 | 300.115 | 67.717 | 18.872 | 36.011 | 16.72 |  | 39.6736 | 0.1 | 4
| 3.1139 | 302.847 | 300.671 | 67.732 | 18.877 | 36.019 | 16.723 |  | 39.6944 | 0.1 | 4
| 3.1153 | 302.707 | 300.498 | 67.744 | 18.881 | 36.024 | 16.728 |  | 39.7153 | 0.1 | 4
| 3.1167 | 302.655 | 301.026 | 67.758 | 18.881 | 36.033 | 16.729 |  | 39.7361 | 0.1 | 4
| 3.1181 | 303.551 | 300.369 | 67.778 | 18.881 | 36.044 | 16.731 |  | 39.7569 | 0.1 | 4
| 3.1194 | 303.103 | 300.69 | 67.797 | 18.886 | 36.051 | 16.728 |  | 39.7778 | 0.1 | 4
| 3.1208 | 301.958 | 299.504 | 67.8 | 18.888 | 36.05 | 16.732 |  | 39.7986 | 0.2 | 4
| 3.1222 | 302.204 | 300.387 | 67.801 | 18.887 | 36.049 | 16.735 |  | 39.8194 | 0.1 | 4
| 3.1236 | 301.945 | 300.127 | 67.806 | 18.891 | 36.051 | 16.738 |  | 39.8403 | 0.1 | 4
| 3.125 | 302.07 | 299.577 | 67.811 | 18.893 | 36.053 | 16.737 |  | 39.8611 | 0.1 | 4
| 3.1264 | 301.668 | 299.927 | 67.817 | 18.896 | 36.051 | 16.739 |  | 39.8819 | 0.1 | 4
| 3.1278 | 302.659 | 299.544 | 67.821 | 18.898 | 36.047 | 16.746 |  | 39.9028 | 0.1 | 4
| 3.1292 | 302.857 | 299.819 | 67.826 | 18.898 | 36.053 | 16.744 |  | 39.9236 | 0.1 | 4
| 3.1306 | 302.429 | 300.598 | 67.849 | 18.906 | 36.064 | 16.746 |  | 39.9444 | 0 | 4
| 3.1319 | 303.103 | 299.853 | 67.861 | 18.907 | 36.071 | 16.751 |  | 39.9653 | 0 | 4
| 3.1333 | 302.595 | 300.593 | 67.87 | 18.907 | 36.072 | 16.746 |  | 39.9861 | 0 | 4
| 3.1347 | 302.966 | 299.689 | 67.873 | 18.914 | 36.075 | 16.752 |  | 40.0069 | 0 | 4
| 3.1361 | 302.568 | 300.119 | 67.886 | 18.912 | 36.082 | 16.753 |  | 40.0278 | 0.1 | 4
| 3.1375 | 302.972 | 300.075 | 67.897 | 18.915 | 36.085 | 16.754 |  | 40.0486 | 0 | 4
| 3.1389 | 302.95 | 299.8 | 67.904 | 18.914 | 36.092 | 16.76 |  | 40.0694 | 0 | 4
| 3.1403 | 302.383 | 300.633 | 67.912 | 18.917 | 36.091 | 16.762 |  | 40.0903 | 0 | 4
| 3.1417 | 302.51 | 300.381 | 67.919 | 18.921 | 36.093 | 16.759 |  | 40.1111 | 0 | 4
| 3.1431 | 302.686 | 300.342 | 67.928 | 18.921 | 36.098 | 16.759 |  | 40.1319 | -0.1 | 4
| 3.1444 | 302.708 | 300.955 | 67.939 | 18.93 | 36.112 | 16.762 |  | 40.1528 | -0.1 | 4
| 3.1458 | 302.647 | 300.689 | 67.947 | 18.932 | 36.106 | 16.767 |  | 40.1736 | -0.2 | 4
| 3.1472 | 303.359 | 300.491 | 67.964 | 18.931 | 36.113 | 16.769 |  | 40.1944 | -0.2 | 4
| 3.1486 | 303.003 | 300.766 | 67.969 | 18.932 | 36.124 | 16.772 |  | 40.2153 | -0.2 | 4
| 3.15 | 303.78 | 300.459 | 67.981 | 18.937 | 36.131 | 16.773 |  | 40.2361 | -0.2 | 4
| 3.1514 | 303.623 | 300.539 | 67.994 | 18.936 | 36.137 | 16.776 |  | 40.2569 | -0.2 | 4
| 3.1528 | 303.225 | 300.074 | 68.007 | 18.939 | 36.136 | 16.78 |  | 40.2778 | -0.2 | 4
| 3.1542 | 303.426 | 300.326 | 68.017 | 18.942 | 36.144 | 16.78 |  | 40.2986 | -0.2 | 4
| 3.1556 | 303.03 | 300.522 | 68.024 | 18.945 | 36.145 | 16.78 |  | 40.3194 | -0.1 | 4
| 3.1569 | 302.899 | 300.874 | 68.026 | 18.948 | 36.15 | 16.782 |  | 40.3403 | -0.2 | 4
| 3.1583 | 303.621 | 300.473 | 68.037 | 18.946 | 36.154 | 16.786 |  | 40.3611 | -0.2 | 4
| 3.1597 | 302.924 | 301.047 | 68.051 | 18.951 | 36.159 | 16.783 |  | 40.3819 | -0.2 | 4
| 3.1611 | 302.886 | 300.881 | 68.062 | 18.952 | 36.161 | 16.786 |  | 40.4028 | -0.2 | 4
| 3.1625 | 302.967 | 300.834 | 68.066 | 18.959 | 36.165 | 16.791 |  | 40.4236 | -0.3 | 4
| 3.1639 | 302.586 | 300.859 | 68.072 | 18.957 | 36.166 | 16.793 |  | 40.4444 | -0.3 | 4
| 3.1653 | 302.96 | 300.176 | 68.078 | 18.959 | 36.166 | 16.79 |  | 40.4653 | -0.3 | 4
| 3.1667 | 303.453 | 300.424 | 68.085 | 18.964 | 36.169 | 16.794 |  | 40.4861 | -0.3 | 4
| 3.1681 | 303.178 | 300.476 | 68.094 | 18.964 | 36.172 | 16.798 |  | 40.5069 | -0.4 | 4
| 3.1694 | 303.055 | 300.145 | 68.098 | 18.965 | 36.176 | 16.798 |  | 40.5278 | -0.4 | 4
| 3.1708 | 303.253 | 300.538 | 68.108 | 18.969 | 36.181 | 16.802 |  | 40.5486 | -0.3 | 4
| 3.1722 | 303.209 | 300.848 | 68.115 | 18.972 | 36.187 | 16.798 |  | 40.5694 | -0.3 | 4
| 3.1736 | 303.456 | 301.056 | 68.126 | 18.977 | 36.196 | 16.805 |  | 40.5903 | -0.3 | 4
| 3.175 | 303.253 | 301.234 | 68.142 | 18.978 | 36.203 | 16.807 |  | 40.6111 | -0.3 | 4
| 3.1764 | 303.664 | 300.574 | 68.15 | 18.979 | 36.208 | 16.81 |  | 40.6319 | -0.2 | 3.9
| 3.1778 | 302.951 | 300.52 | 68.16 | 18.983 | 36.209 | 16.811 |  | 40.6528 | -0.2 | 3.9
| 3.1792 | 303.499 | 300.565 | 68.162 | 18.982 | 36.213 | 16.814 |  | 40.6736 | -0.2 | 3.9
| 3.1806 | 302.95 | 301.166 | 68.174 | 18.983 | 36.221 | 16.813 |  | 40.6944 | -0.1 | 3.9
| 3.1819 | 303.479 | 300.301 | 68.188 | 18.989 | 36.227 | 16.815 |  | 40.7153 | -0.1 | 3.9
| 3.1833 | 302.61 | 300.918 | 68.189 | 18.989 | 36.228 | 16.819 |  | 40.7361 | -0.1 | 3.9
| 3.1847 | 302.976 | 300.735 | 68.195 | 18.991 | 36.224 | 16.821 |  | 40.7569 | 0 | 3.9
| 3.1861 | 303.126 | 300.22 | 68.193 | 18.992 | 36.224 | 16.821 |  | 40.7778 | 0 | 3.9
| 3.1875 | 302.808 | 300.746 | 68.206 | 18.998 | 36.229 | 16.823 |  | 40.7986 | -0.1 | 3.9
| 3.1889 | 302.922 | 300.94 | 68.21 | 18.999 | 36.231 | 16.827 |  | 40.8194 | 0 | 3.9
| 3.1903 | 302.754 | 300.874 | 68.216 | 19.003 | 36.241 | 16.826 |  | 40.8403 | 0 | 3.9
| 3.1917 | 302.984 | 301.252 | 68.225 | 19.006 | 36.238 | 16.832 |  | 40.8611 | 0 | 3.9
| 3.1931 | 303.696 | 300.855 | 68.236 | 19.007 | 36.247 | 16.836 |  | 40.8819 | 0 | 3.9
| 3.1944 | 303.355 | 301.289 | 68.246 | 19.005 | 36.255 | 16.833 |  | 40.9028 | -0.1 | 3.9
| 3.1958 | 303.607 | 300.406 | 68.252 | 19.01 | 36.259 | 16.836 |  | 40.9236 | 0 | 3.9
| 3.1972 | 303.282 | 300.717 | 68.262 | 19.01 | 36.261 | 16.835 |  | 40.9444 | -0.1 | 3.9
| 3.1986 | 302.963 | 300.918 | 68.268 | 19.017 | 36.273 | 16.841 |  | 40.9653 | -0.1 | 3.9
| 3.2 | 302.683 | 301.048 | 68.279 | 19.022 | 36.274 | 16.844 |  | 40.9861 | -0.2 | 3.9
| 3.2014 | 303.358 | 300.447 | 68.275 | 19.031 | 36.277 | 16.844 |  | 41.0069 | -0.1 | 3.9
| 3.2028 | 303.085 | 300.316 | 68.279 | 19.028 | 36.274 | 16.846 |  | 41.0278 | -0.1 | 3.9
| 3.2042 | 302.89 | 300.093 | 68.284 | 19.027 | 36.276 | 16.845 |  | 41.0486 | -0.1 | 3.9
| 3.2056 | 302.564 | 300.455 | 68.28 | 19.027 | 36.269 | 16.847 |  | 41.0694 | -0.1 | 3.9
| 3.2069 | 302.75 | 299.908 | 68.276 | 19.031 | 36.27 | 16.853 |  | 41.0903 | 0 | 3.9
| 3.2083 | 302.251 | 300.091 | 68.278 | 19.035 | 36.263 | 16.85 |  | 41.1111 | 0 | 3.9
| 3.2097 | 302.063 | 300.579 | 68.276 | 19.034 | 36.26 | 16.852 |  | 41.1319 | 0 | 3.9
| 3.2111 | 302.079 | 300.387 | 68.277 | 19.033 | 36.26 | 16.858 |  | 41.1528 | 0 | 3.9
| 3.2125 | 302.5 | 299.676 | 68.276 | 19.038 | 36.262 | 16.857 |  | 41.1736 | 0 | 3.9
| 3.2139 | 302.759 | 299.632 | 68.272 | 19.037 | 36.256 | 16.861 |  | 41.1944 | 0 | 3.9
| 3.2153 | 302.171 | 300.103 | 68.272 | 19.042 | 36.259 | 16.86 |  | 41.2153 | 0.1 | 3.9
| 3.2167 | 301.969 | 300.3 | 68.274 | 19.041 | 36.257 | 16.866 |  | 41.2361 | 0.1 | 3.9
| 3.2181 | 302.631 | 299.453 | 68.273 | 19.046 | 36.263 | 16.865 |  | 41.2569 | 0.1 | 3.9
| 3.2194 | 301.746 | 300.057 | 68.267 | 19.048 | 36.259 | 16.867 |  | 41.2778 | 0.1 | 3.9
| 3.2208 | 301.693 | 300.207 | 68.268 | 19.051 | 36.263 | 16.865 |  | 41.2986 | 0.1 | 3.9
| 3.2222 | 302.514 | 299.872 | 68.261 | 19.055 | 36.257 | 16.871 |  | 41.3194 | 0.2 | 3.9
| 3.2236 | 302.771 | 299.62 | 68.265 | 19.053 | 36.263 | 16.87 |  | 41.3403 | 0.2 | 3.9
| 3.225 | 302.046 | 300.378 | 68.266 | 19.055 | 36.264 | 16.874 |  | 41.3611 | 0.2 | 3.9
| 3.2264 | 302.355 | 299.537 | 68.266 | 19.055 | 36.257 | 16.875 |  | 41.3819 | 0.2 | 3.9
| 3.2278 | 301.361 | 299.601 | 68.261 | 19.06 | 36.262 | 16.881 |  | 41.4028 | 0.2 | 3.9
| 3.2292 | 301.838 | 299.24 | 68.259 | 19.061 | 36.257 | 16.881 |  | 41.4236 | 0.2 | 3.9
| 3.2306 | 301.12 | 299.408 | 68.247 | 19.058 | 36.254 | 16.882 |  | 41.4444 | 0.3 | 3.9
| 3.2319 | 302.076 | 299.308 | 68.244 | 19.063 | 36.251 | 16.883 |  | 41.4653 | 0.3 | 3.9
| 3.2333 | 301.535 | 299.683 | 68.242 | 19.07 | 36.254 | 16.886 |  | 41.4861 | 0.3 | 3.9
| 3.2347 | 301.539 | 299.652 | 68.236 | 19.067 | 36.252 | 16.887 |  | 41.5069 | 0.3 | 3.9
| 3.2361 | 301.384 | 299.395 | 68.231 | 19.07 | 36.249 | 16.89 |  | 41.5278 | 0.3 | 3.9
| 3.2375 | 301.627 | 299.315 | 68.228 | 19.071 | 36.247 | 16.891 |  | 41.5486 | 0.3 | 3.9
| 3.2389 | 302.3 | 299.033 | 68.219 | 19.076 | 36.244 | 16.893 |  | 41.5694 | 0.3 | 3.9
| 3.2403 | 302.04 | 298.618 | 68.218 | 19.073 | 36.242 | 16.894 |  | 41.5903 | 0.3 | 3.9
| 3.2417 | 301.782 | 298.628 | 68.21 | 19.082 | 36.239 | 16.893 |  | 41.6111 | 0.4 | 3.9
| 3.2431 | 301.869 | 299.621 | 68.208 | 19.085 | 36.252 | 16.899 |  | 41.6319 | 0.4 | 3.9
| 3.2444 | 301.946 | 300.004 | 68.211 | 19.085 | 36.242 | 16.902 |  | 41.6528 | 0.3 | 3.9
| 3.2458 | 301.518 | 299.616 | 68.214 | 19.086 | 36.253 | 16.902 |  | 41.6736 | 0.4 | 3.8
| 3.2472 | 302.093 | 298.802 | 68.206 | 19.084 | 36.252 | 16.9 |  | 41.6944 | 0.4 | 3.8
| 3.2486 | 301.699 | 299.538 | 68.205 | 19.083 | 36.252 | 16.909 |  | 41.7153 | 0.4 | 3.8
| 3.25 | 301.882 | 298.859 | 68.198 | 19.084 | 36.25 | 16.906 |  | 41.7361 | 0.4 | 3.8
| 3.2514 | 301.47 | 299.352 | 68.192 | 19.088 | 36.252 | 16.907 |  | 41.7569 | 0.4 | 3.8
| 3.2528 | 302.435 | 299.543 | 68.193 | 19.089 | 36.256 | 16.914 |  | 41.7847 | 0.4 | 3.8
| 3.2542 | 302.122 | 299.298 | 68.198 | 19.09 | 36.256 | 16.909 |  | 41.8056 | 0.4 | 3.8
| 3.2556 | 302.321 | 299.198 | 68.201 | 19.095 | 36.261 | 16.911 |  | 41.8264 | 0.4 | 3.8
| 3.2569 | 301.773 | 299.234 | 68.199 | 19.095 | 36.27 | 16.914 |  | 41.8472 | 0.4 | 3.8
| 3.2583 | 301.156 | 299.439 | 68.199 | 19.093 | 36.264 | 16.92 |  | 41.8681 | 0.4 | 3.8
| 3.2597 | 301.433 | 299.338 | 68.195 | 19.096 | 36.266 | 16.92 |  | 41.8889 | 0.5 | 3.8
| 3.2611 | 301.405 | 299.653 | 68.189 | 19.099 | 36.269 | 16.922 |  | 41.9097 | 0.5 | 3.8
| 3.2625 | 300.605 | 298.833 | 68.186 | 19.108 | 36.266 | 16.922 |  | 41.9306 | 0.5 | 3.8
| 3.2639 | 300.476 | 297.857 | 68.165 | 19.106 | 36.257 | 16.925 |  | 41.9514 | 0.5 | 3.8
| 3.2653 | 300.832 | 297.856 | 68.149 | 19.109 | 36.243 | 16.925 |  | 41.9722 | 0.5 | 3.8
| 3.2667 | 300.866 | 297.802 | 68.133 | 19.109 | 36.237 | 16.926 |  | 41.9931 | 0.5 | 3.8
| 3.2681 | 300.967 | 297.888 | 68.119 | 19.108 | 36.224 | 16.925 |  | 42.0139 | 0.5 | 3.8
| 3.2694 | 300.707 | 297.517 | 68.108 | 19.108 | 36.221 | 16.928 |  | 42.0347 | 0.5 | 3.8
| 3.2708 | 299.914 | 298.176 | 68.101 | 19.111 | 36.213 | 16.93 |  | 42.0556 | 0.5 | 3.8
| 3.2722 | 300.569 | 297.669 | 68.086 | 19.113 | 36.206 | 16.931 |  | 42.0764 | 0.5 | 3.8
| 3.2736 | 299.768 | 297.539 | 68.068 | 19.112 | 36.199 | 16.931 |  | 42.0972 | 0.5 | 3.8
| 3.275 | 299.451 | 297.561 | 68.048 | 19.114 | 36.193 | 16.934 |  | 42.1181 | 0.5 | 3.8
| 3.2764 | 299.186 | 297.621 | 68.034 | 19.12 | 36.185 | 16.937 |  | 42.1389 | 0.5 | 3.8
| 3.2778 | 299.936 | 297.787 | 68.022 | 19.116 | 36.183 | 16.939 |  | 42.1597 | 0.5 | 3.8
| 3.2792 | 299.863 | 297.81 | 68.011 | 19.122 | 36.177 | 16.945 |  | 42.1806 | 0.5 | 3.8
| 3.2806 | 299.742 | 298.049 | 68 | 19.122 | 36.171 | 16.94 |  | 42.2014 | 0.5 | 3.8
| 3.2819 | 300.457 | 297.183 | 67.987 | 19.118 | 36.17 | 16.944 |  | 42.2222 | 0.5 | 3.8
| 3.2833 | 299.628 | 297.805 | 67.98 | 19.125 | 36.173 | 16.946 |  | 42.2431 | 0.5 | 3.8
| 3.2847 | 299.424 | 297.515 | 67.964 | 19.124 | 36.166 | 16.945 |  | 42.2639 | 0.6 | 3.8
| 3.2861 | 299.248 | 296.938 | 67.944 | 19.127 | 36.157 | 16.948 |  | 42.2847 | 0.5 | 3.8
| 3.2875 | 301.607 | 298.964 | 67.94 | 19.125 | 36.16 | 16.951 |  | 42.3056 | 0.5 | 3.8
| 3.2889 | 302.077 | 300.109 | 67.974 | 19.127 | 36.185 | 16.948 |  | 42.3264 | 0.5 | 3.8
| 3.2903 | 302.261 | 300.373 | 67.995 | 19.128 | 36.211 | 16.952 |  | 42.3472 | 0.6 | 3.8
| 3.2917 | 302.465 | 299.689 | 68.016 | 19.134 | 36.228 | 16.948 |  | 42.3681 | 0.6 | 3.8
| 3.2931 | 302.18 | 300.449 | 68.026 | 19.129 | 36.248 | 16.954 |  | 42.3889 | 0.6 | 3.8
| 3.2944 | 302.657 | 299.395 | 68.038 | 19.129 | 36.259 | 16.952 |  | 42.4097 | 0.6 | 3.8
| 3.2958 | 302.097 | 299.817 | 68.045 | 19.139 | 36.27 | 16.957 |  | 42.4306 | 0.6 | 3.8
| 3.2972 | 302.116 | 298.987 | 68.052 | 19.136 | 36.276 | 16.963 |  | 42.4514 | 0.6 | 3.8
| 3.2986 | 302.041 | 299.243 | 68.056 | 19.136 | 36.278 | 16.961 |  | 42.4722 | 0.6 | 3.8
| 3.3 | 301.674 | 299.724 | 68.056 | 19.135 | 36.276 | 16.959 |  | 42.4931 | 0.7 | 3.8
| 3.3014 | 302.251 | 299.115 | 68.066 | 19.136 | 36.278 | 16.961 |  | 42.5139 | 0.7 | 3.8
| 3.3028 | 300.855 | 299.251 | 68.064 | 19.142 | 36.285 | 16.964 |  | 42.5347 | 0.7 | 3.8
| 3.3042 | 300.483 | 298.771 | 68.06 | 19.139 | 36.275 | 16.961 |  | 42.5556 | 0.6 | 3.8
| 3.3056 | 300.704 | 298.983 | 68.048 | 19.147 | 36.277 | 16.965 |  | 42.5764 | 0.6 | 3.8
| 3.3069 | 301.294 | 298.365 | 68.047 | 19.145 | 36.271 | 16.967 |  | 42.5972 | 0.6 | 3.8
| 3.3083 | 301.131 | 298.491 | 68.036 | 19.146 | 36.263 | 16.964 |  | 42.6181 | 0.6 | 3.8
| 3.3097 | 301.213 | 298.905 | 68.035 | 19.148 | 36.264 | 16.968 |  | 42.6389 | 0.6 | 3.8
| 3.3111 | 300.731 | 298.876 | 68.03 | 19.15 | 36.264 | 16.965 |  | 42.6597 | 0.7 | 3.8
| 3.3125 | 300.682 | 298.723 | 68.025 | 19.151 | 36.262 | 16.974 |  | 42.6806 | 0.7 | 3.8
| 3.3139 | 300.942 | 298.94 | 68.024 | 19.15 | 36.253 | 16.975 |  | 42.7014 | 0.6 | 3.8
| 3.3153 | 301.612 | 298.429 | 68.027 | 19.152 | 36.262 | 16.974 |  | 42.7222 | 0.6 | 3.8
| 3.3167 | 301.548 | 298.297 | 68.03 | 19.156 | 36.268 | 16.978 |  | 42.7431 | 0.6 | 3.8
| 3.3181 | 300.934 | 298.753 | 68.023 | 19.159 | 36.263 | 16.977 |  | 42.7639 | 0.6 | 3.8
| 3.3194 | 300.649 | 298.776 | 68.027 | 19.161 | 36.264 | 16.978 |  | 42.7847 | 0.6 | 3.8
| 3.3208 | 301.491 | 298.216 | 68.02 | 19.156 | 36.261 | 16.979 |  | 42.8056 | 0.7 | 3.8
| 3.3222 | 301.304 | 298.52 | 68.017 | 19.162 | 36.256 | 16.98 |  | 42.8264 | 0.7 | 3.8
| 3.3236 | 300.948 | 297.844 | 68.015 | 19.159 | 36.258 | 16.985 |  | 42.8472 | 0.7 | 3.8
| 3.325 | 300.82 | 298.121 | 68.006 | 19.165 | 36.249 | 16.982 |  | 42.8681 | 0.7 | 3.7
| 3.3264 | 300.461 | 297.771 | 68.003 | 19.165 | 36.257 | 16.983 |  | 42.8889 | 0.7 | 3.7
| 3.3278 | 300.583 | 297.273 | 67.99 | 19.162 | 36.245 | 16.987 |  | 42.9097 | 0.7 | 3.7
| 3.3292 | 300.831 | 297.945 | 67.984 | 19.169 | 36.241 | 16.986 |  | 42.9306 | 0.8 | 3.7
| 3.3306 | 300.205 | 298.337 | 67.98 | 19.167 | 36.239 | 16.991 |  | 42.9514 | 0.8 | 3.7
| 3.3319 | 300.731 | 297.681 | 67.975 | 19.165 | 36.243 | 16.987 |  | 42.9722 | 0.8 | 3.7
| 3.3333 | 300.381 | 297.305 | 67.964 | 19.173 | 36.24 | 16.988 |  | 42.9931 | 0.8 | 3.7
| 3.3347 | 300.193 | 297.302 | 67.952 | 19.17 | 36.23 | 16.988 |  | 43.0139 | 0.8 | 3.7
| 3.3361 | 299.605 | 296.507 | 67.94 | 19.174 | 36.218 | 16.99 |  | 43.0347 | 0.8 | 3.7
| 3.3375 | 300.136 | 297.125 | 67.928 | 19.172 | 36.215 | 16.994 |  | 43.0556 | 0.8 | 3.7
| 3.3389 | 299.673 | 297.556 | 67.919 | 19.172 | 36.206 | 16.995 |  | 43.0764 | 0.8 | 3.7
| 3.3403 | 299.768 | 297.361 | 67.903 | 19.176 | 36.202 | 16.995 |  | 43.0972 | 0.8 | 3.7
| 3.3417 | 299.499 | 297.302 | 67.903 | 19.175 | 36.204 | 16.998 |  | 43.1181 | 0.8 | 3.7
| 3.3431 | 299.137 | 297.056 | 67.884 | 19.177 | 36.196 | 16.999 |  | 43.1389 | 0.8 | 3.7
| 3.3444 | 299.077 | 297.106 | 67.869 | 19.178 | 36.194 | 16.998 |  | 43.1597 | 0.8 | 3.7
| 3.3458 | 299.589 | 296.487 | 67.848 | 19.177 | 36.183 | 17 |  | 43.1806 | 0.8 | 3.7
| 3.3472 | 299.139 | 295.765 | 67.838 | 19.181 | 36.173 | 16.999 |  | 43.2014 | 0.8 | 3.7
| 3.3486 | 299.615 | 296.745 | 67.818 | 19.181 | 36.166 | 17.003 |  | 43.2222 | 0.8 | 3.7
| 3.35 | 300.958 | 299.161 | 67.813 | 19.185 | 36.166 | 17.004 |  | 43.2431 | 0.8 | 3.7
| 3.3514 | 301.241 | 298.15 | 67.831 | 19.182 | 36.186 | 17.005 |  | 43.2639 | 0.7 | 3.7
| 3.3528 | 301.033 | 297.783 | 67.834 | 19.184 | 36.199 | 17.003 |  | 43.2847 | 0.8 | 3.7
| 3.3542 | 300.566 | 298.746 | 67.842 | 19.183 | 36.207 | 17.007 |  | 43.3056 | 0.8 | 3.7
| 3.3556 | 300.856 | 298.434 | 67.847 | 19.181 | 36.215 | 17.013 |  | 43.3264 | 0.8 | 3.7
| 3.3569 | 300.722 | 298.811 | 67.85 | 19.187 | 36.224 | 17.008 |  | 43.3472 | 0.8 | 3.7
| 3.3583 | 301.322 | 298.903 | 67.858 | 19.188 | 36.233 | 17.01 |  | 43.3681 | 0.8 | 3.7
| 3.3597 | 301.706 | 299.024 | 67.873 | 19.191 | 36.244 | 17.012 |  | 43.3889 | 0.8 | 3.7
| 3.3611 | 301.004 | 299.206 | 67.882 | 19.189 | 36.254 | 17.012 |  | 43.4097 | 0.8 | 3.7
| 3.3625 | 301.457 | 298.216 | 67.888 | 19.189 | 36.259 | 17.013 |  | 43.4306 | 0.8 | 3.7
| 3.3639 | 301.166 | 298.599 | 67.889 | 19.191 | 36.265 | 17.012 |  | 43.4514 | 0.8 | 3.7
| 3.3653 | 301.551 | 298.457 | 67.89 | 19.195 | 36.267 | 17.015 |  | 43.4722 | 0.8 | 3.7
| 3.3667 | 301.328 | 298.277 | 67.888 | 19.194 | 36.265 | 17.014 |  | 43.4931 | 0.8 | 3.7
| 3.3681 | 300.971 | 298.239 | 67.888 | 19.197 | 36.267 | 17.02 |  | 43.5139 | 0.8 | 3.7
| 3.3694 | 301.153 | 297.873 | 67.89 | 19.198 | 36.266 | 17.016 |  | 43.5347 | 0.8 | 3.7
| 3.3708 | 300.55 | 297.589 | 67.89 | 19.202 | 36.264 | 17.024 |  | 43.5556 | 0.8 | 3.7
| 3.3722 | 300.233 | 298.134 | 67.884 | 19.199 | 36.259 | 17.024 |  | 43.5764 | 0.8 | 3.7
| 3.3736 | 301.091 | 297.946 | 67.88 | 19.202 | 36.264 | 17.025 |  | 43.5972 | 0.8 | 3.7
| 3.375 | 301.05 | 297.855 | 67.887 | 19.198 | 36.259 | 17.026 |  | 43.6181 | 0.8 | 3.7
| 3.3764 | 301.311 | 298.162 | 67.879 | 19.204 | 36.261 | 17.026 |  | 43.6389 | 0.8 | 3.7
| 3.3778 | 300.548 | 298.61 | 67.885 | 19.206 | 36.263 | 17.025 |  | 43.6597 | 0.9 | 3.7
| 3.3792 | 300.924 | 297.735 | 67.885 | 19.209 | 36.266 | 17.027 |  | 43.6806 | 0.9 | 3.7
| 3.3806 | 300.468 | 297.961 | 67.879 | 19.209 | 36.262 | 17.026 |  | 43.7014 | 0.9 | 3.7
| 3.3819 | 300.36 | 297.489 | 67.876 | 19.213 | 36.258 | 17.027 |  | 43.7222 | 0.9 | 3.7
| 3.3833 | 300.012 | 297.985 | 67.873 | 19.209 | 36.256 | 17.032 |  | 43.8333 | 0.9 | 3.7
| 3.3847 | 300.312 | 297.617 | 67.866 | 19.214 | 36.251 | 17.033 |  | 43.8542 | 0.9 | 3.7
| 3.3861 | 300.017 | 297.102 | 67.859 | 19.212 | 36.242 | 17.032 |  | 43.875 | 1 | 3.7
| 3.3875 | 300.243 | 297.192 | 67.848 | 19.214 | 36.24 | 17.034 |  | 43.8958 | 1 | 3.7
| 3.3889 | 300.312 | 298.392 | 67.849 | 19.212 | 36.236 | 17.032 |  | 43.9167 | 1 | 3.7
| 3.3903 | 299.689 | 297.825 | 67.848 | 19.218 | 36.241 | 17.036 |  | 43.9375 | 1.1 | 3.7
| 3.3917 | 300.064 | 298.064 | 67.842 | 19.215 | 36.241 | 17.033 |  | 43.9583 | 1.1 | 3.7
| 3.3931 | 299.925 | 296.676 | 67.837 | 19.219 | 36.238 | 17.033 |  | 43.9792 | 1.1 | 3.7
| 3.3944 | 299.121 | 296.175 | 67.82 | 19.217 | 36.229 | 17.039 |  | 44 | 1.2 | 3.7
| 3.3958 | 299.867 | 296.453 | 67.803 | 19.223 | 36.223 | 17.038 |  | 44.0208 | 1.2 | 3.7
| 3.3972 | 299.558 | 297.87 | 67.798 | 19.219 | 36.219 | 17.042 |  | 44.0417 | 1.2 | 3.7
| 3.3986 | 299.582 | 297.417 | 67.792 | 19.224 | 36.218 | 17.043 |  | 44.0625 | 1.2 | 3.7
| 3.4 | 298.94 | 297.233 | 67.78 | 19.225 | 36.215 | 17.043 |  | 44.0833 | 1.2 | 3.7
| 3.4014 | 299.084 | 297.075 | 67.774 | 19.224 | 36.209 | 17.043 |  | 44.1042 | 1.3 | 3.7
| 3.4028 | 298.878 | 296.461 | 67.759 | 19.229 | 36.202 | 17.05 |  | 44.125 | 1.3 | 3.7
| 3.4042 | 298.813 | 297.029 | 67.746 | 19.228 | 36.194 | 17.045 |  | 44.1458 | 1.3 | 3.7
| 3.4056 | 299.243 | 295.966 | 67.735 | 19.228 | 36.188 | 17.047 |  | 44.1667 | 1.3 | 3.7
| 3.4069 | 299.168 | 296.916 | 67.73 | 19.23 | 36.19 | 17.049 |  | 44.1875 | 1.3 | 3.7
| 3.4083 | 298.695 | 296.918 | 67.716 | 19.229 | 36.185 | 17.046 |  | 44.2083 | 1.3 | 3.7
| 3.4097 | 298.827 | 296.541 | 67.704 | 19.231 | 36.178 | 17.054 |  | 44.2292 | 1.4 | 3.7
| 3.4111 | 299.027 | 296.477 | 67.697 | 19.23 | 36.182 | 17.051 |  | 44.25 | 1.4 | 3.7
| 3.4125 | 299.044 | 295.995 | 67.689 | 19.232 | 36.169 | 17.053 |  | 44.2708 | 1.5 | 3.7
| 3.4139 | 298.643 | 296.779 | 67.679 | 19.235 | 36.172 | 17.05 |  | 44.2917 | 1.5 | 3.7
| 3.4153 | 299.309 | 296.12 | 67.666 | 19.233 | 36.169 | 17.053 |  | 44.3125 | 1.6 | 3.7
| 3.4167 | 298.696 | 296.888 | 67.662 | 19.236 | 36.169 | 17.054 |  | 44.3333 | 1.6 | 3.7
| 3.4181 | 299.226 | 296.39 | 67.655 | 19.235 | 36.168 | 17.056 |  | 44.3542 | 1.7 | 3.7
| 3.4194 | 298.636 | 296.752 | 67.645 | 19.235 | 36.165 | 17.057 |  | 44.375 | 1.7 | 3.7
| 3.4208 | 298.484 | 296.17 | 67.628 | 19.241 | 36.159 | 17.057 |  | 44.3958 | 1.7 | 3.7
| 3.4222 | 298.273 | 296.559 | 67.615 | 19.238 | 36.156 | 17.058 |  | 44.4167 | 1.7 | 3.7
| 3.4236 | 298.068 | 296.136 | 67.6 | 19.239 | 36.15 | 17.058 |  | 44.4375 | 1.8 | 3.7
| 3.425 | 298.261 | 296.361 | 67.586 | 19.241 | 36.146 | 17.061 |  | 44.4583 | 1.8 | 3.7
| 3.4264 | 298.658 | 296.201 | 67.578 | 19.242 | 36.14 | 17.06 |  | 44.4792 | 1.8 | 3.7
| 3.4278 | 300.966 | 299.152 | 67.583 | 19.24 | 36.146 | 17.063 |  | 44.5 | 1.9 | 3.7
| 3.4292 | 302.301 | 299.476 | 67.622 | 19.241 | 36.184 | 17.061 |  | 44.5208 | 1.9 | 3.7
| 3.4306 | 301.682 | 299.742 | 67.668 | 19.24 | 36.215 | 17.064 |  | 44.5417 | 1.9 | 3.7
| 3.4319 | 302.258 | 299.188 | 67.691 | 19.243 | 36.239 | 17.061 |  | 44.5625 | 2 | 3.7
| 3.4333 | 302.09 | 298.942 | 67.708 | 19.245 | 36.261 | 17.066 |  | 44.5833 | 2 | 3.7
| 3.4347 | 302.287 | 298.973 | 67.729 | 19.244 | 36.277 | 17.065 |  | 44.6042 | 2 | 3.7
| 3.4361 | 301.378 | 298.841 | 67.736 | 19.244 | 36.282 | 17.065 |  | 44.625 | 2 | 3.7
| 3.4375 | 301.935 | 298.701 | 67.746 | 19.247 | 36.291 | 17.066 |  | 44.6458 | 2 | 3.7
| 3.4389 | 301.143 | 299.051 | 67.76 | 19.249 | 36.302 | 17.069 |  | 44.6667 | 1.9 | 3.7
| 3.4403 | 301.488 | 299.03 | 67.772 | 19.251 | 36.303 | 17.069 |  | 44.6875 | 1.9 | 3.7
| 3.4417 | 301.046 | 299.169 | 67.787 | 19.253 | 36.315 | 17.072 |  | 44.7083 | 1.9 | 3.7
| 3.4431 | 301.675 | 298.804 | 67.802 | 19.252 | 36.322 | 17.07 |  | 44.7292 | 1.9 | 3.7
| 3.4444 | 301.432 | 299.294 | 67.817 | 19.257 | 36.329 | 17.069 |  | 44.75 | 1.9 | 3.7
| 3.4458 | 301.506 | 298.628 | 67.823 | 19.258 | 36.33 | 17.069 |  | 44.7708 | 1.9 | 3.7
| 3.4472 | 302.002 | 298.872 | 67.835 | 19.255 | 36.336 | 17.074 |  | 44.7917 | 1.9 | 3.7
| 3.4486 | 301.333 | 299.299 | 67.846 | 19.259 | 36.336 | 17.072 |  | 44.8125 | 2 | 3.7
| 3.45 | 301.034 | 299.25 | 67.854 | 19.26 | 36.343 | 17.075 |  | 44.8333 | 2 | 3.7
| 3.4514 | 300.997 | 298.07 | 67.854 | 19.262 | 36.339 | 17.072 |  | 44.8542 | 2.1 | 3.7
| 3.4528 | 300.61 | 298.651 | 67.86 | 19.264 | 36.342 | 17.08 |  | 44.875 | 2.1 | 3.7
| 3.4542 | 301.111 | 298.417 | 67.865 | 19.268 | 36.339 | 17.079 |  | 44.8958 | 2 | 3.7
| 3.4556 | 300.915 | 298.746 | 67.869 | 19.265 | 36.343 | 17.079 |  | 44.9167 | 2 | 3.7
| 3.4569 | 301.99 | 299.54 | 67.879 | 19.266 | 36.341 | 17.081 |  | 44.9375 | 2 | 3.7
| 3.4583 | 299.578 | 297.718 | 67.872 | 19.269 | 36.332 | 17.082 |  | 44.9583 | 2 | 3.7
| 3.4597 | 300.733 | 297.788 | 67.864 | 19.272 | 36.321 | 17.079 |  | 44.9792 | 2 | 3.7
| 3.4611 | 300.477 | 298.699 | 67.863 | 19.272 | 36.322 | 17.083 |  | 45 | 2 | 3.7
| 3.4625 | 301.051 | 297.904 | 67.871 | 19.273 | 36.323 | 17.083 |  | 45.0208 | 2 | 3.7
| 3.4639 | 300.051 | 298.341 | 67.872 | 19.273 | 36.326 | 17.087 |  | 45.0417 | 2 | 3.7
| 3.4653 | 300.433 | 297.404 | 67.873 | 19.274 | 36.322 | 17.087 |  | 45.0625 | 2.1 | 3.7
| 3.4667 | 300.112 | 298.129 | 67.869 | 19.278 | 36.316 | 17.087 |  | 45.0833 | 2.2 | 3.7
| 3.4681 | 299.522 | 297.743 | 67.86 | 19.278 | 36.315 | 17.09 |  | 45.1042 | 2.2 | 3.7
| 3.4694 | 300.049 | 297.075 | 67.857 | 19.283 | 36.309 | 17.088 |  | 45.125 | 2.3 | 3.7
| 3.4708 | 299.586 | 297.657 | 67.848 | 19.285 | 36.301 | 17.091 |  | 45.1458 | 2.4 | 3.7
| 3.4722 | 299.221 | 297.557 | 67.842 | 19.282 | 36.3 | 17.091 |  | 45.1667 | 2.4 | 3.7
| 3.4736 | 299.624 | 297.338 | 67.832 | 19.285 | 36.293 | 17.093 |  | 45.1875 | 2.4 | 3.7
| 3.475 | 299.888 | 297.687 | 67.834 | 19.289 | 36.292 | 17.096 |  | 45.2083 | 2.5 | 3.7
| 3.4764 | 299.761 | 297.241 | 67.825 | 19.285 | 36.285 | 17.097 |  | 45.2292 | 2.5 | 3.7
| 3.4778 | 299.208 | 297.661 | 67.816 | 19.289 | 36.276 | 17.102 |  | 45.25 | 2.5 | 3.7
| 3.4792 | 299.758 | 297.409 | 67.814 | 19.289 | 36.281 | 17.099 |  | 45.2708 | 2.5 | 3.7
| 3.4806 | 299.413 | 297.757 | 67.811 | 19.29 | 36.281 | 17.1 |  | 45.2917 | 2.4 | 3.7
| 3.4819 | 300.17 | 297.255 | 67.808 | 19.293 | 36.278 | 17.101 |  | 45.3125 | 2.3 | 3.7
| 3.4833 | 299.508 | 297.27 | 67.804 | 19.295 | 36.279 | 17.101 |  | 45.3333 | 2.4 | 3.7
| 3.4847 | 299.495 | 297.382 | 67.798 | 19.291 | 36.276 | 17.105 |  | 45.3542 | 2.4 | 3.7
| 3.4861 | 299.11 | 297.276 | 67.787 | 19.296 | 36.272 | 17.104 |  | 45.375 | 2.4 | 3.7
| 3.4875 | 299.811 | 296.983 | 67.782 | 19.298 | 36.269 | 17.106 |  | 45.3958 | 2.4 | 3.7
| 3.4889 | 299.626 | 296.315 | 67.774 | 19.298 | 36.267 | 17.103 |  | 45.4167 | 2.5 | 3.7
| 3.4903 | 298.628 | 297.058 | 67.769 | 19.3 | 36.267 | 17.106 |  | 45.4375 | 2.5 | 3.7
| 3.4917 | 299.565 | 296.258 | 67.761 | 19.299 | 36.269 | 17.108 |  | 45.4583 | 2.5 | 3.7
| 3.4931 | 299.744 | 296.578 | 67.751 | 19.303 | 36.26 | 17.112 |  | 45.4792 | 2.5 | 3.7
| 3.4944 | 298.838 | 297.119 | 67.756 | 19.302 | 36.26 | 17.111 |  | 45.5 | 2.5 | 3.7
| 3.4958 | 299.212 | 297.481 | 67.747 | 19.305 | 36.256 | 17.112 |  | 45.5208 | 2.4 | 3.7
| 3.4972 | 298.996 | 296.798 | 67.741 | 19.305 | 36.258 | 17.112 |  | 45.5417 | 2.4 | 3.7
| 3.4986 | 298.869 | 297.171 | 67.733 | 19.306 | 36.256 | 17.113 |  | 45.5625 | 2.5 | 3.7
| 3.5 | 299.925 | 296.758 | 67.729 | 19.306 | 36.254 | 17.113 |  | 45.5833 | 2.5 | 3.7
| 3.5014 | 299.69 | 297.643 | 67.728 | 19.309 | 36.255 | 17.114 |  | 45.6042 | 2.5 | 3.7
| 3.5028 | 300.451 | 297.331 | 67.736 | 19.308 | 36.265 | 17.114 |  | 45.625 | 2.4 | 3.7
| 3.5042 | 299.67 | 297.327 | 67.736 | 19.311 | 36.268 | 17.117 |  | 45.6458 | 2.4 | 3.7
| 3.5056 | 299.551 | 297.758 | 67.739 | 19.311 | 36.274 | 17.12 |  | 45.6667 | 2.4 | 3.7
| 3.5069 | 299.562 | 297.787 | 67.744 | 19.313 | 36.276 | 17.118 |  | 45.6875 | 2.4 | 3.7
| 3.5083 | 299.739 | 297.225 | 67.738 | 19.316 | 36.276 | 17.12 |  | 45.7083 | 2.4 | 3.7
| 3.5097 | 299.627 | 298.045 | 67.737 | 19.315 | 36.283 | 17.121 |  | 45.7292 | 2.5 | 3.7
| 3.5111 | 300.366 | 297.455 | 67.736 | 19.314 | 36.281 | 17.116 |  | 45.75 | 2.5 | 3.7
| 3.5125 | 300.621 | 297.319 | 67.746 | 19.317 | 36.287 | 17.122 |  | 45.7708 | 2.4 | 3.7
| 3.5139 | 299.774 | 298.159 | 67.749 | 19.315 | 36.298 | 17.123 |  | 45.7917 | 2.4 | 3.7
| 3.5153 | 300.186 | 298.49 | 67.757 | 19.319 | 36.307 | 17.123 |  | 45.8125 | 2.3 | 3.7
| 3.5167 | 300.849 | 297.606 | 67.764 | 19.316 | 36.309 | 17.123 |  | 45.8333 | 2.4 | 3.7
| 3.5181 | 300.241 | 297.235 | 67.765 | 19.321 | 36.317 | 17.126 |  | 45.8542 | 2.4 | 3.7
| 3.5194 | 299.459 | 297.652 | 67.76 | 19.319 | 36.309 | 17.13 |  | 45.875 | 2.5 | 3.7
| 3.5208 | 299.15 | 297.318 | 67.755 | 19.32 | 36.303 | 17.13 |  | 45.8958 | 2.5 | 3.7
| 3.5222 | 300.014 | 297.622 | 67.753 | 19.327 | 36.3 | 17.132 |  | 45.9167 | 2.6 | 3.7
| 3.5236 | 299.759 | 297.852 | 67.758 | 19.327 | 36.304 | 17.129 |  | 45.9375 | 2.6 | 3.7
| 3.525 | 299.441 | 297.562 | 67.75 | 19.324 | 36.302 | 17.132 |  | 45.9583 | 2.6 | 3.7
| 3.5264 | 298.778 | 296.933 | 67.743 | 19.329 | 36.296 | 17.134 |  | 45.9792 | 2.6 | 3.7
| 3.5278 | 299.588 | 296.778 | 67.734 | 19.33 | 36.285 | 17.133 |  | 46 | 2.6 | 3.7
| 3.5292 | 298.962 | 296.802 | 67.728 | 19.33 | 36.287 | 17.135 |  | 46.0208 | 2.6 | 3.7
| 3.5306 | 299.414 | 296.729 | 67.721 | 19.331 | 36.28 | 17.133 |  | 46.0417 | 2.6 | 3.7
| 3.5319 | 299.079 | 297.176 | 67.711 | 19.333 | 36.277 | 17.136 |  | 46.0625 | 2.6 | 3.7
| 3.5333 | 299.661 | 296.65 | 67.711 | 19.332 | 36.274 | 17.138 |  | 46.0833 | 2.6 | 3.7
| 3.5347 | 298.9 | 297.277 | 67.703 | 19.335 | 36.272 | 17.14 |  | 46.1042 | 2.6 | 3.7
| 3.5361 | 299.439 | 296.474 | 67.7 | 19.336 | 36.269 | 17.14 |  | 46.125 | 2.6 | 3.7
| 3.5375 | 299.178 | 296.959 | 67.694 | 19.334 | 36.27 | 17.144 |  | 46.1458 | 2.6 | 3.7
| 3.5389 | 298.9 | 296.484 | 67.681 | 19.338 | 36.266 | 17.14 |  | 46.1667 | 2.6 | 3.7
| 3.5403 | 302.643 | 300.073 | 67.736 | 19.337 | 36.3 | 17.14 |  | 46.1875 | 2.6 | 3.7
| 3.5417 | 303.044 | 300.409 | 67.787 | 19.337 | 36.339 | 17.144 |  | 46.2083 | 2.6 | 3.7
| 3.5431 | 302.74 | 300.772 | 67.823 | 19.338 | 36.368 | 17.145 |  | 46.2292 | 2.6 | 3.7
| 3.5444 | 302.337 | 300.578 | 67.852 | 19.337 | 36.395 | 17.146 |  | 46.25 | 2.5 | 3.7
| 3.5458 | 303.175 | 299.791 | 67.875 | 19.343 | 36.412 | 17.147 |  | 46.2708 | 2.5 | 3.7
| 3.5472 | 302.636 | 300.602 | 67.901 | 19.346 | 36.424 | 17.151 |  | 46.2917 | 2.6 | 3.7
| 3.5486 | 302.778 | 300.985 | 67.929 | 19.346 | 36.441 | 17.146 |  | 46.3125 | 2.5 | 3.7
| 3.55 | 302.57 | 300.902 | 67.952 | 19.344 | 36.454 | 17.15 |  | 46.3333 | 2.5 | 3.7
| 3.5514 | 302.573 | 299.87 | 67.974 | 19.348 | 36.465 | 17.145 |  | 46.3542 | 2.5 | 3.7
| 3.5528 | 302.413 | 300.766 | 67.986 | 19.354 | 36.472 | 17.154 |  | 46.375 | 2.5 | 3.7
| 3.5542 | 302.565 | 300.613 | 68.006 | 19.354 | 36.482 | 17.153 |  | 46.3958 | 2.5 | 3.7
| 3.5556 | 302.904 | 299.782 | 68.023 | 19.356 | 36.491 | 17.153 |  | 46.4167 | 2.4 | 3.7
| 3.5569 | 302.441 | 300.801 | 68.046 | 19.36 | 36.493 | 17.158 |  | 46.4375 | 2.4 | 3.7
| 3.5583 | 302.716 | 299.865 | 68.068 | 19.362 | 36.503 | 17.158 |  | 46.4583 | 2.4 | 3.7
| 3.5597 | 302.813 | 300.415 | 68.091 | 19.358 | 36.511 | 17.155 |  | 46.4792 | 2.4 | 3.7
| 3.5611 | 302.753 | 300.628 | 68.109 | 19.364 | 36.523 | 17.159 |  | 46.5 | 2.3 | 3.7
| 3.5625 | 303.676 | 300.724 | 68.133 | 19.362 | 36.531 | 17.159 |  | 46.5208 | 2.1 | 3.7
| 3.5639 | 302.703 | 300.945 | 68.159 | 19.367 | 36.544 | 17.162 |  | 46.5417 | 2.1 | 3.7
| 3.5653 | 302.838 | 301.167 | 68.182 | 19.372 | 36.551 | 17.159 |  | 46.5625 | 2.1 | 3.7
| 3.5667 | 303.469 | 300.238 | 68.204 | 19.367 | 36.56 | 17.166 |  | 46.5833 | 2 | 3.7
| 3.5681 | 303.225 | 300.916 | 68.221 | 19.376 | 36.562 | 17.164 |  | 46.6042 | 1.9 | 3.7
| 3.5694 | 303.521 | 300.273 | 68.242 | 19.379 | 36.572 | 17.162 |  | 46.625 | 1.8 | 3.7
| 3.5708 | 302.963 | 300.748 | 68.261 | 19.376 | 36.579 | 17.17 |  | 46.6458 | 1.7 | 3.7
| 3.5722 | 303.862 | 300.644 | 68.284 | 19.38 | 36.587 | 17.169 |  | 46.6667 | 1.7 | 3.7
| 3.5736 | 303.444 | 300.895 | 68.305 | 19.381 | 36.593 | 17.168 |  | 46.6875 | 1.6 | 3.7
| 3.575 | 303.476 | 300.721 | 68.327 | 19.386 | 36.605 | 17.172 |  | 46.7083 | 1.6 | 3.7
| 3.5764 | 303.898 | 300.848 | 68.341 | 19.383 | 36.607 | 17.174 |  | 46.7292 | 1.5 | 3.7
| 3.5778 | 303.592 | 301.273 | 68.357 | 19.386 | 36.61 | 17.174 |  | 46.75 | 1.4 | 3.7
| 3.5792 | 303.45 | 300.865 | 68.38 | 19.387 | 36.62 | 17.177 |  | 46.7708 | 1.2 | 3.7
| 3.5806 | 304.196 | 300.775 | 68.399 | 19.392 | 36.634 | 17.18 |  | 46.7917 | 1 | 3.7
| 3.5819 | 304.16 | 300.728 | 68.421 | 19.397 | 36.634 | 17.18 |  | 46.8125 | 0.9 | 3.7
| 3.5833 | 303.217 | 301.298 | 68.435 | 19.397 | 36.637 | 17.179 |  | 46.8333 | 0.8 | 3.7
| 3.5847 | 303.935 | 300.726 | 68.457 | 19.403 | 36.65 | 17.184 |  | 46.8542 | 0.7 | 3.7
| 3.5861 | 304.006 | 301.01 | 68.475 | 19.402 | 36.656 | 17.183 |  | 46.875 | 0.6 | 3.7
| 3.5875 | 304.34 | 301.128 | 68.496 | 19.405 | 36.66 | 17.183 |  | 46.8958 | 0.5 | 3.7
| 3.5889 | 304.698 | 301.355 | 68.523 | 19.408 | 36.673 | 17.185 |  | 46.9167 | 0.4 | 3.7
| 3.5903 | 304.727 | 301.443 | 68.544 | 19.412 | 36.686 | 17.187 |  | 46.9375 | 0.3 | 3.7
| 3.5917 | 305.002 | 301.739 | 68.575 | 19.412 | 36.696 | 17.19 |  | 46.9583 | 0.2 | 3.7
| 3.5931 | 303.771 | 302.072 | 68.596 | 19.417 | 36.706 | 17.19 |  | 46.9792 | 0.1 | 3.7
| 3.5944 | 304.584 | 301.7 | 68.61 | 19.419 | 36.715 | 17.194 |  | 47 | 0 | 3.7
| 3.5958 | 304.608 | 302.12 | 68.639 | 19.421 | 36.719 | 17.195 |  | 47.0208 | 0 | 3.7
| 3.5972 | 304.435 | 301.766 | 68.661 | 19.422 | 36.736 | 17.197 |  | 47.0417 | 0 | 3.7
| 3.5986 | 304.287 | 302.401 | 68.684 | 19.426 | 36.747 | 17.198 |  | 47.0625 | -0.1 | 3.7
| 3.6 | 305.265 | 301.988 | 68.702 | 19.429 | 36.751 | 17.201 |  | 47.0833 | 0 | 3.7
| 3.6014 | 304.801 | 301.576 | 68.724 | 19.434 | 36.759 | 17.198 |  | 47.1042 | 0 | 3.7
| 3.6028 | 304.447 | 302.381 | 68.735 | 19.431 | 36.765 | 17.202 |  | 47.125 | -0.3 | 3.7
| 3.6042 | 304.732 | 301.95 | 68.762 | 19.433 | 36.769 | 17.206 |  | 47.1458 | -0.3 | 3.7
| 3.6056 | 304.938 | 302.844 | 68.784 | 19.44 | 36.778 | 17.205 |  | 47.1667 | -0.3 | 3.7
| 3.6069 | 304.343 | 302.577 | 68.809 | 19.441 | 36.79 | 17.21 |  | 47.1875 | -0.3 | 3.7
| 3.6083 | 305.419 | 302.126 | 68.829 | 19.446 | 36.797 | 17.214 |  | 47.2083 | -0.3 | 3.7
| 3.6097 | 304.86 | 302.428 | 68.852 | 19.447 | 36.806 | 17.212 |  | 47.2292 | -0.3 | 3.7
| 3.6111 | 305.236 | 301.805 | 68.868 | 19.449 | 36.812 | 17.216 |  | 47.25 | -0.5 | 3.7
| 3.6125 | 305.016 | 302.594 | 68.888 | 19.452 | 36.813 | 17.216 |  | 47.2708 | -0.4 | 3.7
| 3.6139 | 304.939 | 301.68 | 68.904 | 19.455 | 36.818 | 17.22 |  | 47.2917 | -0.3 | 3.7
| 3.6153 | 304.873 | 302.482 | 68.923 | 19.458 | 36.824 | 17.219 |  | 47.3125 | -0.4 | 3.7
| 3.6167 | 304.71 | 302.718 | 68.946 | 19.459 | 36.836 | 17.22 |  | 47.3333 | -0.3 | 3.7
| 3.6181 | 305.71 | 302.763 | 68.973 | 19.468 | 36.848 | 17.225 |  | 47.3542 | -0.3 | 3.7
| 3.6194 | 305.983 | 302.871 | 68.994 | 19.463 | 36.86 | 17.226 |  | 47.375 | -0.2 | 3.7
| 3.6208 | 305.815 | 302.581 | 69.026 | 19.468 | 36.871 | 17.227 |  | 47.3958 | -0.3 | 3.7
| 3.6222 | 305.535 | 303.531 | 69.049 | 19.472 | 36.886 | 17.233 |  | 47.4167 | -0.3 | 3.7
| 3.6236 | 305.86 | 302.832 | 69.074 | 19.478 | 36.895 | 17.232 |  | 47.4375 | -0.2 | 3.7
| 3.625 | 306.076 | 302.503 | 69.098 | 19.476 | 36.903 | 17.234 |  | 47.4583 | -0.2 | 3.7
| 3.6264 | 305.632 | 303.429 | 69.12 | 19.483 | 36.914 | 17.233 |  | 47.4792 | -0.2 | 3.7
| 3.6278 | 305.75 | 302.865 | 69.145 | 19.482 | 36.921 | 17.24 |  | 47.5417 | -0.2 | 3.7
| 3.6292 | 305.803 | 303.713 | 69.165 | 19.49 | 36.932 | 17.239 |  | 47.5625 | -0.2 | 3.7
| 3.6306 | 302.003 | 300.026 | 69.175 | 19.49 | 36.933 | 17.243 |  | 47.5833 | -0.2 | 3.7
| 3.6319 | 302.368 | 299.742 | 69.128 | 19.491 | 36.896 | 17.243 |  | 47.6042 | -0.2 | 3.7
| 3.6333 | 302.626 | 299.526 | 69.099 | 19.496 | 36.866 | 17.248 |  | 47.625 | -0.2 | 3.7
| 3.6347 | 300.364 | 297.063 | 69.077 | 19.5 | 36.84 | 17.244 |  | 47.6458 | -0.2 | 3.7
| 3.6361 | 299.976 | 298.099 | 69.023 | 19.502 | 36.797 | 17.251 |  | 47.6667 | -0.2 | 3.7
| 3.6375 | 300.321 | 297.224 | 68.987 | 19.506 | 36.759 | 17.252 |  | 47.6875 | -0.2 | 3.7
| 3.6389 | 299.963 | 296.656 | 68.951 | 19.506 | 36.729 | 17.256 |  | 47.7083 | -0.2 | 3.7
| 3.6403 | 299.481 | 296.866 | 68.912 | 19.508 | 36.697 | 17.258 |  | 47.7292 | -0.2 | 3.7
| 3.6417 | 299.923 | 296.773 | 68.883 | 19.51 | 36.676 | 17.26 |  | 47.75 | -0.2 | 3.7
| 3.6431 | 299.964 | 296.789 | 68.847 | 19.51 | 36.656 | 17.262 |  | 47.7708 | -0.2 | 3.7
| 3.6444 | 299.749 | 296.765 | 68.822 | 19.511 | 36.64 | 17.26 |  | 47.7917 | -0.2 | 3.7
| 3.6458 | 300.106 | 296.67 | 68.797 | 19.513 | 36.628 | 17.268 |  | 47.8125 | -0.2 | 3.7
| 3.6472 | 300.041 | 297.593 | 68.771 | 19.518 | 36.619 | 17.269 |  | 47.8333 | -0.2 | 3.7
| 3.6486 | 299.879 | 297.736 | 68.755 | 19.518 | 36.612 | 17.267 |  | 47.8542 | -0.2 | 3.7
| 3.65 | 299.738 | 297.437 | 68.731 | 19.52 | 36.603 | 17.274 |  | 47.875 | -0.2 | 3.7
| 3.6514 | 299.382 | 297.514 | 68.708 | 19.522 | 36.599 | 17.271 |  | 47.8958 | -0.2 | 3.7
| 3.6528 | 299.675 | 297.377 | 68.69 | 19.519 | 36.596 | 17.274 |  | 47.9167 | -0.2 | 3.7
| 3.6542 | 299.823 | 297.229 | 68.671 | 19.524 | 36.589 | 17.272 |  | 47.9375 | -0.2 | 3.7
| 3.6556 | 300.212 | 297.806 | 68.655 | 19.525 | 36.588 | 17.28 |  | 47.9583 | -0.2 | 3.7
| 3.6569 | 299.612 | 297.789 | 68.643 | 19.526 | 36.588 | 17.28 |  | 47.9792 | -0.2 | 3.7
| 3.6583 | 299.798 | 297.781 | 68.629 | 19.526 | 36.588 | 17.279 |  | 48 | -0.2 | 3.7
| 3.6597 | 300.068 | 297.882 | 68.616 | 19.528 | 36.591 | 17.282 |  | 48.0208 | -0.2 | 3.7
| 3.6611 | 300.513 | 298.621 | 68.603 | 19.529 | 36.594 | 17.289 |  | 48.0417 | -0.2 | 3.7
| 3.6625 | 300.999 | 298.063 | 68.605 | 19.527 | 36.606 | 17.288 |  | 48.0625 | -0.2 | 3.7
| 3.6639 | 300.348 | 298.372 | 68.594 | 19.529 | 36.606 | 17.291 |  | 48.0833 | -0.3 | 3.7
| 3.6653 | 300.435 | 298.35 | 68.583 | 19.525 | 36.607 | 17.289 |  | 48.1042 | -0.3 | 3.7
| 3.6667 | 300.843 | 298.525 | 68.571 | 19.534 | 36.605 | 17.287 |  | 48.125 | -0.3 | 3.7
| 3.6681 | 300.352 | 298.07 | 68.565 | 19.533 | 36.608 | 17.291 |  | 48.1458 | -0.3 | 3.7
| 3.6694 | 300.92 | 297.876 | 68.551 | 19.534 | 36.604 | 17.291 |  | 48.1667 | -0.3 | 3.7
| 3.6708 | 300.45 | 297.741 | 68.541 | 19.536 | 36.606 | 17.296 |  | 48.1875 | -0.3 | 3.7
| 3.6722 | 300.861 | 297.429 | 68.525 | 19.538 | 36.607 | 17.296 |  | 48.2083 | -0.3 | 3.7
| 3.6736 | 300.323 | 298.161 | 68.517 | 19.535 | 36.604 | 17.296 |  | 48.2292 | -0.3 | 3.7
| 3.675 | 300.095 | 298.135 | 68.508 | 19.539 | 36.598 | 17.297 |  | 48.25 | -0.3 | 3.7
| 3.6764 | 299.784 | 297.663 | 68.496 | 19.537 | 36.597 | 17.298 |  | 48.2708 | -0.3 | 3.7
| 3.6778 | 300.191 | 297.439 | 68.479 | 19.54 | 36.597 | 17.298 |  | 48.2917 | -0.3 | 3.7
| 3.6792 | 299.214 | 296.488 | 68.467 | 19.541 | 36.585 | 17.305 |  | 48.3125 | -0.3 | 3.7
| 3.6806 | 299.009 | 295.683 | 68.436 | 19.544 | 36.57 | 17.302 |  | 48.3333 | -0.3 | 3.7
| 3.6819 | 299.042 | 296.963 | 68.411 | 19.54 | 36.56 | 17.304 |  | 48.3542 | -0.3 | 3.7
| 3.6833 | 298.983 | 296.444 | 68.386 | 19.547 | 36.55 | 17.303 |  | 48.375 | -0.3 | 3.7
| 3.6847 | 299.462 | 296.081 | 68.371 | 19.547 | 36.544 | 17.313 |  | 48.3958 | -0.3 | 3.7
| 3.6861 | 298.868 | 296.506 | 68.349 | 19.545 | 36.536 | 17.308 |  | 48.4167 | -0.3 | 3.7
| 3.6875 | 299.417 | 296.127 | 68.339 | 19.545 | 36.532 | 17.312 |  | 48.4375 | -0.3 | 3.7
| 3.6889 | 298.808 | 297.078 | 68.323 | 19.55 | 36.521 | 17.311 |  | 48.4583 | -0.3 | 3.7
| 3.6903 | 299.744 | 297.25 | 68.305 | 19.548 | 36.521 | 17.311 |  | 48.4792 | -0.3 | 3.7
| 3.6917 | 299.834 | 296.637 | 68.303 | 19.547 | 36.528 | 17.313 |  | 48.5 | -0.3 | 3.7
| 3.6931 | 299.359 | 297.256 | 68.288 | 19.549 | 36.53 | 17.307 |  | 48.5208 | -0.3 | 3.7
| 3.6944 | 299.406 | 296.817 | 68.28 | 19.547 | 36.529 | 17.316 |  | 48.5417 | -0.3 | 3.7
| 3.6958 | 299.412 | 297.004 | 68.267 | 19.548 | 36.529 | 17.316 |  | 48.5625 | -0.2 | 3.7
| 3.6972 | 299.708 | 296.569 | 68.253 | 19.551 | 36.526 | 17.317 |  | 48.5833 | -0.3 | 3.7
| 3.6986 | 298.912 | 296.881 | 68.237 | 19.55 | 36.523 | 17.321 |  | 48.6042 | -0.3 | 3.7
| 3.7 | 298.832 | 296.381 | 68.222 | 19.551 | 36.516 | 17.316 |  | 48.625 | -0.3 | 3.7
| 3.7014 | 298.91 | 295.849 | 68.201 | 19.555 | 36.508 | 17.32 |  | 48.6458 | -0.3 | 3.7
| 3.7028 | 299.139 | 295.855 | 68.183 | 19.55 | 36.499 | 17.321 |  | 48.6667 | -0.3 | 3.7
| 3.7042 | 301.844 | 299.636 | 68.166 | 19.552 | 36.493 | 17.32 |  | 48.6875 | -0.3 | 3.7
| 3.7056 | 301.647 | 299.244 | 68.212 | 19.552 | 36.53 | 17.324 |  | 48.7083 | -0.2 | 3.7
| 3.7069 | 301.961 | 299.92 | 68.241 | 19.552 | 36.558 | 17.326 |  | 48.7292 | -0.2 | 3.7
| 3.7083 | 302.22 | 299.712 | 68.259 | 19.552 | 36.579 | 17.326 |  | 48.75 | -0.2 | 3.7
| 3.7097 | 301.625 | 299.889 | 68.278 | 19.558 | 36.602 | 17.323 |  | 48.7708 | -0.2 | 3.7
| 3.7111 | 299.607 | 297.184 | 68.263 | 19.556 | 36.598 | 17.326 |  | 48.7917 | -0.2 | 3.7
| 3.7125 | 299.481 | 296.272 | 68.232 | 19.554 | 36.579 | 17.327 |  | 48.8125 | -0.2 | 3.7
| 3.7139 | 299.203 | 295.763 | 68.208 | 19.555 | 36.561 | 17.328 |  | 48.8333 | -0.2 | 3.7
| 3.7153 | 299.541 | 297.764 | 68.185 | 19.557 | 36.548 | 17.331 |  | 48.8542 | -0.2 | 3.7
| 3.7167 | 301.182 | 297.954 | 68.199 | 19.558 | 36.558 | 17.333 |  | 48.875 | -0.2 | 3.7
| 3.7181 | 300.592 | 298.1 | 68.207 | 19.557 | 36.562 | 17.335 |  | 48.8958 | -0.2 | 3.7
| 3.7194 | 300.542 | 297.284 | 68.204 | 19.561 | 36.565 | 17.333 |  | 48.9167 | -0.3 | 3.7
| 3.7208 | 300.665 | 297.452 | 68.196 | 19.56 | 36.562 | 17.33 |  | 48.9375 | -0.2 | 3.7
| 3.7222 | 299.896 | 297.278 | 68.189 | 19.563 | 36.559 | 17.334 |  | 48.9583 | -0.3 | 3.7
| 3.7236 | 300.117 | 296.826 | 68.182 | 19.56 | 36.557 | 17.333 |  | 48.9792 | -0.2 | 3.7
| 3.725 | 299.471 | 297.463 | 68.176 | 19.567 | 36.551 | 17.336 |  | 49 | -0.2 | 3.7
| 3.7264 | 299.252 | 297.291 | 68.164 | 19.563 | 36.545 | 17.336 |  | 49.0208 | -0.1 | 3.7
| 3.7278 | 299.438 | 297.161 | 68.147 | 19.566 | 36.538 | 17.338 |  | 49.0417 | -0.1 | 3.7
| 3.7292 | 299.866 | 296.736 | 68.137 | 19.568 | 36.535 | 17.339 |  | 49.0625 | -0.1 | 3.7
| 3.7306 | 299.976 | 296.974 | 68.134 | 19.567 | 36.531 | 17.341 |  | 49.0833 | -0.2 | 3.7
| 3.7319 | 299.807 | 296.772 | 68.119 | 19.57 | 36.527 | 17.341 |  | 49.1042 | -0.2 | 3.7
| 3.7333 | 299.965 | 296.611 | 68.111 | 19.567 | 36.526 | 17.342 |  | 49.125 | -0.1 | 3.7
| 3.7347 | 299.798 | 296.632 | 68.104 | 19.567 | 36.522 | 17.344 |  | 49.1458 | -0.1 | 3.7
| 3.7361 | 299.559 | 296.567 | 68.088 | 19.567 | 36.514 | 17.345 |  | 49.1667 | -0.1 | 3.7
| 3.7375 | 299.948 | 296.844 | 68.087 | 19.569 | 36.512 | 17.346 |  | 49.1875 | -0.1 | 3.7
| 3.7389 | 299.048 | 296.594 | 68.081 | 19.57 | 36.515 | 17.348 |  | 49.2083 | -0.1 | 3.7
| 3.7403 | 299.355 | 296.774 | 68.067 | 19.571 | 36.508 | 17.348 |  | 49.2292 | -0.1 | 3.7
| 3.7417 | 299.599 | 296.899 | 68.054 | 19.571 | 36.502 | 17.349 |  | 49.25 | -0.1 | 3.7
| 3.7431 | 298.867 | 296.924 | 68.05 | 19.571 | 36.501 | 17.351 |  | 49.2708 | -0.1 | 3.7
| 3.7444 | 298.784 | 296.917 | 68.034 | 19.574 | 36.497 | 17.352 |  | 49.2917 | -0.1 | 3.7
| 3.7458 | 298.955 | 296.82 | 68.028 | 19.579 | 36.498 | 17.355 |  | 49.3125 | -0.1 | 3.7
| 3.7472 | 299.779 | 296.627 | 68.017 | 19.575 | 36.492 | 17.35 |  | 49.3333 | 0 | 3.7
| 3.7486 | 300.005 | 296.816 | 68.023 | 19.576 | 36.498 | 17.352 |  | 49.3542 | -0.1 | 3.7
| 3.75 | 299.729 | 297.309 | 68.017 | 19.577 | 36.5 | 17.353 |  | 49.375 | -0.1 | 3.7
| 3.7514 | 299.902 | 296.817 | 68.021 | 19.577 | 36.504 | 17.355 |  | 49.3958 | -0.1 | 3.7
| 3.7528 | 299.844 | 297.21 | 68.014 | 19.576 | 36.508 | 17.357 |  | 49.4167 | -0.1 | 3.7
| 3.7542 | 299.959 | 296.579 | 68.007 | 19.574 | 36.5 | 17.355 |  | 49.4375 | -0.1 | 3.7
| 3.7556 | 300.107 | 296.976 | 68.009 | 19.583 | 36.504 | 17.359 |  | 49.4583 | -0.1 | 3.7
| 3.7569 | 299.489 | 297.762 | 68.004 | 19.582 | 36.511 | 17.362 |  | 49.4792 | -0.2 | 3.7
| 3.7583 | 299.758 | 297.228 | 68.011 | 19.579 | 36.511 | 17.362 |  | 49.5 | -0.3 | 3.7
| 3.7597 | 299.654 | 297.888 | 68.011 | 19.581 | 36.516 | 17.357 |  | 49.5208 | -0.3 | 3.7
| 3.7611 | 300.207 | 296.87 | 68.011 | 19.579 | 36.516 | 17.361 |  | 49.5417 | -0.2 | 3.7
| 3.7625 | 300.297 | 297.036 | 68.008 | 19.583 | 36.519 | 17.366 |  | 49.5625 | -0.1 | 3.7
| 3.7639 | 299.604 | 296.778 | 68.008 | 19.582 | 36.521 | 17.362 |  | 49.5833 | -0.1 | 3.7
| 3.7653 | 299.781 | 297.4 | 67.994 | 19.581 | 36.515 | 17.364 |  | 49.6042 | -0.1 | 3.7
| 3.7667 | 299.784 | 297.811 | 68.001 | 19.584 | 36.519 | 17.367 |  | 49.625 | 0 | 3.7
| 3.7681 | 300.038 | 296.61 | 67.996 | 19.583 | 36.519 | 17.364 |  | 49.6458 | -0.2 | 3.7
| 3.7694 | 299.436 | 297.682 | 67.993 | 19.585 | 36.516 | 17.369 |  | 49.6667 | -0.1 | 3.7
| 3.7708 | 299.898 | 297.309 | 67.991 | 19.587 | 36.516 | 17.367 |  | 49.6875 | -0.1 | 3.7
| 3.7722 | 300.785 | 297.952 | 67.989 | 19.586 | 36.518 | 17.369 |  | 49.7083 | -0.2 | 3.7
| 3.7736 | 301.048 | 298.298 | 68.013 | 19.586 | 36.538 | 17.366 |  | 49.7292 | -0.3 | 3.7
| 3.775 | 300.741 | 298.044 | 68.024 | 19.589 | 36.542 | 17.372 |  | 49.75 | -0.2 | 3.7
| 3.7764 | 300.515 | 298.361 | 68.028 | 19.59 | 36.552 | 17.369 |  | 49.7708 | -0.2 | 3.7
| 3.7778 | 301.234 | 298.121 | 68.033 | 19.592 | 36.557 | 17.372 |  | 49.7917 | -0.2 | 3.7
| 3.7792 | 300.107 | 297.864 | 68.039 | 19.592 | 36.567 | 17.374 |  | 49.8125 | -0.2 | 3.7
| 3.7806 | 300.702 | 297.345 | 68.045 | 19.594 | 36.563 | 17.378 |  | 49.8333 | -0.1 | 3.7
| 3.7819 | 300.637 | 297.997 | 68.054 | 19.591 | 36.567 | 17.375 |  | 49.8542 | 0.1 | 3.7
| 3.7833 | 301.204 | 297.706 | 68.057 | 19.596 | 36.572 | 17.377 |  | 49.875 | 0 | 3.7
| 3.7847 | 300.82 | 298.195 | 68.067 | 19.595 | 36.576 | 17.382 |  | 49.8958 | -0.1 | 3.7
| 3.7861 | 300.86 | 298.267 | 68.076 | 19.598 | 36.584 | 17.377 |  | 49.9167 | -0.1 | 3.7
| 3.7875 | 300.604 | 298.661 | 68.078 | 19.599 | 36.588 | 17.379 |  | 49.9375 | -0.1 | 3.7
| 3.7889 | 300.891 | 298.299 | 68.089 | 19.603 | 36.591 | 17.383 |  | 49.9583 | -0.1 | 3.7
| 3.7903 | 301.341 | 298.008 | 68.099 | 19.605 | 36.601 | 17.383 |  | 49.9792 | 0 | 3.7
| 3.7917 | 301.494 | 298.572 | 68.105 | 19.603 | 36.601 | 17.383 |  | 50 | 0 | 3.7
| 3.7931 | 301.266 | 298.082 | 68.111 | 19.605 | 36.608 | 17.385 |  | 50.0208 | 0 | 3.7
| 3.7944 | 301.419 | 298.6 | 68.125 | 19.604 | 36.612 | 17.385 |  | 50.0417 | 0 | 3.7
| 3.7958 | 300.974 | 298.963 | 68.13 | 19.608 | 36.613 | 17.387 |  | 50.0625 | 0 | 3.7
| 3.7972 | 301.136 | 298.908 | 68.139 | 19.605 | 36.623 | 17.388 |  | 50.0833 | 0 | 3.7
| 3.7986 | 301.485 | 298.949 | 68.152 | 19.605 | 36.626 | 17.386 |  | 50.1042 | 0.6 | 3.7
| 3.8 | 301.823 | 298.933 | 68.164 | 19.611 | 36.636 | 17.389 |  | 50.125 | 0.3 | 3.7
| 3.8014 | 301.681 | 299.526 | 68.18 | 19.612 | 36.645 | 17.386 |  | 50.1458 | 0.2 | 3.7
| 3.8028 | 301.395 | 299.26 | 68.195 | 19.612 | 36.651 | 17.388 |  | 50.1667 | 0.2 | 3.7
| 3.8042 | 301.308 | 298.614 | 68.205 | 19.615 | 36.656 | 17.393 |  | 50.1875 | 0.3 | 3.7
| 3.8056 | 302.173 | 298.84 | 68.214 | 19.615 | 36.66 | 17.392 |  | 50.2083 | 0.3 | 3.7
| 3.8069 | 301.635 | 298.567 | 68.226 | 19.616 | 36.667 | 17.396 |  | 50.2292 | 0.5 | 3.7
| 3.8083 | 301.586 | 299.06 | 68.236 | 19.62 | 36.669 | 17.398 |  | 50.25 | 0.6 | 3.7
| 3.8097 | 302.4 | 299.377 | 68.247 | 19.62 | 36.679 | 17.396 |  | 50.2708 | 0.6 | 3.7
| 3.8111 | 301.877 | 298.573 | 68.266 | 19.62 | 36.678 | 17.398 |  | 50.2917 | 0.7 | 3.7
| 3.8125 | 301.807 | 298.31 | 68.267 | 19.623 | 36.684 | 17.399 |  | 50.3125 | --- | 3.7
| 3.8139 | 301.586 | 298.856 | 68.277 | 19.624 | 36.691 | 17.396 |  | 50.3333 | --- | 3.7
| 3.8153 | 301.931 | 299.263 | 68.285 | 19.627 | 36.693 | 17.397 |  | 50.3542 | --- | 3.7
| 3.8167 | 302.301 | 298.746 | 68.298 | 19.628 | 36.696 | 17.399 |  | 50.375 | 1 | 3.7
| 3.8181 | 301.351 | 299.37 | 68.313 | 19.624 | 36.698 | 17.402 |  | 50.3958 | 1.1 | 3.7
| 3.8194 | 302.193 | 299.484 | 68.328 | 19.629 | 36.706 | 17.404 |  | 50.4167 | 1.1 | 3.7
| 3.8208 | 302.541 | 299.275 | 68.342 | 19.629 | 36.717 | 17.401 |  | 50.4375 | 1.1 | 3.7
| 3.8222 | 302.668 | 300.131 | 68.359 | 19.631 | 36.723 | 17.405 |  | 50.4583 | 1.2 | 3.7
| 3.8236 | 302.618 | 300.124 | 68.375 | 19.629 | 36.736 | 17.406 |  | 50.4792 | 1.5 | 3.7
| 3.825 | 302.887 | 299.631 | 68.391 | 19.638 | 36.746 | 17.408 |  | 50.5 | 1.6 | 3.7
| 3.8264 | 301.985 | 300.146 | 68.407 | 19.637 | 36.75 | 17.409 |  | 50.5208 | 1.8 | 3.7
| 3.8278 | 302.673 | 299.422 | 68.421 | 19.64 | 36.759 | 17.409 |  | 50.5417 | 2 | 3.7
| 3.8292 | 302.611 | 299.925 | 68.432 | 19.641 | 36.763 | 17.412 |  | 50.5625 | 2 | 3.7
| 3.8306 | 302.517 | 300.542 | 68.448 | 19.644 | 36.769 | 17.406 |  | 50.5833 | 2.1 | 3.7
| 3.8319 | 302.826 | 300.32 | 68.469 | 19.646 | 36.781 | 17.41 |  | 50.6042 | 2.1 | 3.7
| 3.8333 | 302.622 | 300.734 | 68.491 | 19.648 | 36.791 | 17.415 |  | 50.625 | 2.1 | 3.7
| 3.8347 | 303.545 | 299.971 | 68.508 | 19.648 | 36.8 | 17.414 |  | 50.6458 | 2.1 | 3.7
| 3.8361 | 303.303 | 300.626 | 68.528 | 19.65 | 36.803 | 17.415 |  | 50.6667 | 2 | 3.7
| 3.8375 | 302.846 | 300.956 | 68.55 | 19.652 | 36.814 | 17.419 |  | 50.6875 | 1.9 | 3.7
| 3.8389 | 303.109 | 300.967 | 68.567 | 19.653 | 36.824 | 17.419 |  | 50.7083 | 1.8 | 3.7
| 3.8403 | 303.481 | 301.252 | 68.586 | 19.653 | 36.834 | 17.419 |  | 50.7292 | 1.7 | 3.7
| 3.8417 | 303.362 | 301.258 | 68.609 | 19.656 | 36.842 | 17.421 |  | 50.75 | 1.6 | 3.7
| 3.8431 | 303.026 | 301.2 | 68.632 | 19.66 | 36.848 | 17.425 |  | 50.7708 | 1.6 | 3.7
| 3.8444 | 303.362 | 301.289 | 68.649 | 19.662 | 36.86 | 17.424 |  | 50.7917 | 1.4 | 3.7
| 3.8458 | 304.447 | 301.255 | 68.672 | 19.659 | 36.867 | 17.424 |  | 50.8125 | 1.3 | 3.7
| 3.8472 | 302.764 | 299.825 | 68.693 | 19.665 | 36.882 | 17.432 |  | 50.8333 | 1.3 | 3.7
| 3.8486 | 302.343 | 299.133 | 68.673 | 19.665 | 36.87 | 17.426 |  | 50.8542 | 1.3 | 3.7
| 3.85 | 302.222 | 299.848 | 68.673 | 19.667 | 36.859 | 17.426 |  | 50.875 | 1.2 | 3.7
| 3.8514 | 301.983 | 300.022 | 68.68 | 19.676 | 36.852 | 17.43 |  | 50.8958 | 1.1 | 3.7
| 3.8528 | 302.523 | 299.518 | 68.682 | 19.673 | 36.853 | 17.432 |  | 50.9167 | 1.1 | 3.7
| 3.8542 | 302.125 | 299.973 | 68.692 | 19.672 | 36.85 | 17.434 |  | 50.9375 | 1.2 | 3.7
| 3.8556 | 302.555 | 299.632 | 68.698 | 19.681 | 36.853 | 17.432 |  | 50.9583 | 0.2 | 3.7
| 3.8569 | 302.702 | 299.439 | 68.7 | 19.68 | 36.851 | 17.436 |  | 50.9792 | -0.2 | 3.7
| 3.8583 | 302.604 | 299.329 | 68.711 | 19.682 | 36.85 | 17.431 |  | 51 | -0.5 | 3.7
| 3.8597 | 302.863 | 299.165 | 68.717 | 19.685 | 36.85 | 17.434
| 3.8611 | 302.862 | 299.128 | 68.723 | 19.685 | 36.853 | 17.438
| 3.8625 | 302.835 | 299.137 | 68.733 | 19.684 | 36.855 | 17.438
| 3.8639 | 302.918 | 300.352 | 68.735 | 19.686 | 36.858 | 17.444
| 3.8653 | 301.743 | 299.749 | 68.745 | 19.691 | 36.863 | 17.44
| 3.8667 | 302.347 | 299.101 | 68.746 | 19.695 | 36.862 | 17.441
| 3.8681 | 302.24 | 300.104 | 68.755 | 19.694 | 36.861 | 17.447
| 3.8694 | 302.54 | 300.318 | 68.763 | 19.698 | 36.865 | 17.446
| 3.8708 | 303.132 | 299.965 | 68.775 | 19.697 | 36.875 | 17.448
| 3.8722 | 302.747 | 300.487 | 68.786 | 19.697 | 36.883 | 17.445
| 3.8736 | 303.65 | 300.091 | 68.803 | 19.7 | 36.889 | 17.451
| 3.875 | 303.588 | 299.916 | 68.816 | 19.701 | 36.898 | 17.452
| 3.8764 | 303.694 | 300.21 | 68.826 | 19.704 | 36.904 | 17.451
| 3.8778 | 303.639 | 300.432 | 68.842 | 19.705 | 36.911 | 17.454
| 3.8792 | 303.402 | 300.374 | 68.855 | 19.706 | 36.918 | 17.456
| 3.8806 | 303.31 | 301.263 | 68.87 | 19.71 | 36.928 | 17.451
| 3.8819 | 303.361 | 301.229 | 68.885 | 19.716 | 36.94 | 17.459
| 3.8833 | 304.032 | 300.46 | 68.904 | 19.718 | 36.952 | 17.458
| 3.8847 | 303.158 | 301.173 | 68.914 | 19.716 | 36.953 | 17.46
| 3.8861 | 303.535 | 301.543 | 68.936 | 19.718 | 36.959 | 17.463
| 3.8875 | 304.76 | 301.342 | 68.952 | 19.718 | 36.974 | 17.465
| 3.8889 | 304.359 | 301.261 | 68.969 | 19.721 | 36.984 | 17.465
| 3.8903 | 303.533 | 301.368 | 68.984 | 19.726 | 36.994 | 17.465
| 3.8917 | 303.917 | 300.941 | 68.993 | 19.725 | 36.995 | 17.469
| 3.8931 | 303.651 | 300.728 | 69.001 | 19.725 | 36.998 | 17.469
| 3.8944 | 303.024 | 300.969 | 69.008 | 19.73 | 36.998 | 17.47
| 3.8958 | 303.132 | 301.03 | 69.018 | 19.732 | 37.001 | 17.474
| 3.8972 | 303.51 | 300.885 | 69.03 | 19.732 | 37.001 | 17.471
| 3.8986 | 303.985 | 300.563 | 69.032 | 19.735 | 37.003 | 17.475
| 3.9 | 303.194 | 301.046 | 69.043 | 19.738 | 37.007 | 17.471
| 3.9014 | 303.323 | 301.095 | 69.046 | 19.74 | 37.008 | 17.475
| 3.9028 | 303.78 | 300.173 | 69.063 | 19.744 | 37.014 | 17.474
| 3.9042 | 303.932 | 300.394 | 69.071 | 19.744 | 37.012 | 17.478
| 3.9056 | 303.361 | 301.277 | 69.079 | 19.749 | 37.02 | 17.478
| 3.9069 | 304.329 | 300.995 | 69.093 | 19.746 | 37.025 | 17.479
| 3.9083 | 304.304 | 300.905 | 69.099 | 19.75 | 37.026 | 17.481
| 3.9097 | 303.296 | 301.198 | 69.112 | 19.751 | 37.035 | 17.483
| 3.9111 | 303.808 | 301.408 | 69.118 | 19.755 | 37.037 | 17.486
| 3.9125 | 303.391 | 301.263 | 69.129 | 19.758 | 37.045 | 17.487
| 3.9139 | 303.709 | 301.469 | 69.138 | 19.754 | 37.045 | 17.482
| 3.9153 | 304.486 | 300.841 | 69.15 | 19.754 | 37.055 | 17.488
| 3.9167 | 304.299 | 301.135 | 69.158 | 19.756 | 37.057 | 17.487
| 3.9181 | 304.051 | 301.726 | 69.171 | 19.765 | 37.06 | 17.488
| 3.9194 | 304.137 | 302.206 | 69.182 | 19.758 | 37.066 | 17.49
| 3.9208 | 304.636 | 301.81 | 69.199 | 19.766 | 37.078 | 17.493
| 3.9222 | 304.401 | 301.001 | 69.213 | 19.764 | 37.086 | 17.492
| 3.9236 | 304.004 | 301.793 | 69.22 | 19.767 | 37.09 | 17.494
| 3.925 | 304.392 | 301.696 | 69.229 | 19.768 | 37.095 | 17.496
| 3.9264 | 304.496 | 301.307 | 69.243 | 19.773 | 37.101 | 17.499
| 3.9278 | 304.136 | 300.675 | 69.253 | 19.776 | 37.105 | 17.498
| 3.9292 | 304.31 | 302.652 | 69.257 | 19.777 | 37.106 | 17.5
| 3.9306 | 305.124 | 302.701 | 69.281 | 19.777 | 37.122 | 17.498
| 3.9319 | 305.186 | 302.249 | 69.301 | 19.779 | 37.131 | 17.501
| 3.9333 | 304.838 | 302.343 | 69.313 | 19.781 | 37.137 | 17.503
| 3.9347 | 304.514 | 302.368 | 69.325 | 19.784 | 37.14 | 17.504
| 3.9361 | 304.951 | 301.848 | 69.334 | 19.782 | 37.144 | 17.505
| 3.9375 | 304.885 | 302.258 | 69.347 | 19.788 | 37.148 | 17.506
| 3.9389 | 304.542 | 302.594 | 69.354 | 19.792 | 37.157 | 17.506
| 3.9403 | 305.234 | 302.325 | 69.375 | 19.79 | 37.158 | 17.503
| 3.9417 | 300.952 | 298.926 | 69.353 | 19.794 | 37.152 | 17.507
| 3.9431 | 300.951 | 298.666 | 69.304 | 19.796 | 37.104 | 17.508
| 3.9444 | 300.611 | 298.84 | 69.267 | 19.792 | 37.077 | 17.506
| 3.9458 | 300.7 | 298.986 | 69.236 | 19.797 | 37.048 | 17.511
| 3.9472 | 301.031 | 298.366 | 69.216 | 19.798 | 37.026 | 17.509
| 3.9486 | 300.803 | 299.132 | 69.19 | 19.803 | 37.01 | 17.514
| 3.95 | 301.875 | 298.942 | 69.176 | 19.803 | 36.999 | 17.508
| 3.9514 | 301.307 | 299.595 | 69.158 | 19.801 | 36.993 | 17.514
| 3.9528 | 300.935 | 299.404 | 69.142 | 19.806 | 36.988 | 17.513
| 3.9542 | 302.149 | 299.171 | 69.136 | 19.804 | 36.988 | 17.51
| 3.9556 | 301.982 | 298.989 | 69.123 | 19.8 | 36.985 | 17.509
| 3.9569 | 301.971 | 299.056 | 69.111 | 19.805 | 36.984 | 17.515
| 3.9583 | 301.713 | 300.077 | 69.105 | 19.808 | 36.992 | 17.513
| 3.9597 | 301.931 | 299.652 | 69.097 | 19.813 | 36.994 | 17.512
| 3.9611 | 302.637 | 299.771 | 69.092 | 19.804 | 36.997 | 17.516
| 3.9625 | 302.156 | 299.771 | 69.085 | 19.806 | 37 | 17.514
| 3.9639 | 301.975 | 300.154 | 69.078 | 19.808 | 37.001 | 17.517
| 3.9653 | 302.071 | 300.217 | 69.077 | 19.808 | 37.004 | 17.515
| 3.9667 | 302.182 | 300.281 | 69.074 | 19.81 | 37.005 | 17.517
| 3.9681 | 302.823 | 300.061 | 69.073 | 19.81 | 37.013 | 17.513
| 3.9694 | 301.965 | 300.358 | 69.07 | 19.816 | 37.015 | 17.515
| 3.9708 | 302.96 | 300.005 | 69.073 | 19.813 | 37.02 | 17.512
| 3.9722 | 302.321 | 300.666 | 69.074 | 19.813 | 37.024 | 17.513
| 3.9736 | 303.164 | 300.605 | 69.078 | 19.814 | 37.027 | 17.515
| 3.975 | 303.452 | 300.235 | 69.077 | 19.815 | 37.037 | 17.512
| 3.9764 | 303.69 | 300.561 | 69.087 | 19.814 | 37.047 | 17.514
| 3.9778 | 303.026 | 300.639 | 69.088 | 19.811 | 37.055 | 17.513
| 3.9792 | 302.66 | 299.659 | 69.086 | 19.815 | 37.054 | 17.517
| 3.9806 | 302.038 | 299.545 | 69.071 | 19.816 | 37.044 | 17.515
| 3.9819 | 301.787 | 299.015 | 69.056 | 19.818 | 37.035 | 17.512
| 3.9833 | 301.355 | 299.375 | 69.038 | 19.817 | 37.023 | 17.509
| 3.9847 | 302.076 | 299.013 | 69.028 | 19.814 | 37.014 | 17.51
| 3.9861 | 301.711 | 299.537 | 69.017 | 19.815 | 37.013 | 17.518
| 3.9875 | 301.536 | 298.99 | 69.007 | 19.813 | 37.012 | 17.511
| 3.9889 | 301.483 | 299.011 | 68.992 | 19.814 | 37 | 17.51
| 3.9903 | 301.072 | 299.199 | 68.98 | 19.819 | 36.996 | 17.508
| 3.9917 | 301.845 | 298.786 | 68.969 | 19.819 | 36.993 | 17.51
| 3.9931 | 301.766 | 299.369 | 68.957 | 19.823 | 36.988 | 17.508
| 3.9944 | 301.566 | 299.449 | 68.952 | 19.82 | 36.991 | 17.504
| 3.9958 | 302.353 | 299.754 | 68.951 | 19.822 | 36.995 | 17.507
| 3.9972 | 301.851 | 299.557 | 68.953 | 19.818 | 36.997 | 17.509
| 3.9986 | 301.783 | 300.089 | 68.944 | 19.822 | 36.998 | 17.504
| 4 | 302.728 | 299.608 | 68.948 | 19.82 | 37.001 | 17.503
| 4.0014 | 301.989 | 300.28 | 68.946 | 19.82 | 37.011 | 17.501
| 4.0028 | 302.53 | 299.988 | 68.944 | 19.82 | 37.011 | 17.495
| 4.0042 | 301.937 | 300.201 | 68.948 | 19.822 | 37.02 | 17.498
| 4.0056 | 302.341 | 299.905 | 68.943 | 19.819 | 37.019 | 17.494
| 4.0069 | 302.658 | 300.992 | 68.953 | 19.822 | 37.027 | 17.494
| 4.0083 | 303.306 | 300.577 | 68.959 | 19.826 | 37.042 | 17.495
| 4.0097 | 303.448 | 301.521 | 68.976 | 19.823 | 37.05 | 17.49
| 4.0111 | 303.69 | 301.738 | 68.992 | 19.821 | 37.065 | 17.491
| 4.0125 | 305.007 | 301.757 | 69.01 | 19.821 | 37.08 | 17.489
| 4.0139 | 300.064 | 298.324 | 68.992 | 19.826 | 37.075 | 17.487
| 4.0153 | 299.866 | 298.2 | 68.939 | 19.82 | 37.042 | 17.487
| 4.0167 | 300.662 | 297.447 | 68.909 | 19.823 | 37.019 | 17.485
| 4.0181 | 300.314 | 298.547 | 68.887 | 19.821 | 36.997 | 17.487
| 4.0194 | 300.853 | 297.809 | 68.869 | 19.821 | 36.984 | 17.483
| 4.0208 | 300.671 | 297.619 | 68.857 | 19.823 | 36.983 | 17.483
| 4.0222 | 300.992 | 298.109 | 68.834 | 19.823 | 36.97 | 17.481
| 4.0236 | 300.803 | 298.17 | 68.818 | 19.825 | 36.964 | 17.478
| 4.025 | 301.315 | 298.217 | 68.811 | 19.823 | 36.962 | 17.483
| 4.0264 | 300.977 | 298.572 | 68.792 | 19.824 | 36.961 | 17.475
| 4.0278 | 300.515 | 298.826 | 68.792 | 19.823 | 36.959 | 17.474
| 4.0292 | 298.777 | 296.398 | 68.749 | 19.824 | 36.939 | 17.474
| 4.0306 | 298.179 | 296.351 | 68.703 | 19.819 | 36.91 | 17.47
| 4.0319 | 298.461 | 296.427 | 68.663 | 19.822 | 36.881 | 17.471
| 4.0333 | 298.501 | 295.762 | 68.632 | 19.823 | 36.866 | 17.47
| 4.0347 | 298.14 | 296.526 | 68.595 | 19.821 | 36.852 | 17.465
| 4.0361 | 297.981 | 296.174 | 68.562 | 19.818 | 36.835 | 17.467
| 4.0375 | 297.252 | 295.452 | 68.527 | 19.818 | 36.819 | 17.462
| 4.0389 | 301.391 | 299.447 | 68.519 | 19.819 | 36.82 | 17.461
| 4.0403 | 301.965 | 298.789 | 68.544 | 19.815 | 36.849 | 17.464
| 4.0417 | 301.302 | 299.337 | 68.563 | 19.816 | 36.87 | 17.457
| 4.0431 | 301.437 | 299.258 | 68.564 | 19.818 | 36.888 | 17.459
| 4.0444 | 301.528 | 299.329 | 68.574 | 19.812 | 36.905 | 17.458
| 4.0458 | 301.639 | 299.4 | 68.572 | 19.811 | 36.915 | 17.454
| 4.0472 | 301.599 | 299.722 | 68.578 | 19.811 | 36.92 | 17.451
| 4.0486 | 301.825 | 299.765 | 68.581 | 19.813 | 36.934 | 17.451
| 4.05 | 302.348 | 299.286 | 68.588 | 19.813 | 36.945 | 17.443
| 4.0514 | 301.683 | 299.817 | 68.591 | 19.81 | 36.953 | 17.445
| 4.0528 | 302.328 | 299.231 | 68.596 | 19.814 | 36.958 | 17.446
| 4.0542 | 302.494 | 299.675 | 68.599 | 19.814 | 36.966 | 17.439
| 4.0556 | 302.443 | 300.222 | 68.612 | 19.809 | 36.974 | 17.437
| 4.0569 | 302.7 | 299.945 | 68.62 | 19.813 | 36.983 | 17.437
| 4.0583 | 302.303 | 300.397 | 68.635 | 19.81 | 36.992 | 17.436
| 4.0597 | 302.082 | 299.945 | 68.635 | 19.809 | 37.001 | 17.433
| 4.0611 | 302.422 | 300.009 | 68.64 | 19.808 | 37.005 | 17.433
| 4.0625 | 301.871 | 300.085 | 68.648 | 19.812 | 37.005 | 17.427
| 4.0639 | 302.188 | 300.304 | 68.655 | 19.811 | 37.01 | 17.427
| 4.0653 | 302.61 | 300.258 | 68.657 | 19.812 | 37.018 | 17.424
| 4.0667 | 302.704 | 299.852 | 68.673 | 19.805 | 37.023 | 17.42
| 4.0681 | 302.557 | 300.119 | 68.676 | 19.812 | 37.028 | 17.423
| 4.0694 | 302.616 | 299.459 | 68.685 | 19.808 | 37.027 | 17.419
| 4.0708 | 302.71 | 299.685 | 68.688 | 19.81 | 37.032 | 17.417
| 4.0722 | 302.345 | 299.665 | 68.686 | 19.809 | 37.034 | 17.416
| 4.0736 | 302.923 | 299.454 | 68.693 | 19.807 | 37.036 | 17.412
| 4.075 | 302.768 | 299.505 | 68.694 | 19.809 | 37.035 | 17.415
| 4.0764 | 303.063 | 299.862 | 68.702 | 19.806 | 37.036 | 17.411
| 4.0778 | 302.387 | 300.339 | 68.71 | 19.807 | 37.04 | 17.409
| 4.0792 | 302.804 | 299.92 | 68.719 | 19.808 | 37.042 | 17.406
| 4.0806 | 302.771 | 300.24 | 68.719 | 19.809 | 37.051 | 17.404
| 4.0819 | 302.992 | 300.274 | 68.728 | 19.811 | 37.052 | 17.405
| 4.0833 | 303.231 | 300.04 | 68.735 | 19.808 | 37.06 | 17.407
| 4.0847 | 303.184 | 300.149 | 68.743 | 19.809 | 37.064 | 17.405
| 4.0861 | 303.168 | 300.756 | 68.753 | 19.811 | 37.069 | 17.4
| 4.0875 | 303.39 | 300.481 | 68.769 | 19.811 | 37.076 | 17.399
| 4.0889 | 303.364 | 301.122 | 68.782 | 19.807 | 37.086 | 17.401
| 4.0903 | 303.083 | 301.425 | 68.791 | 19.812 | 37.094 | 17.391
| 4.0917 | 303.768 | 300.611 | 68.804 | 19.811 | 37.102 | 17.391
| 4.0931 | 303.336 | 300.929 | 68.813 | 19.81 | 37.1 | 17.393
| 4.0944 | 303.626 | 300.299 | 68.819 | 19.812 | 37.106 | 17.395
| 4.0958 | 300.939 | 298.268 | 68.822 | 19.809 | 37.102 | 17.39
| 4.0972 | 300.693 | 297.937 | 68.783 | 19.811 | 37.081 | 17.391
| 4.0986 | 300.661 | 297.702 | 68.755 | 19.811 | 37.052 | 17.394
| 4.1 | 300.598 | 298.29 | 68.734 | 19.816 | 37.034 | 17.389
| 4.1014 | 299.985 | 298.458 | 68.715 | 19.814 | 37.02 | 17.388
| 4.1028 | 300.729 | 298.462 | 68.702 | 19.813 | 37.012 | 17.387
| 4.1042 | 300.219 | 298.542 | 68.688 | 19.814 | 37.001 | 17.381
| 4.1056 | 300.851 | 298.126 | 68.676 | 19.815 | 36.991 | 17.382
| 4.1069 | 301.067 | 298.181 | 68.669 | 19.811 | 36.982 | 17.38
| 4.1083 | 300.815 | 298.46 | 68.658 | 19.81 | 36.982 | 17.381
| 4.1097 | 300.731 | 298.642 | 68.645 | 19.81 | 36.979 | 17.384
| 4.1111 | 301.009 | 298.302 | 68.636 | 19.809 | 36.98 | 17.381
| 4.1125 | 301.369 | 299.581 | 68.632 | 19.813 | 36.978 | 17.378
| 4.1139 | 301.139 | 299.425 | 68.636 | 19.813 | 36.986 | 17.374
| 4.1153 | 301.271 | 299.483 | 68.635 | 19.809 | 36.987 | 17.377
| 4.1167 | 301.162 | 299.191 | 68.63 | 19.81 | 36.99 | 17.373
| 4.1181 | 301.091 | 298.721 | 68.629 | 19.81 | 36.993 | 17.375
| 4.1194 | 301.411 | 298.678 | 68.623 | 19.807 | 36.991 | 17.379
| 4.1208 | 301.106 | 298.894 | 68.613 | 19.809 | 36.991 | 17.367
| 4.1222 | 300.755 | 299.109 | 68.606 | 19.807 | 36.989 | 17.369
| 4.1236 | 301.097 | 298.551 | 68.595 | 19.81 | 36.98 | 17.371
| 4.125 | 300.553 | 298.843 | 68.581 | 19.811 | 36.979 | 17.372
| 4.1264 | 300.897 | 298.698 | 68.579 | 19.807 | 36.978 | 17.368
| 4.1278 | 301.761 | 298.595 | 68.572 | 19.806 | 36.973 | 17.368
| 4.1292 | 301.806 | 298.633 | 68.574 | 19.808 | 36.976 | 17.369
| 4.1306 | 301.528 | 299.157 | 68.574 | 19.805 | 36.979 | 17.364
| 4.1319 | 301.111 | 298.972 | 68.572 | 19.805 | 36.987 | 17.363
| 4.1333 | 301.147 | 299.125 | 68.567 | 19.804 | 36.989 | 17.362
| 4.1347 | 301.231 | 298.994 | 68.562 | 19.81 | 36.989 | 17.365
| 4.1361 | 301.175 | 299.424 | 68.556 | 19.808 | 36.984 | 17.366
| 4.1375 | 301.366 | 299.228 | 68.557 | 19.805 | 36.984 | 17.358
| 4.1389 | 301.582 | 299.792 | 68.56 | 19.806 | 36.99 | 17.358
| 4.1403 | 302.348 | 299.041 | 68.565 | 19.804 | 36.995 | 17.361
| 4.1417 | 301.745 | 299.883 | 68.574 | 19.807 | 37.006 | 17.356
| 4.1431 | 301.789 | 299.634 | 68.574 | 19.808 | 37.009 | 17.356
| 4.1444 | 302.228 | 299.468 | 68.58 | 19.806 | 37.011 | 17.355
| 4.1458 | 302.003 | 298.987 | 68.579 | 19.806 | 37.013 | 17.358
| 4.1472 | 302.174 | 298.911 | 68.576 | 19.808 | 37.015 | 17.354
| 4.1486 | 301.36 | 299.472 | 68.575 | 19.809 | 37.017 | 17.355
| 4.15 | 302.292 | 299.23 | 68.577 | 19.803 | 37.012 | 17.352
| 4.1514 | 302.097 | 299.062 | 68.578 | 19.801 | 37.018 | 17.35
| 4.1528 | 302.303 | 299.041 | 68.581 | 19.805 | 37.018 | 17.352
| 4.1542 | 302.412 | 299.346 | 68.58 | 19.802 | 37.021 | 17.351
| 4.1556 | 301.859 | 300.113 | 68.587 | 19.804 | 37.025 | 17.354
| 4.1569 | 301.813 | 299.888 | 68.587 | 19.805 | 37.024 | 17.35
| 4.1583 | 301.864 | 299.97 | 68.595 | 19.806 | 37.032 | 17.35
| 4.1597 | 301.78 | 299.688 | 68.592 | 19.804 | 37.032 | 17.347
| 4.1611 | 301.615 | 299.334 | 68.589 | 19.805 | 37.027 | 17.346
| 4.1625 | 301.47 | 299.575 | 68.587 | 19.807 | 37.03 | 17.349
| 4.1639 | 301.849 | 300.146 | 68.592 | 19.801 | 37.026 | 17.345
| 4.1653 | 301.596 | 299.533 | 68.593 | 19.806 | 37.032 | 17.345
| 4.1667 | 302.118 | 298.819 | 68.592 | 19.807 | 37.026 | 17.348
| 4.1681 | 301.598 | 299.539 | 68.589 | 19.808 | 37.027 | 17.344
| 4.1694 | 301.917 | 299.386 | 68.588 | 19.803 | 37.027 | 17.344
| 4.1708 | 302.085 | 299.352 | 68.588 | 19.802 | 37.025 | 17.341
| 4.1722 | 302.082 | 300.032 | 68.595 | 19.805 | 37.033 | 17.346
| 4.1736 | 301.616 | 299.638 | 68.595 | 19.806 | 37.029 | 17.341
| 4.175 | 302.208 | 299.565 | 68.595 | 19.806 | 37.033 | 17.342
| 4.1764 | 302.205 | 299.452 | 68.601 | 19.803 | 37.037 | 17.34
| 4.1778 | 301.736 | 299.763 | 68.594 | 19.807 | 37.036 | 17.343
| 4.1792 | 302.079 | 299.37 | 68.601 | 19.803 | 37.037 | 17.343
| 4.1806 | 302.504 | 299.317 | 68.597 | 19.809 | 37.036 | 17.339
| 4.1819 | 302.364 | 299.157 | 68.599 | 19.803 | 37.032 | 17.345
| 4.1833 | 301.786 | 299.538 | 68.6 | 19.803 | 37.035 | 17.344
| 4.1847 | 302.321 | 299.07 | 68.601 | 19.804 | 37.038 | 17.338
| 4.1861 | 301.488 | 299.661 | 68.599 | 19.803 | 37.033 | 17.339
| 4.1875 | 301.917 | 298.881 | 68.599 | 19.809 | 37.036 | 17.34
| 4.1889 | 301.677 | 299.09 | 68.587 | 19.805 | 37.03 | 17.336
| 4.1903 | 301.345 | 299.27 | 68.584 | 19.803 | 37.027 | 17.34
| 4.1917 | 301.727 | 298.995 | 68.582 | 19.805 | 37.024 | 17.341
| 4.1931 | 301.529 | 299.628 | 68.585 | 19.808 | 37.025 | 17.335
| 4.1944 | 302.065 | 298.811 | 68.582 | 19.801 | 37.025 | 17.339
| 4.1958 | 301.483 | 299.611 | 68.585 | 19.807 | 37.027 | 17.338
| 4.1972 | 301.734 | 299.659 | 68.586 | 19.808 | 37.03 | 17.336
| 4.1986 | 301.68 | 299.654 | 68.585 | 19.803 | 37.028 | 17.337
| 4.2 | 301.867 | 299.134 | 68.59 | 19.806 | 37.028 | 17.344
| 4.2014 | 301.549 | 299.197 | 68.582 | 19.803 | 37.029 | 17.337
| 4.2028 | 301.246 | 299.275 | 68.575 | 19.807 | 37.029 | 17.337
| 4.2042 | 301.38 | 299.223 | 68.568 | 19.806 | 37.024 | 17.334
| 4.2056 | 301.846 | 298.885 | 68.57 | 19.808 | 37.02 | 17.336
| 4.2069 | 301.353 | 299.708 | 68.57 | 19.811 | 37.028 | 17.338
| 4.2083 | 301.56 | 299.327 | 68.579 | 19.808 | 37.023 | 17.339
| 4.2097 | 301.784 | 298.986 | 68.568 | 19.808 | 37.023 | 17.335
| 4.2111 | 301.897 | 298.92 | 68.57 | 19.81 | 37.027 | 17.34
| 4.2125 | 301.685 | 299.315 | 68.573 | 19.809 | 37.025 | 17.338
| 4.2139 | 301.785 | 299.083 | 68.571 | 19.807 | 37.027 | 17.333
| 4.2153 | 302.131 | 298.902 | 68.566 | 19.809 | 37.027 | 17.335
| 4.2167 | 301.509 | 299.511 | 68.566 | 19.808 | 37.021 | 17.334
| 4.2181 | 301.361 | 299.764 | 68.565 | 19.809 | 37.027 | 17.332
| 4.2194 | 301.704 | 299.317 | 68.561 | 19.808 | 37.025 | 17.336
| 4.2208 | 301.691 | 300.141 | 68.567 | 19.81 | 37.026 | 17.337
| 4.2222 | 301.376 | 299.721 | 68.571 | 19.808 | 37.032 | 17.333
| 4.2236 | 301.283 | 299.594 | 68.569 | 19.809 | 37.031 | 17.335
| 4.225 | 302.106 | 298.915 | 68.564 | 19.807 | 37.033 | 17.333
| 4.2264 | 301.317 | 299.556 | 68.566 | 19.81 | 37.03 | 17.335
| 4.2278 | 301.592 | 298.987 | 68.56 | 19.812 | 37.031 | 17.336
| 4.2292 | 302.13 | 299.144 | 68.553 | 19.812 | 37.026 | 17.335
| 4.2306 | 301.541 | 298.826 | 68.553 | 19.812 | 37.023 | 17.334
| 4.2319 | 301.637 | 299.216 | 68.551 | 19.809 | 37.023 | 17.332
| 4.2333 | 301.641 | 298.981 | 68.545 | 19.812 | 37.022 | 17.333
| 4.2347 | 301.202 | 299.619 | 68.543 | 19.811 | 37.013 | 17.333
| 4.2361 | 301.228 | 299.35 | 68.541 | 19.809 | 37.016 | 17.336
| 4.2375 | 301.813 | 298.782 | 68.537 | 19.81 | 37.015 | 17.334
| 4.2389 | 301.523 | 298.32 | 68.533 | 19.808 | 37.011 | 17.332
| 4.2403 | 301.66 | 298.579 | 68.525 | 19.81 | 37.009 | 17.333
| 4.2417 | 300.85 | 298.985 | 68.521 | 19.81 | 37.001 | 17.334
| 4.2431 | 301.826 | 298.996 | 68.518 | 19.811 | 37.002 | 17.334
| 4.2444 | 301.443 | 299.148 | 68.517 | 19.812 | 37.009 | 17.332
| 4.2458 | 301.736 | 299.175 | 68.516 | 19.812 | 37.011 | 17.337
| 4.2472 | 301.306 | 299.494 | 68.511 | 19.809 | 37.01 | 17.335
| 4.2486 | 301.708 | 298.915 | 68.518 | 19.811 | 37.011 | 17.338
| 4.25 | 301.957 | 298.625 | 68.515 | 19.811 | 37.013 | 17.334
| 4.2514 | 301.475 | 299.099 | 68.517 | 19.808 | 37.017 | 17.333
| 4.2528 | 301.627 | 300.156 | 68.518 | 19.815 | 37.011 | 17.334
| 4.2542 | 301.693 | 299.922 | 68.514 | 19.813 | 37.022 | 17.332
| 4.2556 | 301.568 | 299.926 | 68.523 | 19.807 | 37.023 | 17.333
| 4.2569 | 301.927 | 298.681 | 68.525 | 19.809 | 37.022 | 17.334
| 4.2583 | 301.24 | 299.489 | 68.517 | 19.812 | 37.022 | 17.334
| 4.2597 | 301.163 | 299.512 | 68.516 | 19.812 | 37.022 | 17.334
| 4.2611 | 301.397 | 298.74 | 68.515 | 19.811 | 37.015 | 17.338
| 4.2625 | 301.124 | 298.772 | 68.502 | 19.813 | 37.014 | 17.336
| 4.2639 | 300.947 | 298.456 | 68.493 | 19.814 | 37.011 | 17.333
| 4.2653 | 301.302 | 298.19 | 68.486 | 19.815 | 37.006 | 17.334
| 4.2667 | 300.824 | 298.448 | 68.477 | 19.81 | 36.999 | 17.336
| 4.2681 | 300.8 | 298.906 | 68.477 | 19.813 | 37.001 | 17.334
| 4.2694 | 300.771 | 298.716 | 68.476 | 19.818 | 36.99 | 17.334
| 4.2708 | 300.798 | 298.728 | 68.47 | 19.814 | 36.992 | 17.335
| 4.2722 | 300.551 | 298.561 | 68.458 | 19.814 | 36.987 | 17.338
| 4.2736 | 301.003 | 297.983 | 68.454 | 19.814 | 36.982 | 17.336
| 4.275 | 300.798 | 297.944 | 68.44 | 19.815 | 36.979 | 17.341
| 4.2764 | 300.847 | 297.838 | 68.431 | 19.818 | 36.969 | 17.335
| 4.2778 | 300.646 | 297.922 | 68.424 | 19.816 | 36.963 | 17.336
| 4.2792 | 301.16 | 297.772 | 68.416 | 19.818 | 36.964 | 17.343
| 4.2806 | 300.323 | 298.434 | 68.412 | 19.817 | 36.963 | 17.335
| 4.2819 | 300.963 | 297.575 | 68.405 | 19.815 | 36.961 | 17.336
| 4.2833 | 300.731 | 297.5 | 68.401 | 19.82 | 36.955 | 17.337
| 4.2847 | 300.136 | 298.245 | 68.386 | 19.817 | 36.951 | 17.336
| 4.2861 | 300.622 | 297.849 | 68.38 | 19.817 | 36.947 | 17.336
| 4.2875 | 300.522 | 297.978 | 68.372 | 19.816 | 36.947 | 17.339
| 4.2889 | 300.41 | 298.128 | 68.367 | 19.819 | 36.944 | 17.338
| 4.2903 | 300.332 | 297.767 | 68.36 | 19.818 | 36.941 | 17.339
| 4.2917 | 300.24 | 298.397 | 68.351 | 19.816 | 36.937 | 17.336
| 4.2931 | 300.535 | 297.638 | 68.345 | 19.816 | 36.938 | 17.338
| 4.2944 | 301.005 | 297.726 | 68.334 | 19.816 | 36.932 | 17.338
| 4.2958 | 300.673 | 297.615 | 68.331 | 19.816 | 36.93 | 17.337
| 4.2972 | 300.094 | 298.297 | 68.322 | 19.817 | 36.932 | 17.337
| 4.2986 | 300.257 | 298.335 | 68.316 | 19.815 | 36.93 | 17.338
| 4.3 | 300.837 | 297.697 | 68.315 | 19.816 | 36.928 | 17.342
| 4.3014 | 300.632 | 298.228 | 68.313 | 19.816 | 36.929 | 17.343
| 4.3028 | 301.028 | 297.904 | 68.305 | 19.814 | 36.93 | 17.339
| 4.3042 | 299.711 | 297.924 | 68.292 | 19.818 | 36.921 | 17.343
| 4.3056 | 299.822 | 298.138 | 68.28 | 19.816 | 36.921 | 17.339
| 4.3069 | 300.316 | 297.649 | 68.279 | 19.818 | 36.913 | 17.34
| 4.3083 | 300.591 | 298.177 | 68.276 | 19.817 | 36.918 | 17.339
| 4.3097 | 300.12 | 297.981 | 68.262 | 19.815 | 36.917 | 17.341
| 4.3111 | 300.853 | 297.66 | 68.266 | 19.819 | 36.914 | 17.34
| 4.3125 | 299.766 | 298.23 | 68.256 | 19.816 | 36.913 | 17.342
| 4.3139 | 300.028 | 297.863 | 68.25 | 19.816 | 36.909 | 17.342
| 4.3153 | 299.83 | 298.203 | 68.235 | 19.817 | 36.906 | 17.344
| 4.3167 | 300.241 | 298.144 | 68.232 | 19.816 | 36.907 | 17.339
| 4.3181 | 299.848 | 297.976 | 68.227 | 19.817 | 36.904 | 17.342
| 4.3194 | 300.071 | 298.193 | 68.222 | 19.815 | 36.896 | 17.342
| 4.3208 | 300.112 | 298.155 | 68.217 | 19.816 | 36.901 | 17.342
| 4.3222 | 300.277 | 297.302 | 68.209 | 19.816 | 36.894 | 17.34
| 4.3236 | 300.253 | 297.997 | 68.203 | 19.816 | 36.894 | 17.341
| 4.325 | 300.008 | 298.016 | 68.201 | 19.812 | 36.896 | 17.34
| 4.3264 | 300.21 | 297.331 | 68.19 | 19.814 | 36.891 | 17.339
| 4.3278 | 300.383 | 297.245 | 68.188 | 19.813 | 36.888 | 17.345
| 4.3292 | 300.28 | 297.066 | 68.178 | 19.815 | 36.884 | 17.344
| 4.3306 | 300.47 | 297.247 | 68.171 | 19.814 | 36.884 | 17.343
| 4.3319 | 300.088 | 297.668 | 68.168 | 19.814 | 36.885 | 17.343
| 4.3333 | 300.268 | 297.458 | 68.161 | 19.817 | 36.883 | 17.343
| 4.3347 | 299.829 | 297.816 | 68.159 | 19.818 | 36.881 | 17.347
| 4.3361 | 299.905 | 297.428 | 68.152 | 19.818 | 36.88 | 17.342
| 4.3375 | 300.054 | 296.765 | 68.144 | 19.816 | 36.877 | 17.34
| 4.3389 | 300.319 | 296.858 | 68.134 | 19.815 | 36.874 | 17.344
| 4.3403 | 299.804 | 297.325 | 68.125 | 19.817 | 36.868 | 17.342
| 4.3417 | 299.472 | 297.285 | 68.116 | 19.814 | 36.862 | 17.347
| 4.3431 | 300.254 | 297.276 | 68.11 | 19.815 | 36.862 | 17.345
| 4.3444 | 300.763 | 297.41 | 68.106 | 19.817 | 36.86 | 17.346
| 4.3458 | 300.496 | 296.965 | 68.108 | 19.816 | 36.864 | 17.348
| 4.3472 | 302.027 | 298.689 | 68.124 | 19.817 | 36.877 | 17.342
| 4.3486 | 301.915 | 298.727 | 68.142 | 19.812 | 36.896 | 17.346
| 4.35 | 301.784 | 299.276 | 68.16 | 19.817 | 36.913 | 17.349
| 4.3514 | 301.95 | 298.991 | 68.174 | 19.816 | 36.929 | 17.344
| 4.3528 | 301.701 | 299.329 | 68.189 | 19.811 | 36.937 | 17.345
| 4.3542 | 301.928 | 299.126 | 68.192 | 19.817 | 36.943 | 17.346
| 4.3556 | 301.903 | 298.497 | 68.201 | 19.818 | 36.951 | 17.345
| 4.3569 | 301.381 | 298.977 | 68.216 | 19.816 | 36.956 | 17.347
| 4.3583 | 301.418 | 299.119 | 68.213 | 19.819 | 36.958 | 17.347
| 4.3597 | 301.128 | 299.346 | 68.22 | 19.818 | 36.959 | 17.348
| 4.3611 | 301.803 | 299.359 | 68.23 | 19.814 | 36.959 | 17.35
| 4.3625 | 302.072 | 299.652 | 68.244 | 19.818 | 36.97 | 17.348
| 4.3639 | 301.655 | 299.734 | 68.252 | 19.822 | 36.979 | 17.35
| 4.3653 | 302.324 | 299.329 | 68.271 | 19.82 | 36.981 | 17.349
| 4.3667 | 302.404 | 299.292 | 68.278 | 19.817 | 36.987 | 17.348
| 4.3681 | 302.308 | 299.141 | 68.289 | 19.821 | 36.994 | 17.349
| 4.3694 | 301.801 | 299.401 | 68.298 | 19.825 | 36.994 | 17.351
| 4.3708 | 301.799 | 299.916 | 68.305 | 19.82 | 36.997 | 17.35
| 4.3722 | 301.854 | 300.009 | 68.32 | 19.82 | 37.006 | 17.353
| 4.3736 | 302.385 | 299.968 | 68.334 | 19.822 | 37.006 | 17.352
| 4.375 | 302.59 | 299.544 | 68.344 | 19.822 | 37.01 | 17.354
| 4.3764 | 302.304 | 299.12 | 68.352 | 19.824 | 37.015 | 17.355
| 4.3778 | 302.682 | 299.48 | 68.362 | 19.823 | 37.017 | 17.355
| 4.3792 | 301.713 | 299.742 | 68.371 | 19.826 | 37.022 | 17.352
| 4.3806 | 301.893 | 299.072 | 68.375 | 19.825 | 37.021 | 17.351
| 4.3819 | 301.772 | 298.756 | 68.375 | 19.824 | 37.018 | 17.354
| 4.3833 | 301.917 | 299.099 | 68.374 | 19.83 | 37.012 | 17.352
| 4.3847 | 301.825 | 298.813 | 68.378 | 19.833 | 37.01 | 17.357
| 4.3861 | 301.27 | 298.927 | 68.375 | 19.832 | 37 | 17.358
| 4.3875 | 300.817 | 299.117 | 68.374 | 19.83 | 36.999 | 17.356
| 4.3889 | 301.297 | 298.782 | 68.374 | 19.831 | 36.995 | 17.36
| 4.3903 | 301.11 | 298.978 | 68.375 | 19.836 | 36.999 | 17.357
| 4.3917 | 300.854 | 298.234 | 68.362 | 19.831 | 36.985 | 17.361
| 4.3931 | 299.984 | 298.264 | 68.349 | 19.837 | 36.974 | 17.363
| 4.3944 | 300.402 | 298.16 | 68.35 | 19.838 | 36.972 | 17.359
| 4.3958 | 300.62 | 297.824 | 68.346 | 19.838 | 36.964 | 17.36
| 4.3972 | 300.874 | 297.609 | 68.336 | 19.836 | 36.957 | 17.365
| 4.3986 | 300.547 | 298.157 | 68.327 | 19.835 | 36.953 | 17.363
| 4.4 | 300.057 | 298.035 | 68.319 | 19.837 | 36.944 | 17.365
| 4.4014 | 300.618 | 297.907 | 68.316 | 19.842 | 36.942 | 17.363
| 4.4028 | 299.739 | 298.072 | 68.302 | 19.838 | 36.937 | 17.364
| 4.4042 | 300.188 | 298.121 | 68.295 | 19.841 | 36.931 | 17.364
| 4.4056 | 300.195 | 297.587 | 68.287 | 19.839 | 36.923 | 17.365
| 4.4069 | 299.671 | 297.302 | 68.276 | 19.842 | 36.919 | 17.366
| 4.4083 | 300.534 | 297.211 | 68.262 | 19.842 | 36.915 | 17.365
| 4.4097 | 300.092 | 297.519 | 68.259 | 19.84 | 36.914 | 17.369
| 4.4111 | 300.345 | 297.536 | 68.252 | 19.838 | 36.908 | 17.369
| 4.4125 | 300.337 | 297.787 | 68.245 | 19.842 | 36.907 | 17.37
| 4.4139 | 300.259 | 297.798 | 68.248 | 19.844 | 36.907 | 17.374
| 4.4153 | 299.809 | 297.985 | 68.238 | 19.839 | 36.903 | 17.372
| 4.4167 | 300.341 | 297.095 | 68.229 | 19.842 | 36.904 | 17.372
| 4.4181 | 300.486 | 297.07 | 68.219 | 19.841 | 36.904 | 17.375
| 4.4194 | 300.262 | 296.947 | 68.204 | 19.845 | 36.891 | 17.371
| 4.4208 | 299.883 | 296.687 | 68.199 | 19.849 | 36.891 | 17.371
| 4.4222 | 299.877 | 297.116 | 68.188 | 19.845 | 36.884 | 17.374
| 4.4236 | 299.283 | 297.528 | 68.173 | 19.844 | 36.882 | 17.373
| 4.425 | 299.684 | 296.449 | 68.159 | 19.847 | 36.872 | 17.378
| 4.4264 | 299.498 | 296.244 | 68.148 | 19.845 | 36.863 | 17.379
| 4.4278 | 299.44 | 296.232 | 68.128 | 19.848 | 36.853 | 17.376
| 4.4292 | 298.825 | 297.11 | 68.116 | 19.846 | 36.851 | 17.377
| 4.4306 | 299.425 | 296.242 | 68.101 | 19.849 | 36.84 | 17.379
| 4.4319 | 298.045 | 296.398 | 68.083 | 19.848 | 36.833 | 17.381
| 4.4333 | 298.837 | 296.171 | 68.059 | 19.852 | 36.823 | 17.377
| 4.4347 | 298.391 | 295.98 | 68.042 | 19.851 | 36.813 | 17.38
| 4.4361 | 297.996 | 296.225 | 68.022 | 19.849 | 36.801 | 17.38
| 4.4375 | 298.557 | 295.316 | 68.001 | 19.848 | 36.794 | 17.379
| 4.4389 | 298.251 | 296.161 | 67.986 | 19.848 | 36.784 | 17.381
| 4.4403 | 297.878 | 296.106 | 67.966 | 19.843 | 36.78 | 17.383
| 4.4417 | 301.636 | 299.245 | 68.018 | 19.847 | 36.813 | 17.385
| 4.4431 | 301.768 | 300.122 | 68.055 | 19.843 | 36.849 | 17.385
| 4.4444 | 302.25 | 300.186 | 68.085 | 19.846 | 36.881 | 17.382
| 4.4458 | 302.636 | 299.703 | 68.103 | 19.846 | 36.903 | 17.381
| 4.4472 | 302.256 | 299.19 | 68.119 | 19.847 | 36.921 | 17.386
| 4.4486 | 302.075 | 299.54 | 68.143 | 19.849 | 36.933 | 17.383
| 4.45 | 301.67 | 299.964 | 68.152 | 19.855 | 36.943 | 17.388
| 4.4514 | 302.663 | 299.403 | 68.167 | 19.852 | 36.953 | 17.389
| 4.4528 | 302.112 | 299.018 | 68.178 | 19.852 | 36.962 | 17.385
| 4.4542 | 302.147 | 299.296 | 68.188 | 19.85 | 36.971 | 17.387
| 4.4556 | 301.555 | 299.108 | 68.196 | 19.85 | 36.972 | 17.386
| 4.4569 | 301.746 | 299.321 | 68.214 | 19.85 | 36.976 | 17.387
| 4.4583 | 301.634 | 299.169 | 68.218 | 19.855 | 36.976 | 17.391
| 4.4597 | 301.5 | 299.543 | 68.218 | 19.855 | 36.977 | 17.388
| 4.4611 | 301.53 | 299.736 | 68.234 | 19.854 | 36.978 | 17.388
| 4.4625 | 301.966 | 298.823 | 68.246 | 19.858 | 36.986 | 17.393
| 4.4639 | 302.101 | 299.095 | 68.256 | 19.86 | 36.989 | 17.389
| 4.4653 | 301.24 | 299.559 | 68.258 | 19.859 | 36.991 | 17.389
| 4.4667 | 301.773 | 298.504 | 68.265 | 19.862 | 36.991 | 17.389
| 4.4681 | 301.53 | 298.512 | 68.27 | 19.858 | 36.987 | 17.388
| 4.4694 | 300.914 | 299.289 | 68.27 | 19.861 | 36.98 | 17.395
| 4.4708 | 301.524 | 298.511 | 68.269 | 19.864 | 36.98 | 17.396
| 4.4722 | 300.705 | 298.907 | 68.268 | 19.863 | 36.975 | 17.392
| 4.4736 | 301.284 | 298.788 | 68.271 | 19.864 | 36.971 | 17.395
| 4.475 | 300.462 | 298.596 | 68.27 | 19.865 | 36.967 | 17.397
| 4.4764 | 301.002 | 299.302 | 68.265 | 19.866 | 36.966 | 17.395
| 4.4778 | 302.393 | 300.653 | 68.299 | 19.864 | 36.982 | 17.397
| 4.4792 | 303.005 | 300.295 | 68.328 | 19.868 | 37.003 | 17.399
| 4.4806 | 302.63 | 300.167 | 68.351 | 19.865 | 37.018 | 17.397
| 4.4819 | 302.36 | 300.548 | 68.374 | 19.868 | 37.03 | 17.4
| 4.4833 | 302.752 | 300.224 | 68.39 | 19.869 | 37.038 | 17.403
| 4.4847 | 302.265 | 300.564 | 68.402 | 19.87 | 37.049 | 17.404
| 4.4861 | 302.923 | 300.267 | 68.417 | 19.871 | 37.053 | 17.403
| 4.4875 | 302.477 | 300.626 | 68.434 | 19.872 | 37.06 | 17.408
| 4.4889 | 302.211 | 300.422 | 68.445 | 19.876 | 37.064 | 17.405
| 4.4903 | 302.154 | 299.55 | 68.451 | 19.875 | 37.061 | 17.406
| 4.4917 | 302.231 | 299.488 | 68.46 | 19.879 | 37.062 | 17.407
| 4.4931 | 302.467 | 299.338 | 68.458 | 19.879 | 37.059 | 17.406
| 4.4944 | 301.988 | 299.531 | 68.464 | 19.882 | 37.06 | 17.408
| 4.4958 | 302.562 | 299.484 | 68.473 | 19.882 | 37.066 | 17.409
| 4.4972 | 302.038 | 299.63 | 68.478 | 19.88 | 37.063 | 17.409
| 4.4986 | 302.05 | 300.063 | 68.487 | 19.882 | 37.063 | 17.414
| 4.5 | 302.122 | 299.702 | 68.491 | 19.885 | 37.067 | 17.414
| 4.5014 | 302.576 | 299.375 | 68.498 | 19.888 | 37.066 | 17.414
| 4.5028 | 302.464 | 299.19 | 68.511 | 19.886 | 37.075 | 17.413
| 4.5042 | 302.256 | 299.278 | 68.522 | 19.888 | 37.076 | 17.413
| 4.5056 | 302.544 | 299.565 | 68.527 | 19.894 | 37.072 | 17.416
| 4.5069 | 302.444 | 299.203 | 68.53 | 19.894 | 37.077 | 17.418
| 4.5083 | 302.173 | 299.852 | 68.539 | 19.893 | 37.076 | 17.419
| 4.5097 | 301.647 | 299.534 | 68.54 | 19.895 | 37.079 | 17.421
| 4.5111 | 301.389 | 299.612 | 68.538 | 19.898 | 37.071 | 17.422
| 4.5125 | 301.904 | 298.92 | 68.546 | 19.896 | 37.072 | 17.423
| 4.5139 | 301.736 | 299.455 | 68.543 | 19.893 | 37.073 | 17.423
| 4.5153 | 301.705 | 299.349 | 68.542 | 19.898 | 37.065 | 17.424
| 4.5278 | 301.451 | 299.208 | 68.552 | 19.909 | 37.062 | 17.436
| 4.5347 | 300.901 | 299.159 | 68.531 | 19.914 | 37.048 | 17.437
| 4.5417 | 304.121 | 300.994 | 68.666 | 19.916 | 37.148 | 17.445
| 4.5486 | 303.733 | 301.502 | 68.765 | 19.928 | 37.2 | 17.449
| 4.5556 | 304.709 | 301.568 | 68.855 | 19.929 | 37.237 | 17.457
| 4.5625 | 304.228 | 302.542 | 68.935 | 19.943 | 37.266 | 17.462
| 4.5694 | 304.278 | 302.409 | 69.026 | 19.953 | 37.301 | 17.465
| 4.5764 | 304.872 | 301.967 | 69.102 | 19.959 | 37.326 | 17.477
| 4.5833 | 300.931 | 297.732 | 69.017 | 19.98 | 37.25 | 17.49
| 4.5903 | 301.476 | 298.368 | 68.936 | 19.976 | 37.164 | 17.488
| 4.5972 | 301.301 | 298.618 | 68.877 | 19.982 | 37.14 | 17.497
| 4.6042 | 301.544 | 299.027 | 68.849 | 19.985 | 37.149 | 17.499
| 4.6111 | 301.232 | 298.527 | 68.813 | 19.994 | 37.143 | 17.509
| 4.6181 | 302.13 | 299.417 | 68.799 | 19.996 | 37.147 | 17.513
| 4.625 | 301.614 | 299.718 | 68.804 | 19.999 | 37.17 | 17.519
| 4.6319 | 302.736 | 299.673 | 68.805 | 20.006 | 37.179 | 17.518
| 4.6389 | 301.929 | 300.109 | 68.825 | 20.01 | 37.192 | 17.528
| 4.6458 | 301.738 | 300.174 | 68.827 | 20.016 | 37.198 | 17.531
| 4.6528 | 301.873 | 299.922 | 68.841 | 20.021 | 37.205 | 17.538
| 4.6597 | 302.358 | 299.99 | 68.841 | 20.031 | 37.212 | 17.542
| 4.6667 | 302.13 | 300.205 | 68.853 | 20.029 | 37.217 | 17.55
| 4.6736 | 301.882 | 300.265 | 68.866 | 20.041 | 37.23 | 17.555
| 4.6806 | 302.093 | 300.03 | 68.869 | 20.045 | 37.225 | 17.559
| 4.6875 | 301.929 | 298.939 | 68.848 | 20.053 | 37.211 | 17.566
| 4.6944 | 301.95 | 300.291 | 68.859 | 20.06 | 37.224 | 17.572
| 4.7014 | 301.412 | 299.266 | 68.845 | 20.059 | 37.215 | 17.575
| 4.7083 | 300.66 | 297.702 | 68.775 | 20.066 | 37.169 | 17.583
| 4.7153 | 302.346 | 299.399 | 68.719 | 20.071 | 37.143 | 17.587
| 4.7222 | 299.63 | 296.755 | 68.648 | 20.071 | 37.116 | 17.592
| 4.7292 | 301.564 | 298.991 | 68.644 | 20.078 | 37.135 | 17.598
| 4.7361 | 301.456 | 299.791 | 68.659 | 20.077 | 37.167 | 17.608
| 4.7431 | 301.055 | 298.538 | 68.637 | 20.082 | 37.155 | 17.611
| 4.75 | 302.724 | 300.93 | 68.761 | 20.084 | 37.249 | 17.615
| 4.7569 | 303.492 | 300.817 | 68.842 | 20.096 | 37.295 | 17.619
| 4.7639 | 302.441 | 300.355 | 68.881 | 20.103 | 37.303 | 17.626
| 4.7708 | 302.836 | 300.756 | 68.912 | 20.108 | 37.305 | 17.629
| 4.7778 | 303.246 | 300.55 | 68.97 | 20.113 | 37.331 | 17.637
| 4.7847 | 302.785 | 301.165 | 69.017 | 20.119 | 37.342 | 17.645
| 4.7917 | 302.839 | 301.278 | 69.051 | 20.126 | 37.355 | 17.652
| 4.7986 | 303.31 | 301.483 | 69.108 | 20.135 | 37.383 | 17.66
| 4.8056 | 303.408 | 301.852 | 69.167 | 20.143 | 37.411 | 17.667
| 4.8125 | 303.161 | 301.504 | 69.205 | 20.151 | 37.417 | 17.673
| 4.8194 | 303.637 | 300.995 | 69.234 | 20.162 | 37.425 | 17.68
| 4.8264 | 303.889 | 301.422 | 69.27 | 20.168 | 37.44 | 17.687
| 4.8333 | 303.794 | 302.141 | 69.323 | 20.18 | 37.463 | 17.701
| 4.8403 | 304.313 | 301.739 | 69.384 | 20.185 | 37.496 | 17.704
| 4.8472 | 301.212 | 299.227 | 69.362 | 20.195 | 37.466 | 17.717
| 4.8542 | 299.029 | 297.442 | 69.258 | 20.205 | 37.384 | 17.722
| 4.8611 | 300.142 | 297.042 | 69.103 | 20.209 | 37.285 | 17.738
| 4.8681 | 300.058 | 298.153 | 69.009 | 20.214 | 37.253 | 17.741
| 4.875 | 300.869 | 297.799 | 68.945 | 20.219 | 37.252 | 17.75
| 4.8819 | 300.67 | 298.417 | 68.917 | 20.218 | 37.268 | 17.757
| 4.8889 | 301.338 | 298.565 | 68.9 | 20.223 | 37.288 | 17.765
| 4.8958 | 300.53 | 297.335 | 68.824 | 20.225 | 37.257 | 17.769
| 4.9028 | 300.815 | 298.219 | 68.783 | 20.226 | 37.246 | 17.776
| 4.9097 | 300.837 | 298.903 | 68.76 | 20.23 | 37.252 | 17.783
| 4.9167 | 300.953 | 298.875 | 68.763 | 20.234 | 37.274 | 17.79
| 4.9236 | 300.839 | 298.41 | 68.752 | 20.237 | 37.274 | 17.793
| 4.9306 | 298.493 | 296.677 | 68.632 | 20.242 | 37.199 | 17.804
| 4.9375 | 298.128 | 296.535 | 68.532 | 20.243 | 37.147 | 17.807
| 4.9444 | 299.202 | 296.045 | 68.454 | 20.249 | 37.118 | 17.812
| 4.9514 | 298.869 | 297.01 | 68.398 | 20.246 | 37.118 | 17.815
| 4.9583 | 299.35 | 297.778 | 68.38 | 20.252 | 37.141 | 17.823
| 4.9653 | 299.378 | 297.475 | 68.364 | 20.25 | 37.155 | 17.827
| 4.9722 | 300.867 | 297.922 | 68.373 | 20.25 | 37.17 | 17.836
| 4.9792 | 301.827 | 298.821 | 68.447 | 20.249 | 37.23 | 17.838
| 4.9861 | 300.957 | 299.307 | 68.496 | 20.256 | 37.259 | 17.842
| 4.9931 | 301.211 | 299.424 | 68.546 | 20.262 | 37.277 | 17.847
| 5 | 302.09 | 299.592 | 68.606 | 20.267 | 37.302 | 17.852
| 5.0069 | 302.193 | 299.117 | 68.663 | 20.274 | 37.33 | 17.861
| 5.0139 | 303.212 | 301.152 | 68.745 | 20.279 | 37.368 | 17.865
| 5.0208 | 303.309 | 300.313 | 68.846 | 20.29 | 37.425 | 17.872
| 5.0278 | 303.076 | 300.139 | 68.907 | 20.295 | 37.432 | 17.881
| 5.0347 | 302.996 | 300.105 | 68.971 | 20.305 | 37.447 | 17.888
| 5.0417 | 302.108 | 299.547 | 68.969 | 20.317 | 37.429 | 17.898
| 5.0486 | 302.032 | 299.364 | 68.985 | 20.322 | 37.422 | 17.903
| 5.0556 | 302.189 | 300.508 | 69.025 | 20.331 | 37.438 | 17.916
| 5.0625 | 303.037 | 300.224 | 69.078 | 20.338 | 37.468 | 17.922
| 5.0694 | 303.648 | 300.838 | 69.138 | 20.35 | 37.496 | 17.929
| 5.0764 | 302.961 | 301.214 | 69.193 | 20.357 | 37.52 | 17.937
| 5.0833 | 303.543 | 300.263 | 69.236 | 20.367 | 37.547 | 17.946
| 5.0903 | 303.336 | 300.969 | 69.291 | 20.38 | 37.563 | 17.957
| 5.0972 | 302.895 | 301.199 | 69.338 | 20.385 | 37.581 | 17.968
| 5.1042 | 304.061 | 301.035 | 69.393 | 20.396 | 37.606 | 17.974
| 5.1111 | 300.009 | 297.842 | 69.457 | 20.406 | 37.636 | 17.985
| 5.1181 | 299.482 | 297.834 | 69.269 | 20.414 | 37.479 | 17.993
| 5.125 | 300.249 | 297.214 | 69.166 | 20.422 | 37.426 | 18.005
| 5.1319 | 300.763 | 297.712 | 69.088 | 20.424 | 37.403 | 18.01
| 5.1389 | 300.55 | 298.573 | 69.039 | 20.433 | 37.404 | 18.018
| 5.1458 | 300.8 | 299.114 | 69.031 | 20.433 | 37.43 | 18.024
| 5.1528 | 300.963 | 298.275 | 69.007 | 20.439 | 37.438 | 18.031
| 5.1597 | 299.875 | 296.632 | 68.955 | 20.444 | 37.411 | 18.037
| 5.1667 | 299.46 | 296.616 | 68.877 | 20.449 | 37.37 | 18.047
| 5.1736 | 299.486 | 296.388 | 68.805 | 20.448 | 37.346 | 18.053
| 5.1806 | 298.93 | 296.829 | 68.731 | 20.454 | 37.323 | 18.062
| 5.1875 | 298.899 | 296.139 | 68.667 | 20.453 | 37.305 | 18.067
| 5.1944 | 298.564 | 296.169 | 68.598 | 20.456 | 37.285 | 18.066
| 5.2014 | 298.521 | 295.745 | 68.52 | 20.454 | 37.265 | 18.073
| 5.2083 | 298.376 | 295.755 | 68.458 | 20.457 | 37.244 | 18.077
| 5.2153 | 298.028 | 295.18 | 68.378 | 20.457 | 37.218 | 18.083
| 5.2222 | 300.598 | 298.34 | 68.478 | 20.459 | 37.32 | 18.087
| 5.2292 | 299.849 | 298.134 | 68.51 | 20.462 | 37.349 | 18.094
| 5.2361 | 300.378 | 298.497 | 68.532 | 20.47 | 37.355 | 18.099
| 5.2431 | 300.309 | 297.822 | 68.568 | 20.473 | 37.375 | 18.105
| 5.25 | 301.905 | 299.541 | 68.645 | 20.478 | 37.424 | 18.105
| 5.2569 | 302.03 | 298.941 | 68.736 | 20.484 | 37.472 | 18.112
| 5.2639 | 298.556 | 296.377 | 68.708 | 20.49 | 37.439 | 18.118
| 5.2708 | 298.295 | 295.733 | 68.607 | 20.497 | 37.338 | 18.124
| 5.2778 | 301.99 | 300.032 | 68.734 | 20.499 | 37.441 | 18.133
| 5.2847 | 302.368 | 300.173 | 68.862 | 20.505 | 37.525 | 18.138
| 5.2917 | 302.273 | 299.186 | 68.931 | 20.514 | 37.555 | 18.142
| 5.2986 | 301.5 | 298.501 | 68.95 | 20.523 | 37.544 | 18.148
| 5.3056 | 299.561 | 297.075 | 68.914 | 20.536 | 37.492 | 18.158
| 5.3125 | 298.74 | 296.032 | 68.85 | 20.54 | 37.447 | 18.165
| 5.3194 | 298.757 | 295.891 | 68.782 | 20.549 | 37.404 | 18.171
| 5.3264 | 302.412 | 299.109 | 68.889 | 20.548 | 37.5 | 18.177
| 5.3333 | 300.406 | 297.049 | 68.892 | 20.554 | 37.51 | 18.187
| 5.3403 | 302.592 | 299.903 | 69.012 | 20.561 | 37.585 | 18.193
| 5.3472 | 305.086 | 302.567 | 69.152 | 20.575 | 37.665 | 18.203
| 5.3542 | 304.735 | 302.883 | 69.31 | 20.58 | 37.751 | 18.206
| 5.3611 | 305.432 | 302.046 | 69.463 | 20.594 | 37.816 | 18.216
| 5.3681 | 304.87 | 302.489 | 69.584 | 20.607 | 37.848 | 18.221
| 5.375 | 304.844 | 302.917 | 69.718 | 20.62 | 37.896 | 18.231
| 5.3819 | 305.963 | 302.945 | 69.826 | 20.635 | 37.924 | 18.24
| 5.3889 | 301.803 | 299.806 | 69.816 | 20.644 | 37.874 | 18.253
| 5.3958 | 302.167 | 299.191 | 69.761 | 20.657 | 37.803 | 18.259
| 5.4028 | 301.288 | 299.187 | 69.701 | 20.67 | 37.759 | 18.265
| 5.4097 | 300.908 | 298.666 | 69.642 | 20.681 | 37.738 | 18.278
| 5.4167 | 301.688 | 298.673 | 69.6 | 20.686 | 37.725 | 18.287
| 5.4236 | 300.693 | 298.81 | 69.563 | 20.689 | 37.723 | 18.298
| 5.4306 | 301.243 | 298.703 | 69.524 | 20.7 | 37.722 | 18.301
| 5.4375 | 301.342 | 299.061 | 69.51 | 20.706 | 37.729 | 18.308
| 5.4444 | 301.508 | 298.748 | 69.499 | 20.709 | 37.738 | 18.318
| 5.4514 | 300.23 | 298.407 | 69.481 | 20.715 | 37.737 | 18.324
| 5.4583 | 300.561 | 298.625 | 69.447 | 20.726 | 37.727 | 18.334
| 5.4653 | 300.727 | 298.707 | 69.437 | 20.732 | 37.727 | 18.336
| 5.4722 | 300.982 | 298.979 | 69.426 | 20.736 | 37.734 | 18.344
| 5.4792 | 300.709 | 298.414 | 69.397 | 20.742 | 37.725 | 18.349
| 5.4861 | 300.594 | 298.577 | 69.383 | 20.744 | 37.724 | 18.355
| 5.4931 | 300.879 | 298.616 | 69.376 | 20.753 | 37.722 | 18.361
| 5.5 | 300.467 | 298.003 | 69.369 | 20.756 | 37.729 | 18.362
| 5.5069 | 301.325 | 298.206 | 69.353 | 20.765 | 37.724 | 18.371
| 5.5139 | 301.476 | 300.032 | 69.383 | 20.766 | 37.756 | 18.372
| 5.5208 | 300.84 | 299.174 | 69.42 | 20.773 | 37.779 | 18.377
| 5.5278 | 300.261 | 297.413 | 69.366 | 20.78 | 37.743 | 18.386
| 5.5347 | 300.725 | 299.124 | 69.352 | 20.786 | 37.732 | 18.391
| 5.5417 | 300.996 | 297.777 | 69.357 | 20.792 | 37.746 | 18.392
| 5.5486 | 301.43 | 298.205 | 69.362 | 20.797 | 37.75 | 18.396
| 5.5556 | 300.631 | 298.37 | 69.379 | 20.799 | 37.759 | 18.402
| 5.5625 | 301.319 | 298.281 | 69.356 | 20.81 | 37.743 | 18.403
| 5.5694 | 300.428 | 297.753 | 69.333 | 20.811 | 37.735 | 18.409
| 5.5764 | 300.608 | 297.301 | 69.306 | 20.814 | 37.724 | 18.419
| 5.5833 | 299.677 | 297.745 | 69.281 | 20.823 | 37.707 | 18.42
| 5.5903 | 300.859 | 298.862 | 69.279 | 20.826 | 37.724 | 18.424
| 5.5972 | 300.788 | 298.92 | 69.313 | 20.831 | 37.755 | 18.423
| 5.6042 | 301.121 | 298.478 | 69.331 | 20.835 | 37.771 | 18.43
| 5.6111 | 301.478 | 299.389 | 69.373 | 20.842 | 37.798 | 18.432
| 5.6181 | 300.6 | 298.517 | 69.366 | 20.849 | 37.784 | 18.432
| 5.625 | 301.305 | 298.437 | 69.372 | 20.852 | 37.788 | 18.435
| 5.6319 | 301.362 | 298.989 | 69.4 | 20.861 | 37.81 | 18.441
| 5.6389 | 301.437 | 298.483 | 69.414 | 20.86 | 37.82 | 18.448
| 5.6458 | 300.74 | 299.181 | 69.435 | 20.874 | 37.824 | 18.45
| 5.6528 | 301.329 | 298.425 | 69.453 | 20.879 | 37.833 | 18.457
| 5.6597 | 301.355 | 298.469 | 69.47 | 20.884 | 37.838 | 18.459
| 5.6667 | 301.227 | 298.452 | 69.462 | 20.889 | 37.837 | 18.461
| 5.6736 | 301.184 | 299.562 | 69.481 | 20.895 | 37.853 | 18.469
| 5.6806 | 300.997 | 298.053 | 69.475 | 20.901 | 37.842 | 18.469
| 5.6875 | 300.889 | 298.897 | 69.468 | 20.908 | 37.84 | 18.474
| 5.6944 | 300.446 | 298.298 | 69.468 | 20.91 | 37.843 | 18.478
| 5.7014 | 300.207 | 298.651 | 69.449 | 20.918 | 37.833 | 18.486
| 5.7083 | 300.661 | 298.617 | 69.451 | 20.919 | 37.84 | 18.487
| 5.7153 | 298.826 | 297.272 | 69.388 | 20.929 | 37.805 | 18.488
| 5.7222 | 299.242 | 297.707 | 69.289 | 20.929 | 37.744 | 18.493
| 5.7292 | 300.896 | 298.342 | 69.35 | 20.929 | 37.815 | 18.498
| 5.7361 | 300.81 | 298.236 | 69.359 | 20.936 | 37.825 | 18.499
| 5.7431 | 300.67 | 298.615 | 69.364 | 20.938 | 37.839 | 18.506
| 5.75 | 300.903 | 298.046 | 69.37 | 20.946 | 37.844 | 18.51
| 5.7569 | 301.392 | 298.704 | 69.384 | 20.95 | 37.849 | 18.511
| 5.7639 | 301.662 | 299.65 | 69.426 | 20.957 | 37.885 | 18.513
| 5.7708 | 301.863 | 299.372 | 69.478 | 20.959 | 37.913 | 18.515
| 5.7778 | 301.441 | 298.929 | 69.501 | 20.967 | 37.918 | 18.523
| 5.7847 | 301.522 | 298.44 | 69.517 | 20.972 | 37.915 | 18.522
| 5.7917 | 302.202 | 299.164 | 69.562 | 20.979 | 37.938 | 18.531
| 5.7986 | 302.547 | 299.361 | 69.608 | 20.989 | 37.966 | 18.536
| 5.8056 | 302.294 | 300.479 | 69.66 | 20.996 | 37.986 | 18.542
| 5.8125 | 302.427 | 300.602 | 69.724 | 21.001 | 38.025 | 18.546
| 5.8194 | 303.724 | 300.543 | 69.815 | 21.009 | 38.069 | 18.554
| 5.8264 | 304.407 | 301.264 | 69.904 | 21.016 | 38.109 | 18.555
| 5.8333 | 303.932 | 301.854 | 70.017 | 21.028 | 38.166 | 18.562
| 5.8403 | 303.665 | 301.692 | 70.081 | 21.035 | 38.188 | 18.572
| 5.8472 | 304.489 | 302.895 | 70.146 | 21.053 | 38.197 | 18.581
| 5.8542 | 303.893 | 301.417 | 70.207 | 21.06 | 38.225 | 18.587
| 5.8611 | 304.998 | 301.525 | 70.274 | 21.069 | 38.243 | 18.597
| 5.8681 | 301.262 | 299.011 | 70.213 | 21.083 | 38.18 | 18.604
| 5.875 | 301.6 | 298.971 | 70.153 | 21.091 | 38.125 | 18.615
| 5.8819 | 301.838 | 299.771 | 70.114 | 21.092 | 38.113 | 18.621
| 5.8889 | 302.679 | 299.445 | 70.118 | 21.101 | 38.136 | 18.631
| 5.8958 | 300.807 | 296.991 | 70.023 | 21.103 | 38.083 | 18.633
| 5.9028 | 301.788 | 298.08 | 69.979 | 21.111 | 38.069 | 18.642
| 5.9097 | 301.595 | 298.278 | 69.956 | 21.123 | 38.075 | 18.654
| 5.9167 | 302.183 | 299.545 | 69.958 | 21.124 | 38.099 | 18.657
| 5.9236 | 302.165 | 300.231 | 69.994 | 21.128 | 38.144 | 18.662
| 5.9306 | 304.26 | 301.167 | 70.072 | 21.138 | 38.201 | 18.67
| 5.9375 | 303.722 | 300.732 | 70.142 | 21.142 | 38.238 | 18.673
| 5.9444 | 304.564 | 301.405 | 70.235 | 21.147 | 38.278 | 18.681
| 5.9514 | 305.454 | 302.307 | 70.325 | 21.157 | 38.328 | 18.685
| 5.9583 | 301.526 | 299.556 | 70.239 | 21.172 | 38.257 | 18.695
| 5.9653 | 299.951 | 298.12 | 70.215 | 21.177 | 38.229 | 18.7
| 5.9722 | 302.026 | 298.641 | 70.124 | 21.187 | 38.167 | 18.71
| 5.9792 | 299.324 | 296.865 | 70.042 | 21.191 | 38.13 | 18.719
| 5.9861 | 299.457 | 296.478 | 69.921 | 21.193 | 38.062 | 18.724
| 5.9931 | 299.148 | 297.12 | 69.839 | 21.197 | 38.035 | 18.727
| 6 | 299.647 | 297.73 | 69.777 | 21.197 | 38.035 | 18.732
| 6.0069 | 299.838 | 297.545 | 69.718 | 21.199 | 38.033 | 18.742
| 6.0139 | 300.896 | 298.707 | 69.701 | 21.203 | 38.04 | 18.737
| 6.0208 | 302.072 | 298.891 | 69.746 | 21.202 | 38.093 | 18.742
| 6.0278 | 301.199 | 298.507 | 69.774 | 21.205 | 38.125 | 18.749
| 6.0347 | 301.344 | 298.74 | 69.786 | 21.207 | 38.131 | 18.752
| 6.0417 | 300.723 | 297.84 | 69.761 | 21.209 | 38.112 | 18.751
| 6.0486 | 300.66 | 298.363 | 69.752 | 21.222 | 38.108 | 18.758
| 6.0556 | 301.634 | 298.218 | 69.757 | 21.221 | 38.108 | 18.759
| 6.0625 | 301.535 | 298.102 | 69.775 | 21.228 | 38.129 | 18.766
| 6.0694 | 301.682 | 297.971 | 69.805 | 21.231 | 38.14 | 18.768
| 6.0764 | 301.904 | 297.743 | 69.825 | 21.237 | 38.156 | 18.776
| 6.0833 | 301.543 | 298.691 | 69.846 | 21.242 | 38.165 | 18.776
| 6.0903 | 302.498 | 298.81 | 69.885 | 21.25 | 38.19 | 18.785
| 6.0972 | 302.895 | 299.12 | 69.943 | 21.253 | 38.224 | 18.783
| 6.1042 | 302.703 | 299.664 | 69.991 | 21.264 | 38.25 | 18.79
| 6.1111 | 302.604 | 299.615 | 70.041 | 21.27 | 38.269 | 18.792
| 6.1181 | 302.286 | 299.761 | 70.082 | 21.276 | 38.283 | 18.8
| 6.125 | 302.725 | 299.108 | 70.111 | 21.281 | 38.288 | 18.803
| 6.1319 | 302.66 | 299.131 | 70.141 | 21.291 | 38.294 | 18.806
| 6.1389 | 303.044 | 299.165 | 70.167 | 21.296 | 38.304 | 18.814
| 6.1458 | 303.124 | 298.87 | 70.202 | 21.303 | 38.324 | 18.816
| 6.1528 | 302.987 | 299.063 | 70.215 | 21.318 | 38.333 | 18.824
| 6.1597 | 302.255 | 299.747 | 70.234 | 21.32 | 38.329 | 18.827
| 6.1667 | 302.205 | 299.943 | 70.25 | 21.325 | 38.339 | 18.833
| 6.1736 | 302.956 | 299.646 | 70.269 | 21.333 | 38.348 | 18.836
| 6.1806 | 302.339 | 299.33 | 70.287 | 21.341 | 38.357 | 18.846
| 6.1875 | 302.95 | 299.205 | 70.296 | 21.348 | 38.357 | 18.848
| 6.1944 | 302.258 | 300.017 | 70.321 | 21.359 | 38.383 | 18.849
| 6.2014 | 302.664 | 299.444 | 70.322 | 21.363 | 38.378 | 18.853
| 6.2083 | 302.41 | 298.886 | 70.315 | 21.371 | 38.37 | 18.863
| 6.2153 | 302.04 | 298.662 | 70.303 | 21.375 | 38.358 | 18.864
| 6.2222 | 301.587 | 298.093 | 70.279 | 21.377 | 38.346 | 18.867
| 6.2292 | 300.463 | 298.049 | 70.229 | 21.384 | 38.318 | 18.872
| 6.2361 | 300.553 | 296.931 | 70.17 | 21.385 | 38.285 | 18.875
| 6.2431 | 300.6 | 297.036 | 70.097 | 21.39 | 38.255 | 18.878
| 6.25 | 300.4 | 296.887 | 70.032 | 21.393 | 38.233 | 18.879
| 6.2569 | 299.924 | 297.23 | 69.967 | 21.4 | 38.223 | 18.886
| 6.2639 | 301.74 | 298.656 | 69.898 | 21.399 | 38.195 | 18.883
| 6.2708 | 303.015 | 299.321 | 70.046 | 21.402 | 38.325 | 18.887
| 6.2778 | 302.558 | 298.846 | 70.086 | 21.408 | 38.354 | 18.889
| 6.2847 | 301.156 | 298.809 | 70.091 | 21.408 | 38.347 | 18.887
| 6.2917 | 302.553 | 299.282 | 70.132 | 21.412 | 38.351 | 18.894
| 6.2986 | 301.804 | 298.851 | 70.149 | 21.423 | 38.362 | 18.899
| 6.3056 | 301.636 | 299.427 | 70.164 | 21.424 | 38.362 | 18.896
| 6.3125 | 300.592 | 297.809 | 70.144 | 21.427 | 38.346 | 18.898
| 6.3194 | 300.004 | 297.783 | 70.079 | 21.435 | 38.296 | 18.898
| 6.3264 | 302.74 | 299.737 | 70.047 | 21.434 | 38.28 | 18.901
| 6.3333 | 300.954 | 298.644 | 70.092 | 21.439 | 38.334 | 18.906
| 6.3403 | 300.811 | 298.448 | 70.065 | 21.435 | 38.309 | 18.904
| 6.3472 | 303.914 | 301.201 | 70.185 | 21.44 | 38.405 | 18.907
| 6.3542 | 304.142 | 300.767 | 70.313 | 21.448 | 38.491 | 18.91
| 6.3611 | 304.397 | 301.993 | 70.42 | 21.459 | 38.534 | 18.909
| 6.3681 | 304.652 | 301.63 | 70.54 | 21.465 | 38.579 | 18.909
| 6.375 | 305.392 | 301.68 | 70.645 | 21.474 | 38.615 | 18.915
| 6.3819 | 305.601 | 301.923 | 70.758 | 21.484 | 38.655 | 18.924
| 6.3889 | 305.621 | 302.829 | 70.861 | 21.493 | 38.69 | 18.921
| 6.3958 | 305.952 | 302.687 | 70.972 | 21.505 | 38.733 | 18.928
| 6.4028 | 304.346 | 302.062 | 71.029 | 21.52 | 38.731 | 18.936
| 6.4097 | 305.022 | 301.33 | 71.064 | 21.531 | 38.729 | 18.937
| 6.4167 | 304.358 | 302.28 | 71.099 | 21.536 | 38.732 | 18.942
| 6.4236 | 304.066 | 301.808 | 71.125 | 21.549 | 38.73 | 18.948
| 6.4306 | 303.499 | 301.449 | 71.12 | 21.558 | 38.716 | 18.952
| 6.4375 | 303.395 | 300.609 | 71.116 | 21.568 | 38.709 | 18.96
| 6.4444 | 302.988 | 300.608 | 71.094 | 21.575 | 38.701 | 18.966
| 6.4514 | 302.595 | 300.509 | 71.065 | 21.578 | 38.679 | 18.968
| 6.4583 | 302.933 | 299.458 | 71.03 | 21.589 | 38.662 | 18.972
| 6.4653 | 302.834 | 299.02 | 70.995 | 21.594 | 38.65 | 18.976
| 6.4722 | 302.337 | 298.925 | 70.947 | 21.594 | 38.631 | 18.983
| 6.4792 | 302.592 | 299.248 | 70.905 | 21.604 | 38.625 | 18.986
| 6.4861 | 302.306 | 299.685 | 70.868 | 21.604 | 38.617 | 18.982
| 6.4931 | 302.356 | 299.696 | 70.838 | 21.611 | 38.609 | 18.985
| 6.5 | 303.004 | 299.773 | 70.81 | 21.616 | 38.612 | 18.989
| 6.5069 | 302.459 | 300.361 | 70.797 | 21.614 | 38.617 | 18.988
| 6.5139 | 303.364 | 300.002 | 70.801 | 21.616 | 38.63 | 18.991
| 6.5208 | 302.415 | 300.407 | 70.82 | 21.62 | 38.659 | 18.991
| 6.5278 | 304.038 | 300.531 | 70.859 | 21.622 | 38.686 | 18.994
| 6.5347 | 302.765 | 300.122 | 70.859 | 21.629 | 38.687 | 18.997
| 6.5417 | 303.031 | 300.884 | 70.867 | 21.631 | 38.685 | 19.001
| 6.5486 | 303.214 | 299.809 | 70.883 | 21.64 | 38.699 | 19.004
| 6.5556 | 303.354 | 300.176 | 70.893 | 21.645 | 38.702 | 19.004
| 6.5625 | 302.403 | 299.842 | 70.879 | 21.651 | 38.68 | 19.005
| 6.5694 | 303.772 | 300.668 | 70.891 | 21.657 | 38.69 | 19.007
| 6.5764 | 303.334 | 299.956 | 70.905 | 21.66 | 38.704 | 19.011
| 6.5833 | 303.978 | 300.947 | 70.961 | 21.663 | 38.743 | 19.01
| 6.5903 | 304.092 | 301.532 | 70.999 | 21.665 | 38.764 | 19.011
| 6.5972 | 305.355 | 301.963 | 71.073 | 21.669 | 38.801 | 19.017
| 6.6042 | 304.427 | 302.304 | 71.128 | 21.678 | 38.828 | 19.012
| 6.6111 | 304.601 | 301.786 | 71.171 | 21.686 | 38.837 | 19.018
| 6.6181 | 304.181 | 301.815 | 71.199 | 21.694 | 38.843 | 19.02
| 6.625 | 304.742 | 302.633 | 71.247 | 21.701 | 38.865 | 19.021
| 6.6319 | 304.727 | 301.825 | 71.314 | 21.706 | 38.898 | 19.023
| 6.6389 | 304.621 | 302.301 | 71.358 | 21.713 | 38.917 | 19.029
| 6.6458 | 305.783 | 302.233 | 71.41 | 21.721 | 38.932 | 19.03
| 6.6528 | 301.693 | 298.24 | 71.234 | 21.727 | 38.788 | 19.031
| 6.6597 | 301.451 | 299.383 | 71.143 | 21.732 | 38.737 | 19.04
| 6.6667 | 301.765 | 298.552 | 71.067 | 21.731 | 38.713 | 19.039
| 6.6736 | 301.181 | 299.043 | 71.002 | 21.734 | 38.702 | 19.04
| 6.6806 | 301.279 | 297.782 | 70.931 | 21.735 | 38.685 | 19.038
| 6.6875 | 301.566 | 298.906 | 70.857 | 21.735 | 38.656 | 19.044
| 6.6944 | 301.913 | 298.79 | 70.829 | 21.736 | 38.676 | 19.043
| 6.7014 | 300.591 | 297.942 | 70.759 | 21.739 | 38.643 | 19.044
| 6.7083 | 299.569 | 297.59 | 70.657 | 21.74 | 38.592 | 19.045
| 6.7153 | 301.249 | 299.051 | 70.548 | 21.739 | 38.545 | 19.042
| 6.7222 | 300.461 | 297.249 | 70.545 | 21.735 | 38.579 | 19.041
| 6.7292 | 299.871 | 297.58 | 70.482 | 21.731 | 38.556 | 19.043
| 6.7361 | 299.636 | 297.485 | 70.41 | 21.728 | 38.53 | 19.039
| 6.7431 | 299.686 | 297.265 | 70.329 | 21.731 | 38.495 | 19.039
| 6.75 | 299.599 | 296.074 | 70.248 | 21.726 | 38.461 | 19.034
| 6.7569 | 299.72 | 297.307 | 70.195 | 21.721 | 38.45 | 19.034
| 6.7639 | 300.261 | 298.319 | 70.195 | 21.723 | 38.482 | 19.03
| 6.7708 | 300.605 | 297.192 | 70.191 | 21.722 | 38.496 | 19.028
| 6.7778 | 300.324 | 297.14 | 70.178 | 21.722 | 38.491 | 19.027
| 6.7847 | 300.093 | 297.802 | 70.179 | 21.723 | 38.506 | 19.025
| 6.7917 | 302.216 | 300.078 | 70.285 | 21.724 | 38.577 | 19.022
| 6.7986 | 303.023 | 299.835 | 70.371 | 21.723 | 38.627 | 19.02
| 6.8056 | 303.906 | 300.803 | 70.487 | 21.725 | 38.687 | 19.025
| 6.8125 | 304.91 | 301.46 | 70.626 | 21.732 | 38.758 | 19.025
| 6.8194 | 305.516 | 302.038 | 70.793 | 21.738 | 38.831 | 19.02
| 6.8264 | 301.535 | 298.131 | 70.69 | 21.745 | 38.71 | 19.026
| 6.8333 | 301.383 | 298.83 | 70.66 | 21.751 | 38.668 | 19.028
| 6.8403 | 302.392 | 299.64 | 70.673 | 21.752 | 38.671 | 19.032
| 6.8472 | 302.037 | 299.315 | 70.716 | 21.758 | 38.713 | 19.033
| 6.8542 | 301.436 | 298.812 | 70.695 | 21.76 | 38.69 | 19.028
| 6.8611 | 300.797 | 298.506 | 70.648 | 21.763 | 38.65 | 19.034
| 6.8681 | 301.715 | 298.084 | 70.621 | 21.764 | 38.641 | 19.032
| 6.875 | 302.082 | 299.796 | 70.634 | 21.771 | 38.656 | 19.037
| 6.8819 | 302.396 | 299.983 | 70.68 | 21.77 | 38.694 | 19.037
| 6.8889 | 301.459 | 298.908 | 70.673 | 21.777 | 38.693 | 19.039
| 6.8958 | 301.154 | 297.624 | 70.606 | 21.778 | 38.644 | 19.037
| 6.9028 | 301.629 | 298.531 | 70.585 | 21.785 | 38.635 | 19.037
| 6.9097 | 301.396 | 299.033 | 70.575 | 21.782 | 38.642 | 19.04
| 6.9167 | 301.433 | 299.195 | 70.599 | 21.787 | 38.665 | 19.04
| 6.9236 | 302.058 | 298.597 | 70.6 | 21.789 | 38.666 | 19.045
| 6.9306 | 303.597 | 300.62 | 70.64 | 21.788 | 38.704 | 19.046
| 6.9375 | 304.234 | 300.64 | 70.755 | 21.797 | 38.778 | 19.045
| 6.9444 | 304.254 | 301.67 | 70.863 | 21.803 | 38.835 | 19.047
| 6.9514 | 304.353 | 301.844 | 70.968 | 21.8 | 38.879 | 19.045
| 6.9583 | 304.973 | 302.407 | 71.067 | 21.809 | 38.92 | 19.052
| 6.9653 | 300.696 | 298.46 | 70.971 | 21.823 | 38.817 | 19.056
| 6.9722 | 302.771 | 300.44 | 70.953 | 21.825 | 38.79 | 19.061
| 6.9792 | 300.233 | 297.933 | 70.864 | 21.83 | 38.734 | 19.061
| 6.9861 | 300.985 | 297.317 | 70.791 | 21.828 | 38.687 | 19.066
| 6.9931 | 302.137 | 298.862 | 70.752 | 21.832 | 38.685 | 19.067
| 7 | 301.507 | 298.808 | 70.737 | 21.831 | 38.696 | 19.07
| 7.0069 | 302.785 | 299.025 | 70.744 | 21.834 | 38.717 | 19.07
| 7.0139 | 304.008 | 301.22 | 70.821 | 21.835 | 38.781 | 19.071
| 7.0208 | 301.678 | 298.075 | 70.89 | 21.841 | 38.832 | 19.071
| 7.0278 | 299.024 | 295.526 | 70.656 | 21.842 | 38.641 | 19.074
| 7.0347 | 297.828 | 296.042 | 70.499 | 21.841 | 38.552 | 19.075
| 7.0417 | 302.137 | 298.609 | 70.542 | 21.842 | 38.626 | 19.077
| 7.0486 | 302.374 | 298.66 | 70.572 | 21.844 | 38.676 | 19.077
| 7.0556 | 301.789 | 299.149 | 70.592 | 21.843 | 38.694 | 19.081
| 7.0625 | 301.933 | 299.859 | 70.626 | 21.847 | 38.714 | 19.076
| 7.0694 | 302.745 | 299.375 | 70.663 | 21.849 | 38.733 | 19.079
| 7.0764 | 302.555 | 299.28 | 70.694 | 21.853 | 38.752 | 19.082
| 7.0833 | 302.753 | 299.274 | 70.722 | 21.856 | 38.765 | 19.084
| 7.0903 | 302.539 | 299.914 | 70.759 | 21.862 | 38.767 | 19.084
| 7.0972 | 303.236 | 301.001 | 70.812 | 21.869 | 38.805 | 19.084
| 7.1042 | 303.737 | 300.313 | 70.866 | 21.869 | 38.828 | 19.089
| 7.1111 | 303.628 | 300.644 | 70.926 | 21.876 | 38.86 | 19.09
| 7.1181 | 303.096 | 300.889 | 70.974 | 21.886 | 38.873 | 19.095
| 7.125 | 302.652 | 300.723 | 71.011 | 21.884 | 38.871 | 19.098
| 7.1319 | 302.72 | 300.247 | 71.027 | 21.886 | 38.871 | 19.1
| 7.1389 | 303.334 | 300.124 | 71.057 | 21.896 | 38.88 | 19.102
| 7.1458 | 303.138 | 300.409 | 71.086 | 21.899 | 38.899 | 19.107
| 7.1528 | 303.699 | 300.252 | 71.106 | 21.905 | 38.896 | 19.111
| 7.1597 | 303.419 | 300.264 | 71.133 | 21.91 | 38.906 | 19.115
| 7.1667 | 302.58 | 300.35 | 71.157 | 21.917 | 38.919 | 19.114
| 7.1736 | 302.887 | 301.017 | 71.171 | 21.921 | 38.92 | 19.12
| 7.1806 | 302.571 | 300.622 | 71.185 | 21.929 | 38.922 | 19.122
| 7.1875 | 303.022 | 299.65 | 71.172 | 21.933 | 38.909 | 19.129
| 7.1944 | 302.518 | 300.035 | 71.17 | 21.939 | 38.906 | 19.13
| 7.2014 | 302.937 | 299.657 | 71.161 | 21.941 | 38.902 | 19.134
| 7.2083 | 303.248 | 299.671 | 71.159 | 21.942 | 38.907 | 19.138
| 7.2153 | 301.681 | 298.803 | 71.132 | 21.95 | 38.895 | 19.138
| 7.2222 | 300.001 | 298.313 | 71.048 | 21.952 | 38.84 | 19.144
| 7.2292 | 299.829 | 297.202 | 70.936 | 21.955 | 38.779 | 19.146
| 7.2361 | 299.085 | 297.169 | 70.814 | 21.952 | 38.72 | 19.148
| 7.2431 | 298.327 | 296.313 | 70.688 | 21.952 | 38.669 | 19.153
| 7.25 | 298.393 | 296.448 | 70.563 | 21.953 | 38.626 | 19.152
| 7.2569 | 304.997 | 302.174 | 70.615 | 21.949 | 38.699 | 19.156
| 7.2639 | 302.007 | 300.174 | 70.752 | 21.946 | 38.84 | 19.154
| 7.2708 | 304.263 | 302.06 | 70.815 | 21.95 | 38.872 | 19.154
| 7.2778 | 301.27 | 298.408 | 70.773 | 21.954 | 38.819 | 19.156
| 7.2847 | 297.491 | 295.344 | 70.601 | 21.956 | 38.681 | 19.154
| 7.2917 | 301.775 | 298.463 | 70.662 | 21.958 | 38.742 | 19.159
| 7.2986 | 300.989 | 298.542 | 70.643 | 21.956 | 38.744 | 19.163
| 7.3056 | 299.791 | 297.93 | 70.602 | 21.961 | 38.719 | 19.159
| 7.3125 | 301.129 | 298.967 | 70.49 | 21.961 | 38.653 | 19.164
| 7.3194 | 300.12 | 297.459 | 70.517 | 21.961 | 38.688 | 19.165
| 7.3264 | 299.306 | 297.082 | 70.461 | 21.956 | 38.667 | 19.162
| 7.3333 | 298.451 | 296.771 | 70.388 | 21.963 | 38.624 | 19.165
| 7.3403 | 302.344 | 299.407 | 70.387 | 21.96 | 38.638 | 19.165
| 7.3472 | 301.687 | 298.568 | 70.442 | 21.956 | 38.705 | 19.167
| 7.3542 | 302.086 | 300.244 | 70.533 | 21.956 | 38.777 | 19.168
| 7.3611 | 302.524 | 299.782 | 70.589 | 21.961 | 38.796 | 19.167
| 7.3681 | 302.357 | 299.415 | 70.63 | 21.965 | 38.801 | 19.169
| 7.375 | 302.537 | 300.606 | 70.657 | 21.972 | 38.801 | 19.168
| 7.3819 | 302.519 | 300.797 | 70.767 | 21.978 | 38.861 | 19.174
| 7.3889 | 303.261 | 301.273 | 70.861 | 21.979 | 38.902 | 19.179
| 7.3958 | 303.851 | 302.13 | 70.975 | 21.985 | 38.958 | 19.179
| 7.4028 | 303.207 | 301.016 | 71.041 | 21.996 | 38.966 | 19.179
| 7.4097 | 302.964 | 301.03 | 71.074 | 22.005 | 38.963 | 19.187
| 7.4167 | 302.6 | 299.721 | 71.066 | 22.009 | 38.937 | 19.193
| 7.4236 | 303.026 | 299.707 | 71.066 | 22.015 | 38.923 | 19.198
| 7.4306 | 302.88 | 299.709 | 71.066 | 22.018 | 38.918 | 19.201
| 7.4375 | 302.804 | 300.392 | 71.102 | 22.021 | 38.944 | 19.204
| 7.4444 | 302.962 | 300.931 | 71.119 | 22.029 | 38.954 | 19.211
| 7.4514 | 302.877 | 299.973 | 71.15 | 22.038 | 38.97 | 19.209
| 7.4583 | 302.598 | 300.43 | 71.139 | 22.04 | 38.957 | 19.222
| 7.4653 | 301.817 | 300.239 | 71.13 | 22.042 | 38.946 | 19.22
| 7.4722 | 302.087 | 299.873 | 71.108 | 22.048 | 38.938 | 19.227
| 7.4792 | 302.644 | 299.567 | 71.095 | 22.053 | 38.932 | 19.227
| 7.4861 | 302.728 | 299.549 | 71.107 | 22.06 | 38.948 | 19.236
| 7.4931 | 302.481 | 299.917 | 71.116 | 22.062 | 38.958 | 19.238
| 7.5 | 302.418 | 299.819 | 71.125 | 22.065 | 38.97 | 19.243
| 7.5069 | 302.571 | 300.53 | 71.133 | 22.071 | 38.973 | 19.245
| 7.5139 | 303.877 | 300.85 | 71.181 | 22.076 | 39.008 | 19.255
| 7.5208 | 302.936 | 301.14 | 71.247 | 22.078 | 39.05 | 19.257
| 7.5278 | 303.291 | 300.397 | 71.279 | 22.083 | 39.061 | 19.263
| 7.5347 | 304.385 | 301.378 | 71.319 | 22.092 | 39.078 | 19.262
| 7.5417 | 303.029 | 301.122 | 71.375 | 22.097 | 39.097 | 19.268
| 7.5486 | 303.961 | 302.321 | 71.434 | 22.105 | 39.129 | 19.274
| 7.5556 | 304.263 | 301.572 | 71.482 | 22.106 | 39.141 | 19.281
| 7.5625 | 303.996 | 301.044 | 71.519 | 22.119 | 39.154 | 19.287
| 7.5694 | 304.118 | 302.229 | 71.554 | 22.123 | 39.162 | 19.29
| 7.5764 | 303.508 | 301.888 | 71.596 | 22.132 | 39.173 | 19.297
| 7.5833 | 304.325 | 300.966 | 71.619 | 22.14 | 39.183 | 19.307
| 7.5903 | 304.258 | 302.521 | 71.673 | 22.148 | 39.209 | 19.307
| 7.5972 | 301.315 | 299.503 | 71.596 | 22.152 | 39.144 | 19.312
| 7.6042 | 301.517 | 299.319 | 71.501 | 22.16 | 39.074 | 19.32
| 7.6111 | 301.356 | 298.476 | 71.396 | 22.162 | 39.022 | 19.326
| 7.6181 | 300.975 | 299.016 | 71.324 | 22.162 | 38.994 | 19.331
| 7.625 | 301.07 | 298.186 | 71.232 | 22.165 | 38.971 | 19.335
| 7.6319 | 301.716 | 298.543 | 71.167 | 22.165 | 38.96 | 19.342
| 7.6389 | 301.328 | 299.624 | 71.144 | 22.167 | 38.97 | 19.343
| 7.6458 | 301.815 | 298.804 | 71.111 | 22.167 | 38.977 | 19.348
| 7.6528 | 301.504 | 299.754 | 71.092 | 22.168 | 38.979 | 19.35
| 7.6597 | 298.816 | 296.983 | 70.998 | 22.169 | 38.93 | 19.351
| 7.6667 | 299.627 | 296.855 | 70.879 | 22.169 | 38.866 | 19.356
| 7.6736 | 299.839 | 296.858 | 70.795 | 22.169 | 38.835 | 19.359
| 7.6806 | 299.508 | 296.744 | 70.717 | 22.165 | 38.819 | 19.359
| 7.6875 | 299.215 | 297.434 | 70.649 | 22.164 | 38.804 | 19.363
| 7.6944 | 299.363 | 296.86 | 70.601 | 22.162 | 38.806 | 19.364
| 7.7014 | 299.131 | 296.252 | 70.53 | 22.164 | 38.785 | 19.366
| 7.7083 | 297.863 | 296.426 | 70.45 | 22.164 | 38.743 | 19.368
| 7.7153 | 299.314 | 296.555 | 70.455 | 22.156 | 38.781 | 19.371
| 7.7222 | 297.392 | 295.52 | 70.364 | 22.158 | 38.731 | 19.373
| 7.7292 | 302.982 | 300.391 | 70.469 | 22.161 | 38.819 | 19.374
| 7.7361 | 304.378 | 302.281 | 70.664 | 22.161 | 38.981 | 19.379
| 7.7431 | 303.273 | 301.702 | 70.807 | 22.164 | 39.047 | 19.377
| 7.75 | 303.454 | 301.688 | 70.909 | 22.17 | 39.07 | 19.381
| 7.7569 | 304.167 | 301.179 | 71.029 | 22.18 | 39.109 | 19.385
| 7.7639 | 303.685 | 302.183 | 71.125 | 22.189 | 39.134 | 19.389
| 7.7708 | 303.437 | 301.699 | 71.221 | 22.198 | 39.161 | 19.396
| 7.7778 | 303.71 | 300.788 | 71.277 | 22.207 | 39.17 | 19.401
| 7.7847 | 304.108 | 301.675 | 71.338 | 22.215 | 39.181 | 19.408
| 7.7917 | 303.407 | 301.619 | 71.398 | 22.222 | 39.196 | 19.416
| 7.7986 | 304.245 | 301.245 | 71.458 | 22.232 | 39.219 | 19.426
| 7.8056 | 301.66 | 299.311 | 71.499 | 22.235 | 39.235 | 19.429
| 7.8125 | 301.935 | 298.774 | 71.415 | 22.241 | 39.144 | 19.434
| 7.8194 | 302.283 | 299.353 | 71.382 | 22.252 | 39.12 | 19.45
| 7.8264 | 302.432 | 299.343 | 71.359 | 22.257 | 39.117 | 19.455
| 7.8333 | 301.93 | 299.175 | 71.339 | 22.258 | 39.116 | 19.459
| 7.8403 | 303.045 | 299.904 | 71.338 | 22.265 | 39.124 | 19.462
| 7.8472 | 305.405 | 302.36 | 71.403 | 22.27 | 39.187 | 19.474
| 7.8542 | 302.136 | 299.717 | 71.361 | 22.276 | 39.152 | 19.48
| 7.8611 | 301.004 | 298.954 | 71.292 | 22.277 | 39.106 | 19.484
| 7.8681 | 300.766 | 298.898 | 71.261 | 22.284 | 39.096 | 19.494
| 7.875 | 301.203 | 299.63 | 71.219 | 22.287 | 39.081 | 19.497
| 7.8819 | 301.613 | 299.178 | 71.196 | 22.289 | 39.083 | 19.5
| 7.8889 | 301.918 | 299.203 | 71.185 | 22.292 | 39.095 | 19.508
| 7.8958 | 299.412 | 297.701 | 71.1 | 22.295 | 39.045 | 19.513
| 7.9028 | 299.374 | 297.699 | 71.01 | 22.3 | 39.001 | 19.523
| 7.9097 | 299.405 | 297.845 | 70.952 | 22.302 | 38.986 | 19.521
| 7.9167 | 301.094 | 298.222 | 70.941 | 22.298 | 39.004 | 19.529
| 7.9236 | 300.741 | 298.346 | 70.919 | 22.301 | 39.022 | 19.532
| 7.9306 | 301.668 | 300.159 | 70.959 | 22.304 | 39.065 | 19.539
| 7.9375 | 302.933 | 299.886 | 71.033 | 22.309 | 39.115 | 19.545
| 7.9444 | 303.314 | 300.907 | 71.124 | 22.306 | 39.168 | 19.548
| 7.9514 | 300.465 | 299.069 | 71.106 | 22.321 | 39.148 | 19.557
| 7.9583 | 300.573 | 298.977 | 71.083 | 22.323 | 39.115 | 19.561
| 7.9653 | 300.36 | 298.565 | 71.053 | 22.325 | 39.097 | 19.561
| 7.9722 | 302.35 | 299.84 | 71.069 | 22.328 | 39.115 | 19.574
| 7.9792 | 300.076 | 298.132 | 71.025 | 22.332 | 39.083 | 19.577
| 7.9861 | 301.407 | 298.118 | 71.004 | 22.336 | 39.068 | 19.58
| 7.9931 | 301.324 | 298.399 | 71.016 | 22.341 | 39.092 | 19.589
| 8 | 301 | 297.622 | 71.005 | 22.341 | 39.091 | 19.592
| 8.0069 | 300.656 | 298.907 | 70.998 | 22.345 | 39.09 | 19.599
| 8.0139 | 301.62 | 299.239 | 71.01 | 22.349 | 39.103 | 19.602
| 8.0208 | 301.604 | 298.43 | 71.036 | 22.352 | 39.123 | 19.608
| 8.0278 | 302.467 | 299.34 | 71.067 | 22.357 | 39.154 | 19.61
| 8.0347 | 302.024 | 298.968 | 71.092 | 22.357 | 39.163 | 19.617
| 8.0417 | 300.716 | 298.682 | 71.087 | 22.367 | 39.154 | 19.623
| 8.0486 | 300.917 | 298.991 | 71.09 | 22.373 | 39.147 | 19.629
| 8.0556 | 302.498 | 299.78 | 71.115 | 22.376 | 39.167 | 19.631
| 8.0625 | 302.632 | 299.322 | 71.157 | 22.384 | 39.196 | 19.64
| 8.0694 | 302.474 | 299.403 | 71.194 | 22.387 | 39.208 | 19.643
| 8.0764 | 302.518 | 299.872 | 71.218 | 22.39 | 39.215 | 19.651
| 8.0833 | 302.592 | 300.903 | 71.288 | 22.396 | 39.257 | 19.656
| 8.0903 | 302.467 | 300.484 | 71.32 | 22.401 | 39.266 | 19.664
| 8.0972 | 303.248 | 300.737 | 71.371 | 22.411 | 39.295 | 19.672
| 8.1042 | 303.384 | 300.737 | 71.448 | 22.418 | 39.332 | 19.677
| 8.1111 | 297.924 | 296.385 | 71.345 | 22.428 | 39.24 | 19.685
| 8.1181 | 297.374 | 294.951 | 71.143 | 22.434 | 39.086 | 19.689
| 8.125 | 297.322 | 295.147 | 70.971 | 22.435 | 38.999 | 19.698
| 8.1319 | 301.111 | 299.304 | 70.943 | 22.433 | 39.042 | 19.699
| 8.1389 | 301.981 | 299.89 | 71.027 | 22.43 | 39.151 | 19.709
| 8.1458 | 302.426 | 300.33 | 71.105 | 22.436 | 39.215 | 19.71
| 8.1528 | 302.502 | 299.725 | 71.172 | 22.441 | 39.252 | 19.716
| 8.1597 | 302.265 | 299.371 | 71.216 | 22.445 | 39.27 | 19.719
| 8.1667 | 302.693 | 299.508 | 71.271 | 22.446 | 39.289 | 19.723
| 8.1736 | 301.593 | 299.823 | 71.3 | 22.457 | 39.296 | 19.734
| 8.1806 | 301.895 | 300.081 | 71.335 | 22.461 | 39.305 | 19.734
| 8.1875 | 302.11 | 299.606 | 71.365 | 22.471 | 39.313 | 19.744
| 8.1944 | 302.618 | 300.559 | 71.424 | 22.472 | 39.344 | 19.746
| 8.2014 | 302.292 | 299.933 | 71.449 | 22.482 | 39.351 | 19.757
| 8.2083 | 302.915 | 299.72 | 71.477 | 22.492 | 39.358 | 19.757
| 8.2153 | 302.308 | 299.296 | 71.481 | 22.498 | 39.35 | 19.767
| 8.2222 | 300.335 | 298.719 | 71.447 | 22.498 | 39.326 | 19.773
| 8.2292 | 300.23 | 297.221 | 71.356 | 22.508 | 39.268 | 19.784
| 8.2361 | 299.732 | 297.738 | 71.284 | 22.513 | 39.229 | 19.783
| 8.2431 | 298.633 | 296.705 | 71.197 | 22.513 | 39.194 | 19.791
| 8.25 | 297.954 | 296.224 | 71.093 | 22.515 | 39.148 | 19.796
| 8.2569 | 299.828 | 297.971 | 70.996 | 22.515 | 39.111 | 19.802
| 8.2639 | 297.012 | 294.239 | 70.991 | 22.519 | 39.159 | 19.802
| 8.2708 | 301.375 | 298.824 | 71.071 | 22.517 | 39.23 | 19.808
| 8.2778 | 301.671 | 299.394 | 71.158 | 22.519 | 39.291 | 19.812
| 8.2847 | 301.257 | 299.2 | 71.19 | 22.525 | 39.307 | 19.813
| 8.2917 | 299.818 | 298.19 | 71.176 | 22.532 | 39.274 | 19.818
| 8.2986 | 300.268 | 297.465 | 71.164 | 22.536 | 39.261 | 19.825
| 8.3056 | 298.487 | 296.643 | 71.093 | 22.539 | 39.214 | 19.828
| 8.3125 | 301.871 | 299.434 | 71.057 | 22.54 | 39.196 | 19.832
| 8.3194 | 300.975 | 298.544 | 71.124 | 22.547 | 39.267 | 19.832
| 8.3264 | 301.979 | 300.294 | 71.22 | 22.549 | 39.33 | 19.841
| 8.3333 | 301.439 | 298.699 | 71.24 | 22.553 | 39.332 | 19.844
| 8.3403 | 302.852 | 299.586 | 71.33 | 22.557 | 39.379 | 19.853
| 8.3472 | 303.343 | 300.182 | 71.384 | 22.567 | 39.401 | 19.857
| 8.3542 | 302.654 | 300.7 | 71.415 | 22.569 | 39.401 | 19.862
| 8.3611 | 303.945 | 301.175 | 71.531 | 22.575 | 39.476 | 19.864
| 8.3681 | 304.006 | 300.971 | 71.638 | 22.585 | 39.527 | 19.868
| 8.375 | 303.801 | 300.968 | 71.717 | 22.591 | 39.549 | 19.876
| 8.3819 | 303.824 | 300.844 | 71.777 | 22.603 | 39.559 | 19.886
| 8.3889 | 303.543 | 301.269 | 71.832 | 22.612 | 39.572 | 19.889
| 8.3958 | 303.99 | 302.186 | 71.919 | 22.621 | 39.612 | 19.901
| 8.4028 | 304.387 | 301.937 | 71.983 | 22.632 | 39.633 | 19.903
| 8.4097 | 304.114 | 301.713 | 72.041 | 22.642 | 39.652 | 19.914
| 8.4167 | 303.987 | 300.683 | 72.075 | 22.653 | 39.652 | 19.921
| 8.4236 | 303.385 | 301.087 | 72.086 | 22.66 | 39.652 | 19.926
| 8.4306 | 302.919 | 301.285 | 72.095 | 22.669 | 39.642 | 19.933
| 8.4375 | 303.266 | 301.228 | 72.113 | 22.676 | 39.651 | 19.944
| 8.4444 | 304.098 | 301.094 | 72.166 | 22.686 | 39.686 | 19.946
| 8.4514 | 303.615 | 301.389 | 72.19 | 22.691 | 39.696 | 19.956
| 8.4583 | 303.54 | 301.96 | 72.224 | 22.702 | 39.714 | 19.965
| 8.4653 | 303.089 | 301.353 | 72.248 | 22.708 | 39.722 | 19.975
| 8.4722 | 304.205 | 301.345 | 72.254 | 22.72 | 39.727 | 19.979
| 8.4792 | 303.434 | 301.631 | 72.288 | 22.727 | 39.74 | 19.99
| 8.4861 | 303.528 | 301.95 | 72.31 | 22.734 | 39.751 | 19.992
| 8.4931 | 304.034 | 301.522 | 72.325 | 22.743 | 39.759 | 20.002
| 8.5 | 303.324 | 301.13 | 72.324 | 22.749 | 39.756 | 20.012
| 8.5069 | 302.86 | 300.178 | 72.282 | 22.753 | 39.726 | 20.01
| 8.5139 | 302.488 | 300.477 | 72.263 | 22.758 | 39.722 | 20.023
| 8.5208 | 302.9 | 299.866 | 72.246 | 22.761 | 39.725 | 20.031
| 8.5278 | 301.839 | 299.961 | 72.209 | 22.773 | 39.715 | 20.034
| 8.5347 | 302.504 | 299.884 | 72.181 | 22.776 | 39.701 | 20.035
| 8.5417 | 302.517 | 299.532 | 72.15 | 22.783 | 39.691 | 20.047
| 8.5486 | 301.366 | 299.955 | 72.112 | 22.784 | 39.681 | 20.059
| 8.5556 | 301.801 | 298.953 | 72.065 | 22.791 | 39.663 | 20.063
| 8.5625 | 301.367 | 299.471 | 72.004 | 22.795 | 39.638 | 20.063
| 8.5694 | 301.291 | 298.841 | 71.95 | 22.798 | 39.629 | 20.069
| 8.5764 | 300.992 | 299.389 | 71.903 | 22.798 | 39.611 | 20.076
| 8.5833 | 300.964 | 299.098 | 71.876 | 22.798 | 39.618 | 20.083
| 8.5903 | 301.081 | 299.41 | 71.861 | 22.804 | 39.622 | 20.086
| 8.5972 | 301.87 | 300.016 | 71.865 | 22.807 | 39.638 | 20.085
| 8.6042 | 301.431 | 299.23 | 71.845 | 22.808 | 39.639 | 20.095
| 8.6111 | 301.974 | 299.001 | 71.842 | 22.817 | 39.646 | 20.099
| 8.6181 | 302.076 | 300.11 | 71.851 | 22.817 | 39.651 | 20.099
| 8.625 | 302.254 | 299.837 | 71.859 | 22.822 | 39.663 | 20.105
| 8.6319 | 301.966 | 299.004 | 71.872 | 22.838 | 39.694 | 20.124
| 8.6389 | 301.824 | 299.909 | 71.868 | 22.842 | 39.694 | 20.13
| 8.6458 | 302.18 | 299.953 | 71.902 | 22.845 | 39.717 | 20.132
| 8.6528 | 303.268 | 300.381 | 71.952 | 22.842 | 39.747 | 20.136
| 8.6597 | 302.282 | 300.806 | 71.989 | 22.842 | 39.747 | 20.129
| 8.6667 | 303.098 | 301.052 | 72.027 | 22.848 | 39.766 | 20.134
| 8.6736 | 302.254 | 300.606 | 72.061 | 22.855 | 39.776 | 20.146
| 8.6806 | 302.822 | 301.028 | 72.113 | 22.861 | 39.802 | 20.149
| 8.6875 | 303.636 | 300.832 | 72.146 | 22.866 | 39.813 | 20.153
| 8.6944 | 303.266 | 301.73 | 72.199 | 22.868 | 39.842 | 20.162
| 8.7014 | 303.802 | 300.614 | 72.248 | 22.885 | 39.859 | 20.167
| 8.7083 | 301.432 | 300.061 | 72.21 | 22.89 | 39.819 | 20.175
| 8.7153 | 301.2 | 298.702 | 72.138 | 22.9 | 39.763 | 20.182
| 8.7222 | 301.184 | 298.512 | 72.065 | 22.904 | 39.723 | 20.191
| 8.7292 | 301.17 | 298.841 | 72.003 | 22.907 | 39.703 | 20.197
| 8.7361 | 300.52 | 297.644 | 71.967 | 22.908 | 39.704 | 20.2
| 8.7431 | 300.7 | 298 | 71.915 | 22.912 | 39.685 | 20.207
| 8.75 | 300.99 | 298.883 | 71.874 | 22.912 | 39.673 | 20.215
| 8.7569 | 300.639 | 299.169 | 71.855 | 22.918 | 39.683 | 20.215
| 8.7639 | 301.946 | 299.311 | 71.854 | 22.917 | 39.705 | 20.222
| 8.7708 | 301.747 | 299.464 | 71.87 | 22.924 | 39.725 | 20.224
| 8.7778 | 302.086 | 299.347 | 71.875 | 22.928 | 39.735 | 20.234
| 8.7847 | 300.78 | 298.628 | 71.866 | 22.934 | 39.726 | 20.237
| 8.7917 | 300.674 | 299.201 | 71.852 | 22.938 | 39.726 | 20.246
| 8.7986 | 301.349 | 298.967 | 71.851 | 22.939 | 39.725 | 20.254
| 8.8056 | 301.978 | 300.374 | 71.866 | 22.943 | 39.745 | 20.254
| 8.8125 | 302.604 | 300.109 | 71.93 | 22.948 | 39.795 | 20.262
| 8.8194 | 303.912 | 301.526 | 72.024 | 22.956 | 39.848 | 20.262
| 8.8264 | 303.6 | 301.352 | 72.117 | 22.967 | 39.912 | 20.278
| 8.8333 | 304.119 | 302.1 | 72.216 | 22.971 | 39.945 | 20.277
| 8.8403 | 300.744 | 298.586 | 72.122 | 22.98 | 39.859 | 20.287
| 8.8472 | 302.203 | 299.346 | 72.091 | 22.983 | 39.818 | 20.296
| 8.8542 | 301.874 | 298.927 | 72.098 | 22.986 | 39.837 | 20.302
| 8.8611 | 300.122 | 298.461 | 72.032 | 22.996 | 39.801 | 20.311
| 8.8681 | 300.755 | 299.015 | 71.966 | 22.999 | 39.762 | 20.315
| 8.875 | 300.635 | 299.154 | 71.946 | 23.002 | 39.786 | 20.323
| 8.8819 | 301.512 | 299.915 | 71.94 | 23.002 | 39.794 | 20.326
| 8.8889 | 302.013 | 299.402 | 71.951 | 23.005 | 39.824 | 20.339
| 8.8958 | 302.71 | 299.724 | 71.952 | 23.017 | 39.846 | 20.346
| 8.9028 | 302.075 | 299.244 | 71.978 | 23.021 | 39.874 | 20.349
| 8.9097 | 303.099 | 300.787 | 71.999 | 23.031 | 39.896 | 20.359
| 8.9167 | 303.231 | 301.468 | 72.07 | 23.032 | 39.94 | 20.361
| 8.9236 | 301.488 | 298.807 | 72.016 | 23.044 | 39.894 | 20.372
| 8.9306 | 301.921 | 300.605 | 72.016 | 23.046 | 39.903 | 20.376
| 8.9375 | 303.331 | 300.633 | 72.041 | 23.047 | 39.918 | 20.381
| 8.9444 | 303.3 | 300.743 | 72.093 | 23.057 | 39.956 | 20.387
| 8.9514 | 303.772 | 301.062 | 72.137 | 23.059 | 39.974 | 20.396
| 8.9583 | 303.378 | 301.086 | 72.194 | 23.072 | 40.01 | 20.405
| 8.9653 | 299.297 | 298.083 | 72.234 | 23.076 | 40.023 | 20.407
| 8.9722 | 300.918 | 298.797 | 72.105 | 23.076 | 39.913 | 20.418
| 8.9792 | 302.191 | 299.263 | 72.108 | 23.084 | 39.932 | 20.428
| 8.9861 | 299.766 | 297.684 | 72.052 | 23.09 | 39.902 | 20.43
| 8.9931 | 300.147 | 298.694 | 71.973 | 23.089 | 39.851 | 20.433
| 9 | 301.105 | 298.202 | 71.942 | 23.1 | 39.854 | 20.444
| 9.0069 | 299.913 | 297.99 | 71.912 | 23.101 | 39.865 | 20.453
| 9.0139 | 299.869 | 298.115 | 71.797 | 23.105 | 39.796 | 20.463
| 9.0208 | 301.123 | 298.957 | 71.808 | 23.107 | 39.837 | 20.466
| 9.0278 | 302.015 | 298.908 | 71.835 | 23.103 | 39.875 | 20.468
| 9.0347 | 300.255 | 297.989 | 71.817 | 23.111 | 39.872 | 20.472
| 9.0417 | 299.923 | 297.047 | 71.747 | 23.116 | 39.823 | 20.479
| 9.0486 | 299.297 | 297.662 | 71.698 | 23.116 | 39.805 | 20.488
| 9.0556 | 300.749 | 297.867 | 71.703 | 23.115 | 39.827 | 20.487
| 9.0625 | 301.822 | 299.33 | 71.762 | 23.121 | 39.883 | 20.496
| 9.0694 | 301.656 | 298.669 | 71.782 | 23.125 | 39.898 | 20.502
| 9.0764 | 301.163 | 299.391 | 71.807 | 23.133 | 39.907 | 20.508
| 9.0833 | 301.893 | 298.932 | 71.835 | 23.133 | 39.924 | 20.515
| 9.0903 | 301.101 | 299.582 | 71.855 | 23.136 | 39.926 | 20.52
| 9.0972 | 302.701 | 299.971 | 71.896 | 23.15 | 39.955 | 20.529
| 9.1042 | 302.66 | 299.977 | 71.963 | 23.149 | 40.001 | 20.536
| 9.1111 | 302.449 | 299.62 | 72.01 | 23.151 | 40.019 | 20.543
| 9.1181 | 302.176 | 300.283 | 72.046 | 23.164 | 40.037 | 20.548
| 9.125 | 301.623 | 300.026 | 72.071 | 23.163 | 40.033 | 20.555
| 9.1319 | 301.736 | 300.338 | 72.096 | 23.17 | 40.04 | 20.564
| 9.1389 | 301.295 | 299.925 | 72.104 | 23.179 | 40.036 | 20.572
| 9.1458 | 301.248 | 299.249 | 72.098 | 23.19 | 40.025 | 20.58
| 9.1528 | 301.194 | 299.421 | 72.09 | 23.193 | 40.024 | 20.587
| 9.1597 | 301.737 | 298.796 | 72.079 | 23.2 | 40.019 | 20.593
| 9.1667 | 300.481 | 298.299 | 72.06 | 23.203 | 40.007 | 20.605
| 9.1736 | 300.363 | 298.038 | 72.018 | 23.214 | 39.989 | 20.613
| 9.1806 | 300.262 | 298.661 | 71.979 | 23.214 | 39.977 | 20.618
| 9.1875 | 300.663 | 298.939 | 71.965 | 23.219 | 39.981 | 20.624
| 9.1944 | 300.472 | 297.672 | 71.928 | 23.222 | 39.968 | 20.631
| 9.2014 | 300.677 | 297.794 | 71.894 | 23.228 | 39.95 | 20.638
| 9.2083 | 299.893 | 298.51 | 71.869 | 23.23 | 39.954 | 20.646
| 9.2153 | 299.898 | 297.877 | 71.843 | 23.23 | 39.949 | 20.651
| 9.2222 | 299.072 | 297.423 | 71.808 | 23.238 | 39.944 | 20.658
| 9.2292 | 298.468 | 295.449 | 71.694 | 23.235 | 39.872 | 20.663
| 9.2361 | 298.309 | 295.478 | 71.597 | 23.237 | 39.827 | 20.669
| 9.2431 | 299.523 | 298.2 | 71.62 | 23.236 | 39.878 | 20.668
| 9.25 | 299.068 | 296.898 | 71.593 | 23.24 | 39.885 | 20.678
| 9.2569 | 298.602 | 296.36 | 71.547 | 23.243 | 39.865 | 20.685
| 9.2639 | 297.858 | 296.546 | 71.436 | 23.243 | 39.801 | 20.687
| 9.2708 | 301.28 | 298.226 | 71.511 | 23.241 | 39.877 | 20.691
| 9.2778 | 301.727 | 300.177 | 71.625 | 23.244 | 39.969 | 20.694
| 9.2847 | 300.359 | 298.732 | 71.685 | 23.249 | 39.999 | 20.701
| 9.2917 | 300.013 | 298.511 | 71.703 | 23.26 | 39.996 | 20.708
| 9.2986 | 300.44 | 297.611 | 71.703 | 23.262 | 39.976 | 20.709
| 9.3056 | 298.934 | 296.815 | 71.673 | 23.264 | 39.944 | 20.712
| 9.3125 | 300.165 | 298.619 | 71.599 | 23.272 | 39.894 | 20.723
| 9.3194 | 300.728 | 297.77 | 71.635 | 23.273 | 39.941 | 20.727
| 9.3264 | 298.452 | 295.475 | 71.598 | 23.278 | 39.913 | 20.73
| 9.3333 | 297.74 | 296.162 | 71.522 | 23.279 | 39.866 | 20.735
| 9.3403 | 301.773 | 299.428 | 71.603 | 23.275 | 39.948 | 20.741
| 9.3472 | 300.423 | 297.751 | 71.68 | 23.285 | 40.01 | 20.747
| 9.3542 | 299.75 | 298.061 | 71.668 | 23.29 | 39.986 | 20.756
| 9.3611 | 301.739 | 298.808 | 71.761 | 23.297 | 40.044 | 20.755
| 9.3681 | 300.756 | 298.947 | 71.814 | 23.3 | 40.064 | 20.759
| 9.375 | 301.44 | 299.402 | 71.863 | 23.308 | 40.08 | 20.767
| 9.3819 | 301.718 | 300.206 | 71.935 | 23.312 | 40.115 | 20.769
| 9.3889 | 302.88 | 300.302 | 72.026 | 23.322 | 40.163 | 20.777
| 9.3958 | 302.394 | 300.95 | 72.126 | 23.327 | 40.205 | 20.782
| 9.4028 | 302.779 | 300.852 | 72.215 | 23.337 | 40.24 | 20.786
| 9.4097 | 302.806 | 299.911 | 72.276 | 23.35 | 40.252 | 20.796
| 9.4167 | 302.202 | 300.594 | 72.342 | 23.358 | 40.274 | 20.801
| 9.4236 | 301.413 | 299.965 | 72.358 | 23.365 | 40.255 | 20.807
| 9.4306 | 302.008 | 299.158 | 72.369 | 23.375 | 40.25 | 20.816
| 9.4375 | 301.5 | 299.348 | 72.372 | 23.383 | 40.241 | 20.824
| 9.4444 | 301.899 | 300.317 | 72.393 | 23.392 | 40.251 | 20.83
| 9.4514 | 302.327 | 299.198 | 72.401 | 23.396 | 40.257 | 20.84
| 9.4583 | 301.492 | 299.341 | 72.392 | 23.408 | 40.251 | 20.843
| 9.4653 | 301.143 | 299.47 | 72.39 | 23.41 | 40.254 | 20.853
| 9.4722 | 301.823 | 299.351 | 72.383 | 23.419 | 40.249 | 20.858
| 9.4792 | 301.373 | 298.986 | 72.383 | 23.426 | 40.256 | 20.867
| 9.4861 | 301.314 | 298.354 | 72.367 | 23.434 | 40.255 | 20.87
| 9.4931 | 300.564 | 298.819 | 72.343 | 23.435 | 40.238 | 20.877
| 9.5 | 301.223 | 298.13 | 72.317 | 23.442 | 40.226 | 20.883
| 9.5069 | 301.034 | 298.139 | 72.3 | 23.447 | 40.232 | 20.888
| 9.5139 | 302.511 | 299.989 | 72.336 | 23.451 | 40.266 | 20.897
| 9.5208 | 301.401 | 299.808 | 72.384 | 23.455 | 40.313 | 20.902
| 9.5278 | 302.673 | 299.703 | 72.42 | 23.461 | 40.328 | 20.905
| 9.5347 | 302.707 | 300.373 | 72.465 | 23.467 | 40.357 | 20.914
| 9.5417 | 301.702 | 300.081 | 72.499 | 23.475 | 40.37 | 20.913
| 9.5486 | 302.121 | 300.701 | 72.555 | 23.484 | 40.399 | 20.924
| 9.5556 | 302.422 | 300.054 | 72.601 | 23.49 | 40.411 | 20.931
| 9.5625 | 302.421 | 300.584 | 72.653 | 23.499 | 40.442 | 20.94
| 9.5694 | 302.998 | 301.44 | 72.719 | 23.507 | 40.473 | 20.945
| 9.5764 | 302.601 | 300.126 | 72.757 | 23.514 | 40.485 | 20.948
| 9.5833 | 301.641 | 298.842 | 72.747 | 23.522 | 40.457 | 20.961
| 9.5903 | 301.717 | 299.483 | 72.705 | 23.529 | 40.425 | 20.962
| 9.5972 | 302.485 | 301.292 | 72.713 | 23.534 | 40.428 | 20.974
| 9.6042 | 301.92 | 300.249 | 72.725 | 23.544 | 40.453 | 20.977
| 9.6111 | 302.582 | 299.564 | 72.744 | 23.547 | 40.473 | 20.983
| 9.6181 | 302.551 | 301.088 | 72.755 | 23.556 | 40.477 | 20.996
| 9.625 | 302.8 | 300.275 | 72.804 | 23.563 | 40.51 | 20.997
| 9.6319 | 302.249 | 299.857 | 72.81 | 23.57 | 40.509 | 21.006
| 9.6389 | 303.061 | 300.23 | 72.837 | 23.578 | 40.524 | 21.009
| 9.6458 | 303.922 | 301.048 | 72.891 | 23.584 | 40.559 | 21.017
| 9.6528 | 304.245 | 301.276 | 72.962 | 23.593 | 40.604 | 21.022
| 9.6597 | 304.292 | 301.899 | 73.026 | 23.598 | 40.633 | 21.029
| 9.6667 | 303.693 | 302.333 | 73.09 | 23.607 | 40.656 | 21.037
| 9.6736 | 300.018 | 298.371 | 73.064 | 23.615 | 40.623 | 21.045
| 9.6806 | 300.77 | 298.086 | 72.953 | 23.626 | 40.53 | 21.054
| 9.6875 | 299.895 | 298.518 | 72.864 | 23.632 | 40.479 | 21.062
| 9.6944 | 299.768 | 298 | 72.757 | 23.635 | 40.434 | 21.068
| 9.7014 | 298.577 | 296.276 | 72.625 | 23.637 | 40.386 | 21.073
| 9.7083 | 297.361 | 295.72 | 72.447 | 23.639 | 40.303 | 21.079
| 9.7153 | 299.297 | 297.845 | 72.43 | 23.64 | 40.345 | 21.081
| 9.7222 | 298.656 | 296.828 | 72.354 | 23.641 | 40.336 | 21.088
| 9.7292 | 298.875 | 296.19 | 72.252 | 23.638 | 40.297 | 21.091
| 9.7361 | 299.954 | 297.273 | 72.214 | 23.637 | 40.303 | 21.092
| 9.7431 | 298.602 | 297.046 | 72.172 | 23.636 | 40.306 | 21.096
| 9.75 | 299.078 | 297.613 | 72.139 | 23.636 | 40.299 | 21.101
| 9.7569 | 300.139 | 297.93 | 72.124 | 23.639 | 40.31 | 21.103
| 9.7639 | 301.807 | 299.266 | 72.161 | 23.639 | 40.359 | 21.112
| 9.7708 | 301.41 | 300.029 | 72.236 | 23.645 | 40.419 | 21.112
| 9.7778 | 302.019 | 299.415 | 72.305 | 23.646 | 40.453 | 21.114
| 9.7847 | 300.874 | 299.385 | 72.348 | 23.65 | 40.468 | 21.116
| 9.7917 | 300.957 | 299.085 | 72.369 | 23.662 | 40.467 | 21.121
| 9.7986 | 301.566 | 299.756 | 72.414 | 23.664 | 40.485 | 21.128
| 9.8056 | 303.185 | 301.514 | 72.5 | 23.668 | 40.536 | 21.135
| 9.8125 | 301.785 | 299.213 | 72.552 | 23.68 | 40.557 | 21.138
| 9.8194 | 302.167 | 299.645 | 72.592 | 23.69 | 40.562 | 21.148
| 9.8264 | 302.073 | 300 | 72.637 | 23.691 | 40.576 | 21.15
| 9.8333 | 302.817 | 300 | 72.687 | 23.704 | 40.605 | 21.159
| 9.8403 | 302.76 | 300.191 | 72.738 | 23.706 | 40.618 | 21.168
| 9.8472 | 304.363 | 301.986 | 72.841 | 23.715 | 40.676 | 21.174
| 9.8542 | 303.017 | 300.399 | 72.898 | 23.725 | 40.701 | 21.18
| 9.8611 | 302.98 | 300.062 | 72.921 | 23.729 | 40.692 | 21.187
| 9.8681 | 303.111 | 300.895 | 72.931 | 23.741 | 40.68 | 21.198
| 9.875 | 303.496 | 301.848 | 73.02 | 23.751 | 40.743 | 21.203
| 9.8819 | 304.124 | 301.41 | 73.088 | 23.76 | 40.768 | 21.214
| 9.8889 | 299.958 | 298.81 | 73.051 | 23.765 | 40.729 | 21.216
| 9.8958 | 299.53 | 298.177 | 72.928 | 23.771 | 40.63 | 21.23
| 9.9028 | 300.136 | 298.394 | 72.843 | 23.777 | 40.584 | 21.24
| 9.9097 | 301.001 | 298.456 | 72.806 | 23.778 | 40.588 | 21.247
| 9.9167 | 301.038 | 298.71 | 72.796 | 23.787 | 40.61 | 21.25
| 9.9236 | 300.564 | 299.11 | 72.794 | 23.793 | 40.636 | 21.256
| 9.9306 | 302.133 | 299.804 | 72.812 | 23.793 | 40.653 | 21.262
| 9.9375 | 302.578 | 299.883 | 72.853 | 23.804 | 40.693 | 21.27
| 9.9444 | 302.694 | 301.071 | 72.915 | 23.807 | 40.733 | 21.283
| 9.9514 | 303.307 | 300.951 | 72.968 | 23.812 | 40.763 | 21.282
| 9.9583 | 304.288 | 301.817 | 73.08 | 23.821 | 40.834 | 21.29
| 9.9653 | 302.781 | 300.619 | 73.117 | 23.834 | 40.845 | 21.297
| 9.9722 | 303.514 | 301.555 | 73.164 | 23.836 | 40.855 | 21.301
| 9.9792 | 304.28 | 301.513 | 73.246 | 23.846 | 40.893 | 21.314
| 9.9861 | 300.753 | 298.61 | 73.114 | 23.855 | 40.782 | 21.322
| 9.9931 | 300.413 | 298.063 | 73.036 | 23.858 | 40.729 | 21.331
| 10 | 300.604 | 298.154 | 72.968 | 23.863 | 40.692 | 21.334
| 10.0069 | 301.749 | 298.89 | 72.963 | 23.872 | 40.721 | 21.343
| 10.0139 | 301.299 | 300.15 | 72.973 | 23.87 | 40.748 | 21.352
| 10.0208 | 302.419 | 299.6 | 73.001 | 23.874 | 40.78 | 21.352
| 10.0278 | 302.488 | 299.906 | 73.048 | 23.88 | 40.821 | 21.363
| 10.0347 | 298.917 | 297.346 | 73.025 | 23.883 | 40.8 | 21.372
| 10.0417 | 298.981 | 296.795 | 72.872 | 23.893 | 40.689 | 21.383
| 10.0486 | 299.173 | 297.213 | 72.769 | 23.888 | 40.636 | 21.386
| 10.0556 | 300.453 | 297.699 | 72.726 | 23.894 | 40.642 | 21.39
| 10.0625 | 299.967 | 298.681 | 72.71 | 23.895 | 40.665 | 21.397
| 10.0694 | 299.682 | 298.324 | 72.689 | 23.896 | 40.669 | 21.4
| 10.0764 | 300.27 | 298.491 | 72.665 | 23.9 | 40.67 | 21.411
| 10.0833 | 300.572 | 298.66 | 72.663 | 23.905 | 40.686 | 21.416
| 10.0903 | 300.584 | 299.424 | 72.692 | 23.908 | 40.717 | 21.417
| 10.0972 | 301.605 | 300.423 | 72.748 | 23.909 | 40.751 | 21.425
| 10.1042 | 301.257 | 300.005 | 72.793 | 23.918 | 40.783 | 21.431
| 10.1111 | 301.817 | 299.338 | 72.833 | 23.921 | 40.805 | 21.438
| 10.1181 | 300.5 | 299.241 | 72.855 | 23.931 | 40.801 | 21.443
| 10.125 | 300.419 | 299.362 | 72.841 | 23.935 | 40.779 | 21.445
| 10.1319 | 300.573 | 299.179 | 72.835 | 23.939 | 40.773 | 21.457
| 10.1389 | 300.695 | 299.298 | 72.832 | 23.944 | 40.776 | 21.464
| 10.1458 | 301.313 | 298.962 | 72.841 | 23.952 | 40.784 | 21.468
| 10.1528 | 300.561 | 298.746 | 72.839 | 23.954 | 40.789 | 21.474
| 10.1597 | 300.44 | 298.827 | 72.835 | 23.961 | 40.786 | 21.479
| 10.1667 | 301.292 | 298.739 | 72.835 | 23.967 | 40.786 | 21.484
| 10.1736 | 300.049 | 298.553 | 72.829 | 23.975 | 40.798 | 21.499
| 10.1806 | 300.631 | 299.295 | 72.835 | 23.971 | 40.795 | 21.5
| 10.1875 | 300.902 | 298.329 | 72.833 | 23.979 | 40.801 | 21.507
| 10.1944 | 300.555 | 299.243 | 72.844 | 23.983 | 40.813 | 21.513
| 10.2014 | 301.2 | 298.415 | 72.851 | 23.987 | 40.823 | 21.522
| 10.2083 | 300.944 | 298.255 | 72.846 | 23.986 | 40.823 | 21.528
| 10.2153 | 300.475 | 298.697 | 72.843 | 23.996 | 40.826 | 21.534
| 10.2222 | 300.377 | 299.175 | 72.847 | 24.001 | 40.833 | 21.544
| 10.2292 | 300.81 | 298.127 | 72.824 | 24.005 | 40.818 | 21.547
| 10.2361 | 299.867 | 298.034 | 72.798 | 24.01 | 40.809 | 21.551
| 10.2431 | 299.359 | 297.813 | 72.756 | 24.014 | 40.786 | 21.559
| 10.25 | 299.016 | 297.278 | 72.698 | 24.015 | 40.759 | 21.567
| 10.2569 | 299.52 | 297.258 | 72.636 | 24.018 | 40.742 | 21.567
| 10.2639 | 297.361 | 296.104 | 72.582 | 24.022 | 40.726 | 21.579
| 10.2708 | 297.217 | 295.916 | 72.448 | 24.021 | 40.653 | 21.581
| 10.2778 | 296.182 | 295.153 | 72.337 | 24.019 | 40.606 | 21.59
| 10.2847 | 297.193 | 294.41 | 72.214 | 24.025 | 40.556 | 21.594
| 10.2917 | 295.988 | 294.701 | 72.125 | 24.022 | 40.537 | 21.598
| 10.2986 | 299.175 | 297.263 | 72.174 | 24.019 | 40.619 | 21.601
| 10.3056 | 297.637 | 296.084 | 72.181 | 24.02 | 40.651 | 21.606
| 10.3125 | 300.693 | 298.943 | 72.298 | 24.022 | 40.739 | 21.608
| 10.3194 | 301.657 | 299.153 | 72.391 | 24.025 | 40.788 | 21.612
| 10.3264 | 300.683 | 299.324 | 72.485 | 24.032 | 40.84 | 21.616
| 10.3333 | 301.647 | 299.046 | 72.553 | 24.038 | 40.855 | 21.623
| 10.3403 | 301.255 | 298.623 | 72.613 | 24.038 | 40.874 | 21.628
| 10.3472 | 299.731 | 298.352 | 72.64 | 24.047 | 40.866 | 21.634
| 10.3542 | 301.561 | 300.448 | 72.678 | 24.055 | 40.869 | 21.639
| 10.3611 | 302.769 | 300.237 | 72.796 | 24.062 | 40.947 | 21.652
| 10.3681 | 302.726 | 300.955 | 72.908 | 24.069 | 41.002 | 21.656
| 10.375 | 302.391 | 301.056 | 72.984 | 24.079 | 41.026 | 21.666
| 10.3819 | 302.555 | 300.005 | 73.05 | 24.086 | 41.039 | 21.671
| 10.3889 | 302.4 | 299.6 | 73.094 | 24.094 | 41.049 | 21.682
| 10.3958 | 302.205 | 299.535 | 73.127 | 24.104 | 41.045 | 21.69
| 10.4028 | 301.184 | 298.417 | 73.11 | 24.114 | 41.023 | 21.698
| 10.4097 | 301.01 | 298.376 | 73.095 | 24.118 | 41.004 | 21.709
| 10.4167 | 301.254 | 298.58 | 73.073 | 24.126 | 40.984 | 21.718
| 10.4236 | 300.014 | 298.693 | 73.051 | 24.133 | 40.982 | 21.726
| 10.4306 | 299.447 | 297.424 | 72.98 | 24.14 | 40.944 | 21.735
| 10.4375 | 299.04 | 297.93 | 72.916 | 24.143 | 40.919 | 21.748
| 10.4444 | 299.066 | 296.524 | 72.832 | 24.147 | 40.884 | 21.757
| 10.4514 | 298.703 | 296.701 | 72.769 | 24.151 | 40.865 | 21.759
| 10.4583 | 297.898 | 296.74 | 72.709 | 24.151 | 40.856 | 21.771
| 10.4653 | 298.613 | 295.897 | 72.661 | 24.155 | 40.852 | 21.775
| 10.4722 | 298.151 | 295.98 | 72.625 | 24.155 | 40.85 | 21.78
| 10.4792 | 298.624 | 296.293 | 72.585 | 24.157 | 40.845 | 21.788
| 10.4861 | 298.827 | 296.648 | 72.499 | 24.161 | 40.804 | 21.796
| 10.4931 | 300.325 | 299.191 | 72.628 | 24.161 | 40.925 | 21.803
| 10.5 | 300.869 | 298.401 | 72.684 | 24.165 | 40.966 | 21.806
| 10.5069 | 300.207 | 298.312 | 72.719 | 24.172 | 40.986 | 21.809
| 10.5139 | 300.711 | 299.107 | 72.755 | 24.178 | 40.996 | 21.821
| 10.5208 | 300.871 | 298.022 | 72.776 | 24.186 | 41 | 21.828
| 10.5278 | 300.493 | 298.796 | 72.804 | 24.189 | 41.018 | 21.836
| 10.5347 | 299.716 | 298.475 | 72.803 | 24.195 | 41.008 | 21.848
| 10.5417 | 300.231 | 298.925 | 72.817 | 24.2 | 41.018 | 21.854
| 10.5486 | 301.307 | 298.408 | 72.852 | 24.203 | 41.039 | 21.863
| 10.5556 | 301.117 | 299.647 | 72.916 | 24.208 | 41.082 | 21.872
| 10.5625 | 301.712 | 300.147 | 72.979 | 24.219 | 41.116 | 21.879
| 10.5694 | 301.869 | 300.342 | 73.058 | 24.226 | 41.157 | 21.886
| 10.5764 | 302.185 | 299.816 | 73.119 | 24.231 | 41.186 | 21.901
| 10.5833 | 302.238 | 300.463 | 73.184 | 24.242 | 41.209 | 21.903
| 10.5903 | 302.57 | 300.778 | 73.269 | 24.251 | 41.252 | 21.918
| 10.5972 | 303.871 | 301.371 | 73.36 | 24.26 | 41.294 | 21.924
| 10.6042 | 303.148 | 301.933 | 73.441 | 24.269 | 41.328 | 21.939
| 10.6111 | 303.897 | 301.708 | 73.521 | 24.28 | 41.358 | 21.95
| 10.6181 | 303.483 | 302.05 | 73.597 | 24.295 | 41.388 | 21.963
| 10.625 | 300.591 | 298.16 | 73.532 | 24.307 | 41.315 | 21.976
| 10.6319 | 300.983 | 298.356 | 73.455 | 24.314 | 41.25 | 21.986
| 10.6389 | 300.913 | 299.606 | 73.423 | 24.32 | 41.243 | 21.997
| 10.6458 | 301.563 | 298.964 | 73.418 | 24.328 | 41.261 | 22.01
| 10.6528 | 301.023 | 298.757 | 73.406 | 24.334 | 41.265 | 22.02
| 10.6597 | 300.985 | 299.305 | 73.379 | 24.343 | 41.261 | 22.029
| 10.6667 | 297.827 | 296.542 | 73.286 | 24.349 | 41.213 | 22.038
| 10.6736 | 297.797 | 296.738 | 73.146 | 24.352 | 41.13 | 22.05
| 10.6806 | 297.614 | 296.313 | 73.032 | 24.353 | 41.086 | 22.059
| 10.6875 | 297.53 | 296.162 | 72.911 | 24.353 | 41.051 | 22.073
| 10.6944 | 297.595 | 296.251 | 72.844 | 24.357 | 41.053 | 22.075
| 10.7014 | 300.753 | 298.953 | 72.906 | 24.36 | 41.136 | 22.083
| 10.7083 | 299.818 | 298.558 | 72.936 | 24.367 | 41.187 | 22.094
| 10.7153 | 297.518 | 296.174 | 72.91 | 24.371 | 41.176 | 22.102
| 10.7222 | 299.158 | 297.332 | 72.803 | 24.376 | 41.095 | 22.11
| 10.7292 | 299.169 | 296.522 | 72.807 | 24.376 | 41.115 | 22.112
| 10.7361 | 301.648 | 299.424 | 72.828 | 24.38 | 41.147 | 22.125
| 10.7431 | 301.694 | 299.134 | 72.949 | 24.379 | 41.247 | 22.134
| 10.75 | 301.074 | 298.755 | 73.013 | 24.388 | 41.282 | 22.14
| 10.7569 | 301.148 | 299.191 | 73.079 | 24.396 | 41.309 | 22.148
| 10.7639 | 301.346 | 299.819 | 73.145 | 24.407 | 41.342 | 22.157
| 10.7708 | 301.681 | 299.859 | 73.217 | 24.412 | 41.364 | 22.169
| 10.7778 | 301.395 | 299.362 | 73.266 | 24.419 | 41.376 | 22.178
| 10.7847 | 302.229 | 299.673 | 73.316 | 24.435 | 41.4 | 22.187
| 10.7917 | 302.075 | 299.229 | 73.372 | 24.441 | 41.419 | 22.195
| 10.7986 | 302.551 | 299.907 | 73.419 | 24.455 | 41.439 | 22.205
| 10.8056 | 303.056 | 300.871 | 73.517 | 24.461 | 41.497 | 22.221
| 10.8125 | 302.757 | 300.937 | 73.604 | 24.475 | 41.543 | 22.229
| 10.8194 | 303.642 | 300.853 | 73.686 | 24.483 | 41.579 | 22.24
| 10.8264 | 303.601 | 301.263 | 73.775 | 24.493 | 41.615 | 22.252
| 10.8333 | 301.008 | 298.207 | 73.693 | 24.505 | 41.532 | 22.266
| 10.8403 | 300.549 | 299.203 | 73.661 | 24.513 | 41.503 | 22.279
| 10.8472 | 302.512 | 300.375 | 73.659 | 24.527 | 41.513 | 22.287
| 10.8542 | 303.224 | 301.397 | 73.744 | 24.533 | 41.59 | 22.299
| 10.8611 | 302.059 | 299.659 | 73.717 | 24.543 | 41.568 | 22.307
| 10.8681 | 302.13 | 300.277 | 73.737 | 24.548 | 41.586 | 22.322
| 10.875 | 302.349 | 300.549 | 73.759 | 24.561 | 41.608 | 22.328
| 10.8819 | 303.138 | 300.581 | 73.805 | 24.567 | 41.64 | 22.341
| 10.8889 | 300.558 | 298.481 | 73.859 | 24.575 | 41.683 | 22.351
| 10.8958 | 299.219 | 297.475 | 73.704 | 24.583 | 41.561 | 22.361
| 10.9028 | 299.668 | 297.383 | 73.594 | 24.588 | 41.492 | 22.374
| 10.9097 | 299.028 | 297.395 | 73.505 | 24.596 | 41.47 | 22.384
| 10.9167 | 299.469 | 297.886 | 73.424 | 24.602 | 41.451 | 22.394
| 10.9236 | 300.213 | 298.094 | 73.389 | 24.605 | 41.463 | 22.405
| 10.9306 | 301.615 | 298.999 | 73.396 | 24.608 | 41.5 | 22.409
| 10.9375 | 301.577 | 299.459 | 73.443 | 24.616 | 41.551 | 22.42
| 10.9444 | 302.473 | 299.665 | 73.478 | 24.623 | 41.584 | 22.429
| 10.9514 | 302.514 | 299.867 | 73.518 | 24.633 | 41.614 | 22.435
| 10.9583 | 299.819 | 297.598 | 73.478 | 24.635 | 41.591 | 22.444
| 10.9653 | 299.719 | 298.295 | 73.426 | 24.653 | 41.561 | 22.46
| 10.9722 | 300.404 | 297.898 | 73.408 | 24.651 | 41.553 | 22.462
| 10.9792 | 300.671 | 298.978 | 73.398 | 24.669 | 41.575 | 22.472
| 10.9861 | 301.219 | 299.601 | 73.427 | 24.665 | 41.6 | 22.482
| 10.9931 | 301.577 | 298.764 | 73.444 | 24.664 | 41.605 | 22.488
| 11 | 301.932 | 300.07 | 73.496 | 24.678 | 41.655 | 22.496
| 11.0069 | 303.004 | 300.305 | 73.578 | 24.688 | 41.699 | 22.504
| 11.0139 | 302.984 | 300.1 | 73.645 | 24.685 | 41.736 | 22.515
| 11.0208 | 300.674 | 298.465 | 73.623 | 24.703 | 41.71 | 22.522
| 11.0278 | 300.951 | 298.138 | 73.582 | 24.708 | 41.668 | 22.531
| 11.0347 | 299.89 | 298.499 | 73.561 | 24.711 | 41.656 | 22.538
| 11.0417 | 299.719 | 298.28 | 73.501 | 24.718 | 41.623 | 22.545
| 11.0486 | 299.717 | 298.068 | 73.478 | 24.722 | 41.623 | 22.553
| 11.0556 | 300.977 | 299.565 | 73.498 | 24.729 | 41.655 | 22.567
| 11.0625 | 301.091 | 299.556 | 73.538 | 24.737 | 41.695 | 22.571
| 11.0694 | 302.059 | 299.239 | 73.583 | 24.743 | 41.729 | 22.58
| 11.0764 | 301.647 | 300.039 | 73.621 | 24.75 | 41.746 | 22.591
| 11.0833 | 302.256 | 300.398 | 73.672 | 24.755 | 41.771 | 22.596
| 11.0903 | 301.872 | 300.379 | 73.729 | 24.763 | 41.806 | 22.601
| 11.0972 | 303.652 | 300.788 | 73.815 | 24.773 | 41.856 | 22.608
| 11.1042 | 302.516 | 301.03 | 73.894 | 24.788 | 41.892 | 22.618
| 11.1111 | 299.597 | 297.973 | 73.838 | 24.797 | 41.833 | 22.626
| 11.1181 | 300.215 | 297.549 | 73.755 | 24.802 | 41.761 | 22.637
| 11.125 | 299.852 | 297.544 | 73.685 | 24.81 | 41.725 | 22.651
| 11.1319 | 299.396 | 297.779 | 73.619 | 24.81 | 41.703 | 22.655
| 11.1389 | 300.126 | 297.257 | 73.577 | 24.819 | 41.699 | 22.659
| 11.1458 | 300.349 | 297.429 | 73.552 | 24.825 | 41.714 | 22.669
| 11.1528 | 300.393 | 297.806 | 73.548 | 24.829 | 41.73 | 22.67
| 11.1597 | 299.621 | 298.261 | 73.532 | 24.834 | 41.733 | 22.68
| 11.1667 | 300.604 | 297.692 | 73.518 | 24.838 | 41.732 | 22.688
| 11.1736 | 299.786 | 298.148 | 73.51 | 24.84 | 41.739 | 22.692
| 11.1806 | 301.044 | 298.02 | 73.508 | 24.846 | 41.751 | 22.7
| 11.1875 | 300.493 | 298.35 | 73.514 | 24.852 | 41.765 | 22.702
| 11.1944 | 299.636 | 298.115 | 73.512 | 24.857 | 41.767 | 22.708
| 11.2014 | 299.413 | 297.908 | 73.483 | 24.864 | 41.751 | 22.714
| 11.2083 | 299.468 | 296.421 | 73.433 | 24.864 | 41.726 | 22.716
| 11.2153 | 298.463 | 296.965 | 73.368 | 24.87 | 41.69 | 22.721
| 11.2222 | 299.038 | 296.441 | 73.327 | 24.877 | 41.683 | 22.73
| 11.2292 | 298.18 | 296.773 | 73.283 | 24.878 | 41.676 | 22.734
| 11.2361 | 298.981 | 295.931 | 73.229 | 24.881 | 41.654 | 22.736
| 11.2431 | 298.714 | 296.301 | 73.18 | 24.887 | 41.647 | 22.74
| 11.25 | 298.407 | 295.416 | 73.134 | 24.884 | 41.638 | 22.743
| 11.2569 | 298.175 | 295.953 | 73.09 | 24.888 | 41.628 | 22.747
| 11.2639 | 296.53 | 294.044 | 73.023 | 24.89 | 41.605 | 22.75
| 11.2708 | 300.455 | 297.437 | 73.126 | 24.893 | 41.697 | 22.755
| 11.2778 | 300.58 | 297.97 | 73.203 | 24.898 | 41.752 | 22.758
| 11.2847 | 300.661 | 297.576 | 73.255 | 24.903 | 41.778 | 22.756
| 11.2917 | 300.471 | 297.104 | 73.293 | 24.907 | 41.79 | 22.765
| 11.2986 | 300.084 | 297.888 | 73.323 | 24.913 | 41.799 | 22.763
| 11.3056 | 299.908 | 297.315 | 73.325 | 24.922 | 41.788 | 22.77
| 11.3125 | 299.473 | 297.332 | 73.338 | 24.929 | 41.787 | 22.771
| 11.3194 | 299.393 | 297.376 | 73.341 | 24.933 | 41.786 | 22.779
| 11.3264 | 299.894 | 298.038 | 73.385 | 24.936 | 41.813 | 22.782
| 11.3333 | 300.02 | 296.809 | 73.39 | 24.943 | 41.817 | 22.783
| 11.3403 | 299.992 | 296.728 | 73.391 | 24.946 | 41.811 | 22.787
| 11.3472 | 300.582 | 298.783 | 73.406 | 24.955 | 41.82 | 22.795
| 11.3542 | 300.878 | 297.854 | 73.468 | 24.957 | 41.872 | 22.795
| 11.3611 | 300.899 | 297.893 | 73.519 | 24.967 | 41.899 | 22.802
| 11.3681 | 300.561 | 298.349 | 73.553 | 24.971 | 41.913 | 22.804
| 11.375 | 301.255 | 297.884 | 73.587 | 24.979 | 41.923 | 22.809
| 11.3819 | 300.297 | 297.839 | 73.592 | 24.991 | 41.914 | 22.809
| 11.3889 | 299.317 | 296.803 | 73.591 | 24.993 | 41.911 | 22.813
| 11.3958 | 299.738 | 297.371 | 73.574 | 25 | 41.893 | 22.817
| 11.4028 | 298.962 | 296.194 | 73.537 | 25.003 | 41.871 | 22.822
| 11.4097 | 297.86 | 295.637 | 73.477 | 25.012 | 41.838 | 22.822
| 11.4167 | 298.541 | 295.31 | 73.421 | 25.011 | 41.816 | 22.828
| 11.4236 | 303.324 | 300.101 | 73.622 | 25.017 | 41.984 | 22.829
| 11.4306 | 302.493 | 300.154 | 73.745 | 25.02 | 42.061 | 22.834
| 11.4375 | 302.454 | 299.778 | 73.819 | 25.03 | 42.085 | 22.837
| 11.4444 | 301.764 | 299.552 | 73.882 | 25.043 | 42.105 | 22.839
| 11.4514 | 302.822 | 300.905 | 73.966 | 25.051 | 42.132 | 22.839
| 11.4583 | 303.014 | 299.552 | 74.048 | 25.058 | 42.169 | 22.843
| 11.4653 | 302.507 | 299.858 | 74.113 | 25.069 | 42.182 | 22.85
| 11.4722 | 301.513 | 298.651 | 74.119 | 25.082 | 42.17 | 22.854
| 11.4792 | 301.608 | 298.301 | 74.117 | 25.084 | 42.148 | 22.857
| 11.4861 | 300.826 | 297.775 | 74.091 | 25.095 | 42.124 | 22.861
| 11.4931 | 300.648 | 297.649 | 74.041 | 25.101 | 42.094 | 22.866
| 11.5 | 300.117 | 298.333 | 74.024 | 25.108 | 42.092 | 22.872
| 11.5069 | 300.345 | 297.721 | 74 | 25.115 | 42.09 | 22.873
| 11.5139 | 300.85 | 298.302 | 73.944 | 25.117 | 42.063 | 22.876
| 11.5208 | 298.937 | 297.236 | 73.889 | 25.124 | 42.044 | 22.88
| 11.5278 | 299.607 | 296.456 | 73.83 | 25.127 | 42.025 | 22.882
| 11.5347 | 299.135 | 296.208 | 73.748 | 25.128 | 41.987 | 22.88
| 11.5417 | 299.192 | 296.266 | 73.709 | 25.135 | 41.993 | 22.885
| 11.5486 | 301.893 | 299.794 | 73.815 | 25.134 | 42.095 | 22.884
| 11.5556 | 302.774 | 299.997 | 73.903 | 25.135 | 42.16 | 22.884
| 11.5625 | 302.295 | 300.01 | 74 | 25.148 | 42.215 | 22.886
| 11.5694 | 303.614 | 301.048 | 74.096 | 25.153 | 42.253 | 22.886
| 11.5764 | 303.621 | 301.824 | 74.229 | 25.155 | 42.322 | 22.884
| 11.5833 | 302.966 | 301.162 | 74.311 | 25.168 | 42.346 | 22.891
| 11.5903 | 300.731 | 297.457 | 74.337 | 25.172 | 42.334 | 22.892
| 11.5972 | 301.318 | 299.553 | 74.253 | 25.184 | 42.24 | 22.896
| 11.6042 | 302.294 | 299.313 | 74.266 | 25.191 | 42.249 | 22.899
| 11.6111 | 301.142 | 298.845 | 74.257 | 25.194 | 42.247 | 22.897
| 11.6181 | 301.438 | 299.238 | 74.247 | 25.202 | 42.237 | 22.898
| 11.625 | 302.048 | 299.053 | 74.268 | 25.207 | 42.257 | 22.902
| 11.6319 | 302.178 | 299.718 | 74.274 | 25.213 | 42.265 | 22.901
| 11.6389 | 301.821 | 298.984 | 74.297 | 25.216 | 42.289 | 22.905
| 11.6458 | 301.438 | 299.625 | 74.312 | 25.221 | 42.289 | 22.905
| 11.6528 | 302.143 | 299.381 | 74.328 | 25.231 | 42.303 | 22.908
| 11.6597 | 301.198 | 299.284 | 74.327 | 25.233 | 42.301 | 22.904
| 11.6667 | 301.672 | 299.201 | 74.338 | 25.238 | 42.309 | 22.907
| 11.6736 | 302.592 | 299.598 | 74.357 | 25.244 | 42.32 | 22.904
| 11.6806 | 301.968 | 298.832 | 74.363 | 25.246 | 42.335 | 22.908
| 11.6875 | 301.255 | 298.536 | 74.346 | 25.252 | 42.319 | 22.906
| 11.6944 | 301.827 | 298.844 | 74.312 | 25.257 | 42.301 | 22.912
| 11.7014 | 301.079 | 299.289 | 74.3 | 25.26 | 42.299 | 22.909
| 11.7083 | 300.279 | 297.703 | 74.245 | 25.267 | 42.263 | 22.912
| 11.7153 | 299.237 | 296.267 | 74.144 | 25.27 | 42.21 | 22.908
| 11.7222 | 301.748 | 300.115 | 74.243 | 25.271 | 42.304 | 22.91
| 11.7292 | 300.877 | 299.071 | 74.228 | 25.269 | 42.31 | 22.909
| 11.7361 | 300.687 | 297.331 | 74.159 | 25.276 | 42.26 | 22.909
| 11.7431 | 299.169 | 297.51 | 74.085 | 25.277 | 42.219 | 22.911
| 11.75 | 299.725 | 297.245 | 74.025 | 25.278 | 42.195 | 22.907
| 11.7569 | 299.782 | 296.594 | 73.965 | 25.28 | 42.174 | 22.905
| 11.7639 | 298.557 | 296.622 | 73.913 | 25.283 | 42.159 | 22.906
| 11.7708 | 299.29 | 295.966 | 73.843 | 25.281 | 42.136 | 22.902
| 11.7778 | 299.01 | 297.133 | 73.791 | 25.28 | 42.121 | 22.899
| 11.7847 | 299.595 | 297.078 | 73.757 | 25.28 | 42.127 | 22.896
| 11.7917 | 299.794 | 297.028 | 73.759 | 25.279 | 42.144 | 22.898
| 11.7986 | 300.026 | 296.817 | 73.745 | 25.281 | 42.147 | 22.896
| 11.8056 | 300.89 | 297.701 | 73.77 | 25.279 | 42.172 | 22.897
| 11.8125 | 301.424 | 298.16 | 73.827 | 25.279 | 42.216 | 22.886
| 11.8194 | 300.835 | 299.036 | 73.898 | 25.283 | 42.258 | 22.891
| 11.8264 | 301.442 | 298.93 | 73.946 | 25.283 | 42.275 | 22.885
| 11.8333 | 301.528 | 299.683 | 74.003 | 25.286 | 42.296 | 22.885
| 11.8403 | 301.907 | 299.667 | 74.056 | 25.295 | 42.324 | 22.886
| 11.8472 | 302.064 | 300.37 | 74.127 | 25.296 | 42.352 | 22.886
| 11.8542 | 302.729 | 299.871 | 74.201 | 25.3 | 42.378 | 22.884
| 11.8611 | 303.75 | 300.813 | 74.306 | 25.306 | 42.435 | 22.887
| 11.8681 | 304.292 | 301.15 | 74.402 | 25.313 | 42.479 | 22.89
| 11.875 | 300.522 | 298.95 | 74.394 | 25.319 | 42.436 | 22.888
| 11.8819 | 301.478 | 299.668 | 74.376 | 25.326 | 42.396 | 22.889
| 11.8889 | 302.227 | 299.592 | 74.393 | 25.332 | 42.404 | 22.893
| 11.8958 | 301.524 | 298.887 | 74.381 | 25.333 | 42.396 | 22.89
| 11.9028 | 301.69 | 299.015 | 74.365 | 25.339 | 42.391 | 22.892
| 11.9097 | 302.378 | 299.597 | 74.388 | 25.339 | 42.407 | 22.893
| 11.9167 | 302.525 | 299.697 | 74.422 | 25.348 | 42.432 | 22.899
| 11.9236 | 299.409 | 297.524 | 74.324 | 25.354 | 42.364 | 22.893
| 11.9306 | 300.257 | 298.678 | 74.26 | 25.355 | 42.326 | 22.899
| 11.9375 | 300.831 | 298.1 | 74.246 | 25.365 | 42.335 | 22.901
| 11.9444 | 300.18 | 298.16 | 74.201 | 25.364 | 42.317 | 22.894
| 11.9514 | 300.422 | 298.323 | 74.166 | 25.36 | 42.314 | 22.896
| 11.9583 | 301.075 | 298.057 | 74.163 | 25.362 | 42.332 | 22.892
| 11.9653 | 301.335 | 298.05 | 74.164 | 25.361 | 42.346 | 22.898
| 11.9722 | 302.158 | 300.482 | 74.207 | 25.368 | 42.38 | 22.9
| 11.9792 | 301.722 | 299.812 | 74.259 | 25.375 | 42.426 | 22.9
| 11.9861 | 302.356 | 300.12 | 74.307 | 25.37 | 42.438 | 22.898
| 11.9931 | 302.888 | 299.674 | 74.357 | 25.382 | 42.468 | 22.897
| 12 | 302.709 | 300.793 | 74.415 | 25.382 | 42.486 | 22.895
| 12.0069 | 303.37 | 299.913 | 74.483 | 25.385 | 42.516 | 22.893
| 12.0139 | 303.255 | 301.272 | 74.534 | 25.389 | 42.53 | 22.895
| 12.0208 | 303.268 | 301.359 | 74.61 | 25.388 | 42.566 | 22.897
| 12.0278 | 301.021 | 297.674 | 74.541 | 25.389 | 42.503 | 22.895
| 12.0347 | 300.015 | 298.021 | 74.474 | 25.399 | 42.439 | 22.897
| 12.0417 | 299.487 | 297.389 | 74.397 | 25.4 | 42.392 | 22.897
| 12.0486 | 301.023 | 297.778 | 74.346 | 25.402 | 42.376 | 22.896
| 12.0556 | 300.964 | 297.763 | 74.3 | 25.404 | 42.365 | 22.894
| 12.0625 | 300.85 | 297.974 | 74.28 | 25.403 | 42.374 | 22.896
| 12.0694 | 300.305 | 297.866 | 74.247 | 25.402 | 42.364 | 22.893
| 12.0764 | 300.825 | 298.169 | 74.229 | 25.4 | 42.364 | 22.891
| 12.0833 | 300.674 | 297.259 | 74.2 | 25.402 | 42.356 | 22.889
| 12.0903 | 300.888 | 298.075 | 74.184 | 25.404 | 42.356 | 22.891
| 12.0972 | 301.644 | 298.56 | 74.206 | 25.398 | 42.378 | 22.887
| 12.1042 | 298.758 | 296.558 | 74.167 | 25.403 | 42.361 | 22.884
| 12.1111 | 298.827 | 296.373 | 74.08 | 25.405 | 42.294 | 22.882
| 12.1181 | 299.419 | 295.915 | 74.011 | 25.404 | 42.258 | 22.88
| 12.125 | 299 | 296.466 | 73.962 | 25.399 | 42.25 | 22.879
| 12.1319 | 299.681 | 296.527 | 73.928 | 25.396 | 42.243 | 22.874
| 12.1389 | 299.06 | 296.841 | 73.888 | 25.397 | 42.238 | 22.876
| 12.1458 | 299.137 | 296.83 | 73.856 | 25.396 | 42.237 | 22.869
| 12.1528 | 298.829 | 296.438 | 73.816 | 25.396 | 42.22 | 22.865
| 12.1597 | 299.425 | 296.978 | 73.791 | 25.39 | 42.215 | 22.862
| 12.1667 | 299.109 | 296.211 | 73.752 | 25.389 | 42.203 | 22.861
| 12.1736 | 298.885 | 297.042 | 73.735 | 25.386 | 42.191 | 22.855
| 12.1806 | 299.039 | 296.425 | 73.712 | 25.386 | 42.191 | 22.855
| 12.1875 | 298.612 | 296.758 | 73.687 | 25.383 | 42.181 | 22.851
| 12.1944 | 298.536 | 296.728 | 73.653 | 25.382 | 42.168 | 22.848
| 12.2014 | 298.934 | 295.772 | 73.618 | 25.378 | 42.156 | 22.839
| 12.2083 | 298.226 | 295.959 | 73.555 | 25.377 | 42.114 | 22.838
| 12.2153 | 298.043 | 294.871 | 73.49 | 25.371 | 42.084 | 22.832
| 12.2222 | 300.637 | 297.83 | 73.514 | 25.371 | 42.122 | 22.831
| 12.2292 | 299.71 | 297.023 | 73.556 | 25.37 | 42.168 | 22.827
| 12.2361 | 301.887 | 298.932 | 73.637 | 25.369 | 42.214 | 22.826
| 12.2431 | 300.682 | 297.651 | 73.712 | 25.37 | 42.262 | 22.822
| 12.25 | 301.37 | 298.226 | 73.779 | 25.37 | 42.279 | 22.818
| 12.2569 | 300.084 | 297.96 | 73.807 | 25.371 | 42.278 | 22.817
| 12.2639 | 297.057 | 295.039 | 73.737 | 25.375 | 42.21 | 22.813
| 12.2708 | 302.597 | 299.505 | 73.852 | 25.376 | 42.284 | 22.814
| 12.2778 | 301.411 | 299.246 | 73.932 | 25.378 | 42.327 | 22.811
| 12.2847 | 300.235 | 298.279 | 73.939 | 25.383 | 42.304 | 22.807
| 12.2917 | 300.48 | 298.702 | 73.972 | 25.385 | 42.307 | 22.806
| 12.2986 | 299.684 | 297.936 | 73.969 | 25.389 | 42.291 | 22.809
| 12.3056 | 297.698 | 295.633 | 73.9 | 25.393 | 42.234 | 22.807
| 12.3125 | 300.987 | 299.229 | 73.847 | 25.388 | 42.196 | 22.803
| 12.3194 | 301.268 | 298.197 | 73.924 | 25.39 | 42.27 | 22.8
| 12.3264 | 300.635 | 297.332 | 73.955 | 25.392 | 42.289 | 22.801
| 12.3333 | 299.614 | 296.971 | 73.928 | 25.392 | 42.26 | 22.799
| 12.3403 | 302.22 | 300.621 | 74.028 | 25.395 | 42.326 | 22.797
| 12.3472 | 301.312 | 298.565 | 74.084 | 25.394 | 42.356 | 22.8
| 12.3542 | 299.97 | 297.59 | 74.072 | 25.401 | 42.328 | 22.795
| 12.3611 | 301.102 | 299.41 | 74.146 | 25.403 | 42.373 | 22.797
| 12.3681 | 300.558 | 298.943 | 74.186 | 25.403 | 42.38 | 22.794
| 12.375 | 303.066 | 300.004 | 74.261 | 25.407 | 42.418 | 22.793
| 12.3819 | 303.853 | 300.63 | 74.354 | 25.414 | 42.46 | 22.796
| 12.3889 | 302.728 | 300.75 | 74.438 | 25.417 | 42.497 | 22.797
| 12.3958 | 304.185 | 300.88 | 74.545 | 25.426 | 42.546 | 22.798
| 12.4028 | 303.43 | 301.852 | 74.636 | 25.431 | 42.576 | 22.794
| 12.4097 | 302.584 | 299.778 | 74.684 | 25.439 | 42.571 | 22.796
| 12.4167 | 301.176 | 298.657 | 74.596 | 25.444 | 42.483 | 22.803
| 12.4236 | 300.602 | 299.082 | 74.56 | 25.446 | 42.452 | 22.801
| 12.4306 | 301.251 | 297.924 | 74.505 | 25.447 | 42.413 | 22.802
| 12.4375 | 300.625 | 297.515 | 74.458 | 25.453 | 42.398 | 22.806
| 12.4444 | 300.166 | 298.389 | 74.396 | 25.455 | 42.368 | 22.805
| 12.4514 | 299.223 | 297.588 | 74.331 | 25.455 | 42.351 | 22.804
| 12.4583 | 299.089 | 297.204 | 74.262 | 25.448 | 42.321 | 22.804
| 12.4653 | 299.073 | 295.917 | 74.164 | 25.452 | 42.282 | 22.807
| 12.4722 | 298.765 | 297.027 | 74.103 | 25.45 | 42.265 | 22.803
| 12.4792 | 298.48 | 296.19 | 74.052 | 25.445 | 42.255 | 22.801
| 12.4861 | 300.223 | 297.208 | 74.012 | 25.446 | 42.251 | 22.8
| 12.4931 | 298.986 | 296.179 | 73.988 | 25.444 | 42.253 | 22.8
| 12.5 | 299.331 | 297.556 | 73.97 | 25.444 | 42.256 | 22.794
| 12.5069 | 300.798 | 297.664 | 73.966 | 25.443 | 42.264 | 22.795
| 12.5139 | 300.443 | 298.599 | 73.982 | 25.443 | 42.29 | 22.794
| 12.5208 | 300.695 | 297.605 | 74.012 | 25.438 | 42.315 | 22.794
| 12.5278 | 300.669 | 297.583 | 74.026 | 25.439 | 42.316 | 22.79
| 12.5347 | 300.826 | 297.749 | 74.045 | 25.439 | 42.321 | 22.79
| 12.5417 | 300.705 | 298.545 | 74.059 | 25.44 | 42.332 | 22.787
| 12.5486 | 301.121 | 298.764 | 74.089 | 25.441 | 42.347 | 22.785
| 12.5556 | 301.259 | 298.208 | 74.123 | 25.443 | 42.353 | 22.787
| 12.5625 | 299.918 | 297.109 | 74.101 | 25.445 | 42.33 | 22.784
| 12.5694 | 300.324 | 297.959 | 74.09 | 25.45 | 42.314 | 22.783
| 12.5764 | 301.523 | 298.524 | 74.114 | 25.447 | 42.33 | 22.784
| 12.5833 | 300.975 | 297.844 | 74.137 | 25.449 | 42.342 | 22.785
| 12.5903 | 301.747 | 298.664 | 74.165 | 25.449 | 42.361 | 22.787
| 12.5972 | 302.916 | 299.852 | 74.236 | 25.454 | 42.398 | 22.786
| 12.6042 | 301.844 | 298.673 | 74.275 | 25.459 | 42.422 | 22.788
| 12.6111 | 302.046 | 299.53 | 74.312 | 25.459 | 42.427 | 22.785
| 12.6181 | 301.506 | 300.1 | 74.344 | 25.461 | 42.433 | 22.783
| 12.625 | 302.524 | 299.797 | 74.384 | 25.467 | 42.447 | 22.787
| 12.6319 | 301.79 | 300.269 | 74.438 | 25.468 | 42.473 | 22.786
| 12.6389 | 303.185 | 300.635 | 74.489 | 25.473 | 42.487 | 22.787
| 12.6458 | 302.282 | 300.717 | 74.537 | 25.475 | 42.51 | 22.787
| 12.6528 | 302.46 | 300.37 | 74.6 | 25.48 | 42.529 | 22.791
| 12.6597 | 302.915 | 300.993 | 74.641 | 25.485 | 42.545 | 22.796
| 12.6667 | 302.609 | 299.777 | 74.681 | 25.484 | 42.554 | 22.793
| 12.6736 | 302.378 | 300.17 | 74.728 | 25.492 | 42.575 | 22.799
| 12.6806 | 303.294 | 300.312 | 74.763 | 25.504 | 42.575 | 22.8
| 12.6875 | 302.971 | 299.926 | 74.77 | 25.502 | 42.569 | 22.803
| 12.6944 | 303.036 | 301.611 | 74.811 | 25.508 | 42.591 | 22.807
| 12.7014 | 302.392 | 299.393 | 74.814 | 25.514 | 42.583 | 22.806
| 12.7083 | 302.37 | 299.719 | 74.812 | 25.518 | 42.573 | 22.807
| 12.7153 | 300.269 | 297.461 | 74.72 | 25.521 | 42.51 | 22.814
| 12.7222 | 298.669 | 296.69 | 74.584 | 25.523 | 42.412 | 22.81
| 12.7292 | 298.773 | 296.021 | 74.445 | 25.525 | 42.349 | 22.814
| 12.7361 | 299.19 | 296.429 | 74.312 | 25.525 | 42.294 | 22.818
| 12.7431 | 298.283 | 296.857 | 74.212 | 25.521 | 42.272 | 22.818
| 12.75 | 298.925 | 296.648 | 74.119 | 25.515 | 42.255 | 22.817
| 12.7569 | 299.674 | 297.006 | 74.075 | 25.515 | 42.255 | 22.817
| 12.7639 | 299.276 | 297.973 | 74.048 | 25.512 | 42.272 | 22.817
| 12.7708 | 299.454 | 297.954 | 74.047 | 25.507 | 42.295 | 22.814
| 12.7778 | 299.282 | 297.125 | 74.027 | 25.505 | 42.289 | 22.815
| 12.7847 | 298.632 | 297.11 | 73.98 | 25.504 | 42.264 | 22.81
| 12.7917 | 299.189 | 296.396 | 73.937 | 25.5 | 42.246 | 22.809
| 12.7986 | 299.1 | 297.769 | 73.924 | 25.5 | 42.245 | 22.807
| 12.8056 | 299.404 | 296.508 | 73.898 | 25.497 | 42.241 | 22.805
| 12.8125 | 299.58 | 298.104 | 73.898 | 25.493 | 42.251 | 22.81
| 12.8194 | 300.02 | 297.176 | 73.891 | 25.492 | 42.252 | 22.801
| 12.8264 | 300.073 | 297.858 | 73.89 | 25.495 | 42.248 | 22.803
| 12.8333 | 299.824 | 298.455 | 73.91 | 25.495 | 42.271 | 22.804
| 12.8403 | 300.361 | 298.23 | 73.945 | 25.495 | 42.289 | 22.799
| 12.8472 | 302.164 | 299.434 | 74.01 | 25.494 | 42.333 | 22.803
| 12.8542 | 302.029 | 299.303 | 74.1 | 25.496 | 42.385 | 22.801
| 12.8611 | 301.024 | 299.812 | 74.166 | 25.501 | 42.406 | 22.799
| 12.8681 | 302.07 | 300.422 | 74.242 | 25.504 | 42.432 | 22.799
| 12.875 | 302.219 | 300.709 | 74.328 | 25.507 | 42.467 | 22.802
| 12.8819 | 302.445 | 300.219 | 74.405 | 25.512 | 42.494 | 22.803
| 12.8889 | 303.213 | 302.012 | 74.502 | 25.513 | 42.535 | 22.808
| 12.8958 | 303.98 | 301.246 | 74.623 | 25.523 | 42.593 | 22.811
| 12.9028 | 300.28 | 297.584 | 74.516 | 25.525 | 42.472 | 22.809
| 12.9097 | 301.71 | 299.035 | 74.479 | 25.533 | 42.435 | 22.817
| 12.9167 | 299.739 | 297.659 | 74.496 | 25.534 | 42.461 | 22.82
| 12.9236 | 300.139 | 298.326 | 74.407 | 25.543 | 42.397 | 22.819
| 12.9306 | 302.68 | 300.09 | 74.423 | 25.535 | 42.424 | 22.823
| 12.9375 | 302.358 | 300.868 | 74.511 | 25.54 | 42.499 | 22.823
| 12.9444 | 302.553 | 300.868 | 74.575 | 25.543 | 42.531 | 22.826
| 12.9514 | 303.988 | 301.267 | 74.673 | 25.553 | 42.589 | 22.825
| 12.9583 | 300.946 | 298.577 | 74.625 | 25.561 | 42.543 | 22.834
| 12.9653 | 298.458 | 295.855 | 74.599 | 25.558 | 42.506 | 22.835
| 12.9722 | 299.824 | 296.932 | 74.446 | 25.564 | 42.399 | 22.837
| 12.9792 | 299.666 | 297.503 | 74.39 | 25.563 | 42.38 | 22.839
| 12.9861 | 299.777 | 296.755 | 74.365 | 25.561 | 42.387 | 22.838
| 12.9931 | 297.751 | 295.92 | 74.23 | 25.559 | 42.316 | 22.842
| 13 | 298.797 | 296.066 | 74.151 | 25.562 | 42.287 | 22.846
| 13.0069 | 298.566 | 297.095 | 74.089 | 25.561 | 42.276 | 22.845
| 13.0139 | 299.742 | 298.275 | 74.09 | 25.554 | 42.301 | 22.845
| 13.0208 | 300.604 | 299.057 | 74.134 | 25.556 | 42.359 | 22.843
| 13.0278 | 300.825 | 299 | 74.173 | 25.555 | 42.395 | 22.842
| 13.0347 | 300.93 | 298.813 | 74.219 | 25.553 | 42.416 | 22.843
| 13.0417 | 299.815 | 298.277 | 74.225 | 25.559 | 42.407 | 22.845
| 13.0486 | 300.786 | 297.911 | 74.237 | 25.56 | 42.404 | 22.846
| 13.0556 | 300.479 | 298.853 | 74.255 | 25.563 | 42.41 | 22.848
| 13.0625 | 301.071 | 299.429 | 74.301 | 25.563 | 42.436 | 22.85
| 13.0694 | 301.593 | 299.331 | 74.348 | 25.566 | 42.464 | 22.848
| 13.0764 | 302.558 | 299.41 | 74.398 | 25.574 | 42.481 | 22.851
| 13.0833 | 301.615 | 299.894 | 74.454 | 25.575 | 42.503 | 22.852
| 13.0903 | 301.954 | 299.98 | 74.502 | 25.582 | 42.524 | 22.856
| 13.0972 | 302.29 | 300.559 | 74.569 | 25.58 | 42.55 | 22.858
| 13.1042 | 302.556 | 300.39 | 74.625 | 25.587 | 42.568 | 22.862
| 13.1111 | 302.66 | 300.781 | 74.677 | 25.595 | 42.589 | 22.867
| 13.1181 | 302.626 | 300.836 | 74.729 | 25.602 | 42.608 | 22.868
| 13.125 | 301.031 | 299.52 | 74.714 | 25.61 | 42.576 | 22.871
| 13.1319 | 301.849 | 299.488 | 74.718 | 25.607 | 42.562 | 22.876
| 13.1389 | 301.749 | 298.724 | 74.705 | 25.61 | 42.552 | 22.878
| 13.1458 | 300.817 | 299.617 | 74.692 | 25.617 | 42.541 | 22.874
| 13.1528 | 301.488 | 299.271 | 74.693 | 25.619 | 42.543 | 22.879
| 13.1597 | 301.783 | 299.566 | 74.705 | 25.622 | 42.559 | 22.885
| 13.1667 | 301.624 | 298.788 | 74.685 | 25.621 | 42.549 | 22.887
| 13.1736 | 301.277 | 298.722 | 74.666 | 25.625 | 42.534 | 22.893
| 13.1806 | 300.948 | 298.178 | 74.647 | 25.627 | 42.526 | 22.893
| 13.1875 | 300.563 | 297.814 | 74.597 | 25.632 | 42.5 | 22.896
| 13.1944 | 300.969 | 298.338 | 74.575 | 25.63 | 42.494 | 22.898
| 13.2014 | 300.371 | 297.777 | 74.536 | 25.63 | 42.483 | 22.897
| 13.2083 | 300.534 | 297.588 | 74.502 | 25.627 | 42.472 | 22.899
| 13.2153 | 299.731 | 297.805 | 74.445 | 25.636 | 42.443 | 22.903
| 13.2222 | 298.46 | 296.929 | 74.373 | 25.634 | 42.406 | 22.902
| 13.2292 | 298.549 | 296.961 | 74.264 | 25.629 | 42.358 | 22.906
| 13.2361 | 298.858 | 295.84 | 74.172 | 25.626 | 42.323 | 22.904
| 13.2431 | 298.53 | 296.85 | 74.106 | 25.623 | 42.3 | 22.901
| 13.25 | 298.015 | 296.417 | 74.034 | 25.624 | 42.286 | 22.904
| 13.2569 | 299.577 | 297.652 | 74.092 | 25.62 | 42.354 | 22.902
| 13.2639 | 297.281 | 295.669 | 74.037 | 25.623 | 42.331 | 22.901
| 13.2708 | 300.709 | 298.593 | 74.064 | 25.62 | 42.354 | 22.904
| 13.2778 | 301.325 | 298.428 | 74.122 | 25.621 | 42.399 | 22.902
| 13.2847 | 299.409 | 296.925 | 74.111 | 25.624 | 42.384 | 22.901
| 13.2917 | 298.862 | 297.4 | 74.107 | 25.618 | 42.37 | 22.907
| 13.2986 | 299.147 | 296.323 | 74.064 | 25.622 | 42.334 | 22.903
| 13.3056 | 296.911 | 295.28 | 73.97 | 25.62 | 42.271 | 22.898
| 13.3125 | 299.74 | 297.944 | 73.969 | 25.622 | 42.291 | 22.904
| 13.3194 | 300.708 | 298.288 | 73.997 | 25.617 | 42.33 | 22.906
| 13.3264 | 298.485 | 297.044 | 73.979 | 25.617 | 42.319 | 22.904
| 13.3333 | 298.586 | 297.25 | 73.943 | 25.617 | 42.291 | 22.904
| 13.3403 | 299.672 | 297.157 | 73.956 | 25.615 | 42.301 | 22.9
| 13.3472 | 301.116 | 298.739 | 74.014 | 25.618 | 42.352 | 22.9
| 13.3542 | 300.873 | 298.295 | 74.049 | 25.619 | 42.381 | 22.899
| 13.3611 | 300.671 | 298.649 | 74.128 | 25.62 | 42.421 | 22.9
| 13.3681 | 300.156 | 298.622 | 74.168 | 25.625 | 42.422 | 22.902
| 13.375 | 301.335 | 298.959 | 74.22 | 25.627 | 42.445 | 22.903
| 13.3819 | 301.373 | 299.417 | 74.271 | 25.628 | 42.459 | 22.9
| 13.3889 | 302.824 | 301.411 | 74.35 | 25.634 | 42.492 | 22.899
| 13.3958 | 302.681 | 301.364 | 74.469 | 25.636 | 42.561 | 22.902
| 13.4028 | 302.304 | 300.986 | 74.567 | 25.641 | 42.596 | 22.904
| 13.4097 | 302.921 | 300.81 | 74.658 | 25.651 | 42.628 | 22.909
| 13.4167 | 303.727 | 301.854 | 74.761 | 25.66 | 42.664 | 22.912
| 13.4236 | 303.457 | 300.796 | 74.835 | 25.668 | 42.683 | 22.911
| 13.4306 | 303.855 | 301.541 | 74.914 | 25.671 | 42.703 | 22.92
| 13.4375 | 304.598 | 302.313 | 75.01 | 25.681 | 42.745 | 22.916
| 13.4444 | 304.517 | 302.093 | 75.125 | 25.692 | 42.792 | 22.92
| 13.4514 | 303.472 | 301.564 | 75.189 | 25.698 | 42.802 | 22.927
| 13.4583 | 302.9 | 301.497 | 75.209 | 25.705 | 42.78 | 22.931
| 13.4653 | 302.964 | 301.144 | 75.233 | 25.715 | 42.779 | 22.933
| 13.4722 | 303.102 | 300.875 | 75.247 | 25.718 | 42.777 | 22.94
| 13.4792 | 303.578 | 300.759 | 75.264 | 25.724 | 42.78 | 22.946
| 13.4861 | 303.286 | 301.035 | 75.268 | 25.731 | 42.771 | 22.947
| 13.4931 | 302.814 | 300.038 | 75.269 | 25.739 | 42.765 | 22.948
| 13.5 | 302.508 | 300.916 | 75.26 | 25.738 | 42.762 | 22.952
| 13.5069 | 303.2 | 300.7 | 75.256 | 25.747 | 42.759 | 22.958
| 13.5139 | 303.683 | 302.716 | 75.293 | 25.751 | 42.79 | 22.957
| 13.5208 | 300.533 | 298.409 | 75.255 | 25.755 | 42.764 | 22.961
| 13.5278 | 300.69 | 298.152 | 75.141 | 25.759 | 42.675 | 22.965
| 13.5347 | 299.099 | 297.104 | 74.982 | 25.766 | 42.583 | 22.964
| 13.5417 | 297.781 | 295.453 | 74.83 | 25.777 | 42.531 | 22.984
| 13.5486 | 298.068 | 295.447 | 74.681 | 25.767 | 42.462 | 22.975
| 13.5556 | 298.246 | 296.672 | 74.552 | 25.763 | 42.423 | 22.974
| 13.5625 | 297.039 | 295.851 | 74.423 | 25.771 | 42.392 | 22.978
| 13.5694 | 297.493 | 296.276 | 74.309 | 25.778 | 42.37 | 22.983
| 13.5764 | 299.025 | 297.757 | 74.255 | 25.748 | 42.369 | 22.964
| 13.5833 | 299.046 | 296.648 | 74.229 | 25.747 | 42.393 | 22.968
| 13.5903 | 298.479 | 297.504 | 74.215 | 25.759 | 42.423 | 22.974
| 13.5972 | 298.993 | 298.166 | 74.241 | 25.76 | 42.456 | 22.972
| 13.6042 | 298.559 | 297.616 | 74.197 | 25.759 | 42.431 | 22.967
| 13.6111 | 298.091 | 297.139 | 74.168 | 25.752 | 42.416 | 22.965
| 13.6181 | 299.25 | 297.241 | 74.149 | 25.757 | 42.414 | 22.964
| 13.625 | 299.364 | 298.593 | 74.152 | 25.752 | 42.433 | 22.96
| 13.6319 | 299.691 | 298.313 | 74.197 | 25.754 | 42.46 | 22.958
| 13.6389 | 299.044 | 297.855 | 74.196 | 25.723 | 42.431 | 22.936
| 13.6458 | 299.599 | 298.635 | 74.21 | 25.734 | 42.448 | 22.939
| 13.6528 | 299.735 | 298.846 | 74.225 | 25.723 | 42.442 | 22.936
| 13.6597 | 300.703 | 298.834 | 74.247 | 25.729 | 42.456 | 22.935
| 13.6667 | 300.712 | 299.667 | 74.305 | 25.726 | 42.484 | 22.928
| 13.6736 | 300.649 | 299.695 | 74.365 | 25.741 | 42.531 | 22.941
| 13.6806 | 301.559 | 299.311 | 74.395 | 25.73 | 42.521 | 22.927
| 13.6875 | 300.517 | 298.882 | 74.431 | 25.729 | 42.532 | 22.925
| 13.6944 | 300.995 | 298.683 | 74.468 | 25.732 | 42.539 | 22.926
| 13.7014 | 298.953 | 297.931 | 74.436 | 25.732 | 42.509 | 22.928
| 13.7083 | 297.953 | 297.013 | 74.335 | 25.744 | 42.434 | 22.933
| 13.7153 | 297.437 | 296.667 | 74.245 | 25.732 | 42.378 | 22.928
| 13.7222 | 298.053 | 296.842 | 74.197 | 25.731 | 42.37 | 22.927
| 13.7292 | 300.836 | 298.888 | 74.153 | 25.749 | 42.369 | 22.939
| 13.7361 | 303.584 | 301.739 | 74.348 | 25.745 | 42.543 | 22.938
| 13.7431 | 303.508 | 301.472 | 74.514 | 25.751 | 42.654 | 22.94
| 13.75 | 303.302 | 301.1 | 74.631 | 25.753 | 42.698 | 22.94
| 13.7569 | 303.757 | 302.799 | 74.791 | 25.76 | 42.762 | 22.942
| 13.7639 | 301.413 | 299.158 | 74.72 | 25.767 | 42.661 | 22.943
| 13.7708 | 298.717 | 297.474 | 74.693 | 25.762 | 42.617 | 22.937
| 13.7778 | 298.911 | 296.735 | 74.586 | 25.775 | 42.53 | 22.949
| 13.7847 | 299.343 | 297.981 | 74.52 | 25.776 | 42.495 | 22.949
| 13.7917 | 298.613 | 297.298 | 74.464 | 25.773 | 42.482 | 22.952
| 13.7986 | 299.156 | 298.318 | 74.41 | 25.779 | 42.463 | 22.957
| 13.8056 | 299.9 | 298.941 | 74.405 | 25.781 | 42.484 | 22.957
| 13.8125 | 300.446 | 299.486 | 74.429 | 25.776 | 42.519 | 22.959
| 13.8194 | 300.908 | 299.874 | 74.488 | 25.781 | 42.566 | 22.958
| 13.8264 | 301.103 | 299.631 | 74.514 | 25.783 | 42.578 | 22.959
| 13.8333 | 301.363 | 299.982 | 74.557 | 25.785 | 42.597 | 22.965
| 13.8403 | 302.249 | 301.007 | 74.651 | 25.787 | 42.651 | 22.964
| 13.8472 | 301.306 | 299.159 | 74.648 | 25.794 | 42.632 | 22.971
| 13.8542 | 300.49 | 299.418 | 74.645 | 25.797 | 42.615 | 22.972
| 13.8611 | 301.569 | 299.182 | 74.663 | 25.796 | 42.615 | 22.973
| 13.8681 | 301.608 | 299.306 | 74.687 | 25.803 | 42.631 | 22.98
| 13.875 | 302.091 | 300.437 | 74.74 | 25.804 | 42.655 | 22.982
| 13.8819 | 302.842 | 300.581 | 74.798 | 25.811 | 42.694 | 22.986
| 13.8889 | 303.224 | 301.497 | 74.894 | 25.818 | 42.747 | 22.992
| 13.8958 | 303.282 | 301.1 | 74.953 | 25.82 | 42.781 | 22.993
| 13.9028 | 302.321 | 301.123 | 75.002 | 25.827 | 42.778 | 22.998
| 13.9097 | 300.207 | 298.356 | 75.032 | 25.813 | 42.77 | 22.995
| 13.9167 | 298.333 | 295.984 | 74.843 | 25.839 | 42.625 | 23.012
| 13.9236 | 298.726 | 297.091 | 74.716 | 25.845 | 42.556 | 23.014
| 13.9306 | 299.966 | 298.789 | 74.673 | 25.819 | 42.537 | 23.008
| 13.9375 | 300.228 | 298.367 | 74.641 | 25.843 | 42.571 | 23.027
| 13.9444 | 300.429 | 298.127 | 74.622 | 25.847 | 42.588 | 23.032
| 13.9514 | 300.58 | 299.377 | 74.613 | 25.844 | 42.601 | 23.037
| 13.9583 | 302.534 | 300.179 | 74.697 | 25.853 | 42.686 | 23.037
| 13.9653 | 303.773 | 301.318 | 74.822 | 25.856 | 42.769 | 23.043
| 13.9722 | 300.684 | 298.256 | 74.753 | 25.861 | 42.697 | 23.05
| 13.9792 | 301.307 | 298.99 | 74.75 | 25.867 | 42.685 | 23.056
| 13.9861 | 301.002 | 299.153 | 74.77 | 25.87 | 42.703 | 23.061
| 13.9931 | 301.16 | 299.142 | 74.786 | 25.869 | 42.711 | 23.064
| 14 | 300.25 | 299.215 | 74.752 | 25.85 | 42.656 | 23.052
| 14.0069 | 301.366 | 298.833 | 74.762 | 25.877 | 42.677 | 23.071
| 14.0139 | 302.006 | 300.52 | 74.797 | 25.872 | 42.708 | 23.073
| 14.0208 | 302.581 | 300.169 | 74.851 | 25.88 | 42.747 | 23.082
| 14.0278 | 300.231 | 297.673 | 74.808 | 25.884 | 42.707 | 23.084
| 14.0347 | 298.718 | 297.79 | 74.729 | 25.89 | 42.65 | 23.089
| 14.0417 | 298.879 | 297.784 | 74.643 | 25.884 | 42.59 | 23.093
| 14.0486 | 299.251 | 297.949 | 74.602 | 25.877 | 42.571 | 23.096
| 14.0556 | 299.493 | 297.687 | 74.557 | 25.875 | 42.575 | 23.099
| 14.0625 | 300.014 | 298.057 | 74.545 | 25.879 | 42.585 | 23.108
| 14.0694 | 300.052 | 298.18 | 74.542 | 25.878 | 42.592 | 23.102
| 14.0764 | 299.496 | 297.72 | 74.515 | 25.872 | 42.574 | 23.107
| 14.0833 | 298.824 | 297.304 | 74.492 | 25.89 | 42.573 | 23.116
| 14.0903 | 299.749 | 297.39 | 74.463 | 25.888 | 42.563 | 23.12
| 14.0972 | 299.809 | 298.104 | 74.47 | 25.885 | 42.584 | 23.121
| 14.1042 | 299.882 | 297.781 | 74.471 | 25.883 | 42.589 | 23.124
| 14.1111 | 299.607 | 298.195 | 74.455 | 25.893 | 42.581 | 23.129
| 14.1181 | 300.326 | 297.596 | 74.453 | 25.891 | 42.588 | 23.134
| 14.125 | 300.032 | 297.213 | 74.438 | 25.886 | 42.579 | 23.139
| 14.1319 | 299.289 | 297.733 | 74.423 | 25.9 | 42.577 | 23.144
| 14.1389 | 299.664 | 297.955 | 74.423 | 25.901 | 42.58 | 23.149
| 14.1458 | 299.707 | 297.131 | 74.404 | 25.904 | 42.574 | 23.154
| 14.1528 | 300.094 | 297.731 | 74.394 | 25.906 | 42.576 | 23.16
| 14.1597 | 299.268 | 297.422 | 74.396 | 25.908 | 42.584 | 23.166
| 14.1667 | 299.568 | 297.476 | 74.387 | 25.917 | 42.581 | 23.17
| 14.1736 | 299.597 | 298.135 | 74.387 | 25.902 | 42.576 | 23.166
| 14.1806 | 299.892 | 297.172 | 74.378 | 25.92 | 42.582 | 23.178
| 14.1875 | 299.487 | 296.738 | 74.369 | 25.921 | 42.575 | 23.177
| 14.1944 | 299.731 | 297.192 | 74.366 | 25.919 | 42.577 | 23.182
| 14.2014 | 299.052 | 297.643 | 74.354 | 25.91 | 42.566 | 23.177
| 14.2083 | 298.95 | 296.131 | 74.317 | 25.915 | 42.545 | 23.185
| 14.2153 | 297.891 | 295.676 | 74.253 | 25.911 | 42.499 | 23.183
| 14.2222 | 297.602 | 295.063 | 74.181 | 25.932 | 42.478 | 23.197
| 14.2292 | 298.999 | 297.422 | 74.211 | 25.93 | 42.523 | 23.206
| 14.2361 | 299.042 | 296.584 | 74.187 | 25.93 | 42.517 | 23.204
| 14.2431 | 298.094 | 295.407 | 74.145 | 25.928 | 42.487 | 23.203
| 14.25 | 297.734 | 295.624 | 74.085 | 25.928 | 42.456 | 23.211
| 14.2569 | 297.537 | 295.478 | 74.042 | 25.924 | 42.442 | 23.213
| 14.2639 | 300.813 | 299.521 | 74.185 | 25.916 | 42.549 | 23.212
| 14.2708 | 301.712 | 299.087 | 74.273 | 25.92 | 42.615 | 23.214
| 14.2778 | 301.796 | 298.866 | 74.376 | 25.929 | 42.675 | 23.225
| 14.2847 | 300.641 | 298.138 | 74.438 | 25.938 | 42.687 | 23.226
| 14.2917 | 299.776 | 297.042 | 74.429 | 25.944 | 42.647 | 23.232
| 14.2986 | 300.485 | 297.939 | 74.387 | 25.945 | 42.598 | 23.233
| 14.3056 | 298.456 | 296.144 | 74.37 | 25.95 | 42.597 | 23.243
| 14.3125 | 300.074 | 298.335 | 74.344 | 25.955 | 42.585 | 23.248
| 14.3194 | 301.927 | 300.33 | 74.488 | 25.957 | 42.701 | 23.248
| 14.3264 | 301.665 | 298.528 | 74.565 | 25.963 | 42.743 | 23.255
| 14.3333 | 300.889 | 298.151 | 74.603 | 25.969 | 42.738 | 23.254
| 14.3403 | 301.175 | 298.165 | 74.606 | 25.977 | 42.719 | 23.264
| 14.3472 | 301.728 | 300.247 | 74.618 | 25.982 | 42.717 | 23.275
| 14.3542 | 301.132 | 299.509 | 74.702 | 25.986 | 42.775 | 23.277
| 14.3611 | 303.221 | 300.49 | 74.798 | 25.99 | 42.825 | 23.278
| 14.3681 | 302.265 | 300.705 | 74.851 | 26 | 42.843 | 23.288
| 14.375 | 302.433 | 300.794 | 74.93 | 26.007 | 42.873 | 23.294
| 14.3819 | 302.045 | 300.471 | 74.99 | 26.016 | 42.891 | 23.302
| 14.3889 | 304.006 | 301.983 | 75.094 | 26.027 | 42.946 | 23.307
| 14.3958 | 302.895 | 299.907 | 75.163 | 26.036 | 42.976 | 23.316
| 14.4028 | 301.602 | 300.101 | 75.178 | 26.053 | 42.953 | 23.324
| 14.4097 | 301.792 | 300.147 | 75.178 | 26.061 | 42.937 | 23.332
| 14.4167 | 301.594 | 299.046 | 75.195 | 26.067 | 42.942 | 23.339
| 14.4236 | 300.182 | 298.769 | 75.154 | 26.077 | 42.916 | 23.346
| 14.4306 | 300.631 | 299.182 | 75.101 | 26.077 | 42.88 | 23.352
| 14.4375 | 300.903 | 298.279 | 75.065 | 26.082 | 42.871 | 23.355
| 14.4444 | 300.496 | 298.59 | 75.037 | 26.091 | 42.865 | 23.364
| 14.4514 | 300.15 | 298.422 | 75.003 | 26.094 | 42.858 | 23.368
| 14.4583 | 300.856 | 297.927 | 74.964 | 26.096 | 42.843 | 23.373
| 14.4653 | 299.78 | 298.275 | 74.923 | 26.1 | 42.839 | 23.378
| 14.4722 | 299.317 | 297.795 | 74.867 | 26.102 | 42.809 | 23.383
| 14.4792 | 298.76 | 296.782 | 74.796 | 26.108 | 42.776 | 23.389
| 14.4861 | 300.327 | 298.806 | 74.822 | 26.104 | 42.823 | 23.388
| 14.4931 | 300.688 | 299.223 | 74.846 | 26.109 | 42.858 | 23.392
| 14.5 | 300.765 | 299.244 | 74.86 | 26.112 | 42.872 | 23.396
| 14.5069 | 301.586 | 300.044 | 74.917 | 26.116 | 42.913 | 23.397
| 14.5139 | 302.874 | 301.506 | 75.044 | 26.116 | 42.989 | 23.401
| 14.5208 | 303.663 | 302.018 | 75.151 | 26.112 | 43.038 | 23.395
| 14.5278 | 300.198 | 298.215 | 75.131 | 26.129 | 43.007 | 23.411
| 14.5347 | 298.528 | 295.723 | 74.953 | 26.128 | 42.84 | 23.404
| 14.5417 | 298.84 | 296.033 | 74.82 | 26.126 | 42.77 | 23.413
| 14.5486 | 298.153 | 296.013 | 74.72 | 26.125 | 42.732 | 23.411
| 14.5556 | 298.683 | 295.739 | 74.645 | 26.133 | 42.731 | 23.421
| 14.5625 | 297.744 | 296.221 | 74.564 | 26.138 | 42.709 | 23.425
| 14.5694 | 301.32 | 299.325 | 74.626 | 26.137 | 42.79 | 23.429
| 14.5764 | 300.824 | 299.073 | 74.715 | 26.138 | 42.877 | 23.429
| 14.5833 | 301.298 | 299.431 | 74.771 | 26.138 | 42.908 | 23.428
| 14.5903 | 302.868 | 299.908 | 74.902 | 26.143 | 42.985 | 23.434
| 14.5972 | 303.816 | 301.707 | 75.02 | 26.151 | 43.042 | 23.43
| 14.6042 | 303.143 | 301.225 | 75.136 | 26.16 | 43.087 | 23.435
| 14.6111 | 303.745 | 301.385 | 75.24 | 26.167 | 43.123 | 23.443
| 14.6181 | 303.93 | 301.528 | 75.355 | 26.176 | 43.162 | 23.446
| 14.625 | 304.189 | 302.667 | 75.454 | 26.184 | 43.2 | 23.454
| 14.6319 | 303.666 | 302.358 | 75.556 | 26.193 | 43.228 | 23.452
| 14.6389 | 300.065 | 298.505 | 75.512 | 26.202 | 43.159 | 23.466
| 14.6458 | 300.201 | 297.455 | 75.409 | 26.209 | 43.065 | 23.467
| 14.6528 | 299.824 | 298.493 | 75.326 | 26.211 | 43.02 | 23.476
| 14.6597 | 300.013 | 297.885 | 75.252 | 26.217 | 42.993 | 23.478
| 14.6667 | 300.612 | 297.878 | 75.227 | 26.22 | 42.999 | 23.478
| 14.6736 | 299.393 | 297.646 | 75.145 | 26.22 | 42.962 | 23.483
| 14.6806 | 299.378 | 296.863 | 75.081 | 26.215 | 42.941 | 23.483
| 14.6875 | 299.664 | 297.275 | 75.03 | 26.219 | 42.933 | 23.488
| 14.6944 | 300.975 | 298.255 | 75.011 | 26.224 | 42.951 | 23.492
| 14.7014 | 301.047 | 298.515 | 75.023 | 26.22 | 42.984 | 23.49
| 14.7083 | 300.257 | 296.884 | 75.006 | 26.219 | 42.981 | 23.492
| 14.7153 | 299.549 | 297.026 | 74.955 | 26.227 | 42.958 | 23.497
| 14.7222 | 297.381 | 295.497 | 74.842 | 26.223 | 42.885 | 23.494
| 14.7292 | 299.025 | 296.082 | 74.822 | 26.229 | 42.897 | 23.497
| 14.7361 | 302.07 | 298.806 | 74.916 | 26.234 | 42.993 | 23.501
| 14.7431 | 300.788 | 298.892 | 74.933 | 26.234 | 43.012 | 23.503
| 14.75 | 301.565 | 298.545 | 74.973 | 26.234 | 43.026 | 23.501
| 14.7569 | 301.978 | 300.094 | 75.031 | 26.238 | 43.066 | 23.51
| 14.7639 | 301.558 | 299.856 | 75.106 | 26.244 | 43.108 | 23.509
| 14.7708 | 302.198 | 300.432 | 75.176 | 26.248 | 43.146 | 23.512
| 14.7778 | 302.498 | 299.458 | 75.229 | 26.259 | 43.156 | 23.517
| 14.7847 | 303.128 | 299.832 | 75.279 | 26.262 | 43.17 | 23.514
| 14.7917 | 302.527 | 300.451 | 75.336 | 26.27 | 43.19 | 23.52
| 14.7986 | 301.993 | 298.683 | 75.358 | 26.275 | 43.192 | 23.524
| 14.8056 | 302.139 | 300.317 | 75.358 | 26.283 | 43.17 | 23.53
| 14.8125 | 302.213 | 299.558 | 75.397 | 26.285 | 43.195 | 23.534
| 14.8194 | 302.509 | 299.744 | 75.405 | 26.293 | 43.194 | 23.54
| 14.8264 | 302.626 | 300.551 | 75.45 | 26.3 | 43.22 | 23.537
| 14.8333 | 303.839 | 300.914 | 75.506 | 26.305 | 43.254 | 23.549
| 14.8403 | 304.327 | 301.465 | 75.589 | 26.31 | 43.303 | 23.549
| 14.8472 | 301.251 | 298.735 | 75.479 | 26.317 | 43.208 | 23.557
| 14.8542 | 301.469 | 299.673 | 75.465 | 26.323 | 43.194 | 23.56
| 14.8611 | 300.801 | 297.883 | 75.422 | 26.325 | 43.183 | 23.565
| 14.8681 | 299.888 | 298.244 | 75.326 | 26.324 | 43.118 | 23.569
| 14.875 | 300.621 | 298.814 | 75.304 | 26.342 | 43.133 | 23.579
| 14.8819 | 301.88 | 298.824 | 75.289 | 26.331 | 43.141 | 23.575
| 14.8889 | 301.856 | 300.205 | 75.312 | 26.335 | 43.17 | 23.579
| 14.8958 | 301.499 | 298.296 | 75.291 | 26.34 | 43.17 | 23.578
| 14.9028 | 303.329 | 300.931 | 75.363 | 26.34 | 43.225 | 23.584
| 14.9097 | 303.255 | 301.35 | 75.436 | 26.347 | 43.272 | 23.589
| 14.9167 | 301.029 | 298.232 | 75.421 | 26.349 | 43.253 | 23.591
| 14.9236 | 301.105 | 298.981 | 75.4 | 26.359 | 43.217 | 23.593
| 14.9306 | 303.452 | 301.42 | 75.456 | 26.36 | 43.271 | 23.597
| 14.9375 | 303.706 | 301.505 | 75.56 | 26.361 | 43.34 | 23.597
| 14.9444 | 304.217 | 301.243 | 75.655 | 26.369 | 43.386 | 23.601
| 14.9514 | 300.738 | 299.274 | 75.684 | 26.375 | 43.387 | 23.606
| 14.9583 | 301.744 | 299.76 | 75.609 | 26.38 | 43.312 | 23.606
| 14.9653 | 301.864 | 300.334 | 75.618 | 26.388 | 43.324 | 23.615
| 14.9722 | 300.717 | 298.217 | 75.508 | 26.389 | 43.248 | 23.622
| 14.9792 | 300.778 | 298.075 | 75.474 | 26.391 | 43.233 | 23.62
| 14.9861 | 301.569 | 299.259 | 75.449 | 26.393 | 43.24 | 23.624
| 14.9931 | 302.116 | 299.29 | 75.449 | 26.397 | 43.259 | 23.627
| 15 | 301.977 | 299.809 | 75.469 | 26.397 | 43.283 | 23.627
| 15.0069 | 302.437 | 300.101 | 75.493 | 26.4 | 43.304 | 23.633
| 15.0139 | 303.238 | 300.325 | 75.539 | 26.397 | 43.336 | 23.632
| 15.0208 | 303.311 | 301.32 | 75.622 | 26.408 | 43.386 | 23.635
| 15.0278 | 303.853 | 301.574 | 75.691 | 26.409 | 43.425 | 23.638
| 15.0347 | 299.575 | 297.37 | 75.584 | 26.416 | 43.326 | 23.641
| 15.0417 | 299.632 | 297.462 | 75.461 | 26.418 | 43.241 | 23.642
| 15.0486 | 299.718 | 296.734 | 75.374 | 26.416 | 43.196 | 23.642
| 15.0556 | 300.012 | 297.499 | 75.296 | 26.416 | 43.167 | 23.642
| 15.0625 | 300.36 | 297.635 | 75.27 | 26.416 | 43.186 | 23.647
| 15.0694 | 300.557 | 297.55 | 75.231 | 26.41 | 43.18 | 23.644
| 15.0764 | 300.069 | 298.456 | 75.203 | 26.412 | 43.182 | 23.648
| 15.0833 | 300.652 | 298.092 | 75.191 | 26.417 | 43.188 | 23.646
| 15.0903 | 300.241 | 297.159 | 75.174 | 26.412 | 43.183 | 23.643
| 15.0972 | 301.078 | 297.994 | 75.162 | 26.411 | 43.189 | 23.644
| 15.1042 | 300.731 | 298.279 | 75.191 | 26.414 | 43.212 | 23.641
| 15.1111 | 298.478 | 295.586 | 75.026 | 26.414 | 43.096 | 23.643
| 15.1181 | 298.222 | 295.717 | 74.921 | 26.413 | 43.043 | 23.64
| 15.125 | 297.456 | 295.58 | 74.806 | 26.41 | 42.996 | 23.64
| 15.1319 | 297.4 | 294.886 | 74.718 | 26.402 | 42.969 | 23.638
| 15.1389 | 296.673 | 295.34 | 74.625 | 26.398 | 42.943 | 23.639
| 15.1458 | 297.21 | 295.189 | 74.547 | 26.395 | 42.921 | 23.634
| 15.1528 | 297.242 | 295.177 | 74.48 | 26.392 | 42.902 | 23.628
| 15.1597 | 296.674 | 295.162 | 74.417 | 26.389 | 42.881 | 23.623
| 15.1667 | 297.105 | 294.34 | 74.353 | 26.383 | 42.872 | 23.618
| 15.1736 | 297.238 | 294.512 | 74.294 | 26.373 | 42.845 | 23.613
| 15.1806 | 300.722 | 297.944 | 74.376 | 26.373 | 42.93 | 23.612
| 15.1875 | 299.842 | 298.105 | 74.472 | 26.368 | 43.012 | 23.607
| 15.1944 | 299.774 | 297.708 | 74.518 | 26.37 | 43.021 | 23.602
| 15.2014 | 299.815 | 296.972 | 74.57 | 26.371 | 43.033 | 23.599
| 15.2083 | 299.278 | 296.893 | 74.584 | 26.367 | 43.022 | 23.593
| 15.2153 | 298.639 | 295.787 | 74.568 | 26.371 | 42.989 | 23.591
| 15.2222 | 297.393 | 296.06 | 74.525 | 26.371 | 42.956 | 23.583
| 15.2292 | 301.047 | 298.115 | 74.646 | 26.366 | 43.043 | 23.584
| 15.2361 | 300.43 | 297.685 | 74.694 | 26.371 | 43.069 | 23.582
| 15.2431 | 299.702 | 296.751 | 74.705 | 26.378 | 43.05 | 23.581
| 15.25 | 298.93 | 297.456 | 74.688 | 26.373 | 43.025 | 23.575
| 15.2569 | 299.213 | 296.492 | 74.678 | 26.375 | 43.013 | 23.579
| 15.2639 | 295.334 | 293.947 | 74.585 | 26.376 | 42.94 | 23.574
| 15.2708 | 303.032 | 301.148 | 74.834 | 26.375 | 43.133 | 23.574
| 15.2778 | 303.338 | 301.777 | 75.016 | 26.376 | 43.235 | 23.565
| 15.2847 | 300.996 | 299.516 | 75.115 | 26.389 | 43.255 | 23.568
| 15.2917 | 300.038 | 297.423 | 75.112 | 26.386 | 43.208 | 23.565
| 15.2986 | 299.222 | 296.133 | 75.043 | 26.397 | 43.121 | 23.566
| 15.3056 | 298.129 | 295.532 | 74.963 | 26.392 | 43.054 | 23.562
| 15.3125 | 300.322 | 297.712 | 74.911 | 26.393 | 43.033 | 23.564
| 15.3194 | 300.822 | 298.882 | 75.033 | 26.395 | 43.145 | 23.566
| 15.3264 | 302.002 | 299.299 | 75.067 | 26.401 | 43.16 | 23.562
| 15.3333 | 301.509 | 298.776 | 75.131 | 26.401 | 43.201 | 23.565
| 15.3403 | 301.358 | 298.453 | 75.157 | 26.401 | 43.193 | 23.564
| 15.3472 | 303.067 | 300.258 | 75.176 | 26.406 | 43.188 | 23.559
| 15.3542 | 302.492 | 300.256 | 75.298 | 26.387 | 43.251 | 23.537
| 15.3611 | 302.605 | 299.617 | 75.369 | 26.388 | 43.278 | 23.539
| 15.3681 | 301.978 | 299.837 | 75.398 | 26.4 | 43.267 | 23.542
| 15.375 | 302.863 | 300.276 | 75.467 | 26.397 | 43.296 | 23.539
| 15.3819 | 302.607 | 300.095 | 75.52 | 26.406 | 43.312 | 23.536
| 15.3889 | 302.388 | 300.383 | 75.584 | 26.41 | 43.338 | 23.546
| 15.3958 | 303.103 | 300.474 | 75.639 | 26.419 | 43.353 | 23.539
| 15.4028 | 302.708 | 300.876 | 75.685 | 26.421 | 43.368 | 23.543
| 15.4097 | 302.768 | 299.833 | 75.71 | 26.423 | 43.36 | 23.545
| 15.4167 | 302.883 | 299.793 | 75.717 | 26.431 | 43.352 | 23.545
| 15.4236 | 301.789 | 300.318 | 75.716 | 26.435 | 43.344 | 23.546
| 15.4306 | 302.287 | 299.515 | 75.722 | 26.439 | 43.342 | 23.547
| 15.4375 | 301.361 | 299.744 | 75.737 | 26.443 | 43.351 | 23.55
| 15.4444 | 302.39 | 300.065 | 75.741 | 26.445 | 43.353 | 23.553
| 15.4514 | 302.221 | 299.74 | 75.754 | 26.448 | 43.357 | 23.551
| 15.4583 | 302.068 | 299.499 | 75.749 | 26.452 | 43.35 | 23.553
| 15.4653 | 302.749 | 300.694 | 75.771 | 26.453 | 43.366 | 23.554
| 15.4722 | 302.668 | 300.24 | 75.794 | 26.458 | 43.385 | 23.555
| 15.4792 | 303.201 | 301.224 | 75.845 | 26.458 | 43.413 | 23.554
| 15.4861 | 303.819 | 301.199 | 75.9 | 26.463 | 43.449 | 23.56
| 15.4931 | 303.986 | 301.018 | 75.941 | 26.464 | 43.462 | 23.555
| 15.5 | 303.101 | 300.788 | 75.985 | 26.47 | 43.474 | 23.557
| 15.5069 | 302.787 | 300.316 | 76.008 | 26.48 | 43.479 | 23.557
| 15.5139 | 303.896 | 301.828 | 76.053 | 26.481 | 43.501 | 23.558
| 15.5208 | 304.288 | 301.859 | 76.121 | 26.486 | 43.542 | 23.559
| 15.5278 | 300.372 | 297.8 | 75.963 | 26.491 | 43.41 | 23.564
| 15.5347 | 300.061 | 297.758 | 75.796 | 26.491 | 43.295 | 23.563
| 15.5417 | 299.373 | 296.995 | 75.676 | 26.489 | 43.245 | 23.569
| 15.5486 | 299.066 | 296.984 | 75.562 | 26.485 | 43.206 | 23.564
| 15.5556 | 299.031 | 296.538 | 75.462 | 26.486 | 43.179 | 23.57
| 15.5625 | 298.125 | 296.782 | 75.343 | 26.483 | 43.137 | 23.565
| 15.5694 | 298.942 | 297.1 | 75.262 | 26.475 | 43.119 | 23.565
| 15.5764 | 299.278 | 296.996 | 75.201 | 26.469 | 43.115 | 23.559
| 15.5833 | 298.745 | 297.234 | 75.173 | 26.47 | 43.125 | 23.559
| 15.5903 | 299.935 | 297.736 | 75.15 | 26.462 | 43.134 | 23.556
| 15.5972 | 300.797 | 298.382 | 75.15 | 26.459 | 43.155 | 23.553
| 15.6042 | 300.036 | 298.091 | 75.147 | 26.457 | 43.162 | 23.554
| 15.6111 | 299.985 | 297.594 | 75.14 | 26.455 | 43.157 | 23.547
| 15.6181 | 301.113 | 299.336 | 75.152 | 26.452 | 43.172 | 23.548
| 15.625 | 300.356 | 299.133 | 75.18 | 26.453 | 43.198 | 23.544
| 15.6319 | 301.099 | 298.373 | 75.212 | 26.45 | 43.205 | 23.542
| 15.6389 | 300.33 | 299.122 | 75.208 | 26.452 | 43.195 | 23.543
| 15.6458 | 301.027 | 299.202 | 75.237 | 26.452 | 43.204 | 23.539
| 15.6528 | 300.804 | 299.493 | 75.274 | 26.45 | 43.224 | 23.538
| 15.6597 | 299.834 | 298.226 | 75.247 | 26.453 | 43.192 | 23.542
| 15.6667 | 299.934 | 297.572 | 75.239 | 26.452 | 43.182 | 23.537
| 15.6736 | 299.891 | 298.39 | 75.222 | 26.451 | 43.175 | 23.537
| 15.6806 | 300.681 | 298.447 | 75.209 | 26.453 | 43.164 | 23.538
| 15.6875 | 300.682 | 299.447 | 75.216 | 26.447 | 43.181 | 23.535
| 15.6944 | 301.061 | 298.69 | 75.238 | 26.448 | 43.195 | 23.534
| 15.7014 | 300.881 | 298.38 | 75.255 | 26.455 | 43.207 | 23.536
| 15.7083 | 299.368 | 297.833 | 75.218 | 26.449 | 43.178 | 23.539
| 15.7153 | 297.945 | 296.481 | 75.155 | 26.449 | 43.127 | 23.538
| 15.7222 | 298.115 | 295.718 | 75.031 | 26.452 | 43.052 | 23.533
| 15.7292 | 299.267 | 296.672 | 74.999 | 26.449 | 43.055 | 23.533
| 15.7361 | 298.223 | 296.836 | 74.937 | 26.446 | 43.036 | 23.535
| 15.7431 | 298.805 | 296.308 | 74.879 | 26.44 | 43.014 | 23.532
| 15.75 | 298.599 | 296.377 | 74.826 | 26.443 | 43.001 | 23.534
| 15.7569 | 298.422 | 296.478 | 74.793 | 26.437 | 42.993 | 23.532
| 15.7639 | 299.255 | 298.058 | 74.784 | 26.431 | 43.001 | 23.534
| 15.7708 | 299.39 | 297.215 | 74.792 | 26.428 | 43.029 | 23.53
| 15.7778 | 298.903 | 297.158 | 74.797 | 26.425 | 43.031 | 23.53
| 15.7847 | 299.088 | 297.543 | 74.788 | 26.427 | 43.024 | 23.528
| 15.7917 | 298.584 | 296.632 | 74.785 | 26.429 | 43.02 | 23.526
| 15.7986 | 299.716 | 297.25 | 74.793 | 26.424 | 43.028 | 23.527
| 15.8056 | 299.987 | 297.238 | 74.832 | 26.424 | 43.046 | 23.527
| 15.8125 | 300.203 | 298.15 | 74.879 | 26.422 | 43.076 | 23.523
| 15.8194 | 300.979 | 298.618 | 74.956 | 26.426 | 43.128 | 23.523
| 15.8264 | 301.096 | 299.158 | 75.018 | 26.431 | 43.15 | 23.527
| 15.8333 | 301.703 | 300.194 | 75.093 | 26.43 | 43.181 | 23.529
| 15.8403 | 302.491 | 300.097 | 75.219 | 26.434 | 43.246 | 23.532
| 15.8472 | 302.479 | 301.113 | 75.286 | 26.433 | 43.259 | 23.533
| 15.8542 | 299.552 | 298.417 | 75.337 | 26.442 | 43.271 | 23.535
| 15.8611 | 299.669 | 298.528 | 75.286 | 26.449 | 43.196 | 23.536
| 15.8681 | 298.955 | 297.648 | 75.266 | 26.449 | 43.169 | 23.539
| 15.875 | 298.588 | 297.088 | 75.169 | 26.457 | 43.106 | 23.543
| 15.8819 | 298.906 | 296.721 | 75.093 | 26.457 | 43.07 | 23.545
| 15.8889 | 299.411 | 298.484 | 75.078 | 26.457 | 43.084 | 23.551
| 15.8958 | 298.602 | 297.415 | 75.052 | 26.454 | 43.09 | 23.554
| 15.9028 | 299.295 | 297.405 | 75.02 | 26.457 | 43.077 | 23.555
| 15.9097 | 299.447 | 298.601 | 75.027 | 26.452 | 43.095 | 23.556
| 15.9167 | 301.338 | 298.73 | 75.081 | 26.454 | 43.153 | 23.557
| 15.9236 | 301.472 | 298.963 | 75.142 | 26.456 | 43.189 | 23.556
| 15.9306 | 302.588 | 301.062 | 75.239 | 26.46 | 43.244 | 23.559
| 15.9375 | 303.277 | 301.414 | 75.375 | 26.463 | 43.321 | 23.56
| 15.9444 | 300.291 | 298.615 | 75.333 | 26.467 | 43.259 | 23.563
| 15.9514 | 297.698 | 296.265 | 75.196 | 26.475 | 43.134 | 23.567
| 15.9583 | 298.878 | 297.476 | 75.11 | 26.476 | 43.089 | 23.576
| 15.9653 | 299.653 | 297.529 | 75.088 | 26.48 | 43.107 | 23.578
| 15.9722 | 299.874 | 298.571 | 75.076 | 26.479 | 43.123 | 23.583
| 15.9792 | 300.834 | 298.296 | 75.1 | 26.475 | 43.152 | 23.584
| 15.9861 | 301.266 | 300.019 | 75.149 | 26.47 | 43.187 | 23.577
| 15.9931 | 301.325 | 300.149 | 75.226 | 26.481 | 43.241 | 23.586
| 16 | 302.188 | 300.254 | 75.3 | 26.483 | 43.289 | 23.591
| 16.0069 | 302.823 | 300.764 | 75.398 | 26.481 | 43.324 | 23.587
| 16.0139 | 303.039 | 301.666 | 75.507 | 26.483 | 43.376 | 23.592
| 16.0208 | 303.26 | 301.02 | 75.608 | 26.486 | 43.408 | 23.593
| 16.0278 | 299.328 | 297.926 | 75.689 | 26.492 | 43.442 | 23.598
| 16.0347 | 297.448 | 295.252 | 75.461 | 26.5 | 43.242 | 23.605
| 16.0417 | 300.799 | 298.323 | 75.425 | 26.499 | 43.221 | 23.609
| 16.0486 | 301.459 | 299.067 | 75.45 | 26.504 | 43.274 | 23.612
| 16.0556 | 301.684 | 298.636 | 75.459 | 26.509 | 43.3 | 23.619
| 16.0625 | 302.042 | 299.238 | 75.483 | 26.503 | 43.308 | 23.621
| 16.0694 | 301.913 | 299.255 | 75.505 | 26.506 | 43.32 | 23.622
| 16.0764 | 301.437 | 299.18 | 75.514 | 26.515 | 43.323 | 23.629
| 16.0833 | 301.697 | 299.484 | 75.532 | 26.517 | 43.336 | 23.629
| 16.0903 | 302.299 | 300.131 | 75.552 | 26.515 | 43.345 | 23.633
| 16.0972 | 302.284 | 300.906 | 75.604 | 26.519 | 43.376 | 23.636
| 16.1042 | 302.431 | 301.065 | 75.663 | 26.525 | 43.409 | 23.64
| 16.1111 | 303.388 | 300.659 | 75.725 | 26.533 | 43.45 | 23.646
| 16.1181 | 302.824 | 300.314 | 75.766 | 26.537 | 43.449 | 23.645
| 16.125 | 301.972 | 300.789 | 75.796 | 26.542 | 43.458 | 23.654
| 16.1319 | 302.757 | 299.858 | 75.831 | 26.55 | 43.467 | 23.656
| 16.1389 | 302.418 | 301.016 | 75.856 | 26.553 | 43.475 | 23.664
| 16.1458 | 302.975 | 300.301 | 75.892 | 26.563 | 43.492 | 23.668
| 16.1528 | 302.984 | 300.357 | 75.916 | 26.567 | 43.504 | 23.676
| 16.1597 | 302.447 | 301.06 | 75.939 | 26.571 | 43.51 | 23.68
| 16.1667 | 299.198 | 296.387 | 75.784 | 26.577 | 43.387 | 23.681
| 16.1736 | 299.308 | 297.04 | 75.651 | 26.578 | 43.311 | 23.691
| 16.1806 | 297.856 | 296.193 | 75.516 | 26.572 | 43.247 | 23.695
| 16.1875 | 298.541 | 295.751 | 75.382 | 26.569 | 43.193 | 23.696
| 16.1944 | 298.441 | 296.528 | 75.287 | 26.574 | 43.178 | 23.699
| 16.2014 | 297.913 | 295.477 | 75.165 | 26.568 | 43.138 | 23.701
| 16.2083 | 298.004 | 295.831 | 75.079 | 26.564 | 43.125 | 23.705
| 16.2153 | 296.995 | 294.822 | 74.96 | 26.568 | 43.086 | 23.703
| 16.2222 | 298.66 | 297.369 | 74.878 | 26.563 | 43.069 | 23.704
| 16.2292 | 297.763 | 296.546 | 74.857 | 26.553 | 43.101 | 23.706
| 16.2361 | 298.408 | 295.944 | 74.802 | 26.554 | 43.089 | 23.704
| 16.2431 | 298.583 | 295.917 | 74.744 | 26.548 | 43.056 | 23.703
| 16.25 | 297.315 | 295.992 | 74.685 | 26.547 | 43.045 | 23.703
| 16.2569 | 297.769 | 295.313 | 74.627 | 26.54 | 43.018 | 23.705
| 16.2639 | 299.275 | 298.004 | 74.645 | 26.537 | 43.05 | 23.711
| 16.2708 | 300.686 | 299.052 | 74.698 | 26.538 | 43.112 | 23.705
| 16.2778 | 300.741 | 299.48 | 74.8 | 26.533 | 43.182 | 23.706
| 16.2847 | 299.218 | 297.784 | 74.82 | 26.537 | 43.175 | 23.706
| 16.2917 | 298.399 | 295.659 | 74.781 | 26.535 | 43.122 | 23.707
| 16.2986 | 298.509 | 295.693 | 74.747 | 26.538 | 43.089 | 23.712
| 16.3056 | 296.939 | 294.834 | 74.654 | 26.536 | 43.029 | 23.71
| 16.3125 | 298.844 | 296.804 | 74.69 | 26.541 | 43.067 | 23.711
| 16.3194 | 300.955 | 298.202 | 74.812 | 26.536 | 43.162 | 23.715
| 16.3264 | 299.855 | 298.756 | 74.869 | 26.536 | 43.19 | 23.718
| 16.3333 | 299.442 | 297.701 | 74.894 | 26.544 | 43.182 | 23.717
| 16.3403 | 300.169 | 298.774 | 74.974 | 26.544 | 43.227 | 23.718
| 16.3472 | 300.109 | 299.021 | 75.004 | 26.545 | 43.232 | 23.718
| 16.3542 | 301.822 | 300.658 | 75.087 | 26.554 | 43.275 | 23.726
| 16.3611 | 301.88 | 300.434 | 75.167 | 26.555 | 43.308 | 23.725
| 16.3681 | 301.48 | 298.985 | 75.234 | 26.559 | 43.335 | 23.727
| 16.375 | 301.173 | 299.826 | 75.304 | 26.566 | 43.352 | 23.735
| 16.3819 | 301.958 | 300.168 | 75.351 | 26.573 | 43.361 | 23.738
| 16.3889 | 302.95 | 300.236 | 75.429 | 26.582 | 43.386 | 23.74
| 16.3958 | 303.862 | 301.065 | 75.55 | 26.582 | 43.454 | 23.747
| 16.4028 | 302.218 | 300.045 | 75.622 | 26.594 | 43.475 | 23.753
| 16.4097 | 301.384 | 300.328 | 75.634 | 26.599 | 43.457 | 23.758
| 16.4167 | 301.642 | 299.666 | 75.649 | 26.608 | 43.447 | 23.762
| 16.4236 | 301.37 | 298.967 | 75.644 | 26.609 | 43.427 | 23.773
| 16.4306 | 301.53 | 299.067 | 75.628 | 26.616 | 43.41 | 23.775
| 16.4375 | 300.962 | 299.419 | 75.626 | 26.623 | 43.407 | 23.779
| 16.5 | 302.025 | 299.358 | 75.643 | 26.653 | 43.463 | 23.824
| 16.5069 | 302.545 | 300.009 | 75.671 | 26.656 | 43.48 | 23.821
| 16.5139 | 302.649 | 299.961 | 75.728 | 26.661 | 43.514 | 23.829
| 16.5208 | 300.23 | 297.835 | 75.744 | 26.672 | 43.517 | 23.832
| 16.5278 | 299.191 | 296.548 | 75.607 | 26.671 | 43.408 | 23.842
| 16.5347 | 302.21 | 300.002 | 75.671 | 26.679 | 43.459 | 23.839
| 16.5417 | 303.187 | 300.571 | 75.75 | 26.676 | 43.526 | 23.849
| 16.5486 | 303.078 | 301.583 | 75.819 | 26.687 | 43.572 | 23.853
| 16.5556 | 303.385 | 301.627 | 75.894 | 26.691 | 43.606 | 23.857
| 16.5625 | 303.593 | 301.316 | 75.954 | 26.698 | 43.629 | 23.861
| 16.5694 | 303.528 | 302.195 | 76.045 | 26.705 | 43.671 | 23.866
| 16.5764 | 303.844 | 302.366 | 76.143 | 26.712 | 43.712 | 23.873
| 16.5833 | 304.553 | 303.056 | 76.23 | 26.723 | 43.746 | 23.878
| 16.5903 | 300.722 | 298.446 | 76.219 | 26.728 | 43.712 | 23.883
| 16.5972 | 301.733 | 300.701 | 76.165 | 26.733 | 43.646 | 23.889
| 16.6042 | 300.773 | 299.432 | 76.109 | 26.741 | 43.612 | 23.897
| 16.6111 | 301.992 | 299.77 | 76.082 | 26.741 | 43.601 | 23.902
| 16.6181 | 299.91 | 297.889 | 75.987 | 26.748 | 43.56 | 23.904
| 16.625 | 299.368 | 296.353 | 75.867 | 26.75 | 43.486 | 23.913
| 16.6319 | 299.379 | 297.135 | 75.758 | 26.751 | 43.445 | 23.917
| 16.6389 | 299.129 | 297.755 | 75.669 | 26.748 | 43.42 | 23.921
| 16.6458 | 299.674 | 297.652 | 75.626 | 26.747 | 43.433 | 23.921
| 16.6528 | 299.445 | 296.449 | 75.565 | 26.741 | 43.42 | 23.92
| 16.6597 | 299.177 | 296.433 | 75.512 | 26.745 | 43.405 | 23.925
| 16.6667 | 298.732 | 296.199 | 75.422 | 26.745 | 43.366 | 23.922
| 16.6736 | 298.842 | 297.149 | 75.371 | 26.744 | 43.358 | 23.928
| 16.6806 | 298.938 | 296.679 | 75.32 | 26.741 | 43.349 | 23.927
| 16.6875 | 298.421 | 297.025 | 75.24 | 26.737 | 43.316 | 23.929
| 16.6944 | 297.825 | 296.494 | 75.175 | 26.736 | 43.297 | 23.929
| 16.7014 | 297.049 | 295.538 | 75.082 | 26.731 | 43.259 | 23.933
| 16.7083 | 300.484 | 298.792 | 75.21 | 26.734 | 43.377 | 23.936
| 16.7153 | 300.567 | 299.068 | 75.265 | 26.731 | 43.421 | 23.934
| 16.7222 | 297.909 | 296.296 | 75.202 | 26.729 | 43.368 | 23.941
| 16.7292 | 299.56 | 296.873 | 75.177 | 26.735 | 43.353 | 23.937
| 16.7361 | 299.018 | 297.515 | 75.184 | 26.734 | 43.359 | 23.938
| 16.7431 | 299.534 | 296.929 | 75.163 | 26.736 | 43.358 | 23.939
| 16.75 | 299.213 | 297.71 | 75.153 | 26.734 | 43.355 | 23.942
| 16.7569 | 300.355 | 297.599 | 75.172 | 26.735 | 43.364 | 23.943
| 16.7639 | 300.32 | 297.722 | 75.188 | 26.736 | 43.38 | 23.946
| 16.7708 | 300.402 | 297.774 | 75.229 | 26.74 | 43.407 | 23.95
| 16.7778 | 300.857 | 298.196 | 75.271 | 26.743 | 43.434 | 23.947
| 16.7847 | 300.389 | 299.055 | 75.31 | 26.747 | 43.448 | 23.949
| 16.7917 | 301.202 | 299.227 | 75.361 | 26.749 | 43.469 | 23.958
| 16.7986 | 301.482 | 299.946 | 75.416 | 26.752 | 43.493 | 23.958
| 16.8056 | 301.382 | 300.098 | 75.477 | 26.753 | 43.522 | 23.961
| 16.8125 | 302.144 | 300.693 | 75.553 | 26.762 | 43.549 | 23.96
| 16.8194 | 302.944 | 301.65 | 75.673 | 26.768 | 43.616 | 23.973
| 16.8264 | 303.517 | 300.764 | 75.775 | 26.772 | 43.661 | 23.975
| 16.8333 | 303.472 | 300.789 | 75.849 | 26.782 | 43.68 | 23.98
| 16.8403 | 303.809 | 301.826 | 75.96 | 26.787 | 43.723 | 23.982
| 16.8472 | 301.284 | 298.64 | 76.023 | 26.796 | 43.74 | 23.985
| 16.8542 | 300.858 | 299.333 | 75.965 | 26.807 | 43.664 | 23.993
| 16.8611 | 301.481 | 299.695 | 75.958 | 26.814 | 43.649 | 24.002
| 16.8681 | 302.303 | 299.605 | 75.962 | 26.822 | 43.655 | 24.012
| 16.875 | 302.274 | 300.502 | 75.993 | 26.827 | 43.678 | 24.013
| 16.8819 | 302.386 | 300.254 | 76.012 | 26.827 | 43.687 | 24.021
| 16.8889 | 302.405 | 301.358 | 76.042 | 26.833 | 43.707 | 24.025
| 16.8958 | 301.305 | 299.606 | 76.033 | 26.844 | 43.695 | 24.032
| 16.9028 | 301.781 | 299.956 | 76.032 | 26.844 | 43.691 | 24.031
| 16.9097 | 302.692 | 300.215 | 76.046 | 26.849 | 43.704 | 24.039
| 16.9167 | 302.565 | 300.847 | 76.088 | 26.851 | 43.736 | 24.042
| 16.9236 | 303.363 | 301.053 | 76.144 | 26.859 | 43.783 | 24.051
| 16.9306 | 304.381 | 302.881 | 76.24 | 26.862 | 43.838 | 24.053
| 16.9375 | 300.927 | 298.965 | 76.199 | 26.866 | 43.787 | 24.057
| 16.9444 | 300.136 | 298.194 | 76.081 | 26.875 | 43.686 | 24.066
| 16.9514 | 301.686 | 300.135 | 76.041 | 26.878 | 43.671 | 24.074
| 16.9583 | 303.047 | 300.371 | 76.076 | 26.879 | 43.74 | 24.077
| 16.9653 | 302.182 | 301.074 | 76.129 | 26.889 | 43.788 | 24.076
| 16.9722 | 303.827 | 301.387 | 76.199 | 26.892 | 43.832 | 24.085
| 16.9792 | 304.744 | 302.866 | 76.313 | 26.903 | 43.904 | 24.09
| 16.9861 | 301.737 | 299.065 | 76.21 | 26.907 | 43.804 | 24.097
| 16.9931 | 300.597 | 299.516 | 76.159 | 26.908 | 43.762 | 24.098
| 17 | 301.606 | 299.24 | 76.129 | 26.908 | 43.748 | 24.105
| 17.0069 | 301.713 | 299.512 | 76.109 | 26.917 | 43.752 | 24.11
| 17.0139 | 301.877 | 300.091 | 76.124 | 26.916 | 43.782 | 24.116
| 17.0208 | 302.036 | 299.358 | 76.143 | 26.917 | 43.804 | 24.119
| 17.0278 | 301.967 | 300.734 | 76.165 | 26.925 | 43.828 | 24.123
| 17.0347 | 302.619 | 300.816 | 76.195 | 26.927 | 43.85 | 24.125
| 17.0417 | 298.411 | 297.2 | 76.06 | 26.926 | 43.744 | 24.131
| 17.0486 | 299.222 | 297.727 | 75.958 | 26.935 | 43.678 | 24.134
| 17.0556 | 299.25 | 298 | 75.877 | 26.932 | 43.645 | 24.142
| 17.0625 | 300.339 | 297.611 | 75.812 | 26.931 | 43.637 | 24.141
| 17.0694 | 299.352 | 298.221 | 75.759 | 26.934 | 43.634 | 24.147
| 17.0764 | 299.815 | 298.544 | 75.729 | 26.927 | 43.633 | 24.15
| 17.0833 | 300.731 | 298.155 | 75.714 | 26.93 | 43.653 | 24.148
| 17.0903 | 300.305 | 297.871 | 75.699 | 26.931 | 43.658 | 24.153
| 17.0972 | 300.244 | 298.738 | 75.688 | 26.929 | 43.666 | 24.153
| 17.1042 | 300.39 | 298.969 | 75.703 | 26.93 | 43.684 | 24.158
| 17.1111 | 300.71 | 298.897 | 75.718 | 26.931 | 43.697 | 24.16
| 17.1181 | 300.648 | 299.21 | 75.725 | 26.937 | 43.703 | 24.16
| 17.125 | 300.306 | 298.999 | 75.718 | 26.934 | 43.703 | 24.16
| 17.1319 | 299.934 | 298.868 | 75.721 | 26.938 | 43.703 | 24.165
| 17.1389 | 301.056 | 298.196 | 75.72 | 26.941 | 43.705 | 24.167
| 17.1458 | 300.563 | 298.226 | 75.702 | 26.94 | 43.693 | 24.172
| 17.1528 | 300.805 | 298.214 | 75.713 | 26.947 | 43.704 | 24.173
| 17.1597 | 300.534 | 299.315 | 75.722 | 26.948 | 43.711 | 24.173
| 17.1667 | 301.271 | 298.356 | 75.728 | 26.95 | 43.716 | 24.179
| 17.1736 | 301.125 | 298.133 | 75.732 | 26.95 | 43.724 | 24.179
| 17.1806 | 300.887 | 298.279 | 75.721 | 26.951 | 43.711 | 24.184
| 17.1875 | 300.518 | 299.158 | 75.737 | 26.958 | 43.723 | 24.185
| 17.1944 | 301.041 | 299.063 | 75.752 | 26.958 | 43.739 | 24.185
| 17.2014 | 300.979 | 298.335 | 75.761 | 26.959 | 43.742 | 24.187
| 17.2083 | 301.095 | 298.451 | 75.776 | 26.965 | 43.751 | 24.191
| 17.2153 | 300.213 | 298.973 | 75.765 | 26.967 | 43.743 | 24.194
| 17.2222 | 300.499 | 299.179 | 75.751 | 26.964 | 43.731 | 24.201
| 17.2292 | 300.278 | 299.095 | 75.768 | 26.967 | 43.754 | 24.199
| 17.2361 | 301.341 | 298.793 | 75.779 | 26.97 | 43.759 | 24.202
| 17.2431 | 301.873 | 299.159 | 75.785 | 26.974 | 43.759 | 24.208
| 17.25 | 299.755 | 298.06 | 75.747 | 26.974 | 43.739 | 24.209
| 17.2569 | 299.869 | 298.395 | 75.705 | 26.977 | 43.711 | 24.215
| 17.2639 | 298.32 | 296.63 | 75.645 | 26.982 | 43.687 | 24.213
| 17.2708 | 300.055 | 297.393 | 75.617 | 26.981 | 43.677 | 24.218
| 17.2778 | 299.326 | 297.794 | 75.592 | 26.982 | 43.677 | 24.219
| 17.2847 | 299.485 | 298.334 | 75.568 | 26.981 | 43.675 | 24.216
| 17.2917 | 299.872 | 297.732 | 75.565 | 26.983 | 43.684 | 24.218
| 17.2986 | 299.334 | 297.355 | 75.531 | 26.983 | 43.672 | 24.221
| 17.3056 | 298.064 | 296.741 | 75.472 | 26.985 | 43.632 | 24.224
| 17.3125 | 298.278 | 296.447 | 75.402 | 26.983 | 43.601 | 24.226
| 17.3194 | 298.003 | 296.562 | 75.343 | 26.984 | 43.585 | 24.227
| 17.3264 | 297.688 | 296.116 | 75.274 | 26.977 | 43.557 | 24.225
| 17.3333 | 300.575 | 297.828 | 75.295 | 26.978 | 43.589 | 24.224
| 17.3403 | 300.386 | 298.704 | 75.354 | 26.977 | 43.655 | 24.225
| 17.3472 | 299.915 | 297.595 | 75.382 | 26.978 | 43.669 | 24.229
| 17.3542 | 301.512 | 299.188 | 75.459 | 26.983 | 43.72 | 24.225
| 17.3611 | 301.177 | 298.641 | 75.509 | 26.982 | 43.738 | 24.231
| 17.3681 | 300.356 | 299.184 | 75.548 | 26.987 | 43.748 | 24.228
| 17.375 | 300.353 | 297.598 | 75.561 | 26.99 | 43.736 | 24.227
| 17.3819 | 300.43 | 297.676 | 75.553 | 26.995 | 43.717 | 24.227
| 17.3889 | 298.482 | 297.079 | 75.523 | 26.994 | 43.686 | 24.232
| 17.3958 | 300.503 | 299.296 | 75.553 | 27 | 43.714 | 24.228
| 17.4028 | 300.858 | 298.06 | 75.589 | 26.998 | 43.747 | 24.238
| 17.4097 | 300.619 | 297.85 | 75.596 | 27.003 | 43.74 | 24.235
| 17.4167 | 300.024 | 297.621 | 75.6 | 27.007 | 43.737 | 24.236
| 17.4236 | 299.612 | 298.424 | 75.58 | 27.009 | 43.721 | 24.241
| 17.4306 | 300.311 | 298.622 | 75.59 | 27.012 | 43.735 | 24.241
| 17.4375 | 300.007 | 298.477 | 75.604 | 27.01 | 43.745 | 24.239
| 17.4444 | 300.313 | 298.412 | 75.608 | 27.014 | 43.743 | 24.241
| 17.4514 | 299.654 | 297.838 | 75.59 | 27.017 | 43.733 | 24.243
| 17.4583 | 299.012 | 297.657 | 75.566 | 27.019 | 43.712 | 24.248
| 17.4653 | 298.951 | 297.711 | 75.543 | 27.021 | 43.705 | 24.248
| 17.4722 | 299.456 | 297.252 | 75.515 | 27.017 | 43.694 | 24.249
| 17.4792 | 299.352 | 296.563 | 75.462 | 27.017 | 43.666 | 24.25
| 17.4861 | 298.516 | 297.094 | 75.429 | 27.022 | 43.654 | 24.246
| 17.4931 | 299.006 | 296.813 | 75.399 | 27.022 | 43.648 | 24.246
| 17.5 | 300.181 | 297.502 | 75.402 | 27.019 | 43.669 | 24.247
| 17.5069 | 299.297 | 297.382 | 75.392 | 27.019 | 43.671 | 24.249
| 17.5139 | 299.658 | 298.214 | 75.406 | 27.02 | 43.683 | 24.245
| 17.5208 | 300.396 | 299.201 | 75.428 | 27.024 | 43.702 | 24.246
| 17.5278 | 300.419 | 298.153 | 75.456 | 27.027 | 43.726 | 24.248
| 17.5347 | 300.298 | 298.495 | 75.484 | 27.025 | 43.735 | 24.248
| 17.5417 | 300.981 | 298.974 | 75.513 | 27.029 | 43.756 | 24.247
| 17.5486 | 300.742 | 298.52 | 75.558 | 27.027 | 43.771 | 24.248
| 17.5556 | 300.268 | 298.666 | 75.591 | 27.032 | 43.786 | 24.253
| 17.5625 | 300.904 | 299.413 | 75.644 | 27.036 | 43.808 | 24.251
| 17.5694 | 301.597 | 299.649 | 75.699 | 27.037 | 43.834 | 24.252
| 17.5764 | 301.339 | 300.197 | 75.766 | 27.04 | 43.861 | 24.251
| 17.5833 | 301.964 | 299.437 | 75.835 | 27.046 | 43.893 | 24.253
| 17.5903 | 302.698 | 300.047 | 75.905 | 27.048 | 43.929 | 24.256
| 17.5972 | 303.853 | 301.641 | 75.994 | 27.054 | 43.965 | 24.255
| 17.6042 | 304.022 | 301.898 | 76.132 | 27.061 | 44.043 | 24.258
| 17.6111 | 300.805 | 298.757 | 76.24 | 27.071 | 44.087 | 24.264
| 17.6181 | 300.779 | 298.564 | 76.14 | 27.081 | 43.973 | 24.266
| 17.625 | 301.788 | 299.373 | 76.134 | 27.08 | 43.957 | 24.266
| 17.6319 | 302.086 | 299.259 | 76.153 | 27.086 | 43.969 | 24.274
| 17.6389 | 301.619 | 298.846 | 76.151 | 27.09 | 43.964 | 24.276
| 17.6458 | 301.289 | 299.639 | 76.155 | 27.092 | 43.972 | 24.279
| 17.6528 | 302.595 | 300.559 | 76.185 | 27.097 | 43.994 | 24.282
| 17.6597 | 302.597 | 299.594 | 76.207 | 27.102 | 44.007 | 24.284
| 17.6667 | 299.188 | 297.832 | 76.092 | 27.104 | 43.918 | 24.287
| 17.6736 | 299.973 | 297.269 | 76.004 | 27.108 | 43.864 | 24.291
| 17.6806 | 298.922 | 297.421 | 75.938 | 27.107 | 43.849 | 24.29
| 17.6875 | 299.48 | 297.842 | 75.865 | 27.103 | 43.824 | 24.291
| 17.6944 | 299.656 | 297.115 | 75.819 | 27.106 | 43.823 | 24.295
| 17.7014 | 299.137 | 297.816 | 75.763 | 27.105 | 43.806 | 24.293
| 17.7083 | 298.39 | 297.266 | 75.694 | 27.107 | 43.779 | 24.297
| 17.7153 | 298.27 | 295.632 | 75.586 | 27.103 | 43.733 | 24.294
| 17.7222 | 300.326 | 297.546 | 75.582 | 27.098 | 43.754 | 24.293
| 17.7292 | 298.255 | 295.63 | 75.542 | 27.098 | 43.759 | 24.297
| 17.7361 | 298.168 | 296.808 | 75.476 | 27.098 | 43.726 | 24.295
| 17.7431 | 297.432 | 296.139 | 75.395 | 27.09 | 43.69 | 24.293
| 17.75 | 297.603 | 295.142 | 75.301 | 27.088 | 43.645 | 24.293
| 17.7569 | 302.001 | 299.569 | 75.488 | 27.087 | 43.81 | 24.293
| 17.7639 | 301.172 | 299.74 | 75.568 | 27.089 | 43.862 | 24.291
| 17.7708 | 302.851 | 301.344 | 75.643 | 27.088 | 43.889 | 24.292
| 17.7778 | 303.238 | 301.767 | 75.812 | 27.092 | 43.987 | 24.291
| 17.7847 | 303.948 | 301.43 | 75.937 | 27.098 | 44.036 | 24.293
| 17.7917 | 303.749 | 302.127 | 76.059 | 27.1 | 44.083 | 24.294
| 17.7986 | 300.238 | 298.665 | 76.16 | 27.113 | 44.107 | 24.303
| 17.8056 | 301.148 | 299.512 | 76.072 | 27.119 | 43.993 | 24.3
| 17.8125 | 300.998 | 298.386 | 76.039 | 27.121 | 43.961 | 24.304
| 17.8194 | 300.759 | 299.388 | 76.019 | 27.125 | 43.952 | 24.307
| 17.8264 | 302.055 | 299.312 | 76.043 | 27.126 | 43.976 | 24.314
| 17.8333 | 302.137 | 299.673 | 76.074 | 27.128 | 44.001 | 24.316
| 17.8403 | 303.126 | 300.482 | 76.14 | 27.132 | 44.046 | 24.316
| 17.8472 | 302.247 | 300.042 | 76.208 | 27.138 | 44.089 | 24.323
| 17.8542 | 301.542 | 299.185 | 76.169 | 27.141 | 44.038 | 24.326
| 17.8611 | 301.437 | 299.883 | 76.174 | 27.15 | 44.042 | 24.33
| 17.8681 | 302.637 | 299.981 | 76.199 | 27.152 | 44.056 | 24.336
| 17.875 | 303.099 | 300.226 | 76.266 | 27.154 | 44.099 | 24.339
| 17.8819 | 299.986 | 297.458 | 76.228 | 27.162 | 44.069 | 24.341
| 17.8889 | 301.37 | 299.322 | 76.135 | 27.162 | 43.987 | 24.342
| 17.8958 | 300.808 | 298.732 | 76.11 | 27.165 | 43.994 | 24.348
| 17.9028 | 301.513 | 298.788 | 76.114 | 27.166 | 44.006 | 24.35
| 17.9097 | 301.428 | 299.971 | 76.102 | 27.167 | 44.012 | 24.355
| 17.9167 | 301.651 | 300.138 | 76.12 | 27.172 | 44.036 | 24.355
| 17.9236 | 301.321 | 299.857 | 76.141 | 27.176 | 44.058 | 24.356
| 17.9306 | 302.132 | 299.96 | 76.159 | 27.176 | 44.067 | 24.361
| 17.9375 | 301.81 | 299.993 | 76.181 | 27.178 | 44.082 | 24.365
| 17.9444 | 302.607 | 300.631 | 76.221 | 27.183 | 44.107 | 24.366
| 17.9514 | 302.912 | 301.182 | 76.268 | 27.183 | 44.134 | 24.371
| 17.9583 | 303.876 | 301.798 | 76.364 | 27.188 | 44.19 | 24.369
| 17.9653 | 300.632 | 298.611 | 76.275 | 27.194 | 44.112 | 24.374
| 17.9722 | 302.121 | 299.319 | 76.238 | 27.199 | 44.078 | 24.378
| 17.9792 | 299.237 | 296.517 | 76.236 | 27.2 | 44.095 | 24.382
| 17.9861 | 300.048 | 296.986 | 76.099 | 27.198 | 43.995 | 24.38
| 17.9931 | 300.245 | 297.26 | 76.02 | 27.198 | 43.961 | 24.386
| 18 | 300.512 | 297.893 | 75.997 | 27.2 | 43.978 | 24.386
| 18.0069 | 301.165 | 298.019 | 75.975 | 27.199 | 43.989 | 24.389
| 18.0139 | 302.18 | 300.081 | 76.013 | 27.198 | 44.032 | 24.387
| 18.0208 | 302.539 | 299.647 | 76.08 | 27.195 | 44.085 | 24.388
| 18.0278 | 300.17 | 297.07 | 76.081 | 27.199 | 44.084 | 24.391
| 18.0347 | 299.521 | 297.78 | 76.008 | 27.202 | 44.015 | 24.391
| 18.0417 | 299.456 | 296.386 | 75.909 | 27.204 | 43.952 | 24.392
| 18.0486 | 300.093 | 297.043 | 75.854 | 27.203 | 43.943 | 24.392
| 18.0556 | 299.567 | 297.746 | 75.822 | 27.198 | 43.934 | 24.39
| 18.0625 | 299.761 | 297.321 | 75.791 | 27.194 | 43.934 | 24.392
| 18.0694 | 300.254 | 297.443 | 75.78 | 27.194 | 43.943 | 24.394
| 18.0764 | 300.617 | 297.469 | 75.769 | 27.195 | 43.948 | 24.389
| 18.0833 | 300.048 | 298.037 | 75.768 | 27.199 | 43.951 | 24.396
| 18.0903 | 300.279 | 298.383 | 75.761 | 27.193 | 43.958 | 24.389
| 18.0972 | 300.704 | 298.126 | 75.752 | 27.194 | 43.951 | 24.392
| 18.1042 | 300.516 | 298.231 | 75.775 | 27.197 | 43.975 | 24.392
| 18.1111 | 301.249 | 298.326 | 75.8 | 27.195 | 43.992 | 24.389
| 18.1181 | 300.96 | 298.358 | 75.837 | 27.196 | 44.01 | 24.389
| 18.125 | 301.043 | 298.705 | 75.863 | 27.195 | 44.024 | 24.391
| 18.1319 | 301.291 | 298.593 | 75.887 | 27.204 | 44.031 | 24.39
| 18.1389 | 301.955 | 298.792 | 75.925 | 27.199 | 44.05 | 24.39
| 18.1458 | 300.904 | 299.029 | 75.952 | 27.205 | 44.061 | 24.391
| 18.1528 | 301.099 | 299.165 | 75.989 | 27.203 | 44.079 | 24.391
| 18.1597 | 301.896 | 298.905 | 76.006 | 27.205 | 44.081 | 24.39
| 18.1667 | 301.226 | 298.709 | 76.028 | 27.208 | 44.081 | 24.389
| 18.1736 | 301.451 | 299.096 | 76.053 | 27.212 | 44.087 | 24.39
| 18.1806 | 302.241 | 298.999 | 76.079 | 27.218 | 44.103 | 24.396
| 18.1875 | 301.737 | 299.944 | 76.135 | 27.219 | 44.136 | 24.39
| 18.1944 | 302.167 | 300.162 | 76.177 | 27.225 | 44.152 | 24.398
| 18.2014 | 302.619 | 299.56 | 76.215 | 27.226 | 44.162 | 24.396
| 18.2083 | 302.48 | 299.21 | 76.251 | 27.23 | 44.178 | 24.393
| 18.2153 | 302.581 | 299.676 | 76.264 | 27.232 | 44.179 | 24.4
| 18.2222 | 302.382 | 299.665 | 76.298 | 27.237 | 44.197 | 24.396
| 18.2292 | 301.998 | 299.743 | 76.318 | 27.237 | 44.199 | 24.396
| 18.2361 | 301.819 | 299.638 | 76.324 | 27.24 | 44.197 | 24.399
| 18.2431 | 301.98 | 299.074 | 76.33 | 27.245 | 44.197 | 24.4
| 18.25 | 302.315 | 299.432 | 76.361 | 27.245 | 44.207 | 24.4
| 18.2569 | 301.894 | 300.162 | 76.386 | 27.246 | 44.236 | 24.402
| 18.2639 | 300.855 | 298.118 | 76.376 | 27.252 | 44.22 | 24.403
| 18.2708 | 301.527 | 298.505 | 76.334 | 27.256 | 44.185 | 24.401
| 18.2778 | 301.032 | 298.951 | 76.324 | 27.258 | 44.186 | 24.404
| 18.2847 | 301.404 | 299.431 | 76.319 | 27.258 | 44.179 | 24.399
| 18.2917 | 301.339 | 299.171 | 76.314 | 27.258 | 44.181 | 24.401
| 18.2986 | 301.743 | 298.316 | 76.303 | 27.264 | 44.174 | 24.4
| 18.3056 | 299.659 | 297.974 | 76.248 | 27.264 | 44.147 | 24.402
| 18.3125 | 300.823 | 298.291 | 76.202 | 27.264 | 44.128 | 24.399
| 18.3194 | 300.881 | 297.654 | 76.165 | 27.265 | 44.114 | 24.4
| 18.3264 | 301.104 | 297.809 | 76.146 | 27.264 | 44.116 | 24.392
| 18.3333 | 300.685 | 297.826 | 76.121 | 27.264 | 44.114 | 24.395
| 18.3403 | 300.84 | 298.399 | 76.109 | 27.259 | 44.106 | 24.393
| 18.3472 | 302.031 | 299.723 | 76.148 | 27.258 | 44.154 | 24.387
| 18.3542 | 302.851 | 299.911 | 76.223 | 27.261 | 44.204 | 24.389
| 18.3611 | 302.51 | 300.53 | 76.288 | 27.263 | 44.234 | 24.386
| 18.3681 | 302.884 | 300.395 | 76.349 | 27.266 | 44.266 | 24.379
| 18.375 | 303.02 | 299.539 | 76.398 | 27.273 | 44.275 | 24.381
| 18.3819 | 302.91 | 300.678 | 76.446 | 27.271 | 44.289 | 24.38
| 18.3889 | 302.824 | 299.513 | 76.475 | 27.272 | 44.29 | 24.377
| 18.3958 | 301.951 | 299.844 | 76.498 | 27.275 | 44.292 | 24.375
| 18.4028 | 302.521 | 299.171 | 76.5 | 27.281 | 44.279 | 24.375
| 18.4097 | 302.033 | 299.214 | 76.49 | 27.282 | 44.262 | 24.374
| 18.4167 | 301.941 | 298.556 | 76.464 | 27.282 | 44.241 | 24.374
| 18.4236 | 300.803 | 298.895 | 76.432 | 27.285 | 44.224 | 24.37
| 18.4306 | 301.337 | 298.151 | 76.386 | 27.284 | 44.197 | 24.37
| 18.4375 | 300.454 | 297.565 | 76.324 | 27.286 | 44.164 | 24.369
| 18.4444 | 300.518 | 298.742 | 76.285 | 27.285 | 44.152 | 24.365
| 18.4514 | 299.486 | 297.709 | 76.213 | 27.284 | 44.121 | 24.362
| 18.4583 | 300.26 | 297.605 | 76.159 | 27.28 | 44.105 | 24.358
| 18.4653 | 299.897 | 297.808 | 76.108 | 27.28 | 44.092 | 24.355
| 18.4722 | 298.963 | 297.234 | 76.041 | 27.279 | 44.06 | 24.353
| 18.4792 | 299.191 | 296.404 | 75.966 | 27.273 | 44.033 | 24.346
| 18.4861 | 298.584 | 296.619 | 75.889 | 27.268 | 43.996 | 24.346
| 18.4931 | 298.961 | 296.591 | 75.838 | 27.264 | 43.984 | 24.339
| 18.5 | 299.649 | 296.678 | 75.799 | 27.261 | 43.983 | 24.334
| 18.5069 | 299.492 | 296.147 | 75.769 | 27.258 | 43.979 | 24.329
| 18.5139 | 299.4 | 296.329 | 75.734 | 27.254 | 43.962 | 24.321
| 18.5208 | 298.67 | 296.698 | 75.687 | 27.249 | 43.946 | 24.318
| 18.5278 | 298.809 | 296.075 | 75.646 | 27.243 | 43.927 | 24.311
| 18.5347 | 298.593 | 295.668 | 75.589 | 27.235 | 43.894 | 24.302
| 18.5417 | 298.698 | 296.082 | 75.553 | 27.234 | 43.883 | 24.298
| 18.5486 | 298.954 | 295.776 | 75.514 | 27.23 | 43.876 | 24.295
| 18.5556 | 300.056 | 297.013 | 75.5 | 27.226 | 43.875 | 24.287
| 18.5625 | 300.23 | 297.674 | 75.55 | 27.218 | 43.925 | 24.282
| 18.5694 | 300.298 | 297.643 | 75.59 | 27.217 | 43.951 | 24.273
| 18.5764 | 299.865 | 298.237 | 75.612 | 27.214 | 43.956 | 24.268
| 18.5833 | 300.469 | 298.443 | 75.668 | 27.214 | 43.982 | 24.263
| 18.5903 | 301.113 | 298.747 | 75.701 | 27.21 | 43.993 | 24.261
| 18.5972 | 300.841 | 299.445 | 75.753 | 27.208 | 44.013 | 24.249
| 18.6042 | 301.593 | 298.662 | 75.803 | 27.212 | 44.035 | 24.247
| 18.6111 | 301.743 | 298.803 | 75.847 | 27.21 | 44.041 | 24.243
| 18.6181 | 301.971 | 299.362 | 75.898 | 27.206 | 44.059 | 24.238
| 18.625 | 300.843 | 299.559 | 75.939 | 27.214 | 44.067 | 24.234
| 18.6319 | 302.597 | 299.94 | 76.008 | 27.211 | 44.104 | 24.231
| 18.6389 | 301.059 | 299.442 | 76.044 | 27.216 | 44.108 | 24.231
| 18.6458 | 301.097 | 299.447 | 76.077 | 27.212 | 44.103 | 24.222
| 18.6528 | 301.821 | 299.986 | 76.116 | 27.221 | 44.115 | 24.22
| 18.6597 | 301.685 | 299.405 | 76.135 | 27.221 | 44.118 | 24.221
| 18.6667 | 301.603 | 300.03 | 76.154 | 27.219 | 44.113 | 24.213
| 18.6736 | 301.439 | 299.608 | 76.16 | 27.223 | 44.114 | 24.212
| 18.6806 | 301.103 | 298.019 | 76.136 | 27.222 | 44.093 | 24.206
| 18.6875 | 301.031 | 298.341 | 76.11 | 27.218 | 44.067 | 24.207
| 18.6944 | 300.687 | 298.813 | 76.09 | 27.223 | 44.056 | 24.203
| 18.7014 | 299.772 | 297.797 | 76.034 | 27.22 | 44.029 | 24.2
| 18.7083 | 298.993 | 297.435 | 75.974 | 27.218 | 43.989 | 24.195
| 18.7153 | 299.119 | 296.349 | 75.89 | 27.213 | 43.947 | 24.195
| 18.7222 | 300.956 | 299.31 | 75.846 | 27.215 | 43.929 | 24.188
| 18.7292 | 299.626 | 298.161 | 75.856 | 27.204 | 43.969 | 24.19
| 18.7361 | 298.591 | 296.78 | 75.773 | 27.208 | 43.927 | 24.179
| 18.7431 | 300.628 | 298.025 | 75.711 | 27.202 | 43.892 | 24.176
| 18.75 | 328.611 | 395.9 | 76.122 | 27.2 | 44.696 | 24.173
| 18.7514 | 328.834 | 394.429 | 76.588 | 27.196 | 46.065 | 24.174
| 18.7528 | 328.42 | 393.579 | 76.924 | 27.196 | 47.111 | 24.173
| 18.7542 | 328.013 | 402 | 77.209 | 27.197 | 48.049 | 24.173
| 18.7556 | 328.277 | 400.715 | 77.47 | 27.201 | 48.862 | 24.174
| 18.7569 | 328.044 | 400.619 | 77.706 | 27.202 | 49.535 | 24.173
| 18.7583 | 327.435 | 401.027 | 77.933 | 27.206 | 50.103 | 24.172
| 18.7597 | 327.461 | 400.345 | 78.144 | 27.213 | 50.594 | 24.174
| 18.7611 | 328.247 | 399.609 | 78.344 | 27.219 | 51.024 | 24.176
| 18.7625 | 327.654 | 399.55 | 78.535 | 27.227 | 51.405 | 24.18
| 18.7639 | 328.289 | 399.9 | 78.738 | 27.236 | 51.753 | 24.184
| 18.7653 | 328.637 | 399.865 | 78.928 | 27.242 | 52.068 | 24.184
| 18.7667 | 327.587 | 399.542 | 79.115 | 27.249 | 52.363 | 24.189
| 18.7681 | 328.081 | 399.117 | 79.284 | 27.258 | 52.632 | 24.195
| 18.7694 | 327.018 | 399.887 | 79.445 | 27.266 | 52.861 | 24.206
| 18.7708 | 327.029 | 399.483 | 79.606 | 27.276 | 53.08 | 24.211
| 18.7722 | 327.289 | 399.431 | 79.762 | 27.284 | 53.29 | 24.22
| 18.7736 | 327.586 | 399.697 | 79.92 | 27.29 | 53.484 | 24.234
| 18.775 | 327.62 | 399.318 | 80.067 | 27.3 | 53.663 | 24.247
| 18.7764 | 327.485 | 398.644 | 80.214 | 27.308 | 53.831 | 24.259
| 18.7778 | 327.128 | 399.428 | 80.359 | 27.319 | 53.998 | 24.272
| 18.7792 | 326.896 | 399.534 | 80.496 | 27.329 | 54.151 | 24.288
| 18.7806 | 326.993 | 399.245 | 80.634 | 27.337 | 54.298 | 24.303
| 18.7819 | 327.511 | 398.318 | 80.768 | 27.345 | 54.439 | 24.319
| 18.7833 | 327.359 | 398.672 | 80.89 | 27.354 | 54.57 | 24.338
| 18.7847 | 327.51 | 399.603 | 81.018 | 27.361 | 54.701 | 24.352
| 18.7861 | 326.946 | 398.829 | 81.14 | 27.373 | 54.826 | 24.373
| 18.7875 | 327.841 | 398.694 | 81.265 | 27.38 | 54.955 | 24.395
| 18.7889 | 327.114 | 398.559 | 81.38 | 27.391 | 55.075 | 24.41
| 18.7903 | 327.893 | 398.509 | 81.503 | 27.398 | 55.192 | 24.436
| 18.7917 | 327.516 | 397.935 | 81.616 | 27.41 | 55.31 | 24.456
| 18.7931 | 327.705 | 399.403 | 81.726 | 27.415 | 55.415 | 24.474
| 18.7944 | 327.385 | 398.431 | 81.838 | 27.426 | 55.522 | 24.496
| 18.7958 | 327.57 | 399.13 | 81.947 | 27.437 | 55.634 | 24.523
| 18.7972 | 327.681 | 398.659 | 82.052 | 27.448 | 55.735 | 24.544
| 18.7986 | 327.964 | 398.574 | 82.144 | 27.456 | 55.832 | 24.567
| 18.8 | 327.862 | 398.493 | 82.246 | 27.462 | 55.928 | 24.588
| 18.8014 | 327.874 | 398.496 | 82.347 | 27.471 | 56.028 | 24.611
| 18.8028 | 328.03 | 398.437 | 82.442 | 27.484 | 56.12 | 24.637
| 18.8042 | 327.047 | 399.266 | 82.537 | 27.494 | 56.23 | 24.659
| 18.8056 | 328.196 | 398.858 | 82.628 | 27.502 | 56.316 | 24.687
| 18.8069 | 328.576 | 399.145 | 82.721 | 27.505 | 56.413 | 24.71
| 18.8083 | 327.754 | 398.311 | 82.818 | 27.521 | 56.504 | 24.738
| 18.8097 | 327.2 | 399.156 | 82.898 | 27.526 | 56.588 | 24.762
| 18.8111 | 328.421 | 399.248 | 82.987 | 27.532 | 56.68 | 24.788
| 18.8125 | 328.257 | 399.726 | 83.078 | 27.547 | 56.773 | 24.81
| 18.8139 | 327.768 | 400.165 | 83.166 | 27.55 | 56.863 | 24.835
| 18.8153 | 327.904 | 398.353 | 83.253 | 27.562 | 56.951 | 24.859
| 18.8167 | 327.763 | 399.882 | 83.334 | 27.574 | 57.042 | 24.885
| 18.8181 | 328.122 | 399.352 | 83.413 | 27.582 | 57.125 | 24.914
| 18.8194 | 328.336 | 399.108 | 83.485 | 27.589 | 57.206 | 24.936
| 18.8208 | 328.12 | 400.525 | 83.571 | 27.597 | 57.294 | 24.966
| 18.8222 | 328.621 | 399.882 | 83.647 | 27.607 | 57.373 | 24.99
| 18.8236 | 328.764 | 399.266 | 83.724 | 27.613 | 57.466 | 25.017
| 18.825 | 328.744 | 399.79 | 83.798 | 27.624 | 57.539 | 25.038
| 18.8264 | 328.814 | 399.332 | 83.871 | 27.631 | 57.616 | 25.064
| 18.8278 | 328.245 | 400.312 | 83.937 | 27.643 | 57.691 | 25.096
| 18.8292 | 328.713 | 400.865 | 84.013 | 27.649 | 57.775 | 25.116
| 18.8306 | 329.207 | 400.033 | 84.09 | 27.659 | 57.863 | 25.148
| 18.8319 | 328.841 | 400.333 | 84.157 | 27.668 | 57.94 | 25.169
| 18.8333 | 329.151 | 400.09 | 84.224 | 27.678 | 58.017 | 25.199
| 18.8347 | 328.856 | 401.179 | 84.291 | 27.686 | 58.094 | 25.223
| 18.8361 | 328.661 | 400.553 | 84.362 | 27.696 | 58.175 | 25.243
| 18.8375 | 328.129 | 400.314 | 84.423 | 27.703 | 58.238 | 25.275
| 18.8389 | 328.775 | 400.532 | 84.478 | 27.712 | 58.304 | 25.296
| 18.8403 | 328.936 | 400.421 | 84.545 | 27.721 | 58.382 | 25.325
| 18.8417 | 328.368 | 400.917 | 84.6 | 27.73 | 58.446 | 25.355
| 18.8431 | 329.12 | 400.714 | 84.666 | 27.74 | 58.516 | 25.374
| 18.8444 | 329.333 | 400.052 | 84.725 | 27.746 | 58.59 | 25.405
| 18.8458 | 328.82 | 400.818 | 84.786 | 27.757 | 58.663 | 25.428
| 18.8472 | 329.857 | 400.775 | 84.844 | 27.764 | 58.736 | 25.454
| 18.8486 | 327.946 | 398.524 | 84.906 | 27.774 | 58.808 | 25.482
| 18.85 | 327.884 | 398.218 | 84.919 | 27.78 | 58.828 | 25.506
| 18.8514 | 327.786 | 398.191 | 84.955 | 27.784 | 58.864 | 25.533
| 18.8528 | 326.685 | 398.904 | 84.977 | 27.796 | 58.904 | 25.558
| 18.8542 | 327.661 | 397.994 | 85.01 | 27.803 | 58.94 | 25.584
| 18.8556 | 326.977 | 398.777 | 85.042 | 27.813 | 58.981 | 25.61
| 18.8569 | 327.118 | 399.298 | 85.077 | 27.819 | 59.024 | 25.635
| 18.8583 | 327.001 | 398.711 | 85.102 | 27.826 | 59.074 | 25.658
| 18.8597 | 326.377 | 398.56 | 85.135 | 27.835 | 59.119 | 25.683
| 18.8611 | 327.68 | 398.651 | 85.166 | 27.841 | 59.165 | 25.709
| 18.8625 | 327.063 | 399.083 | 85.205 | 27.852 | 59.226 | 25.734
| 18.8639 | 327.271 | 398.19 | 85.24 | 27.855 | 59.276 | 25.761
| 18.8653 | 327.876 | 399.063 | 85.275 | 27.865 | 59.332 | 25.785
| 18.8667 | 327.676 | 398.111 | 85.308 | 27.873 | 59.392 | 25.812
| 18.8681 | 328.054 | 398.509 | 85.341 | 27.878 | 59.438 | 25.832
| 18.8694 | 327.862 | 399.847 | 85.379 | 27.885 | 59.498 | 25.86
| 18.8708 | 328.264 | 398.78 | 85.413 | 27.892 | 59.552 | 25.885
| 18.8722 | 327.726 | 399.045 | 85.445 | 27.896 | 59.61 | 25.904
| 18.8736 | 328.616 | 398.973 | 85.483 | 27.911 | 59.674 | 25.931
| 18.875 | 328.104 | 399.727 | 85.521 | 27.921 | 59.734 | 25.957
| 18.8764 | 328.642 | 399.875 | 85.563 | 27.921 | 59.796 | 25.98
| 18.8778 | 328.298 | 400.232 | 85.599 | 27.928 | 59.854 | 26.004
| 18.8792 | 328.503 | 400.279 | 85.643 | 27.938 | 59.92 | 26.027
| 18.8806 | 329.29 | 399.691 | 85.684 | 27.946 | 59.985 | 26.052
| 18.8819 | 329.092 | 400.874 | 85.733 | 27.95 | 60.051 | 26.077
| 18.8833 | 329.337 | 400.1 | 85.771 | 27.956 | 60.121 | 26.101
| 18.8847 | 329.151 | 400.354 | 85.818 | 27.964 | 60.185 | 26.118
| 18.8861 | 328.986 | 399.993 | 85.854 | 27.971 | 60.239 | 26.147
| 18.8875 | 329.208 | 401.226 | 85.896 | 27.972 | 60.299 | 26.166
| 18.8889 | 329.933 | 402.12 | 85.942 | 27.984 | 60.361 | 26.192
| 18.8903 | 329.096 | 400.568 | 85.98 | 27.992 | 60.431 | 26.211
| 18.8917 | 328.386 | 400.643 | 86 | 27.995 | 60.476 | 26.238
| 18.8931 | 328.267 | 400.655 | 86.029 | 28.005 | 60.516 | 26.261
| 18.8944 | 328.3 | 400.106 | 86.049 | 28.008 | 60.556 | 26.282
| 18.8958 | 328.725 | 399.476 | 86.074 | 28.015 | 60.597 | 26.306
| 18.8972 | 328.563 | 399.386 | 86.098 | 28.021 | 60.643 | 26.328
| 18.8986 | 328.735 | 399.83 | 86.13 | 28.026 | 60.689 | 26.348
| 18.9 | 328.393 | 400.275 | 86.162 | 28.036 | 60.733 | 26.374
| 18.9014 | 329.176 | 399.613 | 86.19 | 28.043 | 60.783 | 26.398
| 18.9028 | 328.231 | 400.306 | 86.212 | 28.048 | 60.821 | 26.418
| 18.9042 | 328.422 | 400.007 | 86.236 | 28.054 | 60.858 | 26.44
| 18.9056 | 329.394 | 399.916 | 86.264 | 28.056 | 60.909 | 26.463
| 18.9069 | 328.609 | 399.856 | 86.291 | 28.067 | 60.957 | 26.487
| 18.9083 | 328.797 | 401.116 | 86.32 | 28.074 | 61.004 | 26.508
| 18.9097 | 329.411 | 400.806 | 86.355 | 28.081 | 61.06 | 26.533
| 18.9111 | 329.067 | 400.326 | 86.384 | 28.088 | 61.113 | 26.549
| 18.9125 | 329.34 | 399.911 | 86.413 | 28.09 | 61.16 | 26.576
| 18.9139 | 329.4 | 400.32 | 86.441 | 28.099 | 61.208 | 26.593
| 18.9153 | 328.945 | 400.421 | 86.475 | 28.102 | 61.256 | 26.613
| 18.9167 | 329.668 | 400.174 | 86.501 | 28.112 | 61.301 | 26.64
| 18.9181 | 329.267 | 400.843 | 86.523 | 28.113 | 61.351 | 26.66
| 18.9194 | 329.782 | 400.287 | 86.558 | 28.122 | 61.4 | 26.683
| 18.9208 | 329.685 | 401.033 | 86.586 | 28.127 | 61.452 | 26.699
| 18.9222 | 329.454 | 400.864 | 86.609 | 28.134 | 61.499 | 26.724
| 18.9236 | 329.1 | 400.73 | 86.64 | 28.138 | 61.54 | 26.742
| 18.925 | 329.688 | 400.331 | 86.655 | 28.144 | 61.58 | 26.768
| 18.9264 | 328.766 | 400.97 | 86.681 | 28.153 | 61.619 | 26.791
| 18.9278 | 329.353 | 401.082 | 86.7 | 28.157 | 61.658 | 26.813
| 18.9292 | 329.88 | 400.354 | 86.728 | 28.167 | 61.706 | 26.827
| 18.9306 | 330.429 | 401.315 | 86.768 | 28.169 | 61.767 | 26.851
| 18.9319 | 330.064 | 401.065 | 86.802 | 28.174 | 61.818 | 26.872
| 18.9333 | 329.473 | 400.386 | 86.826 | 28.18 | 61.855 | 26.888
| 18.9347 | 329.347 | 400.626 | 86.844 | 28.186 | 61.894 | 26.913
| 18.9361 | 329.184 | 400.876 | 86.86 | 28.189 | 61.928 | 26.928
| 18.9375 | 328.704 | 401.302 | 86.884 | 28.193 | 61.964 | 26.951
| 18.9389 | 329.944 | 400.689 | 86.906 | 28.204 | 62.005 | 26.971
| 18.9403 | 329.392 | 400.853 | 86.924 | 28.21 | 62.042 | 26.998
| 18.9417 | 329.784 | 400.771 | 86.942 | 28.214 | 62.078 | 27.016
| 18.9431 | 329.423 | 400.894 | 86.964 | 28.218 | 62.12 | 27.033
| 18.9444 | 329.015 | 401.306 | 86.99 | 28.223 | 62.158 | 27.048
| 18.9458 | 329.162 | 400.617 | 87.007 | 28.228 | 62.195 | 27.072
| 18.9472 | 329.684 | 400.804 | 87.028 | 28.234 | 62.229 | 27.09
| 18.9486 | 329.296 | 400.861 | 87.045 | 28.24 | 62.266 | 27.114
| 18.95 | 329.086 | 401.556 | 87.063 | 28.247 | 62.303 | 27.135
| 18.9514 | 325.786 | 396.813 | 87.08 | 28.25 | 62.348 | 27.152
| 18.9528 | 325.615 | 397.147 | 87.027 | 28.255 | 62.306 | 27.174
| 18.9542 | 326.55 | 397.102 | 86.994 | 28.261 | 62.281 | 27.192
| 18.9556 | 326.714 | 397.298 | 86.973 | 28.267 | 62.273 | 27.214
| 18.9569 | 326.406 | 397.973 | 86.966 | 28.266 | 62.284 | 27.23
| 18.9583 | 326.754 | 397.743 | 86.963 | 28.279 | 62.294 | 27.251
| 18.9597 | 326.746 | 398.709 | 86.961 | 28.281 | 62.315 | 27.271
| 18.9611 | 326.177 | 397.764 | 86.96 | 28.284 | 62.333 | 27.283
| 18.9625 | 326.36 | 398.231 | 86.949 | 28.294 | 62.344 | 27.307
| 18.9639 | 326.205 | 398.051 | 86.947 | 28.295 | 62.363 | 27.326
| 18.9653 | 326.304 | 398.227 | 86.941 | 28.299 | 62.385 | 27.345
| 18.9667 | 326.027 | 397.468 | 86.939 | 28.302 | 62.407 | 27.362
| 18.9681 | 326.78 | 397.192 | 86.928 | 28.306 | 62.425 | 27.385
| 18.9694 | 326.038 | 397.849 | 86.92 | 28.311 | 62.44 | 27.401
| 18.9708 | 326.046 | 397.65 | 86.912 | 28.317 | 62.456 | 27.415
| 18.9722 | 327.412 | 397.661 | 86.919 | 28.317 | 62.487 | 27.442
| 18.9736 | 327.56 | 397.739 | 86.926 | 28.319 | 62.528 | 27.455
| 18.975 | 326.897 | 398.292 | 86.936 | 28.326 | 62.568 | 27.475
| 18.9764 | 326.826 | 398.752 | 86.945 | 28.328 | 62.603 | 27.489
| 18.9778 | 327.672 | 397.837 | 86.949 | 28.331 | 62.639 | 27.512
| 18.9792 | 327.701 | 398.07 | 86.953 | 28.331 | 62.668 | 27.525
| 18.9806 | 327.774 | 398.823 | 86.96 | 28.336 | 62.706 | 27.544
| 18.9819 | 328.216 | 398.398 | 86.974 | 28.343 | 62.752 | 27.56
| 18.9833 | 327.67 | 399.17 | 86.984 | 28.344 | 62.792 | 27.576
| 18.9847 | 327.459 | 399.705 | 86.996 | 28.346 | 62.822 | 27.595
| 18.9861 | 328.594 | 398.895 | 87.008 | 28.35 | 62.866 | 27.613
| 18.9875 | 327.752 | 399.777 | 87.024 | 28.353 | 62.904 | 27.628
| 18.9889 | 328.569 | 399.014 | 87.037 | 28.36 | 62.942 | 27.65
| 18.9903 | 328.102 | 399.958 | 87.054 | 28.363 | 62.985 | 27.664
| 18.9917 | 328.475 | 398.952 | 87.065 | 28.37 | 63.021 | 27.683
| 18.9931 | 328.624 | 399.078 | 87.081 | 28.372 | 63.055 | 27.699
| 18.9944 | 328.337 | 399.961 | 87.088 | 28.377 | 63.085 | 27.715
| 18.9958 | 328.47 | 400.246 | 87.104 | 28.381 | 63.125 | 27.729
| 18.9972 | 328.198 | 400.352 | 87.128 | 28.382 | 63.166 | 27.744
| 18.9986 | 327.984 | 400.321 | 87.141 | 28.388 | 63.202 | 27.767
| 19 | 329.06 | 399.895 | 87.151 | 28.388 | 63.234 | 27.781
| 19.0014 | 328.521 | 400.829 | 87.174 | 28.394 | 63.276 | 27.798
| 19.0028 | 329.097 | 400.347 | 87.189 | 28.395 | 63.314 | 27.813
| 19.0042 | 329.026 | 399.944 | 87.208 | 28.405 | 63.351 | 27.829
| 19.0056 | 329.111 | 399.848 | 87.226 | 28.407 | 63.39 | 27.844
| 19.0069 | 328.766 | 400.214 | 87.238 | 28.409 | 63.419 | 27.863
| 19.0083 | 328.528 | 400.704 | 87.254 | 28.418 | 63.454 | 27.878
| 19.0097 | 328.532 | 400.861 | 87.276 | 28.419 | 63.496 | 27.894
| 19.0111 | 329.108 | 400.009 | 87.292 | 28.421 | 63.531 | 27.91
| 19.0125 | 330.025 | 400.575 | 87.315 | 28.428 | 63.567 | 27.925
| 19.0139 | 329.537 | 402.265 | 87.344 | 28.433 | 63.619 | 27.944
| 19.0153 | 330.165 | 400.971 | 87.374 | 28.434 | 63.674 | 27.962
| 19.0167 | 327.948 | 400.03 | 87.382 | 28.439 | 63.705 | 27.975
| 19.0181 | 327.705 | 398.419 | 87.37 | 28.44 | 63.697 | 27.992
| 19.0194 | 327.498 | 398.056 | 87.355 | 28.448 | 63.69 | 28.003
| 19.0208 | 327.781 | 397.81 | 87.346 | 28.452 | 63.694 | 28.021
| 19.0222 | 327.313 | 399.23 | 87.343 | 28.456 | 63.699 | 28.037
| 19.0236 | 327.599 | 399.824 | 87.351 | 28.459 | 63.713 | 28.053
| 19.025 | 327.866 | 399.363 | 87.357 | 28.46 | 63.744 | 28.069
| 19.0264 | 327.926 | 398.26 | 87.358 | 28.466 | 63.76 | 28.082
| 19.0278 | 327.193 | 398.938 | 87.356 | 28.47 | 63.776 | 28.096
| 19.0292 | 327.928 | 398.021 | 87.354 | 28.475 | 63.789 | 28.114
| 19.0306 | 327.756 | 398.528 | 87.358 | 28.476 | 63.813 | 28.131
| 19.0319 | 327.757 | 399.572 | 87.364 | 28.48 | 63.83 | 28.143
| 19.0333 | 327.796 | 400.052 | 87.378 | 28.482 | 63.86 | 28.158
| 19.0347 | 328.393 | 399.608 | 87.387 | 28.489 | 63.892 | 28.177
| 19.0361 | 327.544 | 399.05 | 87.386 | 28.488 | 63.914 | 28.191
| 19.0375 | 327.753 | 398.107 | 87.381 | 28.497 | 63.928 | 28.206
| 19.0389 | 327.595 | 397.628 | 87.373 | 28.498 | 63.939 | 28.222
| 19.0403 | 327.074 | 398.37 | 87.37 | 28.504 | 63.95 | 28.241
| 19.0417 | 327.578 | 397.495 | 87.371 | 28.503 | 63.965 | 28.252
| 19.0431 | 326.908 | 398.493 | 87.369 | 28.509 | 63.985 | 28.263
| 19.0444 | 327.908 | 397.585 | 87.375 | 28.513 | 64.011 | 28.28
| 19.0458 | 327.33 | 398.471 | 87.376 | 28.518 | 64.032 | 28.294
| 19.0472 | 327.823 | 398.528 | 87.384 | 28.519 | 64.062 | 28.31
| 19.0486 | 328.209 | 398.489 | 87.393 | 28.521 | 64.087 | 28.325
| 19.05 | 327.716 | 399.299 | 87.406 | 28.525 | 64.124 | 28.339
| 19.0514 | 328.134 | 398.569 | 87.414 | 28.529 | 64.151 | 28.35
| 19.0528 | 327.271 | 398.84 | 87.422 | 28.53 | 64.175 | 28.365
| 19.0542 | 327.912 | 397.943 | 87.42 | 28.534 | 64.194 | 28.381
| 19.0556 | 327.439 | 399.202 | 87.426 | 28.538 | 64.218 | 28.397
| 19.0569 | 328.546 | 398.218 | 87.432 | 28.541 | 64.25 | 28.412
| 19.0583 | 327.86 | 399.582 | 87.442 | 28.54 | 64.273 | 28.428
| 19.0597 | 328.467 | 398.671 | 87.448 | 28.543 | 64.299 | 28.436
| 19.0611 | 328.283 | 399.171 | 87.461 | 28.547 | 64.33 | 28.452
| 19.0625 | 328.134 | 400.049 | 87.471 | 28.551 | 64.355 | 28.468
| 19.0639 | 328.875 | 399.149 | 87.483 | 28.557 | 64.395 | 28.48
| 19.0653 | 328.082 | 399.17 | 87.496 | 28.561 | 64.418 | 28.492
| 19.0667 | 328.418 | 398.716 | 87.499 | 28.563 | 64.445 | 28.508
| 19.0681 | 328.34 | 399.242 | 87.503 | 28.565 | 64.463 | 28.517
| 19.0694 | 328.494 | 398.503 | 87.512 | 28.567 | 64.485 | 28.534
| 19.0708 | 328.317 | 398.507 | 87.517 | 28.569 | 64.51 | 28.549
| 19.0722 | 327.784 | 399.267 | 87.522 | 28.574 | 64.529 | 28.56
| 19.0736 | 328.334 | 398.444 | 87.527 | 28.579 | 64.546 | 28.582
| 19.075 | 327.638 | 399.538 | 87.528 | 28.58 | 64.558 | 28.589
| 19.0764 | 328.01 | 399.3 | 87.534 | 28.584 | 64.58 | 28.606
| 19.0778 | 328.08 | 399.256 | 87.538 | 28.587 | 64.604 | 28.618
| 19.0792 | 327.88 | 398.977 | 87.543 | 28.592 | 64.621 | 28.629
| 19.0806 | 328.627 | 399.034 | 87.553 | 28.596 | 64.645 | 28.638
| 19.0819 | 328.086 | 399.297 | 87.559 | 28.6 | 64.667 | 28.655
| 19.0833 | 328.432 | 399.125 | 87.568 | 28.6 | 64.694 | 28.672
| 19.0847 | 328.257 | 399.463 | 87.578 | 28.602 | 64.72 | 28.685
| 19.0861 | 328.643 | 399.356 | 87.585 | 28.607 | 64.747 | 28.695
| 19.0875 | 328.409 | 399.525 | 87.596 | 28.609 | 64.773 | 28.711
| 19.0889 | 328.481 | 399.814 | 87.603 | 28.61 | 64.798 | 28.719
| 19.0903 | 328.99 | 399.496 | 87.62 | 28.614 | 64.829 | 28.732
| 19.0917 | 328.896 | 399.835 | 87.635 | 28.62 | 64.859 | 28.749
| 19.0931 | 329.047 | 400.725 | 87.657 | 28.623 | 64.897 | 28.762
| 19.0944 | 329.134 | 400.141 | 87.674 | 28.623 | 64.93 | 28.772
| 19.0958 | 329.002 | 400.235 | 87.689 | 28.63 | 64.958 | 28.785
| 19.0972 | 330.141 | 400.74 | 87.709 | 28.635 | 64.993 | 28.8
| 19.0986 | 329.97 | 400.728 | 87.736 | 28.639 | 65.038 | 28.809
| 19.1 | 330.093 | 401.243 | 87.761 | 28.638 | 65.081 | 28.826
| 19.1014 | 329.742 | 401.047 | 87.779 | 28.642 | 65.109 | 28.84
| 19.1028 | 329.42 | 400.905 | 87.79 | 28.646 | 65.135 | 28.851
| 19.1042 | 328.839 | 400.97 | 87.804 | 28.652 | 65.163 | 28.863
| 19.1056 | 330.247 | 400.618 | 87.822 | 28.654 | 65.195 | 28.874
| 19.1069 | 326.213 | 396.042 | 87.842 | 28.657 | 65.227 | 28.888
| 19.1083 | 325.887 | 395.79 | 87.77 | 28.662 | 65.161 | 28.901
| 19.1097 | 326.212 | 395.836 | 87.724 | 28.663 | 65.114 | 28.911
| 19.1111 | 326.035 | 395.941 | 87.7 | 28.668 | 65.082 | 28.926
| 19.1125 | 325.675 | 395.664 | 87.676 | 28.671 | 65.065 | 28.937
| 19.1139 | 325.699 | 396.701 | 87.652 | 28.675 | 65.044 | 28.952
| 19.1153 | 326.293 | 396.008 | 87.638 | 28.675 | 65.033 | 28.964
| 19.1167 | 325.456 | 396.85 | 87.619 | 28.68 | 65.024 | 28.978
| 19.1181 | 326.067 | 395.841 | 87.604 | 28.681 | 65.027 | 28.988
| 19.1194 | 326.058 | 396.441 | 87.581 | 28.685 | 65.022 | 28.998
| 19.1208 | 326.19 | 396.491 | 87.572 | 28.683 | 65.03 | 29.012
| 19.1222 | 325.861 | 395.505 | 87.55 | 28.685 | 65.029 | 29.029
| 19.1236 | 325.519 | 396.44 | 87.534 | 28.687 | 65.031 | 29.037
| 19.125 | 325.435 | 396.562 | 87.52 | 28.693 | 65.033 | 29.044
| 19.1264 | 325.973 | 395.876 | 87.508 | 28.695 | 65.04 | 29.061
| 19.1278 | 326.4 | 396.2 | 87.496 | 28.695 | 65.053 | 29.074
| 19.1292 | 325.851 | 396.695 | 87.486 | 28.696 | 65.06 | 29.086
| 19.1306 | 325.836 | 396.24 | 87.476 | 28.7 | 65.077 | 29.097
| 19.1319 | 326.142 | 395.914 | 87.459 | 28.7 | 65.083 | 29.103
| 19.1333 | 325.265 | 397.006 | 87.449 | 28.701 | 65.093 | 29.116
| 19.1347 | 326.016 | 396.392 | 87.434 | 28.697 | 65.103 | 29.13
| 19.1361 | 326.182 | 395.983 | 87.424 | 28.703 | 65.115 | 29.138
| 19.1375 | 326.601 | 396.253 | 87.422 | 28.701 | 65.131 | 29.152
| 19.1389 | 326.209 | 396.074 | 87.415 | 28.706 | 65.149 | 29.164
| 19.1403 | 326.202 | 396.715 | 87.41 | 28.708 | 65.169 | 29.169
| 19.1417 | 326.123 | 397.354 | 87.405 | 28.71 | 65.186 | 29.184
| 19.1431 | 326.282 | 396.083 | 87.396 | 28.708 | 65.204 | 29.196
| 19.1444 | 325.776 | 396.243 | 87.388 | 28.713 | 65.209 | 29.209
| 19.1458 | 326.093 | 395.806 | 87.383 | 28.713 | 65.221 | 29.216
| 19.1472 | 326.362 | 396.118 | 87.367 | 28.715 | 65.23 | 29.227
| 19.1486 | 325.879 | 396.799 | 87.354 | 28.714 | 65.244 | 29.24
| 19.15 | 326.18 | 396.016 | 87.352 | 28.715 | 65.259 | 29.251
| 19.1514 | 325.777 | 396.789 | 87.34 | 28.72 | 65.272 | 29.261
| 19.1528 | 326.295 | 395.939 | 87.344 | 28.724 | 65.287 | 29.274
| 19.1542 | 326.38 | 395.693 | 87.332 | 28.726 | 65.297 | 29.285
| 19.1556 | 325.922 | 397.318 | 87.336 | 28.724 | 65.318 | 29.296
| 19.1569 | 326.044 | 397.253 | 87.333 | 28.726 | 65.339 | 29.302
| 19.1583 | 325.974 | 397.259 | 87.332 | 28.73 | 65.357 | 29.313
| 19.1597 | 325.863 | 396.167 | 87.327 | 28.732 | 65.376 | 29.323
| 19.1611 | 326.002 | 395.911 | 87.316 | 28.731 | 65.384 | 29.331
| 19.1625 | 325.532 | 396.805 | 87.313 | 28.734 | 65.398 | 29.343
| 19.1639 | 326.406 | 395.901 | 87.31 | 28.738 | 65.411 | 29.35
| 19.1653 | 325.895 | 395.867 | 87.302 | 28.736 | 65.421 | 29.365
| 19.1667 | 326.182 | 396.076 | 87.293 | 28.739 | 65.429 | 29.376
| 19.1681 | 326.155 | 396.123 | 87.29 | 28.737 | 65.443 | 29.386
| 19.1694 | 325.946 | 395.795 | 87.281 | 28.741 | 65.452 | 29.395
| 19.1708 | 325.617 | 396.56 | 87.27 | 28.746 | 65.461 | 29.407
| 19.1722 | 325.883 | 395.803 | 87.268 | 28.745 | 65.469 | 29.416
| 19.1736 | 325.919 | 395.984 | 87.262 | 28.749 | 65.484 | 29.425
| 19.175 | 326.273 | 395.784 | 87.255 | 28.754 | 65.493 | 29.433
| 19.1764 | 325.454 | 396.821 | 87.25 | 28.75 | 65.503 | 29.444
| 19.1778 | 325.967 | 395.565 | 87.248 | 28.751 | 65.515 | 29.453
| 19.1792 | 324.962 | 396.092 | 87.236 | 28.752 | 65.523 | 29.467
| 19.1806 | 324.944 | 396.114 | 87.229 | 28.758 | 65.532 | 29.477
| 19.1819 | 325.16 | 394.576 | 87.209 | 28.757 | 65.529 | 29.484
| 19.1833 | 324.796 | 394.938 | 87.186 | 28.759 | 65.522 | 29.497
| 19.1847 | 324.877 | 394.228 | 87.175 | 28.759 | 65.522 | 29.503
| 19.1861 | 324.48 | 395.051 | 87.154 | 28.759 | 65.514 | 29.508
| 19.1875 | 325.094 | 394.937 | 87.148 | 28.764 | 65.526 | 29.52
| 19.1889 | 324.901 | 395.071 | 87.133 | 28.763 | 65.531 | 29.532
| 19.1903 | 324.924 | 395.431 | 87.13 | 28.765 | 65.54 | 29.536
| 19.1917 | 325.269 | 394.844 | 87.122 | 28.768 | 65.555 | 29.55
| 19.1931 | 324.665 | 395.806 | 87.118 | 28.769 | 65.565 | 29.561
| 19.1944 | 325.542 | 394.967 | 87.117 | 28.773 | 65.582 | 29.566
| 19.1958 | 325.127 | 395.815 | 87.112 | 28.77 | 65.597 | 29.583
| 19.1972 | 325.008 | 395.884 | 87.109 | 28.767 | 65.613 | 29.586
| 19.1986 | 324.951 | 396.028 | 87.099 | 28.772 | 65.625 | 29.595
| 19.2 | 324.899 | 395.929 | 87.095 | 28.774 | 65.641 | 29.604
| 19.2014 | 325.252 | 395.536 | 87.093 | 28.773 | 65.65 | 29.613
| 19.2028 | 325.246 | 395.042 | 87.084 | 28.777 | 65.661 | 29.624
| 19.2042 | 325.586 | 395.147 | 87.076 | 28.778 | 65.677 | 29.633
| 19.2056 | 324.677 | 395.725 | 87.07 | 28.778 | 65.686 | 29.646
| 19.2069 | 324.618 | 395.038 | 87.058 | 28.782 | 65.69 | 29.652
| 19.2083 | 325.051 | 394.198 | 87.057 | 28.783 | 65.701 | 29.663
| 19.2097 | 324.607 | 394.351 | 87.045 | 28.786 | 65.701 | 29.671
| 19.2111 | 324.534 | 395.346 | 87.035 | 28.785 | 65.707 | 29.677
| 19.2125 | 324.734 | 395.802 | 87.024 | 28.788 | 65.717 | 29.686
| 19.2139 | 324.545 | 395.827 | 87.018 | 28.79 | 65.721 | 29.695
| 19.2153 | 324.971 | 394.884 | 87.015 | 28.789 | 65.736 | 29.703
| 19.2167 | 325.066 | 394.691 | 87.009 | 28.786 | 65.746 | 29.711
| 19.2181 | 324.757 | 394.717 | 86.999 | 28.787 | 65.747 | 29.719
| 19.2194 | 325.073 | 394.262 | 86.991 | 28.792 | 65.761 | 29.732
| 19.2208 | 324.662 | 393.895 | 86.973 | 28.793 | 65.758 | 29.741
| 19.2222 | 324.014 | 393.322 | 86.953 | 28.794 | 65.759 | 29.745
| 19.2236 | 322.846 | 393.701 | 86.924 | 28.796 | 65.746 | 29.75
| 19.225 | 323.738 | 401.168 | 86.901 | 28.795 | 65.833 | 29.763
| 19.2264 | 323.008 | 401.286 | 86.884 | 28.797 | 65.974 | 29.772
| 19.2278 | 323.268 | 401.442 | 86.859 | 28.798 | 66.067 | 29.775
| 19.2292 | 327.656 | 406.048 | 86.845 | 28.798 | 66.154 | 29.79
| 19.2306 | 327.102 | 406.836 | 86.914 | 28.798 | 66.324 | 29.796
| 19.2319 | 327.438 | 397.975 | 86.961 | 28.8 | 66.468 | 29.802
| 19.2333 | 326.353 | 398.872 | 86.975 | 28.801 | 66.423 | 29.813
| 19.2347 | 326.308 | 398.293 | 86.988 | 28.799 | 66.403 | 29.819
| 19.2361 | 326.833 | 397.616 | 86.999 | 28.804 | 66.388 | 29.829
| 19.2375 | 326.138 | 398.245 | 87.015 | 28.803 | 66.382 | 29.839
| 19.2389 | 326.216 | 397.395 | 87.015 | 28.807 | 66.375 | 29.848
| 19.2403 | 325.997 | 397.776 | 87.023 | 28.807 | 66.378 | 29.852
| 19.2417 | 325.915 | 398.416 | 87.025 | 28.811 | 66.379 | 29.864
| 19.2431 | 326.288 | 398.131 | 87.024 | 28.807 | 66.374 | 29.869
| 19.2444 | 325.725 | 397.979 | 87.029 | 28.812 | 66.383 | 29.88
| 19.2458 | 326.305 | 397.539 | 87.03 | 28.815 | 66.387 | 29.89
| 19.2472 | 326.251 | 397.927 | 87.034 | 28.811 | 66.395 | 29.897
| 19.2486 | 326.117 | 397.867 | 87.041 | 28.815 | 66.409 | 29.907
| 19.25 | 324.636 | 397.357 | 87.041 | 28.815 | 66.418 | 29.918
| 19.2514 | 325.254 | 397.539 | 87.04 | 28.819 | 66.424 | 29.925
| 19.2528 | 325.711 | 398.622 | 87.041 | 28.821 | 66.429 | 29.932
| 19.2542 | 325.535 | 398.498 | 87.039 | 28.819 | 66.439 | 29.943
| 19.2556 | 325.522 | 398.601 | 87.04 | 28.827 | 66.449 | 29.951
| 19.2569 | 325.24 | 397.88 | 87.045 | 28.824 | 66.465 | 29.954
| 19.2583 | 325.86 | 397.693 | 87.048 | 28.828 | 66.474 | 29.97
| 19.2597 | 325.95 | 397.1 | 87.048 | 28.826 | 66.483 | 29.979
| 19.2611 | 325.289 | 398.28 | 87.055 | 28.828 | 66.5 | 29.985
| 19.2625 | 325.815 | 397.169 | 87.053 | 28.828 | 66.512 | 29.997
| 19.2639 | 323.773 | 395.468 | 87.036 | 28.832 | 66.508 | 30.001
| 19.2653 | 323.475 | 394.873 | 87.006 | 28.838 | 66.482 | 30.012
| 19.2667 | 323.523 | 394.057 | 86.972 | 28.835 | 66.451 | 30.02
| 19.2681 | 326.614 | 399.721 | 86.981 | 28.833 | 66.462 | 30.029
| 19.2694 | 326.699 | 399.649 | 87.029 | 28.837 | 66.528 | 30.036
| 19.2708 | 327.463 | 398.799 | 87.057 | 28.838 | 66.577 | 30.045
| 19.2722 | 326.81 | 398.34 | 87.078 | 28.839 | 66.617 | 30.054
| 19.2736 | 326.159 | 398.747 | 87.078 | 28.837 | 66.639 | 30.065
| 19.275 | 326.232 | 398.424 | 87.084 | 28.843 | 66.662 | 30.073
| 19.2764 | 325.78 | 397.895 | 87.084 | 28.844 | 66.672 | 30.08
| 19.2778 | 326.19 | 397.426 | 87.082 | 28.842 | 66.684 | 30.089
| 19.2792 | 327.218 | 398.733 | 87.09 | 28.846 | 66.687 | 30.101
| 19.2806 | 327.282 | 398.631 | 87.115 | 28.846 | 66.727 | 30.103
| 19.2819 | 326.025 | 398.684 | 87.131 | 28.847 | 66.762 | 30.11
| 19.2833 | 326.295 | 397.486 | 87.139 | 28.848 | 66.778 | 30.119
| 19.2847 | 325.817 | 398.137 | 87.138 | 28.853 | 66.785 | 30.125
| 19.2861 | 326.313 | 397.866 | 87.129 | 28.853 | 66.789 | 30.139
| 19.2875 | 325.143 | 397.158 | 87.127 | 28.853 | 66.794 | 30.144
| 19.2889 | 325.609 | 396.805 | 87.12 | 28.857 | 66.797 | 30.154
| 19.2903 | 325.717 | 397.292 | 87.12 | 28.86 | 66.797 | 30.161
| 19.2917 | 325.306 | 396.589 | 87.115 | 28.862 | 66.797 | 30.172
| 19.2931 | 325.273 | 396.586 | 87.106 | 28.866 | 66.797 | 30.179
| 19.2944 | 324.306 | 396.782 | 87.093 | 28.866 | 66.795 | 30.183
| 19.2958 | 324.379 | 396.447 | 87.082 | 28.865 | 66.791 | 30.193
| 19.2972 | 324.277 | 396.996 | 87.071 | 28.864 | 66.782 | 30.201
| 19.2986 | 324.094 | 396.024 | 87.059 | 28.868 | 66.777 | 30.211
| 19.3 | 324.558 | 395.112 | 87.041 | 28.869 | 66.767 | 30.217
| 19.3014 | 323.395 | 394.911 | 87.022 | 28.868 | 66.754 | 30.231
| 19.3028 | 322.625 | 393.99 | 86.987 | 28.871 | 66.733 | 30.238
| 19.3042 | 326.377 | 399.113 | 86.981 | 28.874 | 66.734 | 30.244
| 19.3056 | 326.064 | 398.747 | 87.03 | 28.872 | 66.801 | 30.25
| 19.3069 | 326.492 | 398.237 | 87.044 | 28.873 | 66.849 | 30.257
| 19.3083 | 325.977 | 397.995 | 87.061 | 28.875 | 66.891 | 30.264
| 19.3097 | 325.974 | 398.356 | 87.076 | 28.879 | 66.917 | 30.273
| 19.3111 | 326.262 | 397.805 | 87.082 | 28.879 | 66.939 | 30.279
| 19.3125 | 329.306 | 400.891 | 87.132 | 28.881 | 67.009 | 30.288
| 19.3139 | 329.411 | 401.187 | 87.18 | 28.879 | 67.088 | 30.299
| 19.3153 | 328.456 | 401.995 | 87.228 | 28.879 | 67.147 | 30.304
| 19.3167 | 328.392 | 400.318 | 87.255 | 28.883 | 67.195 | 30.314
| 19.3181 | 328.781 | 401.34 | 87.281 | 28.888 | 67.235 | 30.318
| 19.3194 | 328.899 | 400.844 | 87.31 | 28.887 | 67.276 | 30.329
| 19.3208 | 328.827 | 400.653 | 87.335 | 28.888 | 67.308 | 30.33
| 19.3222 | 328.659 | 401.125 | 87.359 | 28.893 | 67.343 | 30.343
| 19.3236 | 328.427 | 400.686 | 87.392 | 28.892 | 67.382 | 30.345
| 19.325 | 328.795 | 400.398 | 87.414 | 28.893 | 67.411 | 30.358
| 19.3264 | 327.611 | 400.947 | 87.426 | 28.896 | 67.425 | 30.364
| 19.3278 | 327.854 | 399.852 | 87.439 | 28.896 | 67.436 | 30.371
| 19.3292 | 327.918 | 399.279 | 87.452 | 28.899 | 67.448 | 30.386
| 19.3306 | 328.33 | 399.899 | 87.464 | 28.902 | 67.462 | 30.388
| 19.3319 | 327.022 | 400.299 | 87.478 | 28.905 | 67.47 | 30.397
| 19.3333 | 326.402 | 398.594 | 87.472 | 28.907 | 67.469 | 30.404
| 19.3347 | 327.333 | 398.546 | 87.478 | 28.905 | 67.475 | 30.41
| 19.3361 | 326.83 | 398.767 | 87.474 | 28.913 | 67.465 | 30.418
| 19.3375 | 326.342 | 398.377 | 87.472 | 28.913 | 67.463 | 30.428
| 19.3389 | 326.39 | 398.478 | 87.471 | 28.916 | 67.472 | 30.439
| 19.3403 | 326.079 | 398.983 | 87.472 | 28.917 | 67.471 | 30.444
| 19.3417 | 327.712 | 398.751 | 87.483 | 28.919 | 67.48 | 30.452
| 19.3431 | 326.52 | 399.105 | 87.5 | 28.92 | 67.504 | 30.459
| 19.3444 | 326.103 | 398.834 | 87.498 | 28.921 | 67.511 | 30.469
| 19.3458 | 328.507 | 400.788 | 87.509 | 28.925 | 67.526 | 30.476
| 19.3472 | 328.294 | 401.599 | 87.553 | 28.927 | 67.587 | 30.48
| 19.3486 | 328.516 | 400.375 | 87.585 | 28.932 | 67.636 | 30.491
| 19.35 | 328.78 | 400.434 | 87.603 | 28.933 | 67.664 | 30.495
| 19.3514 | 327.955 | 400.764 | 87.618 | 28.934 | 67.694 | 30.505
| 19.3528 | 328.023 | 400.264 | 87.635 | 28.938 | 67.717 | 30.511
| 19.3542 | 328.655 | 400.041 | 87.657 | 28.936 | 67.741 | 30.52
| 19.3556 | 328.792 | 400.461 | 87.675 | 28.94 | 67.767 | 30.529
| 19.3569 | 328.75 | 400.06 | 87.691 | 28.939 | 67.788 | 30.538
| 19.3583 | 328.88 | 400.451 | 87.706 | 28.943 | 67.808 | 30.549
| 19.3597 | 328.577 | 400.581 | 87.725 | 28.948 | 67.829 | 30.554
| 19.3611 | 327.891 | 401.179 | 87.747 | 28.948 | 67.857 | 30.562
| 19.3625 | 328.76 | 401.611 | 87.759 | 28.951 | 67.88 | 30.569
| 19.3639 | 328.743 | 400.553 | 87.777 | 28.956 | 67.892 | 30.575
| 19.3653 | 328.09 | 400.849 | 87.781 | 28.957 | 67.904 | 30.583
| 19.3667 | 328.987 | 400.644 | 87.802 | 28.959 | 67.919 | 30.592
| 19.3681 | 329.463 | 400.827 | 87.818 | 28.964 | 67.939 | 30.599
| 19.3694 | 328.344 | 401.586 | 87.836 | 28.963 | 67.961 | 30.61
| 19.3708 | 327.598 | 400.744 | 87.85 | 28.968 | 67.981 | 30.619
| 19.3722 | 328.759 | 400.162 | 87.86 | 28.971 | 67.997 | 30.625
| 19.3736 | 327.57 | 399.957 | 87.86 | 28.974 | 67.999 | 30.629
| 19.375 | 327.354 | 399.807 | 87.861 | 28.979 | 67.997 | 30.639
| 19.3764 | 327.49 | 400.314 | 87.856 | 28.979 | 67.995 | 30.648
| 19.3778 | 327.562 | 399.993 | 87.861 | 28.977 | 67.998 | 30.656
| 19.3792 | 327.169 | 400.079 | 87.864 | 28.984 | 68.006 | 30.66
| 19.3806 | 327.281 | 399.266 | 87.863 | 28.983 | 68.003 | 30.672
| 19.3819 | 327.912 | 399.272 | 87.863 | 28.984 | 68.002 | 30.682
| 19.3833 | 327.03 | 398.239 | 87.859 | 28.988 | 68.008 | 30.686
| 19.3847 | 327.335 | 398.686 | 87.859 | 28.984 | 68.01 | 30.695
| 19.3861 | 327.622 | 399.033 | 87.861 | 28.995 | 68.014 | 30.705
| 19.3875 | 327.377 | 400.439 | 87.862 | 28.996 | 68.024 | 30.71
| 19.3889 | 328.317 | 400.8 | 87.877 | 28.998 | 68.054 | 30.719
| 19.3903 | 328.725 | 400.177 | 87.902 | 28.998 | 68.081 | 30.726
| 19.3917 | 328.052 | 400.845 | 87.908 | 29.001 | 68.102 | 30.733
| 19.3931 | 327.991 | 401.034 | 87.922 | 29.001 | 68.129 | 30.743
| 19.3944 | 328.177 | 400.63 | 87.934 | 29.004 | 68.149 | 30.746
| 19.3958 | 328.197 | 401.667 | 87.94 | 29.007 | 68.163 | 30.758
| 19.3972 | 328.395 | 401.418 | 87.959 | 29.01 | 68.194 | 30.766
| 19.3986 | 328.24 | 401.445 | 87.974 | 29.007 | 68.221 | 30.772
| 19.4 | 327.543 | 400.72 | 87.986 | 29.013 | 68.239 | 30.777
| 19.4014 | 328.106 | 400.928 | 87.984 | 29.013 | 68.249 | 30.784
| 19.4028 | 327.71 | 400.017 | 87.983 | 29.014 | 68.246 | 30.796
| 19.4042 | 327.853 | 399.629 | 87.98 | 29.018 | 68.244 | 30.802
| 19.4056 | 326.964 | 400.115 | 87.98 | 29.021 | 68.254 | 30.809
| 19.4069 | 329.077 | 445.511 | 88.008 | 29.022 | 69.207 | 30.817
| 19.4083 | 328.787 | 445.004 | 88.036 | 29.02 | 69.959 | 30.82
| 19.4097 | 328.959 | 444.475 | 88.051 | 29.028 | 70.547 | 30.831
| 19.4111 | 329.276 | 445.052 | 88.063 | 29.027 | 71.03 | 30.836
| 19.4125 | 328.657 | 444.797 | 88.086 | 29.029 | 71.454 | 30.85
| 19.4139 | 328.329 | 445.016 | 88.094 | 29.031 | 71.819 | 30.859
| 19.4153 | 328.968 | 443.762 | 88.108 | 29.034 | 72.145 | 30.863
| 19.4167 | 328.127 | 444.988 | 88.124 | 29.034 | 72.435 | 30.869
| 19.4181 | 328.399 | 444.783 | 88.127 | 29.04 | 72.697 | 30.878
| 19.4194 | 328.419 | 444.102 | 88.134 | 29.04 | 72.926 | 30.892
| 19.4208 | 328.672 | 443.5 | 88.143 | 29.042 | 73.138 | 30.901
| 19.4222 | 329.07 | 453.829 | 88.156 | 29.04 | 73.518 | 30.908
| 19.4236 | 327.8 | 452.441 | 88.167 | 29.045 | 73.855 | 30.924
| 19.425 | 327.863 | 452.36 | 88.166 | 29.052 | 74.14 | 30.935
| 19.4264 | 327.876 | 452.022 | 88.172 | 29.05 | 74.385 | 30.941
| 19.4278 | 327.957 | 452.376 | 88.174 | 29.052 | 74.624 | 30.957
| 19.4292 | 327.903 | 451.946 | 88.183 | 29.053 | 74.831 | 30.971
| 19.4306 | 328.832 | 451.357 | 88.192 | 29.057 | 75.03 | 30.983
| 19.4319 | 328.346 | 451.205 | 88.194 | 29.06 | 75.208 | 31.004
| 19.4333 | 328.115 | 452.47 | 88.201 | 29.058 | 75.377 | 31.013
| 19.4347 | 328.441 | 452.795 | 88.203 | 29.062 | 75.534 | 31.031
| 19.4361 | 328.587 | 452.286 | 88.222 | 29.066 | 75.698 | 31.051
| 19.4375 | 329.218 | 451.812 | 88.232 | 29.065 | 75.847 | 31.067
| 19.4389 | 328.776 | 451.394 | 88.245 | 29.07 | 75.993 | 31.089
| 19.4403 | 328.745 | 451.203 | 88.247 | 29.071 | 76.125 | 31.102
| 19.4417 | 329.436 | 452.779 | 88.262 | 29.071 | 76.252 | 31.123
| 19.4431 | 327.904 | 451.788 | 88.261 | 29.073 | 76.358 | 31.14
| 19.4444 | 328.537 | 452.074 | 88.258 | 29.078 | 76.47 | 31.162
| 19.4458 | 328.686 | 451.021 | 88.269 | 29.078 | 76.578 | 31.184
| 19.4472 | 328.951 | 451.185 | 88.271 | 29.083 | 76.671 | 31.202
| 19.4486 | 327.964 | 452.263 | 88.278 | 29.08 | 76.777 | 31.227
| 19.45 | 328.237 | 451.006 | 88.277 | 29.087 | 76.873 | 31.245
| 19.4514 | 328.363 | 451.815 | 88.283 | 29.089 | 76.961 | 31.271
| 19.4528 | 327.783 | 451.313 | 88.278 | 29.092 | 77.049 | 31.292
| 19.4542 | 328.561 | 451.1 | 88.281 | 29.091 | 77.131 | 31.315
| 19.4556 | 328.862 | 453.197 | 88.293 | 29.092 | 77.225 | 31.335
| 19.4569 | 329.059 | 453.46 | 88.315 | 29.091 | 77.346 | 31.357
| 19.4583 | 329.44 | 452.572 | 88.336 | 29.096 | 77.461 | 31.382
| 19.4597 | 329.355 | 453.898 | 88.359 | 29.094 | 77.576 | 31.403
| 19.4611 | 330.031 | 454.972 | 88.389 | 29.097 | 77.703 | 31.427
| 19.4625 | 330.115 | 453.805 | 88.421 | 29.1 | 77.819 | 31.452
| 19.4639 | 330.535 | 453.613 | 88.44 | 29.101 | 77.927 | 31.476
| 19.4653 | 329.581 | 454 | 88.452 | 29.108 | 78.026 | 31.502
| 19.4667 | 329.389 | 452.083 | 88.47 | 29.108 | 78.109 | 31.527
| 19.4681 | 329.037 | 452.921 | 88.476 | 29.106 | 78.19 | 31.549
| 19.4694 | 329.594 | 453.64 | 88.48 | 29.111 | 78.27 | 31.574
| 19.4708 | 330.355 | 453.66 | 88.51 | 29.115 | 78.371 | 31.6
| 19.4722 | 329.654 | 454.44 | 88.529 | 29.117 | 78.462 | 31.624
| 19.4736 | 328.748 | 452.643 | 88.539 | 29.117 | 78.543 | 31.647
| 19.475 | 328.319 | 452.382 | 88.533 | 29.119 | 78.588 | 31.669
| 19.4764 | 328.768 | 452.046 | 88.528 | 29.122 | 78.627 | 31.698
| 19.4778 | 329.255 | 451.954 | 88.526 | 29.122 | 78.689 | 31.722
| 19.4792 | 328.384 | 451.851 | 88.526 | 29.125 | 78.743 | 31.75
| 19.4806 | 328.573 | 451.068 | 88.519 | 29.125 | 78.787 | 31.768
| 19.4819 | 328.719 | 451.324 | 88.523 | 29.126 | 78.847 | 31.797
| 19.4833 | 329.056 | 451.835 | 88.529 | 29.131 | 78.91 | 31.827
| 19.4847 | 328.21 | 451.919 | 88.531 | 29.135 | 78.973 | 31.848
| 19.4861 | 328.536 | 451.267 | 88.53 | 29.135 | 79.034 | 31.876
| 19.4875 | 328.194 | 451.931 | 88.522 | 29.139 | 79.084 | 31.896
| 19.4889 | 327.998 | 451.152 | 88.528 | 29.14 | 79.148 | 31.923
| 19.4903 | 328.547 | 450.904 | 88.531 | 29.139 | 79.199 | 31.954
| 19.4917 | 327.943 | 451.997 | 88.53 | 29.139 | 79.257 | 31.977
| 19.4931 | 328.085 | 452.063 | 88.525 | 29.142 | 79.311 | 31.996
| 19.4944 | 328.754 | 450.824 | 88.528 | 29.149 | 79.369 | 32.024
| 19.4958 | 328.071 | 452.032 | 88.529 | 29.151 | 79.433 | 32.051
| 19.4972 | 328.382 | 452.047 | 88.531 | 29.15 | 79.492 | 32.076
| 19.4986 | 328.957 | 450.864 | 88.529 | 29.153 | 79.541 | 32.097
| 19.5 | 328.536 | 450.623 | 88.525 | 29.156 | 79.599 | 32.123
| 19.5014 | 328.423 | 451.704 | 88.523 | 29.154 | 79.646 | 32.152
| 19.5028 | 328.328 | 451.471 | 88.526 | 29.154 | 79.707 | 32.176
| 19.5042 | 328.538 | 450.875 | 88.529 | 29.161 | 79.761 | 32.199
| 19.5056 | 328.567 | 452.772 | 88.525 | 29.159 | 79.817 | 32.22
| 19.5069 | 329.266 | 452.007 | 88.539 | 29.162 | 79.894 | 32.249
| 19.5083 | 328.814 | 450.967 | 88.546 | 29.162 | 79.958 | 32.274
| 19.5097 | 328.553 | 451.761 | 88.555 | 29.16 | 80.025 | 32.296
| 19.5111 | 329.16 | 452.972 | 88.562 | 29.168 | 80.091 | 32.322
| 19.5125 | 328.639 | 452.538 | 88.577 | 29.169 | 80.168 | 32.345
| 19.5139 | 329.218 | 453.855 | 88.586 | 29.17 | 80.235 | 32.372
| 19.5153 | 329.687 | 454.139 | 88.605 | 29.171 | 80.32 | 32.393
| 19.5167 | 329.596 | 453.077 | 88.62 | 29.171 | 80.396 | 32.42
| 19.5181 | 329.892 | 453.711 | 88.638 | 29.173 | 80.474 | 32.443
| 19.5194 | 329.785 | 454.714 | 88.663 | 29.177 | 80.558 | 32.468
| 19.5208 | 329.356 | 453.513 | 88.667 | 29.176 | 80.627 | 32.49
| 19.5222 | 329.707 | 454.61 | 88.685 | 29.176 | 80.697 | 32.514
| 19.5236 | 329.675 | 454.698 | 88.705 | 29.184 | 80.781 | 32.539
| 19.525 | 330.404 | 453.441 | 88.719 | 29.184 | 80.854 | 32.565
| 19.5264 | 330.333 | 453.319 | 88.734 | 29.188 | 80.92 | 32.584
| 19.5278 | 330.626 | 453.666 | 88.757 | 29.186 | 81.001 | 32.61
| 19.5292 | 330.861 | 454.086 | 88.785 | 29.19 | 81.081 | 32.634
| 19.5306 | 330.388 | 455.153 | 88.796 | 29.194 | 81.152 | 32.657
| 19.5319 | 331.323 | 454.622 | 88.812 | 29.193 | 81.218 | 32.678
| 19.5333 | 330.659 | 454.177 | 88.835 | 29.194 | 81.296 | 32.708
| 19.5347 | 330.306 | 455.231 | 88.854 | 29.198 | 81.369 | 32.723
| 19.5361 | 330.974 | 454.796 | 88.874 | 29.199 | 81.436 | 32.753
| 19.5375 | 330.711 | 454.805 | 88.897 | 29.201 | 81.514 | 32.771
| 19.5389 | 330.203 | 455.235 | 88.917 | 29.205 | 81.581 | 32.796
| 19.5403 | 331.269 | 454.248 | 88.933 | 29.203 | 81.642 | 32.817
| 19.5417 | 330.679 | 453.417 | 88.947 | 29.207 | 81.701 | 32.842
| 19.5431 | 330.419 | 455.11 | 88.953 | 29.209 | 81.751 | 32.863
| 19.5444 | 331.458 | 454.54 | 88.976 | 29.21 | 81.814 | 32.888
| 19.5458 | 324.71 | 446.288 | 88.867 | 29.215 | 81.706 | 32.913
| 19.5472 | 324.138 | 447.78 | 88.778 | 29.214 | 81.609 | 32.936
| 19.5486 | 323.987 | 447.44 | 88.725 | 29.218 | 81.551 | 32.961
| 19.55 | 324.027 | 447.712 | 88.674 | 29.219 | 81.515 | 32.982
| 19.5514 | 324.011 | 447.733 | 88.633 | 29.223 | 81.489 | 33.007
| 19.5528 | 324.584 | 448.18 | 88.594 | 29.222 | 81.485 | 33.028
| 19.5542 | 325.202 | 447.283 | 88.563 | 29.224 | 81.486 | 33.051
| 19.5556 | 324.41 | 448.173 | 88.534 | 29.224 | 81.496 | 33.07
| 19.5569 | 323.957 | 446.713 | 88.485 | 29.225 | 81.489 | 33.09
| 19.5583 | 323.674 | 446.351 | 88.44 | 29.226 | 81.481 | 33.115
| 19.5597 | 323.44 | 445.865 | 88.405 | 29.227 | 81.481 | 33.142
| 19.5611 | 323.897 | 447.349 | 88.362 | 29.228 | 81.487 | 33.163
| 19.5625 | 323.031 | 446.207 | 88.331 | 29.228 | 81.503 | 33.182
| 19.5639 | 324.195 | 447.554 | 88.296 | 29.228 | 81.515 | 33.206
| 19.5653 | 323.806 | 446.618 | 88.264 | 29.231 | 81.538 | 33.227
| 19.5667 | 324.674 | 446.305 | 88.235 | 29.227 | 81.561 | 33.246
| 19.5681 | 323.87 | 446.463 | 88.2 | 29.229 | 81.58 | 33.265
| 19.5694 | 324.647 | 446.044 | 88.171 | 29.231 | 81.604 | 33.291
| 19.5708 | 324.409 | 446.26 | 88.145 | 29.23 | 81.624 | 33.309
| 19.5722 | 323.7 | 447.372 | 88.112 | 29.232 | 81.647 | 33.331
| 19.5736 | 324.199 | 446.87 | 88.084 | 29.232 | 81.678 | 33.352
| 19.575 | 324.727 | 446.906 | 88.064 | 29.227 | 81.711 | 33.373
| 19.5764 | 324.525 | 446.699 | 88.041 | 29.229 | 81.747 | 33.393
| 19.5778 | 324.364 | 446.677 | 88.021 | 29.228 | 81.777 | 33.417
| 19.5792 | 324.242 | 446.913 | 87.995 | 29.229 | 81.808 | 33.436
| 19.5806 | 325.015 | 446.603 | 87.977 | 29.231 | 81.85 | 33.45
| 19.5819 | 324.831 | 446.343 | 87.958 | 29.231 | 81.896 | 33.473
| 19.5833 | 324.076 | 447.684 | 87.937 | 29.228 | 81.927 | 33.492
| 19.5847 | 324.836 | 446.88 | 87.923 | 29.225 | 81.964 | 33.511
| 19.5861 | 324.744 | 447.057 | 87.903 | 29.23 | 81.995 | 33.533
| 19.5875 | 324.001 | 446.73 | 87.885 | 29.228 | 82.031 | 33.549
| 19.5889 | 325.105 | 447.125 | 87.869 | 29.229 | 82.069 | 33.567
| 19.5903 | 325.02 | 446.859 | 87.847 | 29.225 | 82.107 | 33.587
| 19.5917 | 324.733 | 446.444 | 87.837 | 29.225 | 82.144 | 33.606
| 19.5931 | 323.981 | 446.708 | 87.821 | 29.226 | 82.17 | 33.627
| 19.5944 | 324.291 | 446.684 | 87.8 | 29.224 | 82.196 | 33.641
| 19.5958 | 324.674 | 448.56 | 87.787 | 29.227 | 82.236 | 33.659
| 19.5972 | 325.111 | 448.143 | 87.781 | 29.226 | 82.28 | 33.68
| 19.5986 | 324.403 | 448.175 | 87.769 | 29.225 | 82.328 | 33.697
| 19.6 | 324.988 | 446.818 | 87.751 | 29.227 | 82.357 | 33.717
| 19.6014 | 324.919 | 446.734 | 87.741 | 29.222 | 82.39 | 33.738
| 19.6028 | 323.97 | 447.195 | 87.723 | 29.226 | 82.417 | 33.752
| 19.6042 | 323.994 | 445.793 | 87.691 | 29.224 | 82.421 | 33.768
| 19.6056 | 324.024 | 445.641 | 87.658 | 29.225 | 82.419 | 33.788
| 19.6069 | 322.808 | 446.285 | 87.629 | 29.219 | 82.421 | 33.804
| 19.6083 | 324.071 | 445.698 | 87.607 | 29.224 | 82.429 | 33.823
| 19.6097 | 323.679 | 446.521 | 87.585 | 29.222 | 82.442 | 33.84
| 19.6111 | 322.94 | 446.014 | 87.561 | 29.223 | 82.46 | 33.857
| 19.6125 | 322.898 | 446.01 | 87.539 | 29.22 | 82.468 | 33.876
| 19.6139 | 323.659 | 445.197 | 87.511 | 29.224 | 82.474 | 33.895
| 19.6153 | 323.89 | 446.287 | 87.499 | 29.222 | 82.501 | 33.909
| 19.6167 | 323.981 | 445.85 | 87.486 | 29.219 | 82.534 | 33.924
| 19.6181 | 323.788 | 446.924 | 87.471 | 29.218 | 82.566 | 33.944
| 19.6194 | 323.897 | 447.051 | 87.461 | 29.215 | 82.61 | 33.967
| 19.6208 | 323.611 | 445.751 | 87.454 | 29.213 | 82.639 | 33.98
| 19.6222 | 323.973 | 446.264 | 87.44 | 29.21 | 82.669 | 33.995
| 19.6236 | 323.642 | 446.985 | 87.422 | 29.215 | 82.699 | 34.011
| 19.625 | 323.423 | 446.322 | 87.409 | 29.212 | 82.728 | 34.027
| 19.6264 | 323.468 | 446.325 | 87.393 | 29.214 | 82.749 | 34.045
| 19.6278 | 323.976 | 446.823 | 87.388 | 29.211 | 82.787 | 34.063
| 19.6292 | 324.859 | 446.655 | 87.381 | 29.208 | 82.825 | 34.081
| 19.6306 | 323.944 | 447.123 | 87.378 | 29.208 | 82.866 | 34.095
| 19.6319 | 323.925 | 446.648 | 87.365 | 29.209 | 82.89 | 34.111
| 19.6333 | 323.742 | 446.852 | 87.346 | 29.208 | 82.908 | 34.128
| 19.6347 | 324.338 | 445.995 | 87.338 | 29.21 | 82.931 | 34.146
| 19.6361 | 323.668 | 447.062 | 87.323 | 29.209 | 82.956 | 34.162
| 19.6375 | 323.428 | 444.461 | 87.306 | 29.21 | 82.972 | 34.178
| 19.6389 | 323.187 | 444.522 | 87.287 | 29.206 | 82.974 | 34.193
| 19.6403 | 322.429 | 445.425 | 87.266 | 29.206 | 82.99 | 34.207
| 19.6417 | 322.867 | 445.898 | 87.244 | 29.207 | 82.995 | 34.223
| 19.6431 | 323.831 | 445.231 | 87.235 | 29.207 | 83.014 | 34.241
| 19.6444 | 323.571 | 446.226 | 87.228 | 29.202 | 83.035 | 34.256
| 19.6458 | 322.817 | 445.536 | 87.209 | 29.203 | 83.058 | 34.27
| 19.6472 | 323.297 | 444.804 | 87.195 | 29.205 | 83.077 | 34.29
| 19.6486 | 323.517 | 445.104 | 87.182 | 29.205 | 83.1 | 34.303
| 19.65 | 323.564 | 445.948 | 87.177 | 29.207 | 83.128 | 34.321
| 19.6514 | 324.264 | 445.919 | 87.17 | 29.203 | 83.155 | 34.336
| 19.6528 | 324.485 | 445.809 | 87.159 | 29.203 | 83.188 | 34.346
| 19.6542 | 324.298 | 445.805 | 87.159 | 29.202 | 83.224 | 34.366
| 19.6556 | 324.013 | 446.7 | 87.157 | 29.203 | 83.256 | 34.378
| 19.6569 | 324.22 | 445.533 | 87.146 | 29.201 | 83.28 | 34.394
| 19.6583 | 324.363 | 445.615 | 87.146 | 29.199 | 83.316 | 34.414
| 19.6597 | 324.236 | 445.611 | 87.139 | 29.201 | 83.342 | 34.43
| 19.6611 | 324.024 | 446.712 | 87.135 | 29.201 | 83.367 | 34.438
| 19.6625 | 323.478 | 446.14 | 87.129 | 29.199 | 83.393 | 34.456
| 19.6639 | 324.154 | 445.566 | 87.118 | 29.2 | 83.405 | 34.472
| 19.6653 | 323.2 | 446.561 | 87.117 | 29.201 | 83.432 | 34.485
| 19.6667 | 323.718 | 444.971 | 87.104 | 29.201 | 83.447 | 34.5
| 19.6681 | 324.426 | 445.979 | 87.096 | 29.201 | 83.474 | 34.512
| 19.6694 | 323.712 | 444.989 | 87.094 | 29.199 | 83.499 | 34.533
| 19.6708 | 324.321 | 447.369 | 87.089 | 29.199 | 83.534 | 34.55
| 19.6722 | 324.622 | 446.96 | 87.098 | 29.199 | 83.578 | 34.565
| 19.6736 | 323.962 | 447.551 | 87.103 | 29.198 | 83.621 | 34.575
| 19.675 | 323 | 446.058 | 87.101 | 29.195 | 83.655 | 34.59
| 19.6764 | 323.972 | 446.026 | 87.095 | 29.196 | 83.673 | 34.603
| 19.6778 | 325.372 | 447.204 | 87.091 | 29.199 | 83.696 | 34.618
| 19.6792 | 324.824 | 447.467 | 87.1 | 29.198 | 83.74 | 34.633
| 19.6806 | 324.523 | 447.427 | 87.1 | 29.197 | 83.776 | 34.648
| 19.6819 | 324.572 | 446.107 | 87.096 | 29.196 | 83.799 | 34.659
| 19.6833 | 324.076 | 447.682 | 87.096 | 29.198 | 83.812 | 34.674
| 19.6847 | 324.654 | 446.36 | 87.088 | 29.195 | 83.84 | 34.69
| 19.6861 | 323.827 | 446.261 | 87.083 | 29.196 | 83.857 | 34.703
| 19.6875 | 324.527 | 446.388 | 87.078 | 29.197 | 83.873 | 34.72
| 19.6889 | 324.331 | 445.904 | 87.079 | 29.195 | 83.898 | 34.731
| 19.6903 | 325.121 | 446.697 | 87.077 | 29.193 | 83.923 | 34.744
| 19.6917 | 324.49 | 447.329 | 87.083 | 29.197 | 83.963 | 34.763
| 19.6931 | 325.181 | 448.229 | 87.09 | 29.198 | 84.005 | 34.774
| 19.6944 | 325.31 | 447.755 | 87.094 | 29.197 | 84.042 | 34.787
| 19.6958 | 325.512 | 447.246 | 87.099 | 29.196 | 84.083 | 34.801
| 19.6972 | 325.504 | 447.267 | 87.11 | 29.197 | 84.113 | 34.822
| 19.6986 | 324.564 | 448.175 | 87.109 | 29.2 | 84.145 | 34.833
| 19.7 | 323.732 | 446.981 | 87.11 | 29.194 | 84.171 | 34.842
| 19.7014 | 324.383 | 447.96 | 87.11 | 29.194 | 84.19 | 34.859
| 19.7028 | 325.074 | 447.246 | 87.113 | 29.197 | 84.211 | 34.877
| 19.7042 | 325.067 | 447.208 | 87.109 | 29.197 | 84.225 | 34.887
| 19.7056 | 324.684 | 447.836 | 87.117 | 29.196 | 84.257 | 34.9
| 19.7069 | 324.68 | 447.413 | 87.12 | 29.198 | 84.281 | 34.917
| 19.7083 | 324.607 | 448.042 | 87.119 | 29.195 | 84.305 | 34.929
| 19.7097 | 325.301 | 447.207 | 87.119 | 29.197 | 84.328 | 34.939
| 19.7111 | 324.433 | 447.891 | 87.112 | 29.198 | 84.339 | 34.961
| 19.7125 | 323.702 | 447.094 | 87.111 | 29.197 | 84.349 | 34.968
| 19.7139 | 324.531 | 446.858 | 87.106 | 29.196 | 84.363 | 34.984
| 19.7153 | 324.518 | 445.787 | 87.094 | 29.196 | 84.364 | 34.998
| 19.7167 | 324.124 | 445.569 | 87.084 | 29.202 | 84.371 | 35.013
| 19.7181 | 324.108 | 446.33 | 87.081 | 29.198 | 84.377 | 35.024
| 19.7194 | 324.097 | 445.725 | 87.069 | 29.202 | 84.377 | 35.038
| 19.7208 | 323.697 | 445.244 | 87.057 | 29.199 | 84.38 | 35.052
| 19.7222 | 323.316 | 444.498 | 87.034 | 29.2 | 84.37 | 35.063
| 19.7236 | 321.26 | 441.971 | 87.006 | 29.2 | 84.364 | 35.077
| 19.725 | 319.956 | 441.836 | 86.946 | 29.198 | 84.288 | 35.094
| 19.7264 | 321.475 | 450.763 | 86.902 | 29.202 | 84.289 | 35.107
| 19.7278 | 321.062 | 450.188 | 86.866 | 29.2 | 84.455 | 35.118
| 19.7292 | 320.158 | 450.233 | 86.825 | 29.202 | 84.555 | 35.127
| 19.7306 | 320.852 | 449.172 | 86.788 | 29.203 | 84.642 | 35.145
| 19.7319 | 320.253 | 449.275 | 86.75 | 29.198 | 84.706 | 35.157
| 19.7333 | 319.47 | 449.331 | 86.709 | 29.199 | 84.758 | 35.167
| 19.7347 | 320.433 | 448.827 | 86.662 | 29.198 | 84.79 | 35.18
| 19.7361 | 319.972 | 449.779 | 86.621 | 29.196 | 84.823 | 35.199
| 19.7375 | 319.312 | 448.733 | 86.586 | 29.193 | 84.854 | 35.211
| 19.7389 | 319.881 | 448.513 | 86.547 | 29.191 | 84.886 | 35.223
| 19.7403 | 319.863 | 447.823 | 86.511 | 29.192 | 84.904 | 35.237
| 19.7417 | 319.25 | 447.711 | 86.471 | 29.193 | 84.926 | 35.249
| 19.7431 | 318.882 | 449.106 | 86.428 | 29.194 | 84.939 | 35.26
| 19.7444 | 319.067 | 447.842 | 86.39 | 29.192 | 84.972 | 35.271
| 19.7458 | 319.548 | 447.865 | 86.351 | 29.188 | 84.99 | 35.289
| 19.7472 | 318.913 | 448.009 | 86.319 | 29.186 | 85.01 | 35.297
| 19.7486 | 319.428 | 447.688 | 86.281 | 29.188 | 85.033 | 35.312
| 19.75 | 324.417 | 448.688 | 86.323 | 29.186 | 85.046 | 35.324
| 19.7514 | 324.439 | 447.712 | 86.387 | 29.189 | 85.064 | 35.343
| 19.7528 | 325.648 | 448.982 | 86.437 | 29.184 | 85.094 | 35.352
| 19.7542 | 325.298 | 449.406 | 86.485 | 29.183 | 85.134 | 35.365
| 19.7556 | 326.228 | 448.942 | 86.525 | 29.179 | 85.182 | 35.377
| 19.7569 | 325.057 | 448.157 | 86.552 | 29.179 | 85.223 | 35.393
| 19.7583 | 325.487 | 450.069 | 86.581 | 29.178 | 85.256 | 35.406
| 19.7597 | 326.441 | 449.241 | 86.609 | 29.179 | 85.298 | 35.417
| 19.7611 | 326.436 | 449.169 | 86.638 | 29.177 | 85.328 | 35.43
| 19.7625 | 325.23 | 449.863 | 86.67 | 29.177 | 85.371 | 35.443
| 19.7639 | 326.779 | 449.685 | 86.696 | 29.179 | 85.409 | 35.455
| 19.7653 | 326.598 | 450.162 | 86.723 | 29.177 | 85.447 | 35.472
| 19.7667 | 325.975 | 450.047 | 86.756 | 29.172 | 85.49 | 35.481
| 19.7681 | 327.406 | 450.507 | 86.785 | 29.178 | 85.529 | 35.492
| 19.7694 | 326.823 | 449.745 | 86.817 | 29.179 | 85.57 | 35.506
| 19.7708 | 326.502 | 450.751 | 86.841 | 29.178 | 85.605 | 35.517
| 19.7722 | 326.054 | 450.824 | 86.861 | 29.18 | 85.631 | 35.534
| 19.7736 | 326.436 | 450.177 | 86.882 | 29.181 | 85.657 | 35.547
| 19.775 | 326.231 | 449.344 | 86.898 | 29.18 | 85.672 | 35.557
| 19.7764 | 325.466 | 450.02 | 86.919 | 29.18 | 85.689 | 35.573
| 19.7778 | 325.62 | 449.315 | 86.938 | 29.182 | 85.722 | 35.59
| 19.7792 | 326.211 | 449.686 | 86.953 | 29.183 | 85.736 | 35.6
| 19.7806 | 326.352 | 449.017 | 86.967 | 29.185 | 85.759 | 35.613
| 19.7819 | 325.786 | 449.8 | 86.989 | 29.187 | 85.774 | 35.626
| 19.7833 | 325.66 | 450.052 | 87.005 | 29.19 | 85.797 | 35.637
| 19.7847 | 326.28 | 448.776 | 87.027 | 29.189 | 85.829 | 35.65
| 19.7861 | 326.163 | 450.455 | 87.045 | 29.187 | 85.859 | 35.669
| 19.7875 | 326.5 | 450.736 | 87.071 | 29.188 | 85.897 | 35.679
| 19.7889 | 326.501 | 450.877 | 87.094 | 29.194 | 85.942 | 35.693
| 19.7903 | 326.33 | 450.577 | 87.113 | 29.19 | 85.969 | 35.705
| 19.7917 | 326.853 | 451.881 | 87.142 | 29.193 | 86.014 | 35.718
| 19.7931 | 327.439 | 450.758 | 87.166 | 29.196 | 86.05 | 35.73
| 19.7944 | 327.351 | 450.922 | 87.192 | 29.193 | 86.086 | 35.744
| 19.7958 | 327.469 | 451.154 | 87.209 | 29.195 | 86.121 | 35.758
| 19.7972 | 327.381 | 450.25 | 87.228 | 29.196 | 86.156 | 35.77
| 19.7986 | 326.783 | 451.337 | 87.249 | 29.199 | 86.186 | 35.777
| 19.8 | 326.654 | 451.456 | 87.271 | 29.198 | 86.224 | 35.795
| 19.8014 | 327.028 | 451.566 | 87.297 | 29.199 | 86.26 | 35.806
| 19.8028 | 326.95 | 451.168 | 87.317 | 29.201 | 86.295 | 35.824
| 19.8042 | 327.509 | 451.957 | 87.34 | 29.206 | 86.331 | 35.833
| 19.8056 | 328.711 | 451.997 | 87.378 | 29.205 | 86.393 | 35.848
| 19.8069 | 328.195 | 451.48 | 87.415 | 29.205 | 86.448 | 35.858
| 19.8083 | 328.584 | 452.207 | 87.442 | 29.21 | 86.491 | 35.872
| 19.8097 | 327.914 | 453.108 | 87.472 | 29.21 | 86.542 | 35.887
| 19.8111 | 328.988 | 452.322 | 87.506 | 29.21 | 86.602 | 35.897
| 19.8125 | 328.456 | 452.972 | 87.542 | 29.209 | 86.649 | 35.911
| 19.8139 | 328.697 | 452.893 | 87.571 | 29.215 | 86.695 | 35.922
| 19.8153 | 328.659 | 452.284 | 87.6 | 29.215 | 86.739 | 35.936
| 19.8167 | 328.787 | 454.075 | 87.633 | 29.218 | 86.78 | 35.949
| 19.8181 | 329.096 | 453.427 | 87.661 | 29.218 | 86.822 | 35.962
| 19.8194 | 328.664 | 453.458 | 87.69 | 29.218 | 86.865 | 35.974
| 19.8208 | 329.002 | 453.077 | 87.717 | 29.221 | 86.904 | 35.99
| 19.8222 | 329.679 | 453.326 | 87.751 | 29.224 | 86.947 | 35.999
| 19.8236 | 329.293 | 454.744 | 87.788 | 29.225 | 86.996 | 36.014
| 19.825 | 329.677 | 455.039 | 87.831 | 29.233 | 87.063 | 36.026
| 19.8264 | 329.695 | 455.311 | 87.871 | 29.233 | 87.117 | 36.037
| 19.8278 | 329.963 | 454.46 | 87.902 | 29.237 | 87.169 | 36.05
| 19.8292 | 329.889 | 455.323 | 87.932 | 29.236 | 87.208 | 36.067
| 19.8306 | 330.027 | 454.623 | 87.973 | 29.242 | 87.257 | 36.078
| 19.8319 | 330.292 | 456.398 | 88.012 | 29.242 | 87.303 | 36.091
| 19.8333 | 330.28 | 454.962 | 88.051 | 29.245 | 87.36 | 36.103
| 19.8347 | 329.052 | 454.654 | 88.071 | 29.247 | 87.394 | 36.119
| 19.8361 | 329.423 | 455.155 | 88.095 | 29.251 | 87.418 | 36.134
| 19.8375 | 329.69 | 455.638 | 88.126 | 29.253 | 87.455 | 36.146
| 19.8389 | 330.482 | 455.744 | 88.161 | 29.256 | 87.498 | 36.158
| 19.8403 | 330.059 | 455.82 | 88.193 | 29.26 | 87.543 | 36.171
| 19.8417 | 331.038 | 455.317 | 88.22 | 29.262 | 87.584 | 36.182
| 19.8431 | 330.026 | 456.189 | 88.259 | 29.264 | 87.628 | 36.196
| 19.8444 | 330.778 | 454.938 | 88.295 | 29.267 | 87.678 | 36.212
| 19.8458 | 329.732 | 447.14 | 88.332 | 29.27 | 87.711 | 36.226
| 19.8472 | 331.728 | 448.07 | 88.369 | 29.276 | 87.545 | 36.236
| 19.8486 | 330.805 | 449.257 | 88.402 | 29.275 | 87.429 | 36.251
| 19.85 | 324.837 | 447.325 | 88.385 | 29.279 | 87.354 | 36.264
| 19.8514 | 325.709 | 448.575 | 88.31 | 29.279 | 87.307 | 36.278
| 19.8528 | 320.755 | 443.679 | 88.186 | 29.281 | 87.144 | 36.296
| 19.8542 | 321.534 | 451.059 | 88.092 | 29.287 | 87.117 | 36.307
| 19.8556 | 320.99 | 452.083 | 88.019 | 29.286 | 87.192 | 36.317
| 19.8569 | 321.211 | 451.904 | 87.955 | 29.296 | 87.242 | 36.333
| 19.8583 | 321.692 | 450.805 | 87.901 | 29.295 | 87.284 | 36.342
| 19.8597 | 321.456 | 452.1 | 87.847 | 29.297 | 87.324 | 36.356
| 19.8611 | 322.385 | 451.722 | 87.812 | 29.294 | 87.363 | 36.367
| 19.8625 | 321.543 | 450.273 | 87.757 | 29.297 | 87.39 | 36.385
| 19.8639 | 321.518 | 450.831 | 87.7 | 29.304 | 87.393 | 36.401
| 19.8653 | 320.483 | 451.187 | 87.651 | 29.295 | 87.406 | 36.409
| 19.8667 | 321.83 | 450.846 | 87.607 | 29.3 | 87.424 | 36.427
| 19.8681 | 322.309 | 451.391 | 87.563 | 29.291 | 87.44 | 36.437
| 19.8694 | 322.233 | 452.63 | 87.532 | 29.293 | 87.476 | 36.452
| 19.8708 | 321.828 | 452.897 | 87.499 | 29.293 | 87.513 | 36.462
| 19.8722 | 322.7 | 452.018 | 87.477 | 29.29 | 87.564 | 36.474
| 19.8736 | 322.25 | 453.086 | 87.447 | 29.292 | 87.602 | 36.488
| 19.875 | 322.613 | 453.885 | 87.423 | 29.292 | 87.641 | 36.498
| 19.8764 | 322.858 | 453.163 | 87.406 | 29.289 | 87.691 | 36.511
| 19.8778 | 322.855 | 453.336 | 87.383 | 29.29 | 87.742 | 36.523
| 19.8792 | 323.15 | 452.796 | 87.368 | 29.284 | 87.781 | 36.54
| 19.8806 | 323.472 | 453.171 | 87.345 | 29.288 | 87.827 | 36.548
| 19.8819 | 322.638 | 453.046 | 87.329 | 29.29 | 87.861 | 36.56
| 19.8833 | 323.068 | 453.978 | 87.314 | 29.285 | 87.905 | 36.574
| 19.8847 | 323.613 | 453.305 | 87.294 | 29.283 | 87.944 | 36.588
| 19.8861 | 323.658 | 453.443 | 87.283 | 29.285 | 87.987 | 36.6
| 19.8875 | 323.95 | 454.313 | 87.274 | 29.286 | 88.034 | 36.606
| 19.8889 | 323.949 | 455.841 | 87.268 | 29.286 | 88.089 | 36.618
| 19.8903 | 323.447 | 455.455 | 87.259 | 29.281 | 88.138 | 36.631
| 19.8917 | 323.62 | 453.172 | 87.235 | 29.285 | 88.165 | 36.644
| 19.8931 | 323.723 | 453.842 | 87.228 | 29.28 | 88.189 | 36.656
| 19.8944 | 323.293 | 454.083 | 87.214 | 29.279 | 88.218 | 36.669
| 19.8958 | 323.668 | 453.914 | 87.197 | 29.28 | 88.242 | 36.682
| 19.8972 | 323.415 | 453.842 | 87.184 | 29.281 | 88.271 | 36.694
| 19.8986 | 323.442 | 453.117 | 87.176 | 29.279 | 88.298 | 36.705
| 19.9 | 323.117 | 453.937 | 87.158 | 29.279 | 88.321 | 36.715
| 19.9014 | 323.81 | 455.256 | 87.154 | 29.283 | 88.355 | 36.729
| 19.9028 | 324.123 | 454.72 | 87.149 | 29.284 | 88.393 | 36.741
| 19.9042 | 324.291 | 454.328 | 87.153 | 29.283 | 88.443 | 36.751
| 19.9056 | 321.898 | 453.02 | 87.148 | 29.281 | 88.478 | 36.771
| 19.9069 | 321.538 | 451.797 | 87.087 | 29.285 | 88.415 | 36.778
| 19.9083 | 322.201 | 451.223 | 87.049 | 29.282 | 88.382 | 36.789
| 19.9097 | 321.971 | 453.272 | 87.03 | 29.284 | 88.383 | 36.805
| 19.9111 | 322.717 | 452.081 | 87.007 | 29.278 | 88.389 | 36.812
| 19.9125 | 322.357 | 451.575 | 86.988 | 29.28 | 88.392 | 36.826
| 19.9139 | 322.413 | 453.002 | 86.969 | 29.278 | 88.396 | 36.84
| 19.9153 | 320.377 | 449.336 | 86.922 | 29.28 | 88.358 | 36.847
| 19.9167 | 320.678 | 449.168 | 86.874 | 29.281 | 88.308 | 36.866
| 19.9181 | 320.252 | 448.505 | 86.828 | 29.276 | 88.265 | 36.875
| 19.9194 | 319.928 | 449.215 | 86.785 | 29.277 | 88.234 | 36.887
| 19.9208 | 319.625 | 449.4 | 86.746 | 29.279 | 88.207 | 36.901
| 19.9222 | 319.718 | 448.859 | 86.695 | 29.278 | 88.181 | 36.91
| 19.9236 | 319.464 | 449.641 | 86.661 | 29.275 | 88.165 | 36.924
| 19.925 | 319.491 | 449.67 | 86.628 | 29.27 | 88.151 | 36.935
| 19.9264 | 320.077 | 448.268 | 86.6 | 29.27 | 88.139 | 36.946
| 19.9278 | 319.624 | 449.776 | 86.564 | 29.27 | 88.131 | 36.956
| 19.9292 | 320.532 | 449.17 | 86.536 | 29.267 | 88.136 | 36.971
| 19.9306 | 320.311 | 450.712 | 86.51 | 29.271 | 88.154 | 36.981
| 19.9319 | 320.742 | 450.083 | 86.498 | 29.266 | 88.174 | 36.991
| 19.9333 | 320.372 | 450.449 | 86.477 | 29.266 | 88.198 | 37.003
| 19.9347 | 320.474 | 450.489 | 86.461 | 29.265 | 88.215 | 37.017
| 19.9361 | 320.806 | 450.555 | 86.44 | 29.265 | 88.237 | 37.03
| 19.9375 | 320.789 | 450.188 | 86.428 | 29.267 | 88.262 | 37.04
| 19.9389 | 320.676 | 451.202 | 86.409 | 29.262 | 88.28 | 37.048
| 19.9403 | 321.491 | 451.252 | 86.4 | 29.261 | 88.315 | 37.061
| 19.9417 | 320.935 | 451.499 | 86.388 | 29.26 | 88.339 | 37.072
| 19.9431 | 321.687 | 450.441 | 86.377 | 29.259 | 88.37 | 37.083
| 19.9444 | 321.28 | 451.342 | 86.368 | 29.257 | 88.397 | 37.094
| 19.9458 | 321.499 | 451.71 | 86.36 | 29.259 | 88.424 | 37.105
| 19.9472 | 321.68 | 451.096 | 86.349 | 29.255 | 88.446 | 37.118
| 19.9486 | 322.088 | 450.931 | 86.342 | 29.257 | 88.473 | 37.127
| 19.95 | 321.263 | 451.575 | 86.331 | 29.254 | 88.506 | 37.132
| 19.9514 | 323.201 | 452.709 | 86.334 | 29.254 | 88.547 | 37.146
| 19.9528 | 322.993 | 452.438 | 86.341 | 29.25 | 88.603 | 37.152
| 19.9542 | 322.84 | 454.506 | 86.346 | 29.25 | 88.664 | 37.166
| 19.9556 | 322.094 | 453.685 | 86.357 | 29.25 | 88.722 | 37.178
| 19.9569 | 322.591 | 454.091 | 86.367 | 29.245 | 88.76 | 37.183
| 19.9583 | 322.926 | 453.933 | 86.368 | 29.247 | 88.806 | 37.199
| 19.9597 | 322.966 | 454.125 | 86.377 | 29.247 | 88.858 | 37.21
| 19.9611 | 323.009 | 453.794 | 86.386 | 29.25 | 88.901 | 37.22
| 19.9625 | 322.741 | 453.935 | 86.389 | 29.254 | 88.933 | 37.227
| 19.9639 | 323.747 | 453.469 | 86.398 | 29.249 | 88.97 | 37.244
| 19.9653 | 322.925 | 454.269 | 86.402 | 29.253 | 89.003 | 37.254
| 19.9667 | 323.076 | 453.121 | 86.403 | 29.248 | 89.031 | 37.263
| 19.9681 | 323.919 | 453.848 | 86.419 | 29.244 | 89.058 | 37.268
| 19.9694 | 323.398 | 455.017 | 86.432 | 29.245 | 89.098 | 37.28
| 19.9708 | 323.765 | 454.141 | 86.439 | 29.245 | 89.131 | 37.287
| 19.9722 | 324.652 | 455.253 | 86.459 | 29.243 | 89.188 | 37.3
| 19.9736 | 324.268 | 455.383 | 86.479 | 29.248 | 89.248 | 37.311
| 19.975 | 324.004 | 455.612 | 86.502 | 29.245 | 89.297 | 37.325
| 19.9764 | 324.918 | 454.759 | 86.518 | 29.24 | 89.343 | 37.33
| 19.9778 | 324.352 | 455.404 | 86.538 | 29.242 | 89.392 | 37.344
| 19.9792 | 325.239 | 455.132 | 86.557 | 29.241 | 89.437 | 37.35
| 19.9806 | 324.962 | 455.118 | 86.58 | 29.242 | 89.482 | 37.363
| 19.9819 | 320.85 | 450.284 | 86.525 | 29.242 | 89.403 | 37.377
| 19.9833 | 320.927 | 450.313 | 86.479 | 29.243 | 89.323 | 37.386
| 19.9847 | 320.31 | 450.422 | 86.449 | 29.243 | 89.274 | 37.401
| 19.9861 | 320.672 | 450.389 | 86.423 | 29.242 | 89.229 | 37.41
| 19.9875 | 320.895 | 450.933 | 86.398 | 29.244 | 89.204 | 37.418
| 19.9889 | 321.679 | 450.196 | 86.39 | 29.243 | 89.194 | 37.432
| 19.9903 | 321.752 | 451.247 | 86.389 | 29.242 | 89.208 | 37.437
| 19.9917 | 321.49 | 450.934 | 86.378 | 29.243 | 89.213 | 37.451
| 19.9931 | 320.773 | 451.249 | 86.361 | 29.243 | 89.21 | 37.461
| 19.9944 | 322.01 | 450.897 | 86.361 | 29.243 | 89.222 | 37.473
| 19.9958 | 321.686 | 450.099 | 86.34 | 29.24 | 89.211 | 37.482
| 19.9972 | 322.113 | 450.577 | 86.33 | 29.243 | 89.222 | 37.496
| 19.9986 | 321.97 | 450.796 | 86.323 | 29.241 | 89.23 | 37.505
| 20 | 321.221 | 450.88 | 86.316 | 29.245 | 89.244 | 37.521
| 20.0014 | 321.073 | 451.566 | 86.304 | 29.245 | 89.251 | 37.53
| 20.0028 | 321.537 | 451.903 | 86.296 | 29.239 | 89.26 | 37.539
| 20.0042 | 322.106 | 451.967 | 86.294 | 29.242 | 89.292 | 37.55
| 20.0056 | 321.802 | 452.666 | 86.302 | 29.244 | 89.321 | 37.561
| 20.0069 | 322.377 | 451.937 | 86.302 | 29.243 | 89.352 | 37.572
| 20.0083 | 322.503 | 452.204 | 86.302 | 29.24 | 89.378 | 37.581
| 20.0097 | 322.462 | 451.829 | 86.304 | 29.24 | 89.399 | 37.59
| 20.0111 | 322.451 | 451.799 | 86.297 | 29.241 | 89.42 | 37.6
| 20.0125 | 322.592 | 452.343 | 86.301 | 29.238 | 89.44 | 37.61
| 20.0139 | 324.151 | 453.74 | 86.311 | 29.234 | 89.488 | 37.617
| 20.0153 | 323.106 | 454.244 | 86.333 | 29.235 | 89.544 | 37.629
| 20.0167 | 322.259 | 452.721 | 86.336 | 29.238 | 89.581 | 37.642
| 20.0181 | 322.259 | 452.857 | 86.33 | 29.234 | 89.585 | 37.653
| 20.0194 | 322.235 | 452.889 | 86.322 | 29.24 | 89.593 | 37.66
| 20.0208 | 322.378 | 452.729 | 86.322 | 29.236 | 89.606 | 37.671
| 20.0222 | 322.404 | 452.08 | 86.317 | 29.236 | 89.611 | 37.679
| 20.0236 | 322.708 | 453.494 | 86.314 | 29.236 | 89.624 | 37.691
| 20.025 | 322.419 | 453.435 | 86.317 | 29.236 | 89.657 | 37.702
| 20.0264 | 322.305 | 452.666 | 86.321 | 29.239 | 89.677 | 37.709
| 20.0278 | 323.031 | 452.594 | 86.321 | 29.235 | 89.695 | 37.724
| 20.0292 | 323.031 | 452.489 | 86.327 | 29.231 | 89.725 | 37.732
| 20.0306 | 322.518 | 453.723 | 86.331 | 29.24 | 89.746 | 37.74
| 20.0319 | 322.939 | 452.633 | 86.338 | 29.237 | 89.774 | 37.752
| 20.0333 | 322.638 | 453.662 | 86.336 | 29.235 | 89.79 | 37.762
| 20.0347 | 323.608 | 453.533 | 86.347 | 29.238 | 89.822 | 37.769
| 20.0361 | 323.099 | 452.575 | 86.347 | 29.237 | 89.85 | 37.784
| 20.0375 | 322.641 | 453.501 | 86.344 | 29.236 | 89.852 | 37.791
| 20.0389 | 321.923 | 452.738 | 86.342 | 29.235 | 89.861 | 37.8
| 20.0403 | 321.459 | 452.336 | 86.331 | 29.235 | 89.855 | 37.808
| 20.0417 | 321.7 | 452.593 | 86.319 | 29.24 | 89.854 | 37.823
| 20.0431 | 322.154 | 452.043 | 86.32 | 29.239 | 89.864 | 37.828
| 20.0444 | 322.618 | 452.178 | 86.32 | 29.24 | 89.871 | 37.84
| 20.0458 | 322.415 | 452.332 | 86.32 | 29.239 | 89.882 | 37.846
| 20.0472 | 322.281 | 453.465 | 86.321 | 29.233 | 89.904 | 37.861
| 20.0486 | 323.193 | 452.57 | 86.33 | 29.239 | 89.926 | 37.873
| 20.05 | 323.13 | 452.811 | 86.332 | 29.239 | 89.949 | 37.879
| 20.0514 | 323.015 | 452.739 | 86.34 | 29.235 | 89.967 | 37.889
| 20.0528 | 320.271 | 448.985 | 86.301 | 29.235 | 89.929 | 37.894
| 20.0542 | 320.304 | 449.72 | 86.264 | 29.235 | 89.864 | 37.904
| 20.0556 | 320.319 | 450.501 | 86.235 | 29.239 | 89.838 | 37.916
| 20.0569 | 320.504 | 449.031 | 86.212 | 29.236 | 89.807 | 37.931
| 20.0583 | 320.547 | 449.886 | 86.195 | 29.236 | 89.783 | 37.939
| 20.0597 | 320.548 | 449.379 | 86.171 | 29.241 | 89.771 | 37.947
| 20.0611 | 321.058 | 449.372 | 86.155 | 29.24 | 89.76 | 37.959
| 20.0625 | 320.981 | 449.988 | 86.146 | 29.238 | 89.761 | 37.964
| 20.0639 | 320.462 | 449.738 | 86.127 | 29.237 | 89.753 | 37.977
| 20.0653 | 321.056 | 449.573 | 86.11 | 29.236 | 89.751 | 37.987
| 20.0667 | 319.926 | 450.36 | 86.094 | 29.236 | 89.749 | 37.999
| 20.0681 | 320.462 | 450.732 | 86.08 | 29.235 | 89.748 | 38.007
| 20.0694 | 320.761 | 450.427 | 86.073 | 29.236 | 89.756 | 38.011
| 20.0708 | 320.882 | 449.296 | 86.06 | 29.236 | 89.768 | 38.022
| 20.0722 | 320.829 | 449.972 | 86.048 | 29.229 | 89.765 | 38.032
| 20.0736 | 320.539 | 449.667 | 86.036 | 29.231 | 89.768 | 38.043
| 20.075 | 320.363 | 450.709 | 86.017 | 29.232 | 89.77 | 38.052
| 20.0764 | 320.86 | 449.935 | 86.007 | 29.23 | 89.776 | 38.063
| 20.0778 | 320.702 | 450.28 | 85.998 | 29.235 | 89.789 | 38.071
| 20.0792 | 320.631 | 450.981 | 85.992 | 29.232 | 89.805 | 38.079
| 20.0806 | 320.874 | 451.009 | 85.985 | 29.232 | 89.815 | 38.088
| 20.0819 | 320.34 | 450.827 | 85.973 | 29.232 | 89.822 | 38.095
| 20.0833 | 321.061 | 449.788 | 85.961 | 29.235 | 89.832 | 38.104
| 20.0847 | 321.081 | 450.376 | 85.957 | 29.227 | 89.84 | 38.115
| 20.0861 | 320.928 | 450.23 | 85.948 | 29.229 | 89.851 | 38.125
| 20.0875 | 320.677 | 450.628 | 85.943 | 29.232 | 89.866 | 38.131
| 20.0889 | 320.707 | 451.079 | 85.935 | 29.228 | 89.878 | 38.14
| 20.0903 | 320.786 | 451.645 | 85.931 | 29.227 | 89.902 | 38.149
| 20.0917 | 320.625 | 450.717 | 85.925 | 29.226 | 89.92 | 38.156
| 20.0931 | 321.112 | 451.473 | 85.924 | 29.224 | 89.937 | 38.167
| 20.0944 | 321.092 | 450.764 | 85.924 | 29.228 | 89.957 | 38.178
| 20.0958 | 321.389 | 452.084 | 85.924 | 29.225 | 89.978 | 38.183
| 20.0972 | 322.211 | 451.354 | 85.926 | 29.226 | 90.01 | 38.189
| 20.0986 | 322.15 | 452.043 | 85.94 | 29.226 | 90.053 | 38.202
| 20.1 | 322.384 | 451.708 | 85.944 | 29.228 | 90.085 | 38.204
| 20.1014 | 321.706 | 452.141 | 85.945 | 29.229 | 90.104 | 38.218
| 20.1028 | 322.145 | 451.573 | 85.949 | 29.222 | 90.127 | 38.226
| 20.1042 | 321.699 | 452.286 | 85.95 | 29.223 | 90.151 | 38.235
| 20.1056 | 321.287 | 451.752 | 85.954 | 29.221 | 90.169 | 38.24
| 20.1069 | 321.655 | 452.242 | 85.954 | 29.222 | 90.184 | 38.246
| 20.1083 | 322.228 | 451.305 | 85.955 | 29.22 | 90.204 | 38.257
| 20.1097 | 321.919 | 451.938 | 85.959 | 29.221 | 90.228 | 38.267
| 20.1111 | 322.637 | 451.856 | 85.966 | 29.224 | 90.248 | 38.277
| 20.1125 | 321.92 | 452.746 | 85.97 | 29.221 | 90.267 | 38.283
| 20.1139 | 322.217 | 452.097 | 85.977 | 29.224 | 90.295 | 38.295
| 20.1153 | 322.024 | 452.415 | 85.979 | 29.221 | 90.309 | 38.301
| 20.1167 | 322.152 | 451.995 | 85.98 | 29.22 | 90.326 | 38.309
| 20.1181 | 321.866 | 452.385 | 85.982 | 29.223 | 90.342 | 38.315
| 20.1194 | 322.265 | 451.218 | 85.986 | 29.219 | 90.352 | 38.326
| 20.1208 | 321.972 | 452.342 | 85.987 | 29.22 | 90.37 | 38.333
| 20.1222 | 321.647 | 451.901 | 85.983 | 29.221 | 90.377 | 38.343
| 20.1236 | 321.997 | 451.441 | 85.985 | 29.222 | 90.387 | 38.351
| 20.125 | 321.285 | 451.959 | 85.988 | 29.222 | 90.398 | 38.359
| 20.1264 | 321.802 | 452.25 | 85.983 | 29.223 | 90.402 | 38.369
| 20.1278 | 321.531 | 452.337 | 85.986 | 29.224 | 90.421 | 38.373
| 20.1292 | 321.567 | 452.604 | 85.99 | 29.22 | 90.432 | 38.385
| 20.1306 | 321.814 | 452.914 | 85.993 | 29.218 | 90.45 | 38.395
| 20.1319 | 321.73 | 452.563 | 85.993 | 29.216 | 90.465 | 38.403
| 20.1333 | 321.768 | 452.77 | 85.993 | 29.22 | 90.478 | 38.408
| 20.1347 | 321.482 | 452.408 | 85.993 | 29.221 | 90.489 | 38.416
| 20.1361 | 321.859 | 451.554 | 85.994 | 29.222 | 90.501 | 38.427
| 20.1375 | 321.47 | 452.325 | 85.994 | 29.223 | 90.507 | 38.435
| 20.1389 | 321.445 | 452.278 | 85.994 | 29.227 | 90.523 | 38.441
| 20.1403 | 322.046 | 450.986 | 85.995 | 29.223 | 90.525 | 38.452
| 20.1417 | 322.087 | 451.716 | 85.995 | 29.219 | 90.537 | 38.46
| 20.1431 | 321.059 | 451.682 | 85.99 | 29.222 | 90.545 | 38.467
| 20.1444 | 321.559 | 450.966 | 85.984 | 29.219 | 90.539 | 38.474
| 20.1458 | 321.375 | 451.76 | 85.975 | 29.224 | 90.55 | 38.485
| 20.1472 | 321.363 | 452.16 | 85.981 | 29.22 | 90.558 | 38.491
| 20.1486 | 321.437 | 452.447 | 85.986 | 29.219 | 90.583 | 38.503
| 20.15 | 321.806 | 453.116 | 85.985 | 29.224 | 90.614 | 38.512
| 20.1514 | 322.156 | 452.098 | 85.994 | 29.219 | 90.636 | 38.52
| 20.1528 | 322.026 | 451.953 | 85.997 | 29.224 | 90.655 | 38.523
| 20.1542 | 322.005 | 451.767 | 85.996 | 29.221 | 90.676 | 38.536
| 20.1556 | 322.168 | 451.549 | 85.992 | 29.224 | 90.69 | 38.544
| 20.1569 | 322.069 | 452.344 | 86.001 | 29.225 | 90.702 | 38.549
| 20.1583 | 322.126 | 452.349 | 86.002 | 29.223 | 90.728 | 38.558
| 20.1597 | 322.115 | 452.401 | 86.005 | 29.226 | 90.738 | 38.572
| 20.1611 | 321.685 | 452.774 | 86.005 | 29.226 | 90.752 | 38.575
| 20.1625 | 321.62 | 452.453 | 86.01 | 29.225 | 90.769 | 38.581
| 20.1639 | 322.238 | 452.173 | 86.016 | 29.223 | 90.783 | 38.594
| 20.1653 | 321.972 | 452.829 | 86.021 | 29.221 | 90.802 | 38.6
| 20.1667 | 322.588 | 451.641 | 86.017 | 29.224 | 90.818 | 38.609
| 20.1681 | 321.557 | 452.776 | 86.023 | 29.22 | 90.832 | 38.621
| 20.1694 | 322.423 | 451.712 | 86.024 | 29.224 | 90.838 | 38.63
| 20.1708 | 321.684 | 452.722 | 86.028 | 29.221 | 90.852 | 38.635
| 20.1722 | 322.074 | 450.981 | 86.026 | 29.224 | 90.856 | 38.641
| 20.1736 | 321.783 | 451.221 | 86.014 | 29.226 | 90.85 | 38.649
| 20.175 | 322.245 | 451.441 | 86.008 | 29.227 | 90.85 | 38.662
| 20.1764 | 321.763 | 451.119 | 86.008 | 29.225 | 90.859 | 38.67
| 20.1778 | 321.389 | 452.129 | 86.004 | 29.224 | 90.867 | 38.672
| 20.1792 | 322.214 | 451.254 | 86.004 | 29.228 | 90.874 | 38.685
| 20.1806 | 321.288 | 452.03 | 86.009 | 29.225 | 90.886 | 38.693
| 20.1819 | 321.629 | 451.155 | 85.999 | 29.223 | 90.89 | 38.698
| 20.1833 | 321.141 | 451.468 | 85.998 | 29.227 | 90.894 | 38.71
| 20.1847 | 320.822 | 451.577 | 85.989 | 29.225 | 90.895 | 38.719
| 20.1861 | 321.685 | 450.783 | 85.983 | 29.224 | 90.899 | 38.725
| 20.1875 | 321.058 | 451.058 | 85.975 | 29.226 | 90.893 | 38.733
| 20.1889 | 320.971 | 451.774 | 85.974 | 29.228 | 90.894 | 38.741
| 20.1903 | 321.449 | 450.391 | 85.972 | 29.228 | 90.904 | 38.746
| 20.1917 | 321.652 | 450.86 | 85.958 | 29.226 | 90.899 | 38.756
| 20.1931 | 321.81 | 450.686 | 85.962 | 29.224 | 90.916 | 38.765
| 20.1944 | 321.75 | 451.303 | 85.965 | 29.227 | 90.934 | 38.773
| 20.1958 | 321.091 | 451.497 | 85.963 | 29.225 | 90.946 | 38.787
| 20.1972 | 321.258 | 451.348 | 85.957 | 29.221 | 90.958 | 38.786
| 20.1986 | 321.923 | 451.802 | 85.957 | 29.225 | 90.97 | 38.796
| 20.2 | 321.339 | 452.013 | 85.959 | 29.226 | 90.992 | 38.808
| 20.2014 | 321.992 | 451.193 | 85.959 | 29.227 | 91.003 | 38.815
| 20.2028 | 321.32 | 451.626 | 85.96 | 29.227 | 91.011 | 38.824
| 20.2042 | 321.895 | 450.824 | 85.955 | 29.224 | 91.023 | 38.829
| 20.2056 | 321.57 | 450.515 | 85.944 | 29.228 | 91.023 | 38.837
| 20.2069 | 320.976 | 451.753 | 85.945 | 29.228 | 91.026 | 38.845
| 20.2083 | 321.406 | 450.552 | 85.938 | 29.227 | 91.03 | 38.853
| 20.2097 | 321.022 | 451.048 | 85.931 | 29.225 | 91.029 | 38.862
| 20.2111 | 321.543 | 450.395 | 85.927 | 29.224 | 91.034 | 38.868
| 20.2125 | 320.831 | 451.624 | 85.919 | 29.228 | 91.037 | 38.875
| 20.2139 | 321.588 | 450.444 | 85.916 | 29.226 | 91.04 | 38.882
| 20.2153 | 321.156 | 449.872 | 85.906 | 29.225 | 91.039 | 38.892
| 20.2167 | 321.304 | 450.003 | 85.895 | 29.227 | 91.038 | 38.897
| 20.2181 | 321.111 | 449.815 | 85.883 | 29.226 | 91.033 | 38.909
| 20.2194 | 320.419 | 450.317 | 85.872 | 29.227 | 91.025 | 38.917
| 20.2208 | 320.564 | 449.788 | 85.865 | 29.221 | 91.02 | 38.923
| 20.2222 | 319.647 | 450.374 | 85.838 | 29.226 | 91.01 | 38.931
| 20.2236 | 320.063 | 448.605 | 85.816 | 29.227 | 90.987 | 38.937
| 20.225 | 319.712 | 449.669 | 85.801 | 29.224 | 90.972 | 38.943
| 20.2264 | 319.611 | 448.981 | 85.777 | 29.221 | 90.952 | 38.95
| 20.2278 | 319.646 | 448.399 | 85.754 | 29.225 | 90.934 | 38.958
| 20.2292 | 318.907 | 448.189 | 85.732 | 29.226 | 90.918 | 38.97
| 20.2306 | 318.653 | 448.692 | 85.711 | 29.227 | 90.896 | 38.97
| 20.2319 | 318.768 | 448.119 | 85.69 | 29.227 | 90.876 | 38.988
| 20.2333 | 318.881 | 447.533 | 85.663 | 29.223 | 90.848 | 38.99
| 20.2347 | 317.933 | 447.744 | 85.635 | 29.224 | 90.822 | 39.001
| 20.2361 | 323.904 | 447.825 | 85.654 | 29.223 | 90.796 | 39.003
| 20.2375 | 324.252 | 447.928 | 85.74 | 29.224 | 90.78 | 39.014
| 20.2389 | 328.585 | 453.299 | 85.843 | 29.221 | 90.844 | 39.02
| 20.2403 | 328.662 | 452.758 | 85.957 | 29.22 | 90.962 | 39.027
| 20.2417 | 328.904 | 452.398 | 86.049 | 29.22 | 91.061 | 39.035
| 20.2431 | 327.83 | 453.581 | 86.124 | 29.221 | 91.131 | 39.038
| 20.2444 | 328.441 | 452.964 | 86.191 | 29.22 | 91.185 | 39.046
| 20.2458 | 328.029 | 453.032 | 86.25 | 29.223 | 91.234 | 39.056
| 20.2472 | 327.715 | 452.806 | 86.306 | 29.225 | 91.275 | 39.062
| 20.2486 | 328.364 | 451.911 | 86.354 | 29.226 | 91.296 | 39.067
| 20.25 | 328.092 | 451.844 | 86.409 | 29.224 | 91.332 | 39.075
| 20.2514 | 327.446 | 451.885 | 86.46 | 29.227 | 91.343 | 39.081
| 20.2528 | 327.156 | 450.986 | 86.495 | 29.23 | 91.356 | 39.092
| 20.2542 | 327.399 | 450.599 | 86.537 | 29.233 | 91.362 | 39.092
| 20.2556 | 326.845 | 450.97 | 86.573 | 29.233 | 91.367 | 39.103
| 20.2569 | 329.356 | 454.736 | 86.641 | 29.237 | 91.425 | 39.106
| 20.2583 | 328.963 | 454.829 | 86.713 | 29.237 | 91.502 | 39.116
| 20.2597 | 328.706 | 452.473 | 86.776 | 29.244 | 91.549 | 39.119
| 20.2611 | 328.692 | 452.85 | 86.814 | 29.246 | 91.571 | 39.132
| 20.2625 | 327.789 | 452.979 | 86.854 | 29.248 | 91.584 | 39.139
| 20.2639 | 326.616 | 449.672 | 86.873 | 29.248 | 91.569 | 39.148
| 20.2653 | 325.853 | 450.534 | 86.877 | 29.254 | 91.518 | 39.153
| 20.2667 | 326.052 | 450.744 | 86.892 | 29.254 | 91.495 | 39.158
| 20.2681 | 325.437 | 450.277 | 86.906 | 29.258 | 91.472 | 39.163
| 20.2694 | 325.359 | 449.949 | 86.923 | 29.262 | 91.449 | 39.171
| 20.2708 | 325.833 | 448.668 | 86.927 | 29.261 | 91.404 | 39.18
| 20.2722 | 324.902 | 449.508 | 86.934 | 29.261 | 91.381 | 39.189
| 20.2736 | 324.365 | 448.464 | 86.938 | 29.27 | 91.345 | 39.198
| 20.275 | 324.107 | 448.251 | 86.929 | 29.271 | 91.299 | 39.203
| 20.2764 | 324.404 | 447.209 | 86.931 | 29.273 | 91.262 | 39.21
| 20.2778 | 324.815 | 447.452 | 86.929 | 29.274 | 91.234 | 39.221
| 20.2792 | 324.68 | 447.779 | 86.936 | 29.277 | 91.215 | 39.225
| 20.2806 | 324.226 | 446.548 | 86.93 | 29.277 | 91.187 | 39.231
| 20.2819 | 328.749 | 452.442 | 86.994 | 29.28 | 91.265 | 39.238
| 20.2833 | 328.919 | 452.686 | 87.062 | 29.278 | 91.373 | 39.247
| 20.2847 | 327.209 | 452.455 | 87.113 | 29.285 | 91.441 | 39.253
| 20.2861 | 327.564 | 452.065 | 87.146 | 29.286 | 91.49 | 39.256
| 20.2875 | 327.756 | 451.085 | 87.172 | 29.287 | 91.516 | 39.265
| 20.2889 | 326.734 | 451.706 | 87.203 | 29.291 | 91.539 | 39.278
| 20.2903 | 327.252 | 450.685 | 87.217 | 29.293 | 91.566 | 39.283
| 20.2917 | 326.833 | 451.107 | 87.234 | 29.293 | 91.566 | 39.288
| 20.2931 | 326.729 | 451.791 | 87.255 | 29.296 | 91.575 | 39.29
| 20.2944 | 326.529 | 451.391 | 87.277 | 29.297 | 91.588 | 39.305
| 20.2958 | 327.051 | 450.105 | 87.286 | 29.299 | 91.586 | 39.309
| 20.2972 | 326.346 | 449.985 | 87.299 | 29.307 | 91.58 | 39.314
| 20.2986 | 326.044 | 448.729 | 87.301 | 29.309 | 91.565 | 39.324
| 20.3 | 325.651 | 449.36 | 87.309 | 29.307 | 91.554 | 39.333
| 20.3014 | 326.026 | 450.048 | 87.3 | 29.312 | 91.523 | 39.335
| 20.3028 | 327.69 | 450.567 | 87.347 | 29.314 | 91.584 | 39.343
| 20.3042 | 326.425 | 451.286 | 87.375 | 29.313 | 91.616 | 39.348
| 20.3056 | 325.913 | 449.241 | 87.382 | 29.315 | 91.615 | 39.358
| 20.3069 | 325.825 | 450.579 | 87.37 | 29.321 | 91.593 | 39.363
| 20.3083 | 325.832 | 449.145 | 87.385 | 29.321 | 91.602 | 39.372
| 20.3097 | 326.898 | 451.233 | 87.401 | 29.321 | 91.632 | 39.372
| 20.3111 | 327.563 | 450.589 | 87.433 | 29.324 | 91.672 | 39.382
| 20.3125 | 327.196 | 450.157 | 87.449 | 29.322 | 91.69 | 39.393
| 20.3139 | 327.105 | 450.942 | 87.46 | 29.328 | 91.704 | 39.4
| 20.3153 | 326.148 | 450.55 | 87.472 | 29.332 | 91.713 | 39.405
| 20.3167 | 326.347 | 450.172 | 87.48 | 29.333 | 91.713 | 39.413
| 20.3181 | 326.219 | 449.826 | 87.477 | 29.335 | 91.705 | 39.418
| 20.3194 | 325.546 | 449.832 | 87.481 | 29.335 | 91.691 | 39.426
| 20.3208 | 326.745 | 449.454 | 87.481 | 29.337 | 91.682 | 39.433
| 20.3222 | 326.233 | 448.723 | 87.496 | 29.341 | 91.688 | 39.44
| 20.3236 | 324.865 | 448.848 | 87.492 | 29.343 | 91.678 | 39.446
| 20.325 | 326.688 | 450.054 | 87.487 | 29.341 | 91.658 | 39.45
| 20.3264 | 327.957 | 451.43 | 87.534 | 29.346 | 91.732 | 39.462
| 20.3278 | 327.88 | 452.395 | 87.57 | 29.348 | 91.793 | 39.464
| 20.3292 | 327.532 | 452.657 | 87.608 | 29.349 | 91.854 | 39.471
| 20.3306 | 327.614 | 452.797 | 87.641 | 29.35 | 91.914 | 39.484
| 20.3319 | 328.66 | 453.008 | 87.668 | 29.353 | 91.948 | 39.485
| 20.3333 | 327.891 | 452.224 | 87.693 | 29.355 | 91.987 | 39.491
| 20.3347 | 328.55 | 451.986 | 87.718 | 29.357 | 92.012 | 39.501
| 20.3361 | 327.453 | 452.355 | 87.737 | 29.357 | 92.04 | 39.508
| 20.3375 | 327.881 | 451.784 | 87.751 | 29.361 | 92.049 | 39.514
| 20.3389 | 328.28 | 452.033 | 87.773 | 29.362 | 92.071 | 39.518
| 20.3403 | 327.866 | 452.563 | 87.795 | 29.366 | 92.098 | 39.526
| 20.3417 | 327.656 | 451.695 | 87.817 | 29.365 | 92.123 | 39.539
| 20.3431 | 327.889 | 452.613 | 87.842 | 29.371 | 92.144 | 39.539
| 20.3444 | 328.445 | 452.604 | 87.863 | 29.371 | 92.167 | 39.546
| 20.3458 | 327.875 | 452.54 | 87.88 | 29.373 | 92.189 | 39.553
| 20.3472 | 328.624 | 453.89 | 87.904 | 29.379 | 92.216 | 39.561
| 20.3486 | 329.342 | 455.035 | 87.958 | 29.376 | 92.291 | 39.565
| 20.35 | 329.496 | 454.941 | 87.997 | 29.38 | 92.349 | 39.575
| 20.3514 | 329.81 | 454.808 | 88.034 | 29.384 | 92.403 | 39.584
| 20.3528 | 330.311 | 454.095 | 88.069 | 29.386 | 92.439 | 39.59
| 20.3542 | 329.321 | 454.442 | 88.093 | 29.383 | 92.477 | 39.595
| 20.3556 | 329.794 | 453.445 | 88.124 | 29.388 | 92.507 | 39.602
| 20.3569 | 330.716 | 454.976 | 88.153 | 29.392 | 92.544 | 39.61
| 20.3583 | 329.063 | 454.378 | 88.179 | 29.394 | 92.571 | 39.611
| 20.3597 | 329.633 | 454.28 | 88.202 | 29.397 | 92.587 | 39.625
| 20.3611 | 329.945 | 454.41 | 88.226 | 29.398 | 92.611 | 39.633
| 20.3625 | 330.091 | 453.926 | 88.254 | 29.402 | 92.638 | 39.642
| 20.3639 | 330.187 | 453.767 | 88.28 | 29.407 | 92.655 | 39.644
| 20.3653 | 329.313 | 454.556 | 88.299 | 29.405 | 92.666 | 39.656
| 20.3667 | 328.524 | 453.536 | 88.316 | 29.41 | 92.686 | 39.658
| 20.3681 | 328.461 | 453.099 | 88.335 | 29.411 | 92.699 | 39.671
| 20.3694 | 328.806 | 454.051 | 88.352 | 29.415 | 92.709 | 39.676
| 20.3708 | 329.968 | 453.648 | 88.375 | 29.413 | 92.723 | 39.681
| 20.3722 | 329.727 | 453.554 | 88.395 | 29.419 | 92.739 | 39.684
| 20.3736 | 329.354 | 454.524 | 88.411 | 29.423 | 92.756 | 39.698
| 20.375 | 329.343 | 452.721 | 88.42 | 29.426 | 92.765 | 39.707
| 20.3764 | 329.454 | 452.887 | 88.435 | 29.426 | 92.772 | 39.713
| 20.3778 | 329.422 | 452.96 | 88.455 | 29.431 | 92.787 | 39.719
| 20.3792 | 328.72 | 453.923 | 88.48 | 29.431 | 92.808 | 39.728
| 20.3806 | 329.03 | 454.464 | 88.491 | 29.436 | 92.819 | 39.737
| 20.3819 | 329.426 | 453.416 | 88.512 | 29.443 | 92.843 | 39.744
| 20.3833 | 329.764 | 453.498 | 88.519 | 29.44 | 92.843 | 39.753
| 20.3847 | 330.062 | 453.839 | 88.533 | 29.446 | 92.857 | 39.758
| 20.3861 | 329.732 | 454.199 | 88.549 | 29.447 | 92.877 | 39.771
| 20.3875 | 330.068 | 455.403 | 88.577 | 29.449 | 92.905 | 39.776
| 20.3889 | 330.612 | 455.599 | 88.606 | 29.45 | 92.952 | 39.779
| 20.3903 | 330.496 | 455.193 | 88.634 | 29.452 | 92.998 | 39.791
| 20.3917 | 330.942 | 455.273 | 88.663 | 29.453 | 93.032 | 39.797
| 20.3931 | 329.587 | 455.668 | 88.685 | 29.458 | 93.063 | 39.804
| 20.3944 | 330.466 | 455.726 | 88.707 | 29.461 | 93.092 | 39.812
| 20.3958 | 330.058 | 455.985 | 88.733 | 29.463 | 93.121 | 39.825
| 20.3972 | 330.682 | 454.699 | 88.753 | 29.465 | 93.153 | 39.831
| 20.3986 | 331.188 | 455.454 | 88.774 | 29.469 | 93.168 | 39.834
| 20.4 | 330.387 | 454.258 | 88.789 | 29.473 | 93.194 | 39.847
| 20.4014 | 329.366 | 454.937 | 88.795 | 29.472 | 93.194 | 39.849
| 20.4028 | 330.166 | 454.918 | 88.808 | 29.478 | 93.197 | 39.858
| 20.4042 | 329.419 | 454.788 | 88.821 | 29.479 | 93.211 | 39.869
| 20.4056 | 330.104 | 454.952 | 88.832 | 29.486 | 93.216 | 39.873
| 20.4069 | 330.06 | 453.97 | 88.844 | 29.484 | 93.236 | 39.885
| 20.4083 | 330.132 | 454.549 | 88.86 | 29.488 | 93.245 | 39.895
| 20.4097 | 330.27 | 454.312 | 88.869 | 29.489 | 93.262 | 39.896
| 20.4111 | 330.45 | 454.366 | 88.891 | 29.493 | 93.282 | 39.91
| 20.4125 | 330.095 | 453.988 | 88.895 | 29.493 | 93.291 | 39.913
| 20.4139 | 330.313 | 454.246 | 88.912 | 29.498 | 93.302 | 39.925
| 20.4153 | 329.223 | 453.879 | 88.916 | 29.501 | 93.311 | 39.929
| 20.4167 | 329.502 | 453.409 | 88.919 | 29.5 | 93.306 | 39.938
| 20.4181 | 329.097 | 454.576 | 88.921 | 29.505 | 93.306 | 39.947
| 20.4194 | 328.745 | 453.738 | 88.926 | 29.506 | 93.311 | 39.953
| 20.4208 | 329.523 | 453.284 | 88.925 | 29.512 | 93.309 | 39.962
| 20.4222 | 328.873 | 454.418 | 88.931 | 29.513 | 93.31 | 39.97
| 20.4236 | 328.591 | 453.938 | 88.934 | 29.514 | 93.31 | 39.978
| 20.425 | 329.474 | 453.395 | 88.932 | 29.517 | 93.31 | 39.988
| 20.4264 | 330.111 | 454.399 | 88.937 | 29.521 | 93.317 | 39.994
| 20.4278 | 329.102 | 453.924 | 88.953 | 29.521 | 93.34 | 40
| 20.4292 | 329.905 | 455.276 | 88.973 | 29.525 | 93.379 | 40.009
| 20.4306 | 330.369 | 456.455 | 88.99 | 29.525 | 93.421 | 40.017
| 20.4319 | 331.184 | 450.774 | 89.026 | 29.525 | 93.452 | 40.027
| 20.4333 | 325.051 | 449.637 | 88.967 | 29.532 | 93.352 | 40.032
| 20.4347 | 324.539 | 451.04 | 88.887 | 29.53 | 93.279 | 40.041
| 20.4361 | 324.339 | 450.888 | 88.831 | 29.535 | 93.227 | 40.049
| 20.4375 | 325.176 | 449.867 | 88.788 | 29.538 | 93.185 | 40.055
| 20.4389 | 325.328 | 449.788 | 88.748 | 29.54 | 93.153 | 40.061
| 20.4403 | 325.475 | 450.297 | 88.71 | 29.54 | 93.132 | 40.074
| 20.4417 | 324.98 | 449.805 | 88.685 | 29.543 | 93.114 | 40.081
| 20.4431 | 325.838 | 450.846 | 88.659 | 29.546 | 93.104 | 40.085
| 20.4444 | 325.736 | 450.463 | 88.633 | 29.544 | 93.104 | 40.096
| 20.4458 | 325.205 | 451.418 | 88.613 | 29.545 | 93.108 | 40.102
| 20.4472 | 325.228 | 450.481 | 88.591 | 29.548 | 93.107 | 40.107
| 20.4486 | 325.181 | 452.055 | 88.567 | 29.55 | 93.108 | 40.118
| 20.45 | 325.663 | 451.971 | 88.552 | 29.551 | 93.115 | 40.121
| 20.4514 | 321.512 | 444.758 | 88.462 | 29.55 | 93.006 | 40.131
| 20.4528 | 320.86 | 446.189 | 88.373 | 29.554 | 92.877 | 40.138
| 20.4542 | 321.345 | 444.676 | 88.295 | 29.552 | 92.783 | 40.145
| 20.4556 | 321.115 | 445.139 | 88.231 | 29.551 | 92.696 | 40.149
| 20.4569 | 320.883 | 445.487 | 88.165 | 29.553 | 92.622 | 40.159
| 20.4583 | 320.543 | 445.796 | 88.111 | 29.553 | 92.56 | 40.168
| 20.4597 | 321.084 | 445.453 | 88.051 | 29.556 | 92.512 | 40.176
| 20.4611 | 320.538 | 445.826 | 87.997 | 29.554 | 92.467 | 40.179
| 20.4625 | 321.477 | 445.988 | 87.948 | 29.55 | 92.439 | 40.188
| 20.4639 | 320.913 | 444.898 | 87.907 | 29.553 | 92.41 | 40.192
| 20.4653 | 321.037 | 444.316 | 87.862 | 29.551 | 92.386 | 40.201
| 20.4667 | 321.66 | 445.148 | 87.814 | 29.549 | 92.363 | 40.202
| 20.4681 | 321.382 | 445.22 | 87.768 | 29.551 | 92.339 | 40.211
| 20.4694 | 320.56 | 445.689 | 87.715 | 29.549 | 92.319 | 40.218
| 20.4708 | 320.527 | 445.946 | 87.68 | 29.549 | 92.296 | 40.219
| 20.4722 | 320.724 | 445.876 | 87.639 | 29.546 | 92.27 | 40.228
| 20.4736 | 321.556 | 445.006 | 87.591 | 29.546 | 92.257 | 40.236
| 20.475 | 320.895 | 444.135 | 87.55 | 29.547 | 92.244 | 40.236
| 20.4764 | 320.214 | 445.068 | 87.504 | 29.543 | 92.218 | 40.246
| 20.4778 | 320.056 | 445.134 | 87.459 | 29.543 | 92.197 | 40.252
| 20.4792 | 320.529 | 445.579 | 87.418 | 29.54 | 92.176 | 40.256
| 20.4806 | 321.159 | 444.776 | 87.38 | 29.539 | 92.165 | 40.26
| 20.4819 | 321.336 | 445.872 | 87.353 | 29.541 | 92.176 | 40.264
| 20.4833 | 320.799 | 444.806 | 87.325 | 29.54 | 92.174 | 40.27
| 20.4847 | 319.907 | 444.639 | 87.277 | 29.537 | 92.139 | 40.273
| 20.4861 | 319.775 | 443.963 | 87.227 | 29.536 | 92.099 | 40.275
| 20.4875 | 320.277 | 452.009 | 87.178 | 29.538 | 92.218 | 40.284
| 20.4889 | 319.908 | 451.271 | 87.141 | 29.535 | 92.376 | 40.287
| 20.4903 | 320.44 | 451.815 | 87.108 | 29.533 | 92.491 | 40.29
| 20.4917 | 319.967 | 452.163 | 87.069 | 29.53 | 92.593 | 40.295
| 20.4931 | 319.974 | 451.887 | 87.035 | 29.529 | 92.669 | 40.299
| 20.4944 | 320.072 | 450.913 | 86.989 | 29.528 | 92.72 | 40.302
| 20.4958 | 319.436 | 452.042 | 86.952 | 29.526 | 92.775 | 40.312
| 20.4972 | 320.372 | 451.43 | 86.919 | 29.528 | 92.819 | 40.317
| 20.4986 | 320.155 | 451.698 | 86.883 | 29.523 | 92.863 | 40.32
| 20.5 | 319.381 | 451.842 | 86.859 | 29.527 | 92.904 | 40.322
| 20.5014 | 319.53 | 452.241 | 86.824 | 29.524 | 92.943 | 40.325
| 20.5028 | 320.607 | 451.527 | 86.801 | 29.52 | 92.99 | 40.326
| 20.5042 | 319.846 | 451.936 | 86.77 | 29.516 | 93.024 | 40.336
| 20.5056 | 319.908 | 452.08 | 86.742 | 29.515 | 93.051 | 40.339
| 20.5069 | 320.092 | 452.525 | 86.716 | 29.514 | 93.08 | 40.343
| 20.5083 | 320.554 | 451.25 | 86.69 | 29.51 | 93.109 | 40.35
| 20.5097 | 320.609 | 451.584 | 86.673 | 29.511 | 93.153 | 40.354
| 20.5111 | 321.282 | 452.419 | 86.653 | 29.505 | 93.188 | 40.36
| 20.5125 | 321.237 | 452.422 | 86.64 | 29.506 | 93.229 | 40.362
| 20.5139 | 321.758 | 454.598 | 86.642 | 29.503 | 93.294 | 40.367
| 20.5153 | 321.634 | 454.806 | 86.636 | 29.503 | 93.365 | 40.372
| 20.5167 | 322.011 | 454.695 | 86.632 | 29.501 | 93.426 | 40.376
| 20.5181 | 322.456 | 454.413 | 86.637 | 29.5 | 93.484 | 40.378
| 20.5194 | 322.289 | 455.404 | 86.637 | 29.501 | 93.54 | 40.39
| 20.5208 | 322.317 | 455.048 | 86.64 | 29.495 | 93.601 | 40.392
| 20.5222 | 322.633 | 454.797 | 86.647 | 29.496 | 93.66 | 40.393
| 20.5236 | 323.189 | 455.14 | 86.647 | 29.493 | 93.703 | 40.402
| 20.525 | 322.974 | 454.85 | 86.652 | 29.492 | 93.756 | 40.403
| 20.5264 | 323.143 | 455.56 | 86.65 | 29.491 | 93.792 | 40.415
| 20.5278 | 322.956 | 455.522 | 86.653 | 29.491 | 93.837 | 40.418
| 20.5292 | 322.898 | 456.068 | 86.661 | 29.491 | 93.875 | 40.426
| 20.5306 | 322.277 | 448.294 | 86.666 | 29.488 | 93.733 | 40.43
| 20.5319 | 322.279 | 448.166 | 86.661 | 29.49 | 93.607 | 40.438
| 20.5333 | 322.278 | 447.611 | 86.67 | 29.49 | 93.521 | 40.445
| 20.5347 | 322.859 | 448.379 | 86.673 | 29.487 | 93.457 | 40.444
| 20.5361 | 322.373 | 448.367 | 86.664 | 29.487 | 93.402 | 40.456
| 20.5375 | 322.505 | 448.222 | 86.657 | 29.487 | 93.348 | 40.463
| 20.5389 | 322.439 | 446.717 | 86.658 | 29.491 | 93.302 | 40.463
| 20.5403 | 322.968 | 447.223 | 86.652 | 29.489 | 93.262 | 40.471
| 20.5417 | 321.817 | 446.949 | 86.644 | 29.485 | 93.217 | 40.483
| 20.5431 | 321.997 | 446.288 | 86.637 | 29.484 | 93.181 | 40.487
| 20.5444 | 322.268 | 446.993 | 86.629 | 29.485 | 93.149 | 40.495
| 20.5458 | 321.407 | 446.689 | 86.617 | 29.481 | 93.119 | 40.495
| 20.5472 | 320.45 | 445.092 | 86.602 | 29.485 | 93.079 | 40.506
| 20.5486 | 319.982 | 445.1 | 86.565 | 29.486 | 92.999 | 40.509
| 20.55 | 319.933 | 444.018 | 86.526 | 29.484 | 92.924 | 40.517
| 20.5514 | 319.866 | 443.225 | 86.49 | 29.485 | 92.85 | 40.525
| 20.5528 | 319.941 | 450.33 | 86.459 | 29.482 | 92.879 | 40.528
| 20.5542 | 320.187 | 450.922 | 86.437 | 29.48 | 93.011 | 40.535
| 20.5556 | 319.524 | 450.489 | 86.414 | 29.483 | 93.101 | 40.542
| 20.5569 | 318.947 | 450.657 | 86.383 | 29.476 | 93.163 | 40.541
| 20.5625 | 328.199 | 455.76 | 86.589 | 29.475 | 93.473 | 40.565
| 20.5639 | 328.906 | 454.788 | 86.683 | 29.472 | 93.589 | 40.573
| 20.5653 | 328.841 | 456.61 | 86.758 | 29.478 | 93.681 | 40.578
| 20.5667 | 328.087 | 425.758 | 86.819 | 29.474 | 93.299 | 40.586
| 20.5681 | 328.447 | 426.039 | 86.871 | 29.476 | 92.712 | 40.588
| 20.5694 | 327.674 | 426.735 | 86.919 | 29.475 | 92.277 | 40.597
| 20.5708 | 327.683 | 426.959 | 86.975 | 29.477 | 91.928 | 40.596
| 20.5722 | 327.847 | 425.401 | 87.016 | 29.481 | 91.633 | 40.603
| 20.5736 | 327.715 | 427.236 | 87.058 | 29.477 | 91.383 | 40.606
| 20.575 | 327.957 | 426.118 | 87.102 | 29.478 | 91.17 | 40.614
| 20.5764 | 327.736 | 427.116 | 87.145 | 29.483 | 90.988 | 40.619
| 20.5778 | 329.105 | 427.907 | 87.193 | 29.478 | 90.835 | 40.624
| 20.5792 | 328.115 | 428.51 | 87.245 | 29.483 | 90.707 | 40.628
| 20.5806 | 328.266 | 428.449 | 87.295 | 29.495 | 90.599 | 40.632
| 20.5819 | 328.651 | 427.618 | 87.341 | 29.492 | 90.502 | 40.638
| 20.5833 | 328.824 | 427.873 | 87.39 | 29.489 | 90.41 | 40.642
| 20.5847 | 329.113 | 427.918 | 87.431 | 29.489 | 90.32 | 40.643
| 20.5861 | 328.809 | 428.965 | 87.482 | 29.492 | 90.26 | 40.646
| 20.5875 | 329.446 | 428.534 | 87.523 | 29.496 | 90.199 | 40.651
| 20.5889 | 329.266 | 429.288 | 87.576 | 29.494 | 90.145 | 40.647
| 20.5903 | 329.32 | 429.601 | 87.615 | 29.5 | 90.099 | 40.651
| 20.5917 | 329.793 | 428.545 | 87.66 | 29.504 | 90.048 | 40.656
| 20.5931 | 330.187 | 429.612 | 87.706 | 29.503 | 90.008 | 40.653
| 20.5944 | 329.624 | 429.945 | 87.755 | 29.509 | 89.975 | 40.656
| 20.5958 | 329.626 | 428.687 | 87.8 | 29.508 | 89.935 | 40.656
| 20.5972 | 329.238 | 430.633 | 87.834 | 29.517 | 89.892 | 40.653
| 20.5986 | 328.727 | 429.963 | 87.867 | 29.517 | 89.861 | 40.659
| 20.6 | 329.007 | 427.751 | 87.896 | 29.513 | 89.818 | 40.658
| 20.6014 | 328.89 | 428.602 | 87.932 | 29.521 | 89.773 | 40.652
| 20.6028 | 329.395 | 429.003 | 87.965 | 29.521 | 89.739 | 40.652
| 20.6042 | 328.534 | 428.347 | 87.985 | 29.527 | 89.693 | 40.65
| 20.6056 | 328.578 | 429.396 | 88.017 | 29.526 | 89.651 | 40.651
| 20.6069 | 329.188 | 429.526 | 88.047 | 29.532 | 89.626 | 40.651
| 20.6083 | 328.945 | 429.798 | 88.078 | 29.532 | 89.598 | 40.652
| 20.6097 | 329.005 | 429.137 | 88.108 | 29.533 | 89.568 | 40.644
| 20.6111 | 329.073 | 428.133 | 88.13 | 29.54 | 89.531 | 40.646
| 20.6125 | 328.244 | 428.798 | 88.154 | 29.538 | 89.494 | 40.644
| 20.6139 | 328.835 | 429.63 | 88.18 | 29.544 | 89.461 | 40.641
| 20.6153 | 329.279 | 429.814 | 88.208 | 29.544 | 89.44 | 40.645
| 20.6167 | 329.057 | 428.367 | 88.233 | 29.546 | 89.409 | 40.641
| 20.6181 | 329.438 | 429.131 | 88.249 | 29.546 | 89.378 | 40.635
| 20.6194 | 329.044 | 430.041 | 88.275 | 29.551 | 89.355 | 40.635
| 20.6208 | 328.963 | 429.174 | 88.297 | 29.557 | 89.338 | 40.629
| 20.6222 | 328.767 | 429.868 | 88.33 | 29.556 | 89.317 | 40.63
| 20.6236 | 329.431 | 428.605 | 88.353 | 29.563 | 89.293 | 40.627
| 20.625 | 328.252 | 429.147 | 88.368 | 29.559 | 89.265 | 40.623
| 20.6264 | 329.008 | 429.992 | 88.399 | 29.563 | 89.246 | 40.614
| 20.6278 | 329.23 | 429.233 | 88.414 | 29.57 | 89.226 | 40.622
| 20.6292 | 328.663 | 429.711 | 88.433 | 29.564 | 89.203 | 40.614
| 20.6306 | 328.697 | 429.684 | 88.458 | 29.576 | 89.194 | 40.611
| 20.6319 | 328.209 | 429.296 | 88.475 | 29.573 | 89.165 | 40.604
| 20.6333 | 329.352 | 428.469 | 88.492 | 29.579 | 89.14 | 40.609
| 20.6347 | 329.157 | 430.361 | 88.509 | 29.582 | 89.123 | 40.609
| 20.6361 | 329.251 | 430.282 | 88.534 | 29.581 | 89.101 | 40.6
| 20.6375 | 330.158 | 429.264 | 88.553 | 29.583 | 89.086 | 40.597
| 20.6389 | 329.107 | 429.656 | 88.576 | 29.585 | 89.075 | 40.596
| 20.6403 | 330.121 | 429.378 | 88.598 | 29.59 | 89.062 | 40.595
| 20.6417 | 329.613 | 430.554 | 88.619 | 29.591 | 89.054 | 40.59
| 20.6431 | 330.089 | 429.439 | 88.642 | 29.593 | 89.046 | 40.588
| 20.6444 | 329.632 | 428.961 | 88.663 | 29.597 | 89.032 | 40.583
| 20.6458 | 328.839 | 429.715 | 88.674 | 29.592 | 89.005 | 40.58
| 20.6472 | 329.949 | 429.258 | 88.691 | 29.601 | 88.986 | 40.581
| 20.6486 | 329.199 | 430.437 | 88.706 | 29.604 | 88.973 | 40.572
| 20.65 | 329.629 | 430.162 | 88.738 | 29.608 | 88.971 | 40.574
| 20.6514 | 331.018 | 430.887 | 88.76 | 29.608 | 88.973 | 40.575
| 20.6528 | 330.268 | 429.558 | 88.785 | 29.61 | 88.972 | 40.566
| 20.6542 | 330.358 | 431.289 | 88.812 | 29.612 | 88.973 | 40.562
| 20.6556 | 330.078 | 421.882 | 88.833 | 29.617 | 88.82 | 40.559
| 20.6569 | 329.952 | 422.585 | 88.852 | 29.618 | 88.631 | 40.558
| 20.6583 | 330.405 | 421.402 | 88.875 | 29.619 | 88.493 | 40.555
| 20.6597 | 330.372 | 422.664 | 88.897 | 29.624 | 88.382 | 40.553
| 20.6611 | 330.453 | 422.478 | 88.917 | 29.628 | 88.289 | 40.546
| 20.6625 | 330.064 | 423.379 | 88.938 | 29.632 | 88.205 | 40.545
| 20.6639 | 331.288 | 423.17 | 88.972 | 29.634 | 88.146 | 40.54
| 20.6653 | 330.292 | 423.441 | 88.995 | 29.636 | 88.088 | 40.541
| 20.6667 | 330.958 | 422.703 | 89.019 | 29.635 | 88.037 | 40.537
| 20.6681 | 330.335 | 423.695 | 89.039 | 29.638 | 87.991 | 40.535
| 20.6694 | 330.546 | 423.304 | 89.064 | 29.644 | 87.944 | 40.53
| 20.6708 | 330.359 | 423.903 | 89.081 | 29.641 | 87.904 | 40.525
| 20.6722 | 330.558 | 423.665 | 89.109 | 29.647 | 87.871 | 40.52
| 20.6736 | 331.018 | 424.17 | 89.139 | 29.649 | 87.84 | 40.523
| 20.675 | 330.651 | 422.034 | 89.158 | 29.648 | 87.806 | 40.515
| 20.6764 | 330.501 | 423.516 | 89.164 | 29.653 | 87.764 | 40.51
| 20.6778 | 330.98 | 422.917 | 89.185 | 29.658 | 87.728 | 40.511
| 20.6792 | 330.863 | 423.268 | 89.202 | 29.657 | 87.697 | 40.502
| 20.6806 | 331.223 | 422.678 | 89.225 | 29.662 | 87.676 | 40.501
| 20.6819 | 331.29 | 422.971 | 89.238 | 29.666 | 87.644 | 40.495
| 20.6833 | 328.952 | 420.24 | 89.214 | 29.664 | 87.554 | 40.497
| 20.6847 | 327.981 | 420.791 | 89.191 | 29.671 | 87.474 | 40.488
| 20.6861 | 328.701 | 420.322 | 89.18 | 29.669 | 87.407 | 40.483
| 20.6875 | 328.859 | 419.877 | 89.177 | 29.676 | 87.355 | 40.483
| 20.6889 | 328.878 | 421.168 | 89.175 | 29.677 | 87.304 | 40.479
| 20.6903 | 328.738 | 420.015 | 89.178 | 29.679 | 87.266 | 40.471
| 20.6917 | 328.553 | 421.971 | 89.187 | 29.683 | 87.249 | 40.472
| 20.6931 | 329.171 | 420.564 | 89.187 | 29.684 | 87.216 | 40.468
| 20.6944 | 328.91 | 422.403 | 89.186 | 29.686 | 87.191 | 40.463
| 20.6958 | 328.237 | 421.259 | 89.193 | 29.687 | 87.162 | 40.457
| 20.6972 | 328.378 | 421.51 | 89.183 | 29.689 | 87.122 | 40.455
| 20.6986 | 329.413 | 420.941 | 89.177 | 29.695 | 87.08 | 40.447
| 20.7 | 329.135 | 420.611 | 89.185 | 29.695 | 87.058 | 40.446
| 20.7014 | 329.622 | 422.292 | 89.194 | 29.697 | 87.045 | 40.439
| 20.7028 | 329.346 | 421.529 | 89.2 | 29.696 | 87.031 | 40.437
| 20.7042 | 329.244 | 420.666 | 89.209 | 29.7 | 87.01 | 40.428
| 20.7056 | 329.193 | 421.813 | 89.211 | 29.698 | 86.989 | 40.423
| 20.7069 | 328.269 | 421.076 | 89.21 | 29.702 | 86.959 | 40.422
| 20.7083 | 328.53 | 421.184 | 89.205 | 29.702 | 86.928 | 40.421
| 20.7097 | 328.1 | 421.017 | 89.201 | 29.708 | 86.897 | 40.412
| 20.7111 | 329.273 | 420.708 | 89.197 | 29.707 | 86.869 | 40.411
| 20.7125 | 327.673 | 420.32 | 89.193 | 29.71 | 86.836 | 40.405
| 20.7139 | 328.708 | 420.073 | 89.191 | 29.715 | 86.803 | 40.395
| 20.7153 | 328.022 | 421.129 | 89.185 | 29.716 | 86.774 | 40.391
| 20.7167 | 326.655 | 426.033 | 89.158 | 29.717 | 86.74 | 40.388
| 20.7181 | 326.819 | 425.339 | 89.127 | 29.714 | 86.865 | 40.379
| 20.7194 | 326.823 | 427.155 | 89.104 | 29.719 | 86.939 | 40.381
| 20.7208 | 326.417 | 425.858 | 89.085 | 29.72 | 86.998 | 40.373
| 20.7222 | 325.601 | 424.594 | 89.055 | 29.718 | 87.018 | 40.369
| 20.7236 | 325.673 | 425 | 89.018 | 29.724 | 87.02 | 40.365
| 20.725 | 325.269 | 424.237 | 88.991 | 29.727 | 87.028 | 40.36
| 20.7264 | 325.662 | 425.736 | 88.959 | 29.727 | 87.025 | 40.356
| 20.7278 | 325.677 | 425.518 | 88.941 | 29.724 | 87.036 | 40.352
| 20.7292 | 326.5 | 424.933 | 88.915 | 29.726 | 87.039 | 40.35
| 20.7306 | 325.016 | 424.662 | 88.886 | 29.73 | 87.036 | 40.343
| 20.7319 | 324.992 | 424.93 | 88.863 | 29.726 | 87.018 | 40.336
| 20.7333 | 324.611 | 423.547 | 88.828 | 29.732 | 86.99 | 40.335
| 20.7347 | 328.049 | 426.736 | 88.815 | 29.726 | 87.001 | 40.328
| 20.7361 | 327.756 | 426.955 | 88.838 | 29.73 | 87.068 | 40.325
| 20.7375 | 328.229 | 427.033 | 88.842 | 29.734 | 87.119 | 40.32
| 20.7389 | 327.278 | 427.447 | 88.849 | 29.734 | 87.155 | 40.315
| 20.7403 | 326.525 | 426.955 | 88.843 | 29.734 | 87.172 | 40.316
| 20.7417 | 326.645 | 426.319 | 88.841 | 29.736 | 87.183 | 40.306
| 20.7431 | 327.114 | 426.116 | 88.83 | 29.733 | 87.186 | 40.301
| 20.7444 | 326.847 | 426.27 | 88.812 | 29.74 | 87.178 | 40.301
| 20.7458 | 326.511 | 425.863 | 88.806 | 29.739 | 87.181 | 40.297
| 20.7472 | 326.135 | 426.574 | 88.797 | 29.737 | 87.175 | 40.293
| 20.7486 | 326.962 | 427.073 | 88.786 | 29.738 | 87.175 | 40.293
| 20.75 | 326.711 | 426.606 | 88.781 | 29.739 | 87.169 | 40.283
| 20.7514 | 327.047 | 426.896 | 88.774 | 29.74 | 87.162 | 40.283
| 20.7528 | 327.003 | 427.441 | 88.769 | 29.744 | 87.166 | 40.279
| 20.7542 | 327.399 | 426.04 | 88.771 | 29.741 | 87.178 | 40.277
| 20.7556 | 327.729 | 426.542 | 88.771 | 29.741 | 87.184 | 40.277
| 20.7569 | 327.896 | 426.705 | 88.77 | 29.741 | 87.192 | 40.27
| 20.7583 | 327.246 | 427.178 | 88.772 | 29.743 | 87.196 | 40.272
| 20.7597 | 326.709 | 427.26 | 88.767 | 29.74 | 87.198 | 40.268
| 20.7611 | 327.894 | 426.884 | 88.766 | 29.743 | 87.202 | 40.262
| 20.7625 | 327.894 | 427.081 | 88.778 | 29.743 | 87.22 | 40.264
| 20.7639 | 328.437 | 427.691 | 88.79 | 29.748 | 87.235 | 40.256
| 20.7653 | 328.365 | 427.822 | 88.796 | 29.744 | 87.252 | 40.257
| 20.7667 | 327.972 | 428.33 | 88.806 | 29.746 | 87.271 | 40.25
| 20.7681 | 328.397 | 428.537 | 88.818 | 29.749 | 87.286 | 40.249
| 20.7694 | 328.374 | 427.818 | 88.827 | 29.75 | 87.304 | 40.251
| 20.775 | 329.201 | 428.513 | 88.883 | 29.757 | 87.378 | 40.237
| 20.7764 | 329.369 | 428.67 | 88.892 | 29.753 | 87.389 | 40.242
| 20.7778 | 328.919 | 428.088 | 88.903 | 29.757 | 87.398 | 40.237
| 20.7792 | 329.028 | 428.396 | 88.911 | 29.757 | 87.402 | 40.234
| 20.7806 | 328.174 | 429.304 | 88.917 | 29.757 | 87.401 | 40.233
| 20.7819 | 328.696 | 429.825 | 88.928 | 29.759 | 87.41 | 40.232
| 20.7833 | 329.203 | 429.534 | 88.947 | 29.76 | 87.42 | 40.226
| 20.7847 | 329.616 | 429.595 | 88.959 | 29.759 | 87.436 | 40.226
| 20.7861 | 328.69 | 429.835 | 88.979 | 29.761 | 87.453 | 40.232
| 20.7875 | 329.715 | 429.553 | 88.997 | 29.763 | 87.476 | 40.227
| 20.7889 | 329.199 | 429.858 | 89.014 | 29.768 | 87.489 | 40.225
| 20.7903 | 329.211 | 429.685 | 89.027 | 29.767 | 87.493 | 40.222
| 20.7917 | 329.425 | 430.57 | 89.031 | 29.764 | 87.494 | 40.223
| 20.7931 | 328.902 | 429.924 | 89.051 | 29.77 | 87.508 | 40.222
| 20.7944 | 328.859 | 429.109 | 89.052 | 29.771 | 87.502 | 40.218
| 20.7958 | 328.819 | 428.206 | 89.052 | 29.773 | 87.493 | 40.222
| 20.7972 | 329.058 | 428.982 | 89.052 | 29.776 | 87.488 | 40.214
| 20.7986 | 328.205 | 428.297 | 89.056 | 29.773 | 87.473 | 40.22
| 20.8 | 328.59 | 428.551 | 89.058 | 29.778 | 87.466 | 40.22
| 20.8014 | 328.08 | 428.482 | 89.067 | 29.78 | 87.454 | 40.214
| 20.8028 | 328.546 | 429.167 | 89.07 | 29.783 | 87.451 | 40.212
| 20.8042 | 328.903 | 429.587 | 89.081 | 29.781 | 87.459 | 40.217
| 20.8056 | 328.688 | 429.317 | 89.097 | 29.787 | 87.482 | 40.215
| 20.8069 | 328.77 | 429.902 | 89.106 | 29.784 | 87.487 | 40.215
| 20.8083 | 328.936 | 427.906 | 89.118 | 29.786 | 87.493 | 40.213
| 20.8097 | 329.878 | 429.383 | 89.138 | 29.788 | 87.507 | 40.217
| 20.8111 | 329.204 | 430.171 | 89.152 | 29.79 | 87.521 | 40.214
| 20.8125 | 328.856 | 429.765 | 89.162 | 29.792 | 87.533 | 40.216
| 20.8139 | 330.17 | 429.62 | 89.172 | 29.791 | 87.54 | 40.216
| 20.8153 | 329.501 | 430.615 | 89.186 | 29.792 | 87.542 | 40.216
| 20.8167 | 329.54 | 430.544 | 89.195 | 29.794 | 87.552 | 40.214
| 20.8181 | 330.178 | 429.64 | 89.214 | 29.799 | 87.563 | 40.217
| 20.8194 | 329.668 | 430.76 | 89.228 | 29.798 | 87.571 | 40.209
| 20.8208 | 330.193 | 430.692 | 89.25 | 29.8 | 87.595 | 40.213
| 20.8222 | 330.165 | 430.517 | 89.27 | 29.801 | 87.623 | 40.214
| 20.8236 | 330.822 | 430.636 | 89.287 | 29.804 | 87.642 | 40.213
| 20.825 | 330.142 | 431.375 | 89.311 | 29.806 | 87.661 | 40.213
| 20.8264 | 330.612 | 430.024 | 89.322 | 29.806 | 87.662 | 40.211
| 20.8278 | 330.277 | 431.77 | 89.336 | 29.813 | 87.681 | 40.213
| 20.8292 | 330.556 | 430.513 | 89.357 | 29.814 | 87.7 | 40.216
| 20.8306 | 331.022 | 431.115 | 89.377 | 29.815 | 87.712 | 40.212
| 20.8319 | 330.853 | 432.098 | 89.403 | 29.818 | 87.734 | 40.219
| 20.8333 | 329.962 | 422.903 | 89.416 | 29.816 | 87.578 | 40.219
| 20.8347 | 330.598 | 422.224 | 89.424 | 29.82 | 87.41 | 40.215
| 20.8361 | 330.413 | 421.5 | 89.443 | 29.821 | 87.294 | 40.215
| 20.8375 | 330.218 | 423.112 | 89.451 | 29.829 | 87.187 | 40.216
| 20.8389 | 330.712 | 423.075 | 89.462 | 29.826 | 87.098 | 40.219
| 20.8403 | 330.363 | 423.66 | 89.476 | 29.829 | 87.044 | 40.218
| 20.8417 | 325.839 | 417.318 | 89.438 | 29.827 | 86.903 | 40.221
| 20.8431 | 326.081 | 418.294 | 89.379 | 29.834 | 86.741 | 40.22
| 20.8444 | 327.311 | 425.755 | 89.346 | 29.834 | 86.712 | 40.221
| 20.8458 | 326.318 | 426.561 | 89.318 | 29.837 | 86.792 | 40.224
| 20.8472 | 327.596 | 427.375 | 89.313 | 29.843 | 86.855 | 40.222
| 20.8486 | 327.298 | 428.162 | 89.305 | 29.843 | 86.917 | 40.221
| 20.85 | 327.846 | 427.796 | 89.304 | 29.843 | 86.976 | 40.227
| 20.8514 | 328.137 | 429.042 | 89.304 | 29.84 | 87.019 | 40.223
| 20.8528 | 326.831 | 427.546 | 89.302 | 29.845 | 87.067 | 40.222
| 20.8542 | 327.498 | 426.446 | 89.279 | 29.845 | 87.069 | 40.227
| 20.8556 | 327.308 | 426.712 | 89.265 | 29.848 | 87.071 | 40.227
| 20.8569 | 327.163 | 427.476 | 89.252 | 29.849 | 87.073 | 40.225
| 20.8583 | 327.956 | 427.224 | 89.236 | 29.85 | 87.079 | 40.223
| 20.8597 | 325.336 | 425.736 | 89.227 | 29.849 | 87.078 | 40.224
| 20.8611 | 325.403 | 425.368 | 89.178 | 29.85 | 87.023 | 40.219
| 20.8625 | 325.48 | 424.797 | 89.138 | 29.853 | 86.987 | 40.219
| 20.8639 | 325.365 | 423.321 | 89.103 | 29.859 | 86.939 | 40.222
| 20.8653 | 326.003 | 424.296 | 89.073 | 29.85 | 86.917 | 40.223
| 20.8667 | 325.634 | 426.034 | 89.052 | 29.854 | 86.902 | 40.223
| 20.8681 | 326.435 | 425.806 | 89.042 | 29.854 | 86.897 | 40.222
| 20.8694 | 325.992 | 426.245 | 89.032 | 29.857 | 86.902 | 40.217
| 20.8708 | 326.096 | 425.975 | 89.021 | 29.857 | 86.903 | 40.22
| 20.8722 | 326.657 | 426.367 | 89.01 | 29.859 | 86.907 | 40.221
| 20.8736 | 326.884 | 425.033 | 88.997 | 29.862 | 86.915 | 40.22
| 20.875 | 326.795 | 425.266 | 88.981 | 29.858 | 86.912 | 40.219
| 20.8764 | 326.73 | 426.086 | 88.969 | 29.859 | 86.906 | 40.217
| 20.8778 | 326.519 | 425.367 | 88.956 | 29.855 | 86.895 | 40.216
| 20.8792 | 325.974 | 426.053 | 88.938 | 29.856 | 86.887 | 40.218
| 20.8806 | 326.423 | 424.709 | 88.924 | 29.861 | 86.886 | 40.219
| 20.8819 | 326.962 | 425.701 | 88.911 | 29.865 | 86.881 | 40.22
| 20.8833 | 326.624 | 427.171 | 88.909 | 29.858 | 86.891 | 40.22
| 20.8847 | 327.214 | 426.306 | 88.91 | 29.862 | 86.905 | 40.218
| 20.8861 | 326.85 | 426.524 | 88.906 | 29.857 | 86.911 | 40.218
| 20.8875 | 326.72 | 426.979 | 88.901 | 29.86 | 86.921 | 40.217
| 20.8889 | 327.157 | 427.597 | 88.908 | 29.858 | 86.939 | 40.219
| 20.8903 | 327.119 | 427.237 | 88.911 | 29.864 | 86.961 | 40.218
| 20.8917 | 326.223 | 426.478 | 88.895 | 29.868 | 86.953 | 40.22
| 20.8931 | 326.634 | 426.756 | 88.88 | 29.862 | 86.948 | 40.216
| 20.8944 | 326.667 | 424.932 | 88.867 | 29.861 | 86.928 | 40.217
| 20.8958 | 326.064 | 424.978 | 88.852 | 29.862 | 86.909 | 40.216
| 20.8972 | 326.944 | 425.191 | 88.842 | 29.865 | 86.898 | 40.215
| 20.8986 | 326.105 | 426.385 | 88.834 | 29.865 | 86.888 | 40.215
| 20.9 | 326.984 | 425.517 | 88.829 | 29.866 | 86.893 | 40.218
| 20.9014 | 326.404 | 426.29 | 88.824 | 29.868 | 86.892 | 40.217
| 20.9028 | 326.755 | 426.148 | 88.814 | 29.867 | 86.894 | 40.215
| 20.9042 | 326.898 | 426.488 | 88.807 | 29.867 | 86.894 | 40.215
| 20.9056 | 326.828 | 427.123 | 88.81 | 29.865 | 86.901 | 40.216
| 20.9069 | 327.44 | 426.92 | 88.817 | 29.864 | 86.914 | 40.214
| 20.9083 | 327.179 | 426.982 | 88.817 | 29.869 | 86.931 | 40.211
| 20.9097 | 327.599 | 427.94 | 88.836 | 29.865 | 86.958 | 40.213
| 20.9111 | 327.772 | 428.163 | 88.841 | 29.869 | 86.974 | 40.213
| 20.9125 | 327.915 | 427.984 | 88.858 | 29.869 | 87.004 | 40.218
| 20.9139 | 328.677 | 427.552 | 88.862 | 29.87 | 87.024 | 40.218
| 20.9153 | 328.39 | 427.971 | 88.878 | 29.868 | 87.046 | 40.211
| 20.9167 | 328.562 | 427.581 | 88.891 | 29.87 | 87.065 | 40.214
| 20.9181 | 328.343 | 429.489 | 88.904 | 29.87 | 87.082 | 40.215
| 20.9194 | 329.189 | 428.291 | 88.922 | 29.869 | 87.116 | 40.214
| 20.9208 | 329.26 | 428.766 | 88.941 | 29.874 | 87.15 | 40.215
| 20.9222 | 328.858 | 429.519 | 88.959 | 29.869 | 87.177 | 40.216
| 20.9236 | 329.179 | 428.405 | 88.968 | 29.872 | 87.18 | 40.221
| 20.925 | 328.39 | 429.23 | 88.982 | 29.877 | 87.201 | 40.213
| 20.9264 | 329.28 | 428.663 | 88.993 | 29.873 | 87.221 | 40.216
| 20.9278 | 329.455 | 428.823 | 89.014 | 29.881 | 87.233 | 40.216
| 20.9292 | 328.912 | 429.971 | 89.034 | 29.878 | 87.262 | 40.219
| 20.9306 | 330.457 | 431.676 | 89.065 | 29.877 | 87.308 | 40.213
| 20.9319 | 330.448 | 431.798 | 89.107 | 29.884 | 87.362 | 40.216
| 20.9333 | 330.645 | 423.773 | 89.143 | 29.885 | 87.316 | 40.217
| 20.9347 | 330.279 | 423.985 | 89.173 | 29.884 | 87.191 | 40.223
| 20.9361 | 330.656 | 422.694 | 89.195 | 29.885 | 87.108 | 40.223
| 20.9375 | 330.452 | 423.509 | 89.217 | 29.884 | 87.03 | 40.221
| 20.9389 | 330.844 | 423.989 | 89.245 | 29.887 | 86.987 | 40.221
| 20.9403 | 326.963 | 419.015 | 89.225 | 29.889 | 86.886 | 40.221
| 20.9417 | 326.895 | 426.284 | 89.188 | 29.889 | 86.898 | 40.224
| 20.9431 | 326.891 | 425.985 | 89.161 | 29.895 | 86.91 | 40.228
| 20.9444 | 327.691 | 425.472 | 89.144 | 29.896 | 86.923 | 40.226
| 20.9458 | 327.876 | 426.064 | 89.133 | 29.898 | 86.937 | 40.226
| 20.9472 | 327.229 | 426.939 | 89.126 | 29.899 | 86.941 | 40.223
| 20.9486 | 328.057 | 426.731 | 89.132 | 29.903 | 86.959 | 40.23
| 20.95 | 327.937 | 426.2 | 89.118 | 29.9 | 86.97 | 40.226
| 20.9514 | 325.49 | 424.075 | 89.094 | 29.901 | 86.963 | 40.229
| 20.9528 | 325.899 | 423.947 | 89.053 | 29.902 | 86.906 | 40.231
| 20.9542 | 324.425 | 423.65 | 89.02 | 29.908 | 86.88 | 40.228
| 20.9556 | 325.302 | 424.523 | 88.988 | 29.904 | 86.841 | 40.232
| 20.9569 | 324.958 | 424.546 | 88.963 | 29.905 | 86.816 | 40.229
| 20.9583 | 325.742 | 423.836 | 88.944 | 29.909 | 86.792 | 40.235
| 20.9597 | 325.387 | 425.23 | 88.923 | 29.904 | 86.784 | 40.234
| 20.9611 | 325.979 | 424.275 | 88.903 | 29.905 | 86.771 | 40.234
| 20.9625 | 326.091 | 423.516 | 88.893 | 29.913 | 86.772 | 40.236
| 20.9639 | 324.953 | 424.191 | 88.875 | 29.906 | 86.756 | 40.233
| 20.9653 | 325.323 | 424.184 | 88.85 | 29.913 | 86.74 | 40.238
| 20.9667 | 325.797 | 423.481 | 88.838 | 29.914 | 86.727 | 40.235
| 20.9681 | 325.898 | 423.912 | 88.819 | 29.912 | 86.721 | 40.237
| 20.9694 | 326.143 | 423.776 | 88.809 | 29.91 | 86.718 | 40.236
| 20.9708 | 326.029 | 424.035 | 88.789 | 29.912 | 86.711 | 40.24
| 20.9722 | 326.543 | 425.819 | 88.795 | 29.912 | 86.734 | 40.236
| 20.9736 | 327.296 | 425.811 | 88.805 | 29.917 | 86.77 | 40.24
| 20.975 | 327.611 | 426.679 | 88.814 | 29.915 | 86.802 | 40.241
| 20.9764 | 327.759 | 427.461 | 88.833 | 29.916 | 86.837 | 40.236
| 20.9778 | 328.67 | 426.97 | 88.849 | 29.919 | 86.879 | 40.239
| 20.9792 | 328.138 | 426.784 | 88.857 | 29.911 | 86.909 | 40.244
| 20.9806 | 327.501 | 426.712 | 88.862 | 29.917 | 86.924 | 40.242
| 20.9819 | 327.154 | 426.408 | 88.864 | 29.919 | 86.932 | 40.245
| 20.9833 | 328.398 | 426.776 | 88.864 | 29.914 | 86.938 | 40.242
| 20.9847 | 328.557 | 427.041 | 88.873 | 29.916 | 86.961 | 40.242
| 20.9861 | 328.105 | 426.94 | 88.879 | 29.915 | 86.97 | 40.24
| 20.9875 | 328.682 | 427.46 | 88.892 | 29.918 | 86.997 | 40.243
| 20.9889 | 328.136 | 428.708 | 88.911 | 29.917 | 87.027 | 40.243
| 20.9903 | 328.647 | 427.269 | 88.918 | 29.92 | 87.046 | 40.24
| 20.9917 | 327.662 | 427.982 | 88.923 | 29.924 | 87.056 | 40.249
| 20.9931 | 328.51 | 427.268 | 88.928 | 29.924 | 87.06 | 40.25
| 20.9944 | 328.956 | 427.718 | 88.939 | 29.925 | 87.07 | 40.252
| 20.9958 | 328.532 | 427.682 | 88.951 | 29.928 | 87.089 | 40.248
| 20.9972 | 328.147 | 428.267 | 88.962 | 29.928 | 87.101 | 40.249
| 20.9986 | 327.628 | 428.096 | 88.966 | 29.926 | 87.108 | 40.251
| 21 | 327.936 | 427.821 | 88.963 | 29.929 | 87.1 | 40.25
| 21.0014 | 327.821 | 427.445 | 88.972 | 29.927 | 87.108 | 40.252
| 21.0028 | 328.292 | 428.027 | 88.978 | 29.931 | 87.116 | 40.248
| 21.0042 | 328.283 | 428.468 | 88.991 | 29.928 | 87.128 | 40.252
| 21.0056 | 328.807 | 428.067 | 89.001 | 29.936 | 87.146 | 40.249
| 21.0069 | 328.934 | 428.256 | 89.015 | 29.932 | 87.158 | 40.257
| 21.0083 | 328.754 | 427.56 | 89.022 | 29.937 | 87.169 | 40.258
| 21.0097 | 328.664 | 427.058 | 89.023 | 29.938 | 87.164 | 40.254
| 21.0111 | 328.091 | 426.596 | 89.019 | 29.935 | 87.159 | 40.257
| 21.0125 | 328.041 | 427.906 | 89.026 | 29.938 | 87.16 | 40.257
| 21.0139 | 329.148 | 428.257 | 89.039 | 29.943 | 87.183 | 40.259
| 21.0153 | 328.526 | 428.871 | 89.06 | 29.936 | 87.199 | 40.269
| 21.0167 | 329.484 | 428.11 | 89.072 | 29.941 | 87.222 | 40.262
| 21.0181 | 329.186 | 428.6 | 89.093 | 29.942 | 87.226 | 40.262
| 21.0194 | 329.066 | 427.673 | 89.102 | 29.945 | 87.244 | 40.268
| 21.0208 | 328.224 | 428.44 | 89.108 | 29.942 | 87.25 | 40.267
| 21.0222 | 328.418 | 428.075 | 89.113 | 29.943 | 87.26 | 40.268
| 21.0236 | 328.497 | 427.849 | 89.121 | 29.947 | 87.267 | 40.266
| 21.025 | 329.016 | 428.414 | 89.128 | 29.946 | 87.277 | 40.271
| 21.0264 | 328.557 | 427.649 | 89.139 | 29.95 | 87.285 | 40.272
| 21.0278 | 328.873 | 427.248 | 89.142 | 29.95 | 87.289 | 40.268
| 21.0292 | 328.932 | 427.705 | 89.149 | 29.952 | 87.294 | 40.276
| 21.0306 | 329.088 | 428.327 | 89.168 | 29.953 | 87.309 | 40.277
| 21.0319 | 329.364 | 428.368 | 89.175 | 29.953 | 87.312 | 40.277
| 21.0333 | 329.254 | 428.601 | 89.19 | 29.952 | 87.329 | 40.28
| 21.0347 | 328.624 | 429.139 | 89.2 | 29.956 | 87.335 | 40.282
| 21.0361 | 329.035 | 428.454 | 89.21 | 29.96 | 87.345 | 40.284
| 21.0375 | 327.972 | 428.128 | 89.21 | 29.962 | 87.343 | 40.285
| 21.0389 | 327.513 | 427.132 | 89.204 | 29.963 | 87.32 | 40.285
| 21.0403 | 328.154 | 426.937 | 89.192 | 29.96 | 87.305 | 40.291
| 21.0417 | 327.596 | 427.279 | 89.192 | 29.964 | 87.288 | 40.284
| 21.0431 | 327.753 | 427.197 | 89.19 | 29.967 | 87.271 | 40.292
| 21.0444 | 328.353 | 427.179 | 89.185 | 29.969 | 87.27 | 40.295
| 21.0458 | 328.374 | 427.369 | 89.189 | 29.97 | 87.272 | 40.294
| 21.0472 | 329.029 | 427.297 | 89.198 | 29.972 | 87.276 | 40.298
| 21.0486 | 328.455 | 428.022 | 89.207 | 29.974 | 87.286 | 40.298
| 21.05 | 328.574 | 427.668 | 89.21 | 29.97 | 87.29 | 40.296
| 21.0514 | 328.057 | 428.198 | 89.212 | 29.972 | 87.302 | 40.296
| 21.0528 | 328.785 | 427.921 | 89.227 | 29.976 | 87.305 | 40.307
| 21.0542 | 328.491 | 428.734 | 89.23 | 29.979 | 87.314 | 40.307
| 21.0556 | 329.954 | 429.154 | 89.249 | 29.976 | 87.337 | 40.309
| 21.0569 | 329.945 | 429.138 | 89.275 | 29.979 | 87.379 | 40.304
| 21.0583 | 329.218 | 429.622 | 89.29 | 29.979 | 87.405 | 40.313
| 21.0597 | 329.563 | 430.237 | 89.308 | 29.978 | 87.433 | 40.313
| 21.0611 | 330.03 | 429.394 | 89.328 | 29.982 | 87.458 | 40.314
| 21.0625 | 330.279 | 429.605 | 89.342 | 29.985 | 87.48 | 40.315
| 21.0639 | 329.343 | 430.029 | 89.363 | 29.987 | 87.493 | 40.317
| 21.0653 | 329.539 | 429.694 | 89.37 | 29.985 | 87.506 | 40.316
| 21.0667 | 329.303 | 429.983 | 89.388 | 29.989 | 87.528 | 40.318
| 21.0681 | 329.4 | 429.469 | 89.397 | 29.99 | 87.538 | 40.325
| 21.0694 | 329.817 | 429.661 | 89.41 | 29.991 | 87.548 | 40.327
| 21.0708 | 329.383 | 429.704 | 89.428 | 29.994 | 87.566 | 40.324
| 21.0722 | 329.618 | 429.445 | 89.436 | 29.997 | 87.567 | 40.329
| 21.0736 | 329.827 | 428.824 | 89.442 | 29.995 | 87.571 | 40.33
| 21.075 | 329.812 | 429.535 | 89.46 | 29.994 | 87.578 | 40.333
| 21.0764 | 329.793 | 429.689 | 89.466 | 29.999 | 87.589 | 40.332
| 21.0778 | 329.893 | 429.048 | 89.474 | 30.003 | 87.593 | 40.34
| 21.0792 | 329.808 | 429.771 | 89.489 | 30.004 | 87.597 | 40.341
| 21.0806 | 329.734 | 429.042 | 89.498 | 30.005 | 87.611 | 40.343
| 21.0819 | 329.387 | 430.24 | 89.503 | 30.006 | 87.605 | 40.343
| 21.0833 | 329.875 | 429.914 | 89.516 | 30.01 | 87.622 | 40.345
| 21.0847 | 329.94 | 429.525 | 89.525 | 30.014 | 87.629 | 40.349
| 21.0861 | 329.49 | 430.457 | 89.534 | 30.012 | 87.634 | 40.349
| 21.0875 | 330.112 | 430.155 | 89.552 | 30.018 | 87.644 | 40.353
| 21.0889 | 329.412 | 430.355 | 89.56 | 30.018 | 87.658 | 40.352
| 21.0903 | 329.454 | 430.644 | 89.57 | 30.02 | 87.663 | 40.357
| 21.0917 | 330.346 | 430.174 | 89.579 | 30.019 | 87.679 | 40.363
| 21.0931 | 328.831 | 429.647 | 89.595 | 30.022 | 87.689 | 40.358
| 21.0944 | 327.007 | 427.07 | 89.542 | 30.027 | 87.605 | 40.363
| 21.0958 | 327.666 | 426.039 | 89.513 | 30.029 | 87.549 | 40.363
| 21.0972 | 327.699 | 425.947 | 89.495 | 30.028 | 87.506 | 40.37
| 21.0986 | 327.78 | 426.615 | 89.479 | 30.032 | 87.474 | 40.373
| 21.1 | 327.101 | 427.331 | 89.464 | 30.031 | 87.457 | 40.375
| 21.1014 | 327.07 | 427.069 | 89.456 | 30.031 | 87.436 | 40.377
| 21.1028 | 327.506 | 427.088 | 89.452 | 30.034 | 87.427 | 40.378
| 21.1042 | 327.314 | 427.736 | 89.448 | 30.035 | 87.422 | 40.381
| 21.1056 | 327.83 | 426.369 | 89.438 | 30.033 | 87.398 | 40.385
| 21.1069 | 327.348 | 427.17 | 89.425 | 30.035 | 87.398 | 40.389
| 21.1083 | 327.212 | 427.058 | 89.416 | 30.039 | 87.385 | 40.386
| 21.1097 | 328.059 | 426.581 | 89.409 | 30.043 | 87.378 | 40.387
| 21.1111 | 327.989 | 426.405 | 89.407 | 30.039 | 87.38 | 40.394
| 21.1125 | 328.046 | 426.599 | 89.398 | 30.04 | 87.378 | 40.396
| 21.1139 | 327.305 | 427.17 | 89.384 | 30.037 | 87.366 | 40.396
| 21.1153 | 327.347 | 425.772 | 89.379 | 30.043 | 87.36 | 40.4
| 21.1167 | 327.407 | 426.371 | 89.368 | 30.041 | 87.353 | 40.4
| 21.1181 | 327.009 | 426.736 | 89.362 | 30.042 | 87.353 | 40.402
| 21.1194 | 328.106 | 425.673 | 89.355 | 30.047 | 87.347 | 40.404
| 21.1208 | 327.213 | 426.978 | 89.35 | 30.045 | 87.345 | 40.405
| 21.1222 | 327.921 | 425.94 | 89.338 | 30.044 | 87.337 | 40.409
| 21.1236 | 327.231 | 425.854 | 89.332 | 30.049 | 87.333 | 40.41
| 21.125 | 326.87 | 427.046 | 89.325 | 30.046 | 87.325 | 40.412
| 21.1264 | 327.631 | 426.603 | 89.317 | 30.049 | 87.32 | 40.411
| 21.1278 | 327.455 | 425.644 | 89.31 | 30.049 | 87.321 | 40.418
| 21.1292 | 327.461 | 425.375 | 89.295 | 30.053 | 87.309 | 40.418
| 21.1306 | 326.425 | 425.961 | 89.282 | 30.047 | 87.294 | 40.418
| 21.1319 | 327.637 | 425.6 | 89.28 | 30.056 | 87.29 | 40.424
| 21.1333 | 326.766 | 426.437 | 89.267 | 30.053 | 87.286 | 40.422
| 21.1347 | 327.642 | 426.614 | 89.265 | 30.054 | 87.288 | 40.425
| 21.1361 | 327.655 | 426.275 | 89.265 | 30.057 | 87.298 | 40.426
| 21.1375 | 327.492 | 426.712 | 89.26 | 30.056 | 87.303 | 40.427
| 21.1389 | 327.202 | 426.743 | 89.258 | 30.056 | 87.303 | 40.432
| 21.1403 | 327.706 | 426.369 | 89.257 | 30.056 | 87.309 | 40.43
| 21.1417 | 327.252 | 426.855 | 89.257 | 30.059 | 87.317 | 40.435
| 21.1431 | 327.92 | 426.226 | 89.252 | 30.056 | 87.322 | 40.437
| 21.1444 | 327.396 | 425.69 | 89.25 | 30.061 | 87.313 | 40.438
| 21.1458 | 327.267 | 426.985 | 89.245 | 30.059 | 87.323 | 40.44
| 21.1472 | 327.29 | 426.985 | 89.245 | 30.061 | 87.324 | 40.439
| 21.1486 | 327.298 | 426.905 | 89.245 | 30.059 | 87.328 | 40.437
| 21.15 | 327.902 | 426.541 | 89.24 | 30.062 | 87.337 | 40.44
| 21.1514 | 327.659 | 426.279 | 89.239 | 30.063 | 87.337 | 40.441
| 21.1528 | 327.432 | 426.577 | 89.235 | 30.062 | 87.346 | 40.44
| 21.1542 | 328.053 | 426.069 | 89.236 | 30.064 | 87.342 | 40.445
| 21.1556 | 328.011 | 425.893 | 89.234 | 30.067 | 87.346 | 40.448
| 21.1569 | 328.077 | 425.329 | 89.229 | 30.067 | 87.34 | 40.452
| 21.1583 | 328.099 | 425.662 | 89.23 | 30.066 | 87.353 | 40.45
| 21.1597 | 327.802 | 426.639 | 89.236 | 30.07 | 87.359 | 40.452
| 21.1611 | 327.871 | 426.285 | 89.235 | 30.067 | 87.362 | 40.455
| 21.1625 | 327.614 | 426.802 | 89.232 | 30.07 | 87.361 | 40.458
| 21.1639 | 328.227 | 425.682 | 89.237 | 30.072 | 87.365 | 40.455
| 21.1653 | 327.496 | 426.133 | 89.236 | 30.07 | 87.367 | 40.454
| 21.1667 | 327.962 | 425.433 | 89.227 | 30.068 | 87.366 | 40.457
| 21.1681 | 328.001 | 425.328 | 89.227 | 30.075 | 87.366 | 40.461
| 21.1694 | 328.21 | 425.926 | 89.232 | 30.072 | 87.37 | 40.466
| 21.1708 | 327.843 | 426.72 | 89.237 | 30.081 | 87.376 | 40.462
| 21.1722 | 328.498 | 426.117 | 89.238 | 30.075 | 87.386 | 40.466
| 21.1736 | 328.091 | 425.791 | 89.245 | 30.077 | 87.397 | 40.467
| 21.175 | 327.305 | 425.386 | 89.234 | 30.076 | 87.387 | 40.47
| 21.1764 | 326.866 | 426.139 | 89.22 | 30.079 | 87.371 | 40.47
| 21.1778 | 327.392 | 426.365 | 89.218 | 30.081 | 87.367 | 40.474
| 21.1792 | 326.841 | 426.454 | 89.212 | 30.08 | 87.359 | 40.473
| 21.1806 | 327.309 | 426.453 | 89.211 | 30.079 | 87.354 | 40.474
| 21.1819 | 327.208 | 426.706 | 89.209 | 30.084 | 87.354 | 40.474
| 21.1833 | 327.306 | 425.861 | 89.204 | 30.082 | 87.352 | 40.481
| 21.1847 | 327.298 | 426.226 | 89.196 | 30.081 | 87.341 | 40.479
| 21.1861 | 326.952 | 425.312 | 89.19 | 30.082 | 87.339 | 40.481
| 21.1875 | 327.804 | 425.567 | 89.181 | 30.085 | 87.328 | 40.484
| 21.1889 | 327.647 | 425.087 | 89.179 | 30.086 | 87.323 | 40.484
| 21.1903 | 327.263 | 425.266 | 89.175 | 30.086 | 87.313 | 40.483
| 21.1917 | 326.522 | 425.459 | 89.159 | 30.087 | 87.304 | 40.487
| 21.1931 | 327.451 | 425.376 | 89.154 | 30.086 | 87.295 | 40.487
| 21.1944 | 326.957 | 426.238 | 89.146 | 30.091 | 87.291 | 40.49
| 21.1958 | 327.45 | 426.113 | 89.157 | 30.088 | 87.301 | 40.493
| 21.1972 | 327.591 | 426.632 | 89.155 | 30.093 | 87.316 | 40.496
| 21.1986 | 327.923 | 425.469 | 89.163 | 30.088 | 87.329 | 40.498
| 21.2 | 327.628 | 425.686 | 89.161 | 30.091 | 87.33 | 40.5
| 21.2014 | 327.05 | 425.777 | 89.156 | 30.09 | 87.32 | 40.495
| 21.2028 | 326.809 | 425.496 | 89.147 | 30.088 | 87.313 | 40.503
| 21.2042 | 326.864 | 425.919 | 89.143 | 30.091 | 87.315 | 40.502
| 21.2056 | 327.53 | 425.01 | 89.131 | 30.093 | 87.314 | 40.5
| 21.2069 | 326.562 | 425.253 | 89.135 | 30.098 | 87.313 | 40.504
| 21.2083 | 326.533 | 425.544 | 89.128 | 30.098 | 87.304 | 40.507
| 21.2097 | 326.733 | 425.716 | 89.125 | 30.098 | 87.298 | 40.506
| 21.2111 | 327.192 | 425.589 | 89.115 | 30.096 | 87.296 | 40.508
| 21.2125 | 326.066 | 424.807 | 89.104 | 30.1 | 87.28 | 40.512
| 21.2139 | 326.154 | 424.149 | 89.084 | 30.095 | 87.255 | 40.511
| 21.2153 | 326.296 | 422.993 | 89.071 | 30.098 | 87.234 | 40.511
| 21.2167 | 325.64 | 424.187 | 89.049 | 30.103 | 87.209 | 40.511
| 21.2181 | 325.913 | 424.225 | 89.045 | 30.103 | 87.201 | 40.518
| 21.2194 | 325.979 | 423.452 | 89.028 | 30.1 | 87.182 | 40.514
| 21.2208 | 326.139 | 422.908 | 89.008 | 30.101 | 87.168 | 40.517
| 21.2222 | 325.904 | 422.91 | 88.989 | 30.107 | 87.15 | 40.519
| 21.2236 | 325.453 | 424.054 | 88.974 | 30.105 | 87.136 | 40.521
| 21.225 | 325.999 | 422.686 | 88.951 | 30.106 | 87.116 | 40.52
| 21.2264 | 325.725 | 422.738 | 88.937 | 30.106 | 87.097 | 40.523
| 21.2278 | 325.677 | 422.39 | 88.914 | 30.104 | 87.077 | 40.525
| 21.2292 | 324.678 | 422.516 | 88.898 | 30.106 | 87.059 | 40.522
| 21.2306 | 324.782 | 422.962 | 88.874 | 30.106 | 87.034 | 40.524
| 21.2319 | 324.941 | 421.48 | 88.855 | 30.107 | 87.012 | 40.525
| 21.2333 | 324.948 | 421.733 | 88.822 | 30.099 | 86.982 | 40.527
| 21.2347 | 324.271 | 421.858 | 88.799 | 30.104 | 86.959 | 40.528
| 21.2361 | 325.099 | 421.54 | 88.773 | 30.101 | 86.931 | 40.528
| 21.2375 | 326.012 | 424.852 | 88.759 | 30.101 | 86.918 | 40.533
| 21.2389 | 326.629 | 424.869 | 88.783 | 30.104 | 86.971 | 40.534
| 21.2403 | 326.483 | 424.155 | 88.797 | 30.105 | 87.013 | 40.534
| 21.2417 | 325.847 | 423.858 | 88.797 | 30.105 | 87.028 | 40.535
| 21.2431 | 326.448 | 423.409 | 88.789 | 30.102 | 87.033 | 40.537
| 21.2444 | 325.564 | 423.336 | 88.78 | 30.103 | 87.038 | 40.533
| 21.2458 | 325.813 | 424.35 | 88.778 | 30.107 | 87.051 | 40.538
| 21.2472 | 326.28 | 423.099 | 88.763 | 30.106 | 87.051 | 40.542
| 21.2486 | 325.924 | 422.916 | 88.757 | 30.106 | 87.038 | 40.536
| 21.25 | 327.383 | 424.72 | 88.753 | 30.106 | 87.044 | 40.541
| 21.2514 | 326.842 | 424.654 | 88.766 | 30.107 | 87.075 | 40.541
| 21.2528 | 326.774 | 424.239 | 88.776 | 30.105 | 87.086 | 40.544
| 21.2542 | 327.001 | 424.279 | 88.766 | 30.106 | 87.098 | 40.547
| 21.2556 | 325.862 | 424.967 | 88.768 | 30.104 | 87.106 | 40.542
| 21.2569 | 326.102 | 425.231 | 88.76 | 30.107 | 87.101 | 40.539
| 21.2583 | 325.353 | 424.48 | 88.758 | 30.109 | 87.1 | 40.542
| 21.2597 | 326.181 | 423.679 | 88.741 | 30.11 | 87.09 | 40.547
| 21.2611 | 325.508 | 423.109 | 88.724 | 30.107 | 87.061 | 40.542
| 21.2625 | 325.153 | 422.428 | 88.705 | 30.107 | 87.033 | 40.549
| 21.2639 | 323.751 | 420.901 | 88.673 | 30.11 | 86.996 | 40.549
| 21.2653 | 326.831 | 426.792 | 88.676 | 30.11 | 87.006 | 40.548
| 21.2667 | 327.031 | 425.717 | 88.693 | 30.111 | 87.042 | 40.548
| 21.2681 | 326.83 | 426.395 | 88.715 | 30.109 | 87.081 | 40.549
| 21.2694 | 326.359 | 425.904 | 88.73 | 30.109 | 87.11 | 40.553
| 21.2708 | 328 | 425.941 | 88.741 | 30.11 | 87.129 | 40.55
| 21.2722 | 327.357 | 425.545 | 88.747 | 30.109 | 87.152 | 40.55
| 21.2736 | 326.913 | 426.523 | 88.757 | 30.111 | 87.168 | 40.553
| 21.275 | 327.213 | 425.954 | 88.755 | 30.112 | 87.171 | 40.55
| 21.2764 | 326.769 | 425.031 | 88.746 | 30.11 | 87.164 | 40.549
| 21.2778 | 326.58 | 424.438 | 88.736 | 30.11 | 87.144 | 40.556
| 21.2792 | 326.082 | 423.618 | 88.731 | 30.112 | 87.138 | 40.556
| 21.2806 | 325.971 | 423.153 | 88.716 | 30.112 | 87.114 | 40.556
| 21.2819 | 325.481 | 424.091 | 88.703 | 30.112 | 87.087 | 40.556
| 21.2833 | 326.069 | 423.617 | 88.691 | 30.112 | 87.072 | 40.557
| 21.2847 | 324.455 | 423.32 | 88.672 | 30.113 | 87.045 | 40.558
| 21.2861 | 325.384 | 424.296 | 88.658 | 30.114 | 87.024 | 40.558
| 21.2875 | 325.057 | 424.059 | 88.643 | 30.117 | 87.008 | 40.558
| 21.2889 | 325.279 | 423.116 | 88.631 | 30.115 | 86.991 | 40.56
| 21.2903 | 324.944 | 422.62 | 88.618 | 30.115 | 86.969 | 40.559
| 21.2917 | 323.906 | 422.346 | 88.59 | 30.112 | 86.939 | 40.566
| 21.2931 | 327.895 | 427.386 | 88.635 | 30.115 | 87.013 | 40.569
| 21.2944 | 328.976 | 426.998 | 88.688 | 30.118 | 87.101 | 40.568
| 21.2958 | 328.443 | 426.315 | 88.715 | 30.117 | 87.157 | 40.567
| 21.2972 | 327.362 | 426.772 | 88.732 | 30.115 | 87.196 | 40.57
| 21.2986 | 327.831 | 426.247 | 88.74 | 30.116 | 87.215 | 40.57
| 21.3 | 327.115 | 425.256 | 88.748 | 30.115 | 87.23 | 40.568
| 21.3014 | 326.665 | 425.212 | 88.745 | 30.117 | 87.232 | 40.564
| 21.3028 | 326.616 | 425.534 | 88.746 | 30.118 | 87.223 | 40.571
| 21.3042 | 326.25 | 425.064 | 88.747 | 30.119 | 87.217 | 40.573
| 21.3056 | 326.449 | 423.874 | 88.735 | 30.12 | 87.202 | 40.57
| 21.3069 | 325.472 | 424.547 | 88.719 | 30.122 | 87.186 | 40.572
| 21.3083 | 325.822 | 423.351 | 88.712 | 30.119 | 87.171 | 40.574
| 21.3097 | 328.133 | 427.962 | 88.749 | 30.123 | 87.237 | 40.572
| 21.3111 | 328.714 | 427.91 | 88.801 | 30.124 | 87.303 | 40.575
| 21.3125 | 327.488 | 426.765 | 88.83 | 30.125 | 87.35 | 40.573
| 21.3139 | 328.223 | 425.888 | 88.84 | 30.121 | 87.367 | 40.576
| 21.3153 | 327.725 | 426.805 | 88.847 | 30.127 | 87.375 | 40.578
| 21.3167 | 327.881 | 425.528 | 88.857 | 30.127 | 87.383 | 40.581
| 21.3181 | 327.503 | 426.315 | 88.854 | 30.126 | 87.377 | 40.587
| 21.3194 | 327.699 | 424.705 | 88.858 | 30.125 | 87.371 | 40.583
| 21.3208 | 327.361 | 425.324 | 88.87 | 30.128 | 87.374 | 40.582
| 21.3222 | 327.621 | 425.212 | 88.87 | 30.128 | 87.375 | 40.584
| 21.3236 | 327.801 | 426.061 | 88.881 | 30.132 | 87.385 | 40.585
| 21.325 | 327.387 | 425.44 | 88.889 | 30.135 | 87.39 | 40.585
| 21.3264 | 326.598 | 424.858 | 88.89 | 30.134 | 87.378 | 40.587
| 21.3278 | 326.482 | 424.398 | 88.886 | 30.137 | 87.372 | 40.586
| 21.3292 | 326.679 | 424.982 | 88.885 | 30.135 | 87.368 | 40.584
| 21.3306 | 326.506 | 425.038 | 88.883 | 30.135 | 87.36 | 40.596
| 21.3319 | 326.035 | 423.316 | 88.887 | 30.132 | 87.346 | 40.597
| 21.3333 | 326.019 | 424.227 | 88.871 | 30.135 | 87.327 | 40.595
| 21.3347 | 326.435 | 422.6 | 88.854 | 30.139 | 87.297 | 40.597
| 21.3361 | 325.23 | 423.179 | 88.839 | 30.139 | 87.269 | 40.601
| 21.3375 | 324.97 | 422.308 | 88.82 | 30.14 | 87.241 | 40.6
| 21.3389 | 326.301 | 422.436 | 88.807 | 30.142 | 87.212 | 40.605
| 21.3403 | 325.485 | 423.67 | 88.796 | 30.142 | 87.198 | 40.603
| 21.3417 | 328.334 | 425.551 | 88.826 | 30.142 | 87.247 | 40.604
| 21.3431 | 329.244 | 427.19 | 88.874 | 30.145 | 87.327 | 40.604
| 21.3444 | 329.044 | 426.232 | 88.912 | 30.141 | 87.389 | 40.608
| 21.3458 | 328.828 | 426.475 | 88.935 | 30.143 | 87.437 | 40.608
| 21.3472 | 328.966 | 426.464 | 88.948 | 30.138 | 87.466 | 40.61
| 21.3486 | 327.454 | 425.625 | 88.951 | 30.143 | 87.477 | 40.612
| 21.35 | 328.54 | 426.115 | 88.963 | 30.147 | 87.493 | 40.617
| 21.3514 | 328.974 | 426.293 | 88.982 | 30.148 | 87.511 | 40.614
| 21.3528 | 327.969 | 426.492 | 88.99 | 30.147 | 87.52 | 40.614
| 21.3542 | 328.283 | 427.146 | 88.999 | 30.149 | 87.532 | 40.615
| 21.3556 | 328.605 | 425.295 | 89.013 | 30.15 | 87.536 | 40.615
| 21.3569 | 327.985 | 425.22 | 89.023 | 30.152 | 87.536 | 40.621
| 21.3583 | 327.593 | 426.298 | 89.03 | 30.152 | 87.548 | 40.622
| 21.3597 | 327.195 | 425.993 | 89.031 | 30.154 | 87.545 | 40.625
| 21.3611 | 328.142 | 425.42 | 89.034 | 30.157 | 87.543 | 40.624
| 21.3625 | 328.02 | 425.252 | 89.046 | 30.157 | 87.542 | 40.625
| 21.3639 | 328.225 | 426.317 | 89.047 | 30.157 | 87.545 | 40.624
| 21.3653 | 328.993 | 425.943 | 89.062 | 30.156 | 87.556 | 40.627
| 21.3667 | 327.972 | 426.414 | 89.068 | 30.161 | 87.559 | 40.632
| 21.3681 | 327.807 | 426.667 | 89.08 | 30.159 | 87.568 | 40.631
| 21.3694 | 328.27 | 425.612 | 89.076 | 30.161 | 87.572 | 40.634
| 21.3708 | 327.034 | 425.753 | 89.086 | 30.161 | 87.573 | 40.636
| 21.3722 | 327.45 | 425.932 | 89.086 | 30.165 | 87.569 | 40.641
| 21.3736 | 327.582 | 425.064 | 89.09 | 30.163 | 87.57 | 40.64
| 21.375 | 326.792 | 424.828 | 89.089 | 30.167 | 87.563 | 40.639
| 21.3764 | 327.638 | 426.592 | 89.085 | 30.17 | 87.559 | 40.643
| 21.3778 | 327.627 | 426.53 | 89.094 | 30.169 | 87.569 | 40.645
| 21.3792 | 327.967 | 426.292 | 89.103 | 30.175 | 87.569 | 40.641
| 21.3806 | 327.923 | 427.025 | 89.099 | 30.172 | 87.572 | 40.646
| 21.3819 | 327.993 | 426.134 | 89.11 | 30.175 | 87.585 | 40.653
| 21.3833 | 327.341 | 425.226 | 89.122 | 30.175 | 87.602 | 40.654
| 21.3847 | 328.222 | 426.74 | 89.132 | 30.175 | 87.612 | 40.655
| 21.3861 | 328.096 | 424.84 | 89.14 | 30.175 | 87.625 | 40.656
| 21.3875 | 327.485 | 426.426 | 89.145 | 30.179 | 87.632 | 40.657
| 21.3889 | 328.266 | 426.586 | 89.155 | 30.18 | 87.648 | 40.656
| 21.3903 | 327.654 | 426.361 | 89.176 | 30.179 | 87.675 | 40.658
| 21.3917 | 328.459 | 426.538 | 89.193 | 30.184 | 87.693 | 40.664
| 21.3931 | 329.297 | 426.677 | 89.21 | 30.183 | 87.721 | 40.665
| 21.3944 | 329.076 | 426.504 | 89.223 | 30.186 | 87.736 | 40.664
| 21.3958 | 328.614 | 427.033 | 89.231 | 30.182 | 87.747 | 40.665
| 21.3972 | 328.807 | 426.815 | 89.244 | 30.186 | 87.753 | 40.669
| 21.3986 | 328.327 | 426.235 | 89.253 | 30.188 | 87.769 | 40.672
| 21.4 | 327.878 | 426.793 | 89.256 | 30.188 | 87.764 | 40.675
| 21.4014 | 327.937 | 426.22 | 89.258 | 30.195 | 87.757 | 40.672
| 21.4028 | 328.729 | 426.736 | 89.264 | 30.194 | 87.763 | 40.675
| 21.4042 | 328.625 | 426.423 | 89.267 | 30.196 | 87.766 | 40.676
| 21.4056 | 328.402 | 426.109 | 89.274 | 30.196 | 87.766 | 40.684
| 21.4069 | 326.901 | 426.007 | 89.268 | 30.197 | 87.753 | 40.681
| 21.4083 | 327.326 | 426.914 | 89.263 | 30.2 | 87.738 | 40.685
| 21.4097 | 328.067 | 425.825 | 89.263 | 30.198 | 87.738 | 40.685
| 21.4111 | 327.599 | 427.198 | 89.26 | 30.2 | 87.725 | 40.692
| 21.4125 | 326.727 | 426.203 | 89.256 | 30.201 | 87.717 | 40.694
| 21.4139 | 327.764 | 425.368 | 89.254 | 30.204 | 87.71 | 40.694
| 21.4153 | 327.743 | 425.163 | 89.251 | 30.208 | 87.703 | 40.697
| 21.4167 | 327.298 | 425.939 | 89.249 | 30.208 | 87.686 | 40.701
| 21.4181 | 326.915 | 425.66 | 89.235 | 30.205 | 87.672 | 40.698
| 21.4194 | 327.707 | 425.534 | 89.238 | 30.205 | 87.673 | 40.702
| 21.4208 | 327.407 | 426.373 | 89.235 | 30.208 | 87.671 | 40.703
| 21.4222 | 327.528 | 426.921 | 89.236 | 30.209 | 87.677 | 40.703
| 21.4236 | 326.845 | 425.981 | 89.242 | 30.213 | 87.686 | 40.706
| 21.425 | 327.829 | 425.526 | 89.239 | 30.214 | 87.684 | 40.706
| 21.4264 | 327.097 | 426.299 | 89.233 | 30.216 | 87.682 | 40.714
| 21.4278 | 327.269 | 425.787 | 89.23 | 30.215 | 87.683 | 40.713
| 21.4292 | 327.344 | 425.253 | 89.227 | 30.213 | 87.674 | 40.718
| 21.4306 | 327.545 | 426.942 | 89.233 | 30.217 | 87.694 | 40.719
| 21.4319 | 327.591 | 425.822 | 89.243 | 30.215 | 87.706 | 40.719
| 21.4333 | 327.171 | 425.875 | 89.242 | 30.218 | 87.709 | 40.719
| 21.4347 | 327.156 | 426.565 | 89.253 | 30.22 | 87.728 | 40.722
| 21.4361 | 327.945 | 427.007 | 89.251 | 30.22 | 87.732 | 40.723
| 21.4375 | 327.661 | 426.658 | 89.258 | 30.221 | 87.738 | 40.723
| 21.4389 | 328.306 | 426.327 | 89.259 | 30.223 | 87.748 | 40.728
| 21.4403 | 327.691 | 427.06 | 89.261 | 30.225 | 87.753 | 40.727
| 21.4417 | 328.631 | 426.329 | 89.267 | 30.226 | 87.761 | 40.736
| 21.4431 | 328.198 | 425.391 | 89.276 | 30.228 | 87.776 | 40.734
| 21.4444 | 327.968 | 425.243 | 89.271 | 30.226 | 87.772 | 40.734
| 21.4458 | 327.644 | 426.811 | 89.271 | 30.232 | 87.772 | 40.735
| 21.4472 | 327.91 | 425.516 | 89.279 | 30.231 | 87.774 | 40.74
| 21.4486 | 328.136 | 427.136 | 89.277 | 30.231 | 87.777 | 40.742
| 21.45 | 328.306 | 427.384 | 89.294 | 30.231 | 87.806 | 40.739
| 21.4514 | 328.841 | 426.48 | 89.303 | 30.228 | 87.819 | 40.748
| 21.4528 | 328.07 | 425.599 | 89.304 | 30.229 | 87.823 | 40.746
| 21.4542 | 328.017 | 426.909 | 89.309 | 30.235 | 87.818 | 40.748
| 21.4556 | 327.545 | 426.955 | 89.313 | 30.238 | 87.83 | 40.752
| 21.4569 | 328.142 | 426.171 | 89.31 | 30.234 | 87.823 | 40.751
| 21.4583 | 328.118 | 425.778 | 89.307 | 30.241 | 87.821 | 40.751
| 21.4597 | 327.295 | 426.754 | 89.306 | 30.238 | 87.823 | 40.752
| 21.4611 | 328.141 | 426.431 | 89.319 | 30.238 | 87.837 | 40.754
| 21.4625 | 327.31 | 426.939 | 89.327 | 30.237 | 87.845 | 40.759
| 21.4639 | 327.642 | 427.217 | 89.332 | 30.243 | 87.858 | 40.761
| 21.4653 | 328.643 | 426.555 | 89.329 | 30.243 | 87.857 | 40.762
| 21.4667 | 327.653 | 427.198 | 89.339 | 30.245 | 87.861 | 40.762
| 21.4681 | 327.347 | 426.544 | 89.335 | 30.241 | 87.853 | 40.765
| 21.4694 | 327.835 | 425.062 | 89.328 | 30.246 | 87.838 | 40.767
| 21.4708 | 327.629 | 425.17 | 89.317 | 30.25 | 87.814 | 40.77
| 21.4722 | 326.748 | 425.758 | 89.307 | 30.25 | 87.801 | 40.772
| 21.4736 | 326.896 | 423.868 | 89.295 | 30.247 | 87.788 | 40.769
| 21.475 | 327.219 | 423.876 | 89.279 | 30.251 | 87.758 | 40.775
| 21.4764 | 326.928 | 424.35 | 89.274 | 30.252 | 87.743 | 40.772
| 21.4778 | 327.12 | 425.035 | 89.264 | 30.248 | 87.731 | 40.778
| 21.4792 | 326.794 | 424.111 | 89.258 | 30.253 | 87.727 | 40.779
| 21.4806 | 326.567 | 425.287 | 89.247 | 30.253 | 87.709 | 40.782
| 21.4819 | 327.545 | 425.048 | 89.241 | 30.255 | 87.702 | 40.784
| 21.4833 | 326.878 | 425.002 | 89.242 | 30.252 | 87.712 | 40.791
| 21.4847 | 327.624 | 424.496 | 89.238 | 30.256 | 87.712 | 40.79
| 21.4861 | 326.865 | 425.536 | 89.236 | 30.257 | 87.709 | 40.785
| 21.4875 | 326.971 | 425.558 | 89.232 | 30.254 | 87.712 | 40.791
| 21.4889 | 326.375 | 425.079 | 89.225 | 30.259 | 87.71 | 40.792
| 21.4903 | 326.561 | 425.161 | 89.221 | 30.259 | 87.711 | 40.795
| 21.4917 | 327.417 | 424.884 | 89.221 | 30.262 | 87.717 | 40.794
| 21.4931 | 327.449 | 425.066 | 89.223 | 30.263 | 87.723 | 40.793
| 21.4944 | 326.367 | 425.121 | 89.224 | 30.26 | 87.724 | 40.797
| 21.4958 | 327.456 | 424.591 | 89.212 | 30.262 | 87.72 | 40.802
| 21.4972 | 326.265 | 424.937 | 89.207 | 30.261 | 87.709 | 40.801
| 21.4986 | 325.93 | 423.182 | 89.187 | 30.265 | 87.694 | 40.801
| 21.5 | 326.916 | 425.042 | 89.18 | 30.262 | 87.679 | 40.804
| 21.5014 | 326.958 | 424.567 | 89.177 | 30.261 | 87.679 | 40.806
| 21.5028 | 326.669 | 424.803 | 89.176 | 30.267 | 87.686 | 40.807
| 21.5042 | 327.221 | 424.332 | 89.172 | 30.264 | 87.686 | 40.804
| 21.5056 | 326.974 | 425.539 | 89.169 | 30.265 | 87.683 | 40.809
| 21.5069 | 326.68 | 425.071 | 89.159 | 30.267 | 87.673 | 40.814
| 21.5083 | 326.632 | 423.274 | 89.159 | 30.267 | 87.677 | 40.812
| 21.5097 | 326.266 | 424.689 | 89.151 | 30.268 | 87.68 | 40.818
| 21.5111 | 327.381 | 425.011 | 89.151 | 30.269 | 87.67 | 40.812
| 21.5125 | 327.684 | 424.998 | 89.148 | 30.269 | 87.684 | 40.814
| 21.5139 | 328.343 | 426.926 | 89.161 | 30.27 | 87.708 | 40.818
| 21.5153 | 327.749 | 426.865 | 89.173 | 30.269 | 87.743 | 40.818
| 21.5167 | 328.87 | 426.279 | 89.185 | 30.271 | 87.768 | 40.818
| 21.5181 | 328.905 | 426.328 | 89.197 | 30.269 | 87.8 | 40.818
| 21.5194 | 328.958 | 426.653 | 89.211 | 30.271 | 87.816 | 40.824
| 21.5208 | 327.881 | 427.339 | 89.225 | 30.274 | 87.84 | 40.823
| 21.5222 | 328.68 | 426.615 | 89.235 | 30.271 | 87.864 | 40.829
| 21.5236 | 328.015 | 427.538 | 89.254 | 30.275 | 87.889 | 40.827
| 21.525 | 328.543 | 426.568 | 89.268 | 30.275 | 87.912 | 40.825
| 21.5264 | 328.473 | 427.82 | 89.268 | 30.277 | 87.925 | 40.827
| 21.5278 | 328.491 | 426.17 | 89.279 | 30.276 | 87.936 | 40.827
| 21.5292 | 328.181 | 425.581 | 89.279 | 30.277 | 87.938 | 40.83
| 21.5306 | 327.686 | 427.023 | 89.277 | 30.28 | 87.929 | 40.83
| 21.5319 | 328.408 | 426.287 | 89.284 | 30.279 | 87.928 | 40.832
| 21.5333 | 328.836 | 426.684 | 89.287 | 30.279 | 87.928 | 40.832
| 21.5347 | 328.289 | 426.099 | 89.289 | 30.282 | 87.933 | 40.832
| 21.5361 | 328.039 | 427.578 | 89.296 | 30.284 | 87.944 | 40.837
| 21.5375 | 327.76 | 427.407 | 89.298 | 30.28 | 87.94 | 40.84
| 21.5389 | 328.672 | 426.799 | 89.303 | 30.284 | 87.946 | 40.841
| 21.5403 | 328.46 | 426.289 | 89.312 | 30.283 | 87.958 | 40.838
| 21.5417 | 327.929 | 426.117 | 89.311 | 30.287 | 87.945 | 40.846
| 21.5431 | 327.776 | 427.364 | 89.307 | 30.288 | 87.946 | 40.84
| 21.5444 | 328.235 | 426.037 | 89.318 | 30.286 | 87.948 | 40.846
| 21.5458 | 328.356 | 427.003 | 89.318 | 30.289 | 87.941 | 40.849
| 21.5472 | 328.095 | 425.901 | 89.324 | 30.285 | 87.944 | 40.851
| 21.5486 | 327.71 | 427.054 | 89.315 | 30.291 | 87.94 | 40.847
| 21.55 | 328.191 | 425.739 | 89.323 | 30.292 | 87.94 | 40.849
| 21.5514 | 327.812 | 425.416 | 89.317 | 30.293 | 87.938 | 40.854
| 21.5528 | 327.579 | 426.671 | 89.322 | 30.289 | 87.935 | 40.852
| 21.5542 | 328.004 | 427.254 | 89.326 | 30.295 | 87.937 | 40.858
| 21.5556 | 328.072 | 425.63 | 89.317 | 30.296 | 87.928 | 40.857
| 21.5569 | 327.541 | 426.365 | 89.311 | 30.299 | 87.92 | 40.853
| 21.5583 | 326.534 | 425.738 | 89.306 | 30.298 | 87.91 | 40.863
| 21.5597 | 326.822 | 425.246 | 89.303 | 30.297 | 87.906 | 40.857
| 21.5611 | 327.865 | 425.402 | 89.299 | 30.295 | 87.895 | 40.866
| 21.5625 | 326.439 | 425.732 | 89.291 | 30.3 | 87.886 | 40.864
| 21.5639 | 327.404 | 425.09 | 89.29 | 30.3 | 87.878 | 40.867
| 21.5653 | 326.702 | 425.569 | 89.288 | 30.304 | 87.873 | 40.871
| 21.5667 | 327.408 | 425.225 | 89.279 | 30.303 | 87.869 | 40.869
| 21.5681 | 327.139 | 425.082 | 89.272 | 30.302 | 87.864 | 40.871
| 21.5694 | 327.5 | 425.163 | 89.271 | 30.302 | 87.863 | 40.872
| 21.5708 | 327.139 | 424.228 | 89.266 | 30.305 | 87.857 | 40.876
| 21.5722 | 327.262 | 425.42 | 89.262 | 30.307 | 87.848 | 40.875
| 21.5736 | 327.368 | 425.539 | 89.257 | 30.303 | 87.846 | 40.877
| 21.575 | 327.647 | 426.06 | 89.254 | 30.307 | 87.842 | 40.876
| 21.5764 | 326.477 | 425.677 | 89.248 | 30.309 | 87.845 | 40.878
| 21.5778 | 327.179 | 425.864 | 89.247 | 30.305 | 87.847 | 40.883
| 21.5792 | 327.14 | 425.459 | 89.235 | 30.305 | 87.836 | 40.879
| 21.5806 | 326.839 | 426.242 | 89.236 | 30.309 | 87.834 | 40.887
| 21.5819 | 327.793 | 425.245 | 89.234 | 30.308 | 87.835 | 40.887
| 21.5833 | 327.979 | 425.618 | 89.229 | 30.306 | 87.834 | 40.886
| 21.5847 | 327.705 | 425.238 | 89.231 | 30.309 | 87.837 | 40.885
| 21.5861 | 327.333 | 426.502 | 89.241 | 30.311 | 87.853 | 40.887
| 21.5875 | 327.143 | 425.033 | 89.238 | 30.309 | 87.861 | 40.887
| 21.5889 | 327.968 | 426.293 | 89.243 | 30.311 | 87.868 | 40.89
| 21.5903 | 327.287 | 426.921 | 89.245 | 30.307 | 87.876 | 40.892
| 21.5917 | 327.501 | 426.635 | 89.246 | 30.31 | 87.885 | 40.892
| 21.5931 | 327.245 | 425.846 | 89.254 | 30.313 | 87.895 | 40.895
| 21.5944 | 328.386 | 426.299 | 89.259 | 30.316 | 87.914 | 40.895
| 21.5958 | 327.876 | 427.72 | 89.264 | 30.317 | 87.921 | 40.895
| 21.5972 | 328.619 | 427.105 | 89.277 | 30.314 | 87.944 | 40.899
| 21.5986 | 328.928 | 428.338 | 89.293 | 30.315 | 87.98 | 40.896
| 21.6 | 328.602 | 426.925 | 89.307 | 30.312 | 88.003 | 40.897
| 21.6014 | 328.399 | 427.333 | 89.313 | 30.317 | 88.018 | 40.9
| 21.6028 | 328.298 | 426.154 | 89.31 | 30.313 | 88.012 | 40.905
| 21.6042 | 327.894 | 426.427 | 89.303 | 30.319 | 87.997 | 40.904
| 21.6056 | 327.804 | 427.618 | 89.307 | 30.321 | 88 | 40.904
| 21.6069 | 328.337 | 427.537 | 89.318 | 30.319 | 88.012 | 40.905
| 21.6083 | 328.343 | 426.221 | 89.326 | 30.32 | 88.019 | 40.906
| 21.6097 | 327.978 | 426.902 | 89.333 | 30.322 | 88.033 | 40.909
| 21.6111 | 328.473 | 426.288 | 89.346 | 30.321 | 88.045 | 40.912
| 21.6125 | 328.856 | 426.837 | 89.351 | 30.321 | 88.05 | 40.914
| 21.6139 | 328.368 | 428.454 | 89.359 | 30.323 | 88.052 | 40.913
| 21.6153 | 328.402 | 427.479 | 89.362 | 30.328 | 88.063 | 40.909
| 21.6167 | 328.065 | 427.718 | 89.371 | 30.326 | 88.07 | 40.915
| 21.6181 | 328.336 | 426.417 | 89.376 | 30.328 | 88.076 | 40.915
| 21.6194 | 328.571 | 428.405 | 89.387 | 30.327 | 88.097 | 40.918
| 21.6208 | 328.796 | 427.054 | 89.401 | 30.326 | 88.117 | 40.917
| 21.6222 | 328.564 | 428.528 | 89.416 | 30.324 | 88.141 | 40.925
| 21.6236 | 328.76 | 428.844 | 89.429 | 30.331 | 88.16 | 40.921
| 21.625 | 328.428 | 428.006 | 89.44 | 30.328 | 88.176 | 40.923
| 21.6264 | 328.853 | 428.565 | 89.457 | 30.332 | 88.191 | 40.925
| 21.6278 | 328.681 | 428.558 | 89.469 | 30.336 | 88.212 | 40.929
| 21.6292 | 328.569 | 428.033 | 89.477 | 30.336 | 88.218 | 40.93
| 21.6306 | 328.648 | 428.252 | 89.491 | 30.335 | 88.227 | 40.928
| 21.6319 | 329.497 | 428.083 | 89.504 | 30.337 | 88.242 | 40.932
| 21.6333 | 329.137 | 428.608 | 89.525 | 30.336 | 88.259 | 40.934
| 21.6347 | 329.267 | 427.769 | 89.537 | 30.339 | 88.281 | 40.933
| 21.6361 | 330.322 | 428.472 | 89.549 | 30.34 | 88.294 | 40.935
| 21.6375 | 329.805 | 427.965 | 89.567 | 30.344 | 88.31 | 40.939
| 21.6389 | 329.016 | 429.192 | 89.582 | 30.344 | 88.332 | 40.94
| 21.6403 | 330.799 | 429.347 | 89.607 | 30.34 | 88.362 | 40.941
| 21.6417 | 330.64 | 428.955 | 89.634 | 30.344 | 88.392 | 40.942
| 21.6431 | 330.657 | 428.953 | 89.655 | 30.346 | 88.419 | 40.94
| 21.6444 | 330.471 | 428.975 | 89.675 | 30.347 | 88.441 | 40.946
| 21.6458 | 330.654 | 428.925 | 89.689 | 30.348 | 88.45 | 40.949
| 21.6472 | 330.719 | 428.801 | 89.7 | 30.348 | 88.462 | 40.95
| 21.6486 | 330.495 | 429.13 | 89.72 | 30.352 | 88.483 | 40.949
| 21.65 | 329.658 | 429.547 | 89.738 | 30.353 | 88.507 | 40.951
| 21.6514 | 331.043 | 429.38 | 89.758 | 30.354 | 88.526 | 40.955
| 21.6528 | 329.975 | 429.495 | 89.779 | 30.353 | 88.546 | 40.958
| 21.6542 | 330.784 | 429 | 89.799 | 30.357 | 88.566 | 40.958
| 21.6556 | 330.21 | 429.905 | 89.821 | 30.356 | 88.593 | 40.964
| 21.6569 | 331.081 | 430.388 | 89.842 | 30.363 | 88.618 | 40.962
| 21.6583 | 330.83 | 429.967 | 89.864 | 30.361 | 88.639 | 40.964
| 21.6597 | 329.753 | 429.745 | 89.885 | 30.363 | 88.652 | 40.969
| 21.6611 | 330.394 | 430.079 | 89.905 | 30.368 | 88.669 | 40.971
| 21.6625 | 330.761 | 430.482 | 89.922 | 30.367 | 88.687 | 40.973
| 21.6639 | 330.323 | 430.772 | 89.93 | 30.371 | 88.689 | 40.97
| 21.6653 | 331.596 | 430.264 | 89.95 | 30.37 | 88.7 | 40.979
| 21.6667 | 331.037 | 429.397 | 89.971 | 30.368 | 88.723 | 40.977
| 21.6681 | 331.243 | 429.536 | 89.985 | 30.374 | 88.726 | 40.984
| 21.6694 | 331.041 | 431.198 | 89.994 | 30.377 | 88.738 | 40.984
| 21.6708 | 331.129 | 429.493 | 90.015 | 30.379 | 88.754 | 40.982
| 21.6722 | 330.543 | 430.64 | 90.041 | 30.381 | 88.779 | 40.99
| 21.6736 | 330.392 | 430.689 | 90.052 | 30.383 | 88.791 | 40.989
| 21.675 | 330.015 | 429.777 | 90.068 | 30.379 | 88.799 | 40.995
| 21.6764 | 331.784 | 430.476 | 90.086 | 30.388 | 88.814 | 40.995
| 21.6778 | 324.909 | 430.25 | 90.103 | 30.387 | 88.832 | 41.002
| 21.6792 | 324.939 | 430.498 | 89.984 | 30.387 | 88.857 | 41.002
| 21.6806 | 319.713 | 425.007 | 89.851 | 30.392 | 88.786 | 41.001
| 21.6819 | 321.232 | 425.001 | 89.723 | 30.396 | 88.682 | 41.005
| 21.6833 | 320.963 | 426.074 | 89.625 | 30.396 | 88.604 | 41.007
| 21.6847 | 320.349 | 425.265 | 89.54 | 30.398 | 88.555 | 41.011
| 21.6861 | 321.064 | 425.734 | 89.466 | 30.399 | 88.514 | 41.014
| 21.6875 | 320.662 | 425.5 | 89.391 | 30.399 | 88.473 | 41.017
| 21.6889 | 320.705 | 426.439 | 89.319 | 30.398 | 88.435 | 41.016
| 21.6903 | 320.911 | 426.091 | 89.256 | 30.399 | 88.419 | 41.022
| 21.6917 | 321.748 | 426.217 | 89.199 | 30.394 | 88.408 | 41.023
| 21.6931 | 320.603 | 426.034 | 89.143 | 30.392 | 88.407 | 41.026
| 21.6944 | 321.107 | 426.75 | 89.088 | 30.396 | 88.402 | 41.03
| 21.6958 | 321.419 | 427.214 | 89.039 | 30.392 | 88.396 | 41.031
| 21.6972 | 321.032 | 426.786 | 88.989 | 30.391 | 88.398 | 41.035
| 21.6986 | 321.104 | 427.324 | 88.931 | 30.393 | 88.391 | 41.035
| 21.7 | 321.881 | 426.032 | 88.889 | 30.389 | 88.391 | 41.04
| 21.7014 | 321.842 | 426.454 | 88.842 | 30.388 | 88.385 | 41.041
| 21.7028 | 321.113 | 427.025 | 88.794 | 30.386 | 88.384 | 41.045
| 21.7042 | 321.032 | 426.277 | 88.745 | 30.383 | 88.374 | 41.047
| 21.7056 | 321.496 | 425.679 | 88.7 | 30.386 | 88.371 | 41.047
| 21.7069 | 321.073 | 427.138 | 88.652 | 30.384 | 88.356 | 41.048
| 21.7083 | 320.579 | 424.713 | 88.602 | 30.382 | 88.337 | 41.053
| 21.7097 | 321.749 | 426.327 | 88.559 | 30.376 | 88.334 | 41.051
| 21.7111 | 320.906 | 426.407 | 88.523 | 30.376 | 88.335 | 41.057
| 21.7125 | 321.18 | 425.342 | 88.482 | 30.375 | 88.329 | 41.057
| 21.7139 | 321.236 | 425.31 | 88.442 | 30.374 | 88.33 | 41.058
| 21.7153 | 321.67 | 425.647 | 88.402 | 30.372 | 88.317 | 41.058
| 21.7167 | 321.013 | 425.364 | 88.354 | 30.368 | 88.305 | 41.063
| 21.7181 | 320.74 | 426.573 | 88.321 | 30.367 | 88.301 | 41.062
| 21.7194 | 321.236 | 425.257 | 88.279 | 30.367 | 88.304 | 41.067
| 21.7208 | 317.993 | 422.066 | 88.227 | 30.362 | 88.267 | 41.068
| 21.7222 | 318.276 | 421.654 | 88.127 | 30.361 | 88.164 | 41.071
| 21.7236 | 318.242 | 421.137 | 88.047 | 30.357 | 88.085 | 41.07
| 21.725 | 324.999 | 421.798 | 88.079 | 30.352 | 88.019 | 41.07
| 21.7264 | 324.749 | 420.863 | 88.131 | 30.356 | 87.964 | 41.072
| 21.7278 | 324.007 | 421.639 | 88.147 | 30.349 | 87.914 | 41.075
| 21.7292 | 329.011 | 426.942 | 88.169 | 30.347 | 87.896 | 41.079
| 21.7306 | 326.076 | 422.751 | 88.229 | 30.346 | 87.948 | 41.08
| 21.7319 | 325.078 | 423.003 | 88.234 | 30.343 | 87.93 | 41.08
| 21.7333 | 324.869 | 421.671 | 88.235 | 30.337 | 87.898 | 41.085
| 21.7347 | 325.617 | 422.243 | 88.236 | 30.341 | 87.871 | 41.081
| 21.7361 | 324.556 | 422.76 | 88.232 | 30.339 | 87.844 | 41.085
| 21.7375 | 324.474 | 420.851 | 88.227 | 30.338 | 87.819 | 41.084
| 21.7389 | 325.039 | 421.471 | 88.222 | 30.337 | 87.778 | 41.085
| 21.7403 | 331.536 | 430.774 | 88.312 | 30.335 | 87.894 | 41.083
| 21.7417 | 331.45 | 431.557 | 88.438 | 30.338 | 88.074 | 41.087
| 21.7431 | 331.318 | 431.483 | 88.53 | 30.342 | 88.203 | 41.088
| 21.7444 | 331.612 | 429.884 | 88.596 | 30.334 | 88.293 | 41.091
| 21.7458 | 331.695 | 430.958 | 88.663 | 30.337 | 88.37 | 41.09
| 21.7472 | 324.7 | 422.551 | 88.726 | 30.338 | 88.44 | 41.093
| 21.7486 | 323.963 | 423.306 | 88.627 | 30.339 | 88.3 | 41.089
| 21.75 | 324.486 | 423.328 | 88.573 | 30.336 | 88.203 | 41.093
| 21.7514 | 324.581 | 422.841 | 88.544 | 30.337 | 88.15 | 41.089
| 21.7528 | 325.472 | 423.797 | 88.532 | 30.338 | 88.117 | 41.093
| 21.7542 | 324.696 | 425.011 | 88.518 | 30.341 | 88.084 | 41.097
| 21.7556 | 320.969 | 419.449 | 88.507 | 30.34 | 88.049 | 41.095
| 21.7569 | 321.361 | 418.69 | 88.413 | 30.34 | 87.9 | 41.094
| 21.7583 | 321.363 | 418.685 | 88.354 | 30.339 | 87.785 | 41.1
| 21.7597 | 321.408 | 418.53 | 88.305 | 30.341 | 87.7 | 41.098
| 21.7611 | 321.085 | 418.039 | 88.251 | 30.343 | 87.615 | 41.097
| 21.7625 | 320.484 | 419.244 | 88.209 | 30.342 | 87.55 | 41.101
| 21.7639 | 321.704 | 426.293 | 88.176 | 30.343 | 87.651 | 41.104
| 21.7653 | 320.673 | 426.444 | 88.15 | 30.341 | 87.749 | 41.099
| 21.7667 | 320.458 | 425.898 | 88.113 | 30.338 | 87.807 | 41.097
| 21.7681 | 321.458 | 425.968 | 88.079 | 30.336 | 87.85 | 41.101
| 21.7694 | 320.693 | 425.281 | 88.045 | 30.334 | 87.88 | 41.104
| 21.7708 | 320.324 | 425.095 | 88.007 | 30.33 | 87.901 | 41.104
| 21.7722 | 320.995 | 426.199 | 87.975 | 30.329 | 87.927 | 41.101
| 21.7736 | 321.435 | 424.973 | 87.949 | 30.332 | 87.947 | 41.104
| 21.775 | 320.319 | 425.661 | 87.914 | 30.327 | 87.953 | 41.103
| 21.7764 | 321.046 | 424.591 | 87.876 | 30.328 | 87.954 | 41.104
| 21.7778 | 321.68 | 425.516 | 87.855 | 30.327 | 87.971 | 41.105
| 21.7792 | 321.073 | 426.2 | 87.827 | 30.326 | 87.991 | 41.104
| 21.7806 | 321.365 | 425.838 | 87.802 | 30.323 | 87.998 | 41.107
| 21.7819 | 320.654 | 425.727 | 87.779 | 30.321 | 88.008 | 41.105
| 21.7833 | 321.005 | 426.279 | 87.748 | 30.319 | 88.01 | 41.107
| 21.7847 | 321.321 | 425.409 | 87.727 | 30.319 | 88.021 | 41.108
| 21.7861 | 321.03 | 426.173 | 87.702 | 30.317 | 88.024 | 41.107
| 21.7875 | 321.096 | 426.004 | 87.682 | 30.317 | 88.035 | 41.108
| 21.7889 | 321.302 | 425.418 | 87.662 | 30.31 | 88.045 | 41.108
| 21.7903 | 321.772 | 425.421 | 87.644 | 30.314 | 88.057 | 41.109
| 21.7917 | 321.867 | 425.522 | 87.625 | 30.311 | 88.075 | 41.108
| 21.7931 | 321.698 | 425.675 | 87.613 | 30.31 | 88.083 | 41.111
| 21.7944 | 322.038 | 426.488 | 87.6 | 30.307 | 88.102 | 41.112
| 21.7958 | 322.08 | 426.244 | 87.582 | 30.31 | 88.108 | 41.114
| 21.7972 | 321.961 | 427.07 | 87.574 | 30.303 | 88.125 | 41.113
| 21.7986 | 321.886 | 426.678 | 87.564 | 30.305 | 88.141 | 41.11
| 21.8 | 322.347 | 427.093 | 87.557 | 30.303 | 88.161 | 41.113
| 21.8014 | 322.386 | 427.759 | 87.552 | 30.305 | 88.187 | 41.117
| 21.8028 | 322.586 | 426.899 | 87.548 | 30.304 | 88.203 | 41.114
| 21.8042 | 321.851 | 426.851 | 87.537 | 30.298 | 88.213 | 41.114
| 21.8056 | 322.117 | 428.218 | 87.536 | 30.295 | 88.233 | 41.116
| 21.8069 | 323.251 | 427.39 | 87.528 | 30.296 | 88.252 | 41.115
| 21.8083 | 322.263 | 428.16 | 87.522 | 30.294 | 88.263 | 41.12
| 21.8097 | 322.222 | 428.439 | 87.518 | 30.295 | 88.281 | 41.122
| 21.8111 | 322.808 | 427.384 | 87.525 | 30.294 | 88.311 | 41.12
| 21.8125 | 323.568 | 427.887 | 87.524 | 30.292 | 88.329 | 41.125
| 21.8139 | 323.014 | 428.459 | 87.524 | 30.294 | 88.35 | 41.123
| 21.8153 | 323.182 | 429.326 | 87.534 | 30.291 | 88.374 | 41.123
| 21.8167 | 323.257 | 429.538 | 87.547 | 30.291 | 88.412 | 41.123
| 21.8181 | 323.153 | 429.47 | 87.556 | 30.29 | 88.444 | 41.126
| 21.8194 | 323.914 | 430.33 | 87.564 | 30.286 | 88.469 | 41.13
| 21.8208 | 323.576 | 429.474 | 87.577 | 30.289 | 88.5 | 41.125
| 21.8222 | 324.185 | 428.749 | 87.581 | 30.287 | 88.517 | 41.128
| 21.8236 | 324.517 | 429.061 | 87.586 | 30.285 | 88.538 | 41.132
| 21.825 | 323.827 | 430.552 | 87.6 | 30.287 | 88.568 | 41.133
| 21.8264 | 325.009 | 429.681 | 87.619 | 30.288 | 88.606 | 41.134
| 21.8278 | 324.724 | 429.943 | 87.631 | 30.281 | 88.63 | 41.138
| 21.8292 | 325.279 | 430.051 | 87.646 | 30.284 | 88.665 | 41.136
| 21.8306 | 325.21 | 430.479 | 87.659 | 30.284 | 88.688 | 41.14
| 21.8319 | 324.99 | 430.284 | 87.681 | 30.283 | 88.719 | 41.139
| 21.8333 | 324.451 | 431.049 | 87.691 | 30.286 | 88.745 | 41.143
| 21.8347 | 324.685 | 429.314 | 87.706 | 30.286 | 88.767 | 41.144
| 21.8361 | 324.537 | 430.741 | 87.711 | 30.284 | 88.786 | 41.145
| 21.8375 | 325.062 | 430.756 | 87.727 | 30.281 | 88.806 | 41.147
| 21.8389 | 325.081 | 431.365 | 87.738 | 30.282 | 88.826 | 41.151
| 21.8403 | 325.347 | 430.032 | 87.752 | 30.283 | 88.84 | 41.152
| 21.8417 | 320.759 | 424.809 | 87.743 | 30.281 | 88.824 | 41.152
| 21.8431 | 320.192 | 425.056 | 87.66 | 30.284 | 88.689 | 41.157
| 21.8444 | 320.263 | 425.4 | 87.606 | 30.281 | 88.599 | 41.16
| 21.8458 | 320.729 | 424.232 | 87.568 | 30.283 | 88.532 | 41.158
| 21.8472 | 320.279 | 425.822 | 87.535 | 30.281 | 88.482 | 41.162
| 21.8486 | 320.822 | 425.869 | 87.521 | 30.282 | 88.458 | 41.162
| 21.85 | 321.376 | 424.938 | 87.496 | 30.28 | 88.436 | 41.169
| 21.8514 | 321.35 | 425.624 | 87.478 | 30.282 | 88.417 | 41.168
| 21.8528 | 320.816 | 425.338 | 87.461 | 30.279 | 88.4 | 41.169
| 21.8542 | 320.817 | 425.596 | 87.441 | 30.281 | 88.383 | 41.175
| 21.8556 | 320.565 | 425.916 | 87.421 | 30.28 | 88.367 | 41.177
| 21.8569 | 321.469 | 425.592 | 87.405 | 30.28 | 88.358 | 41.179
| 21.8583 | 320.759 | 425.927 | 87.388 | 30.276 | 88.354 | 41.182
| 21.8597 | 321.237 | 424.716 | 87.372 | 30.276 | 88.344 | 41.183
| 21.8611 | 320.681 | 426.412 | 87.355 | 30.274 | 88.332 | 41.188
| 21.8625 | 320.888 | 426.282 | 87.341 | 30.273 | 88.33 | 41.187
| 21.8639 | 321.135 | 425.716 | 87.316 | 30.275 | 88.32 | 41.189
| 21.8653 | 321.532 | 425.887 | 87.303 | 30.274 | 88.308 | 41.19
| 21.8667 | 321.71 | 426.301 | 87.297 | 30.273 | 88.317 | 41.2
| 21.8681 | 321.733 | 426.917 | 87.291 | 30.27 | 88.33 | 41.195
| 21.8694 | 322.002 | 426.792 | 87.286 | 30.272 | 88.349 | 41.195
| 21.8708 | 321.361 | 427.356 | 87.285 | 30.27 | 88.361 | 41.203
| 21.8722 | 322.074 | 427.801 | 87.282 | 30.268 | 88.379 | 41.201
| 21.8736 | 322.117 | 427.954 | 87.281 | 30.267 | 88.391 | 41.203
| 21.875 | 322.568 | 427.639 | 87.275 | 30.267 | 88.409 | 41.205
| 21.8764 | 322.229 | 428.325 | 87.279 | 30.266 | 88.427 | 41.204
| 21.8778 | 322.397 | 427.593 | 87.285 | 30.27 | 88.449 | 41.205
| 21.8792 | 322.228 | 427.763 | 87.282 | 30.267 | 88.46 | 41.212
| 21.8806 | 320.269 | 424.368 | 87.272 | 30.265 | 88.456 | 41.213
| 21.8819 | 319.943 | 424.837 | 87.22 | 30.262 | 88.388 | 41.215
| 21.8833 | 320.791 | 424.373 | 87.186 | 30.26 | 88.348 | 41.212
| 21.8847 | 320.485 | 424.415 | 87.164 | 30.261 | 88.321 | 41.218
| 21.8861 | 320.484 | 424.232 | 87.141 | 30.261 | 88.29 | 41.215
| 21.8875 | 320.758 | 424.531 | 87.12 | 30.263 | 88.276 | 41.218
| 21.8889 | 321.094 | 426.766 | 87.109 | 30.26 | 88.271 | 41.219
| 21.8903 | 321.147 | 425.175 | 87.097 | 30.258 | 88.272 | 41.223
| 21.8917 | 320.508 | 424.124 | 87.078 | 30.258 | 88.261 | 41.227
| 21.8931 | 320.452 | 424.239 | 87.05 | 30.256 | 88.234 | 41.221
| 21.8944 | 320.481 | 424.234 | 87.025 | 30.257 | 88.213 | 41.226
| 21.8958 | 320.342 | 425.74 | 87.012 | 30.256 | 88.207 | 41.229
| 21.8972 | 319.678 | 424.822 | 86.997 | 30.253 | 88.197 | 41.232
| 21.8986 | 320.807 | 425.118 | 86.977 | 30.252 | 88.188 | 41.23
| 21.9 | 320.772 | 424.393 | 86.968 | 30.252 | 88.187 | 41.235
| 21.9014 | 320.195 | 424.31 | 86.947 | 30.253 | 88.172 | 41.239
| 21.9028 | 319.908 | 425.181 | 86.932 | 30.249 | 88.16 | 41.233
| 21.9042 | 320.05 | 425.39 | 86.917 | 30.248 | 88.16 | 41.239
| 21.9056 | 320.296 | 424.839 | 86.901 | 30.25 | 88.16 | 41.24
| 21.9069 | 320.308 | 426.01 | 86.897 | 30.247 | 88.164 | 41.24
| 21.9083 | 320.66 | 425.573 | 86.883 | 30.245 | 88.167 | 41.239
| 21.9097 | 321.237 | 425.179 | 86.88 | 30.243 | 88.177 | 41.245
| 21.9111 | 321.351 | 425.908 | 86.873 | 30.243 | 88.189 | 41.243
| 21.9125 | 320.872 | 425.497 | 86.875 | 30.244 | 88.208 | 41.247
| 21.9139 | 320.927 | 426.532 | 86.876 | 30.239 | 88.224 | 41.25
| 21.9153 | 320.947 | 426.449 | 86.868 | 30.239 | 88.237 | 41.25
| 21.9167 | 320.742 | 426.28 | 86.865 | 30.24 | 88.244 | 41.248
| 21.9181 | 321.638 | 425.423 | 86.862 | 30.239 | 88.254 | 41.248
| 21.9194 | 322.008 | 425.696 | 86.864 | 30.238 | 88.264 | 41.253
| 21.9208 | 321.681 | 427.261 | 86.87 | 30.238 | 88.291 | 41.252
| 21.9222 | 321.465 | 426.995 | 86.874 | 30.239 | 88.315 | 41.254
| 21.9236 | 321.547 | 426.82 | 86.877 | 30.237 | 88.333 | 41.253
| 21.925 | 321.755 | 427.849 | 86.887 | 30.231 | 88.352 | 41.254
| 21.9264 | 321.342 | 424.921 | 86.898 | 30.23 | 88.379 | 41.26
| 21.9278 | 319.617 | 424.598 | 86.848 | 30.231 | 88.314 | 41.257
| 21.9292 | 320.18 | 423.292 | 86.824 | 30.238 | 88.277 | 41.261
| 21.9306 | 321.007 | 424.872 | 86.81 | 30.234 | 88.259 | 41.259
| 21.9319 | 320.31 | 425.315 | 86.795 | 30.233 | 88.254 | 41.259
| 21.9333 | 321.353 | 424.973 | 86.791 | 30.232 | 88.249 | 41.263
| 21.9347 | 320.526 | 425.516 | 86.786 | 30.233 | 88.244 | 41.264
| 21.9361 | 320.74 | 425.362 | 86.776 | 30.231 | 88.238 | 41.264
| 21.9375 | 320.624 | 425.917 | 86.77 | 30.228 | 88.246 | 41.267
| 21.9389 | 321.615 | 425.3 | 86.776 | 30.227 | 88.261 | 41.268
| 21.9403 | 320.84 | 426.33 | 86.776 | 30.224 | 88.274 | 41.268
| 21.9417 | 321.275 | 426.871 | 86.782 | 30.222 | 88.292 | 41.268
| 21.9431 | 321.086 | 426.685 | 86.787 | 30.222 | 88.312 | 41.273
| 21.9444 | 321.705 | 426.958 | 86.794 | 30.227 | 88.327 | 41.271
| 21.9458 | 321.667 | 426.258 | 86.803 | 30.221 | 88.344 | 41.269
| 21.9472 | 321.603 | 426.745 | 86.806 | 30.224 | 88.365 | 41.276
| 21.9486 | 321.907 | 425.776 | 86.815 | 30.224 | 88.383 | 41.276
| 21.95 | 321.382 | 426.757 | 86.816 | 30.222 | 88.388 | 41.278
| 21.9514 | 322.108 | 427.783 | 86.822 | 30.225 | 88.409 | 41.284
| 21.9528 | 322.904 | 427.712 | 86.834 | 30.225 | 88.441 | 41.278
| 21.9542 | 322.193 | 428.517 | 86.847 | 30.225 | 88.478 | 41.281
| 21.9556 | 323.235 | 427.801 | 86.86 | 30.222 | 88.501 | 41.282
| 21.9569 | 322.541 | 428.758 | 86.879 | 30.218 | 88.529 | 41.281
| 21.9583 | 323.221 | 428.045 | 86.885 | 30.223 | 88.541 | 41.284
| 21.9597 | 322.66 | 428.747 | 86.897 | 30.218 | 88.572 | 41.286
| 21.9611 | 323.356 | 428.051 | 86.911 | 30.219 | 88.586 | 41.288
| 21.9625 | 323.079 | 427.607 | 86.921 | 30.22 | 88.605 | 41.288
| 21.9639 | 323.187 | 428.217 | 86.936 | 30.221 | 88.622 | 41.296
| 21.9653 | 323.538 | 427.647 | 86.945 | 30.219 | 88.631 | 41.293
| 21.9667 | 322.334 | 428.593 | 86.955 | 30.22 | 88.649 | 41.299
| 21.9681 | 322.829 | 428.373 | 86.969 | 30.218 | 88.663 | 41.294
| 21.9694 | 323.545 | 428.171 | 86.98 | 30.22 | 88.667 | 41.298
| 21.9708 | 322.744 | 427.7 | 86.985 | 30.219 | 88.671 | 41.298
| 21.9722 | 323.86 | 428.571 | 86.995 | 30.223 | 88.689 | 41.304
| 21.9736 | 323.672 | 428.803 | 87.014 | 30.219 | 88.714 | 41.302
| 21.975 | 324.089 | 429.032 | 87.036 | 30.219 | 88.745 | 41.307
| 21.9764 | 324.002 | 429.953 | 87.062 | 30.222 | 88.783 | 41.307
| 21.9778 | 323.748 | 429.677 | 87.087 | 30.222 | 88.813 | 41.309
| 21.9792 | 323.561 | 429.607 | 87.106 | 30.221 | 88.835 | 41.307
| 21.9806 | 323.059 | 429.286 | 87.114 | 30.221 | 88.84 | 41.312
| 21.9819 | 323.574 | 428.295 | 87.114 | 30.222 | 88.837 | 41.311
| 21.9833 | 323.178 | 428.137 | 87.124 | 30.22 | 88.839 | 41.316
| 21.9847 | 323.379 | 428.557 | 87.132 | 30.222 | 88.834 | 41.321
| 21.9861 | 323.656 | 429.084 | 87.138 | 30.224 | 88.842 | 41.32
| 21.9875 | 323.482 | 429.254 | 87.154 | 30.221 | 88.861 | 41.322
| 21.9889 | 323.241 | 428.906 | 87.164 | 30.221 | 88.874 | 41.327
| 21.9903 | 324.021 | 428.194 | 87.175 | 30.224 | 88.878 | 41.331
| 21.9917 | 322.777 | 428.696 | 87.18 | 30.224 | 88.883 | 41.33
| 21.9931 | 324.234 | 429.1 | 87.195 | 30.225 | 88.894 | 41.335
| 21.9944 | 323.878 | 429.468 | 87.211 | 30.225 | 88.914 | 41.334
| 21.9958 | 324.509 | 428.907 | 87.227 | 30.229 | 88.931 | 41.335
| 21.9972 | 323.798 | 430.122 | 87.241 | 30.23 | 88.949 | 41.335
| 21.9986 | 319.794 | 424.7 | 87.195 | 30.227 | 88.874 | 41.342
| 22 | 320.332 | 425.466 | 87.152 | 30.231 | 88.787 | 41.347
| 22.0014 | 320.542 | 425.554 | 87.116 | 30.231 | 88.732 | 41.345
| 22.0028 | 320.806 | 424.752 | 87.101 | 30.23 | 88.688 | 41.348
| 22.0042 | 320.242 | 425.071 | 87.077 | 30.229 | 88.653 | 41.352
| 22.0056 | 320.05 | 425.612 | 87.061 | 30.231 | 88.623 | 41.354
| 22.0069 | 319.434 | 422.214 | 87.021 | 30.233 | 88.563 | 41.359
| 22.0083 | 319.512 | 422.47 | 86.977 | 30.231 | 88.494 | 41.359
| 22.0097 | 318.854 | 423.487 | 86.946 | 30.232 | 88.452 | 41.364
| 22.0111 | 319.437 | 422.453 | 86.912 | 30.234 | 88.407 | 41.366
| 22.0125 | 319.339 | 422.966 | 86.884 | 30.228 | 88.374 | 41.369
| 22.0139 | 320.332 | 424.159 | 86.867 | 30.229 | 88.367 | 41.369
| 22.0153 | 319.826 | 425.099 | 86.86 | 30.23 | 88.366 | 41.369
| 22.0167 | 320.086 | 425.289 | 86.852 | 30.228 | 88.371 | 41.371
| 22.0181 | 321.222 | 424.67 | 86.845 | 30.226 | 88.387 | 41.378
| 22.0194 | 320.13 | 424.883 | 86.839 | 30.227 | 88.386 | 41.377
| 22.0208 | 320.675 | 424.113 | 86.821 | 30.227 | 88.383 | 41.379
| 22.0222 | 320.412 | 425.38 | 86.81 | 30.227 | 88.39 | 41.381
| 22.0236 | 320.74 | 424.257 | 86.797 | 30.228 | 88.389 | 41.385
| 22.025 | 320.479 | 426.074 | 86.792 | 30.226 | 88.392 | 41.383
| 22.0264 | 320.308 | 425.517 | 86.786 | 30.229 | 88.41 | 41.383
| 22.0278 | 320.136 | 425.453 | 86.776 | 30.223 | 88.411 | 41.385
| 22.0292 | 320.751 | 425.692 | 86.771 | 30.225 | 88.413 | 41.389
| 22.0306 | 320.762 | 425.648 | 86.766 | 30.225 | 88.421 | 41.389
| 22.0319 | 320.55 | 425.909 | 86.761 | 30.225 | 88.428 | 41.397
| 22.0333 | 321.132 | 425.779 | 86.763 | 30.225 | 88.435 | 41.398
| 22.0347 | 321.864 | 425.902 | 86.759 | 30.223 | 88.449 | 41.396
| 22.0361 | 321.699 | 425.879 | 86.761 | 30.227 | 88.478 | 41.397
| 22.0375 | 320.958 | 424.979 | 86.756 | 30.222 | 88.477 | 41.398
| 22.0389 | 320.986 | 424.75 | 86.741 | 30.219 | 88.467 | 41.396
| 22.0403 | 320.753 | 424.339 | 86.728 | 30.219 | 88.452 | 41.399
| 22.0417 | 320.274 | 425.715 | 86.714 | 30.224 | 88.437 | 41.402
| 22.0431 | 320.835 | 424.676 | 86.7 | 30.222 | 88.439 | 41.405
| 22.0444 | 320.23 | 425.182 | 86.699 | 30.218 | 88.43 | 41.403
| 22.0458 | 320.904 | 424.206 | 86.693 | 30.216 | 88.432 | 41.41
| 22.0472 | 319.837 | 425.175 | 86.682 | 30.221 | 88.423 | 41.408
| 22.0486 | 320.404 | 425.199 | 86.67 | 30.223 | 88.415 | 41.408
| 22.05 | 320.062 | 424.933 | 86.664 | 30.219 | 88.415 | 41.407
| 22.0514 | 320.522 | 424.963 | 86.652 | 30.218 | 88.417 | 41.415
| 22.0528 | 320.437 | 424.505 | 86.647 | 30.218 | 88.412 | 41.415
| 22.0542 | 320.866 | 424.261 | 86.635 | 30.215 | 88.404 | 41.416
| 22.0556 | 320.718 | 424.992 | 86.633 | 30.216 | 88.401 | 41.416
| 22.0569 | 320.56 | 425.873 | 86.633 | 30.217 | 88.42 | 41.412
| 22.0583 | 321.707 | 425.847 | 86.64 | 30.216 | 88.434 | 41.417
| 22.0597 | 321.34 | 425.721 | 86.639 | 30.216 | 88.454 | 41.416
| 22.0611 | 321.947 | 425.393 | 86.652 | 30.218 | 88.469 | 41.423
| 22.0625 | 321.553 | 425.271 | 86.654 | 30.21 | 88.488 | 41.421
| 22.0639 | 321.663 | 425.521 | 86.653 | 30.213 | 88.497 | 41.425
| 22.0653 | 321.593 | 425.36 | 86.656 | 30.21 | 88.508 | 41.425
| 22.0667 | 321.925 | 425.497 | 86.659 | 30.216 | 88.523 | 41.427
| 22.0681 | 321.558 | 426.918 | 86.664 | 30.213 | 88.531 | 41.427
| 22.0694 | 321.97 | 426.403 | 86.67 | 30.214 | 88.549 | 41.43
| 22.0708 | 321.665 | 427.114 | 86.672 | 30.212 | 88.566 | 41.43
| 22.0722 | 321.89 | 426.115 | 86.682 | 30.214 | 88.577 | 41.43
| 22.0736 | 322.213 | 426.83 | 86.697 | 30.21 | 88.597 | 41.435
| 22.075 | 321.99 | 425.893 | 86.696 | 30.212 | 88.604 | 41.433
| 22.0764 | 321.542 | 426.263 | 86.699 | 30.211 | 88.606 | 41.434
| 22.0778 | 322.153 | 426 | 86.712 | 30.21 | 88.626 | 41.439
| 22.0792 | 321.886 | 425.959 | 86.71 | 30.212 | 88.635 | 41.439
| 22.0806 | 321.803 | 426.638 | 86.713 | 30.21 | 88.641 | 41.438
| 22.0819 | 321.615 | 426.728 | 86.728 | 30.213 | 88.657 | 41.441
| 22.0833 | 322.006 | 426.172 | 86.729 | 30.211 | 88.664 | 41.438
| 22.0847 | 322.026 | 426.106 | 86.729 | 30.209 | 88.667 | 41.444
| 22.0861 | 322.487 | 426.055 | 86.734 | 30.208 | 88.674 | 41.448
| 22.0875 | 321.674 | 426.699 | 86.738 | 30.212 | 88.681 | 41.449
| 22.0889 | 322.345 | 425.879 | 86.747 | 30.212 | 88.689 | 41.448
| 22.0903 | 322.199 | 427.039 | 86.752 | 30.21 | 88.7 | 41.451
| 22.0917 | 321.766 | 426.712 | 86.761 | 30.209 | 88.707 | 41.455
| 22.0931 | 322.334 | 426.007 | 86.767 | 30.213 | 88.719 | 41.454
| 22.0944 | 321.613 | 427.129 | 86.771 | 30.211 | 88.72 | 41.456
| 22.0958 | 322.06 | 426.854 | 86.774 | 30.213 | 88.729 | 41.456
| 22.0972 | 322.096 | 427.222 | 86.782 | 30.213 | 88.745 | 41.459
| 22.0986 | 322.012 | 427.732 | 86.795 | 30.214 | 88.763 | 41.459
| 22.1 | 322.934 | 426.873 | 86.807 | 30.215 | 88.778 | 41.463
| 22.1014 | 322.776 | 427.747 | 86.821 | 30.211 | 88.802 | 41.463
| 22.1028 | 322.505 | 426.357 | 86.827 | 30.214 | 88.817 | 41.464
| 22.1042 | 322.279 | 428.056 | 86.837 | 30.213 | 88.823 | 41.468
| 22.1056 | 322.607 | 427.301 | 86.846 | 30.212 | 88.839 | 41.471
| 22.1069 | 322.594 | 428.364 | 86.859 | 30.213 | 88.851 | 41.47
| 22.1083 | 323.434 | 427.43 | 86.875 | 30.211 | 88.872 | 41.471
| 22.1097 | 322.771 | 428.311 | 86.888 | 30.212 | 88.892 | 41.473
| 22.1111 | 322.701 | 427.158 | 86.899 | 30.211 | 88.905 | 41.473
| 22.1125 | 322.712 | 428.098 | 86.904 | 30.218 | 88.911 | 41.48
| 22.1139 | 322.804 | 427.956 | 86.92 | 30.215 | 88.926 | 41.48
| 22.1153 | 322.971 | 427.727 | 86.928 | 30.216 | 88.934 | 41.482
| 22.1167 | 323.417 | 427.242 | 86.942 | 30.215 | 88.957 | 41.486
| 22.1181 | 323.518 | 427.14 | 86.953 | 30.216 | 88.967 | 41.487
| 22.1194 | 322.865 | 427.834 | 86.963 | 30.217 | 88.977 | 41.488
| 22.1208 | 322.494 | 427.912 | 86.97 | 30.22 | 88.984 | 41.49
| 22.1222 | 322.139 | 427.192 | 86.972 | 30.22 | 88.98 | 41.492
| 22.1236 | 322.868 | 426.396 | 86.97 | 30.22 | 88.978 | 41.489
| 22.125 | 322.125 | 427.059 | 86.973 | 30.219 | 88.978 | 41.496
| 22.1264 | 322.092 | 426.961 | 86.98 | 30.221 | 88.973 | 41.493
| 22.1278 | 322.309 | 426.96 | 86.982 | 30.22 | 88.975 | 41.501
| 22.1292 | 322.492 | 426.964 | 86.989 | 30.22 | 88.985 | 41.503
| 22.1306 | 322.728 | 427.162 | 87.003 | 30.226 | 88.991 | 41.507
| 22.1319 | 322.794 | 427.575 | 87.002 | 30.222 | 89.001 | 41.509
| 22.1333 | 322.876 | 427.888 | 87.009 | 30.224 | 89.007 | 41.509
| 22.1347 | 322.762 | 428.371 | 87.025 | 30.221 | 89.028 | 41.51
| 22.1361 | 322.652 | 427.935 | 87.034 | 30.222 | 89.042 | 41.516
| 22.1375 | 323.411 | 427.009 | 87.044 | 30.221 | 89.054 | 41.515
| 22.1389 | 322.872 | 428.454 | 87.056 | 30.227 | 89.07 | 41.516
| 22.1403 | 322.77 | 428.475 | 87.067 | 30.226 | 89.081 | 41.519
| 22.1417 | 323.492 | 427.765 | 87.081 | 30.228 | 89.097 | 41.527
| 22.1431 | 323.29 | 427.201 | 87.087 | 30.229 | 89.107 | 41.523
| 22.1444 | 322.975 | 426.745 | 87.084 | 30.233 | 89.106 | 41.53
| 22.1458 | 322.626 | 427.983 | 87.09 | 30.231 | 89.103 | 41.531
| 22.1472 | 323.059 | 426.77 | 87.092 | 30.231 | 89.103 | 41.534
| 22.1486 | 322.777 | 427.375 | 87.097 | 30.232 | 89.106 | 41.534
| 22.15 | 323.364 | 427.049 | 87.103 | 30.234 | 89.106 | 41.537
| 22.1514 | 322.978 | 427.044 | 87.107 | 30.231 | 89.114 | 41.54
| 22.1528 | 322.742 | 427.221 | 87.109 | 30.234 | 89.116 | 41.54
| 22.1542 | 323.053 | 426.59 | 87.108 | 30.235 | 89.112 | 41.546
| 22.1556 | 323.257 | 426.904 | 87.111 | 30.234 | 89.113 | 41.545
| 22.1569 | 322.599 | 427.829 | 87.123 | 30.232 | 89.125 | 41.554
| 22.1583 | 323.287 | 426.884 | 87.127 | 30.237 | 89.129 | 41.552
| 22.1597 | 323.553 | 426.893 | 87.132 | 30.236 | 89.141 | 41.554
| 22.1611 | 323.128 | 426.994 | 87.137 | 30.238 | 89.15 | 41.555
| 22.1625 | 323.065 | 426.686 | 87.141 | 30.241 | 89.154 | 41.559
| 22.1639 | 322.999 | 426.99 | 87.144 | 30.24 | 89.159 | 41.561
| 22.1653 | 322.825 | 428.135 | 87.15 | 30.241 | 89.163 | 41.562
| 22.1667 | 323.17 | 427.102 | 87.155 | 30.239 | 89.166 | 41.564
| 22.1681 | 322.527 | 427.624 | 87.157 | 30.24 | 89.17 | 41.567
| 22.1694 | 323.066 | 426.996 | 87.165 | 30.242 | 89.173 | 41.576
| 22.1708 | 323.209 | 427.984 | 87.171 | 30.241 | 89.192 | 41.577
| 22.1722 | 323.557 | 428.471 | 87.178 | 30.244 | 89.209 | 41.573
| 22.1736 | 323.161 | 428.45 | 87.189 | 30.243 | 89.228 | 41.577
| 22.175 | 323.411 | 427.198 | 87.198 | 30.246 | 89.234 | 41.585
| 22.1764 | 323.44 | 427.079 | 87.199 | 30.245 | 89.242 | 41.583
| 22.1778 | 322.617 | 428.006 | 87.207 | 30.251 | 89.242 | 41.59
| 22.1792 | 322.737 | 427.841 | 87.202 | 30.244 | 89.237 | 41.591
| 22.1806 | 323.336 | 427.082 | 87.206 | 30.249 | 89.236 | 41.594
| 22.1819 | 322.853 | 427.132 | 87.199 | 30.25 | 89.234 | 41.593
| 22.1833 | 322.411 | 427.689 | 87.206 | 30.25 | 89.238 | 41.598
| 22.1847 | 322.051 | 427.012 | 87.203 | 30.25 | 89.225 | 41.6
| 22.1861 | 321.633 | 426.694 | 87.196 | 30.251 | 89.219 | 41.601
| 22.1875 | 321.972 | 426.86 | 87.184 | 30.253 | 89.208 | 41.607
| 22.1889 | 322.231 | 426.175 | 87.183 | 30.255 | 89.201 | 41.605
| 22.1903 | 322.798 | 426.817 | 87.183 | 30.251 | 89.197 | 41.608
| 22.1917 | 322.755 | 427.077 | 87.184 | 30.25 | 89.207 | 41.61
| 22.1931 | 323.053 | 426.935 | 87.192 | 30.254 | 89.214 | 41.62
| 22.1944 | 322.944 | 426.274 | 87.202 | 30.256 | 89.228 | 41.62
| 22.1958 | 322.659 | 426.049 | 87.193 | 30.256 | 89.229 | 41.622
| 22.1972 | 322.654 | 426.103 | 87.189 | 30.255 | 89.223 | 41.622
| 22.1986 | 322.466 | 427.542 | 87.189 | 30.257 | 89.228 | 41.624
| 22.2 | 322.126 | 427.074 | 87.193 | 30.262 | 89.233 | 41.626
| 22.2014 | 322.88 | 426.05 | 87.192 | 30.261 | 89.237 | 41.631
| 22.2028 | 322.361 | 427.433 | 87.19 | 30.259 | 89.239 | 41.63
| 22.2042 | 321.682 | 426.736 | 87.196 | 30.259 | 89.24 | 41.639
| 22.2056 | 321.85 | 426.951 | 87.188 | 30.262 | 89.228 | 41.637
| 22.2069 | 321.804 | 426.586 | 87.177 | 30.261 | 89.23 | 41.641
| 22.2083 | 321.372 | 426.269 | 87.166 | 30.263 | 89.22 | 41.644
| 22.2097 | 321.785 | 426.358 | 87.162 | 30.261 | 89.208 | 41.645
| 22.2111 | 321.719 | 426.713 | 87.16 | 30.261 | 89.205 | 41.646
| 22.2125 | 321.41 | 426.366 | 87.148 | 30.26 | 89.195 | 41.651
| 22.2139 | 322.22 | 425.155 | 87.141 | 30.26 | 89.183 | 41.654
| 22.2153 | 321.742 | 425.911 | 87.131 | 30.264 | 89.178 | 41.654
| 22.2167 | 321.689 | 426.043 | 87.126 | 30.262 | 89.172 | 41.657
| 22.2181 | 322.122 | 425.897 | 87.13 | 30.265 | 89.178 | 41.657
| 22.2194 | 322.072 | 425.847 | 87.129 | 30.266 | 89.182 | 41.661
| 22.2208 | 321.564 | 424.786 | 87.116 | 30.265 | 89.17 | 41.664
| 22.2222 | 321.139 | 424.416 | 87.096 | 30.266 | 89.155 | 41.666
| 22.2236 | 321.149 | 424.185 | 87.066 | 30.267 | 89.125 | 41.669
| 22.225 | 320.427 | 423.725 | 87.043 | 30.266 | 89.1 | 41.668
| 22.2264 | 320.141 | 424.308 | 87.023 | 30.264 | 89.074 | 41.676
| 22.2278 | 320.624 | 423.419 | 87.003 | 30.269 | 89.049 | 41.676
| 22.2292 | 319.582 | 424.107 | 86.981 | 30.269 | 89.016 | 41.679
| 22.2306 | 320.037 | 423.037 | 86.952 | 30.266 | 88.985 | 41.68
| 22.2319 | 319.505 | 423.561 | 86.934 | 30.264 | 88.968 | 41.682
| 22.2333 | 319.865 | 424.256 | 86.917 | 30.267 | 88.949 | 41.683
| 22.2347 | 319.743 | 424.042 | 86.9 | 30.267 | 88.939 | 41.686
| 22.2361 | 320.261 | 424.007 | 86.885 | 30.265 | 88.928 | 41.686
| 22.2375 | 320.274 | 423.434 | 86.867 | 30.267 | 88.917 | 41.686
| 22.2389 | 319.702 | 422.656 | 86.846 | 30.262 | 88.902 | 41.696
| 22.2403 | 320.257 | 423.099 | 86.829 | 30.268 | 88.888 | 41.694
| 22.2417 | 319.81 | 422.889 | 86.81 | 30.263 | 88.874 | 41.692
| 22.2431 | 319.381 | 423.745 | 86.786 | 30.268 | 88.856 | 41.701
| 22.2444 | 319.918 | 422.447 | 86.773 | 30.266 | 88.845 | 41.699
| 22.2458 | 319.46 | 423.999 | 86.744 | 30.266 | 88.83 | 41.701
| 22.2472 | 319.713 | 422.076 | 86.728 | 30.266 | 88.818 | 41.701
| 22.2486 | 319.278 | 423.438 | 86.71 | 30.265 | 88.802 | 41.706
| 22.25 | 319.159 | 422.864 | 86.688 | 30.265 | 88.786 | 41.704
| 22.2514 | 319.223 | 422.123 | 86.663 | 30.269 | 88.768 | 41.706
| 22.2528 | 320.062 | 424.491 | 86.649 | 30.264 | 88.759 | 41.71
| 22.2542 | 320.243 | 423.184 | 86.647 | 30.263 | 88.78 | 41.712
| 22.2556 | 319.045 | 423.41 | 86.64 | 30.265 | 88.792 | 41.711
| 22.2569 | 320.034 | 424.139 | 86.637 | 30.262 | 88.808 | 41.714
| 22.2583 | 319.807 | 423.31 | 86.623 | 30.263 | 88.801 | 41.716
| 22.2597 | 319.651 | 422.304 | 86.6 | 30.265 | 88.784 | 41.717
| 22.2611 | 318.942 | 423.227 | 86.586 | 30.261 | 88.767 | 41.722
| 22.2625 | 318.848 | 422.706 | 86.57 | 30.261 | 88.75 | 41.718
| 22.2639 | 317.428 | 421.194 | 86.535 | 30.26 | 88.721 | 41.722
| 22.2653 | 323.729 | 421.373 | 86.568 | 30.256 | 88.666 | 41.722
| 22.2667 | 328.366 | 424.972 | 86.707 | 30.255 | 88.713 | 41.721
| 22.2681 | 328.29 | 424.628 | 86.82 | 30.255 | 88.775 | 41.722
| 22.2694 | 326.661 | 424.947 | 86.898 | 30.257 | 88.806 | 41.725
| 22.2708 | 327.519 | 423.979 | 86.963 | 30.257 | 88.819 | 41.725
| 22.2722 | 326.916 | 422.908 | 87.012 | 30.257 | 88.826 | 41.729
| 22.2736 | 326.813 | 424.53 | 87.059 | 30.256 | 88.817 | 41.728
| 22.275 | 326.228 | 423.728 | 87.099 | 30.256 | 88.821 | 41.728
| 22.2764 | 326.538 | 422.737 | 87.136 | 30.26 | 88.802 | 41.729
| 22.2778 | 328.046 | 425.264 | 87.205 | 30.264 | 88.834 | 41.729
| 22.2792 | 327.893 | 424.473 | 87.27 | 30.26 | 88.873 | 41.727
| 22.2806 | 328.414 | 425.2 | 87.33 | 30.262 | 88.906 | 41.733
| 22.2819 | 327.041 | 425.451 | 87.378 | 30.266 | 88.921 | 41.74
| 22.2833 | 327.87 | 424.325 | 87.418 | 30.27 | 88.918 | 41.737
| 22.2847 | 326.84 | 424.901 | 87.46 | 30.272 | 88.915 | 41.737
| 22.2861 | 326.665 | 424.76 | 87.486 | 30.271 | 88.904 | 41.742
| 22.2875 | 326.784 | 422.962 | 87.515 | 30.273 | 88.886 | 41.738
| 22.2889 | 325.909 | 423.583 | 87.539 | 30.276 | 88.864 | 41.736
| 22.2903 | 326.466 | 423.07 | 87.559 | 30.28 | 88.838 | 41.741
| 22.2917 | 325.768 | 422.635 | 87.584 | 30.282 | 88.814 | 41.741
| 22.2931 | 325.504 | 423.119 | 87.603 | 30.285 | 88.801 | 41.743
| 22.2944 | 326.032 | 423.648 | 87.629 | 30.282 | 88.784 | 41.74
| 22.2958 | 326.626 | 422.313 | 87.658 | 30.285 | 88.788 | 41.746
| 22.2972 | 326.693 | 422.667 | 87.672 | 30.288 | 88.77 | 41.743
| 22.2986 | 325.821 | 422.867 | 87.7 | 30.292 | 88.764 | 41.745
| 22.3 | 325.534 | 423.229 | 87.724 | 30.295 | 88.751 | 41.75
| 22.3014 | 324.879 | 422.339 | 87.743 | 30.296 | 88.74 | 41.746
| 22.3028 | 325.34 | 423.155 | 87.752 | 30.297 | 88.718 | 41.75
| 22.3042 | 324.675 | 421.946 | 87.761 | 30.299 | 88.694 | 41.752
| 22.3056 | 324.597 | 421.071 | 87.76 | 30.301 | 88.657 | 41.755
| 22.3069 | 328.623 | 426.561 | 87.762 | 30.303 | 88.63 | 41.755
| 22.3083 | 328.534 | 427.072 | 87.858 | 30.305 | 88.748 | 41.758
| 22.3097 | 328.164 | 425.045 | 87.917 | 30.308 | 88.818 | 41.757
| 22.3111 | 327.462 | 426.09 | 87.965 | 30.311 | 88.862 | 41.755
| 22.3125 | 328.31 | 424.691 | 87.996 | 30.309 | 88.886 | 41.755
| 22.3139 | 327.695 | 424.52 | 88.019 | 30.312 | 88.895 | 41.759
| 22.3153 | 327.549 | 424.451 | 88.047 | 30.317 | 88.905 | 41.758
| 22.3167 | 328.348 | 424.733 | 88.077 | 30.317 | 88.918 | 41.764
| 22.3181 | 327.522 | 423.835 | 88.106 | 30.316 | 88.928 | 41.763
| 22.3194 | 326.738 | 424.572 | 88.125 | 30.321 | 88.929 | 41.762
| 22.3208 | 326.869 | 424.005 | 88.141 | 30.323 | 88.912 | 41.763
| 22.3222 | 326.749 | 423.315 | 88.159 | 30.332 | 88.902 | 41.764
| 22.3236 | 326.98 | 423.313 | 88.177 | 30.332 | 88.895 | 41.768
| 22.325 | 326.784 | 424.942 | 88.188 | 30.33 | 88.88 | 41.764
| 22.3264 | 326.395 | 423.711 | 88.208 | 30.334 | 88.886 | 41.768
| 22.3278 | 325.325 | 421.915 | 88.215 | 30.337 | 88.868 | 41.767
| 22.3292 | 325.855 | 423.777 | 88.221 | 30.346 | 88.842 | 41.771
| 22.3306 | 325.568 | 423.354 | 88.229 | 30.343 | 88.825 | 41.771
| 22.3319 | 325.797 | 421.672 | 88.231 | 30.342 | 88.802 | 41.774
| 22.3333 | 325.485 | 423.297 | 88.235 | 30.348 | 88.788 | 41.772
| 22.3347 | 326.31 | 422.115 | 88.24 | 30.351 | 88.768 | 41.775
| 22.3361 | 325.518 | 421.664 | 88.242 | 30.351 | 88.754 | 41.777
| 22.3375 | 324.96 | 422.205 | 88.247 | 30.354 | 88.741 | 41.779
| 22.3389 | 324.953 | 420.831 | 88.253 | 30.358 | 88.725 | 41.78
| 22.3403 | 325.197 | 421.487 | 88.245 | 30.36 | 88.698 | 41.779
| 22.3417 | 329.32 | 427.381 | 88.305 | 30.355 | 88.762 | 41.786
| 22.3431 | 331.134 | 430.408 | 88.424 | 30.359 | 88.944 | 41.779
| 22.3444 | 332.715 | 432.407 | 88.533 | 30.363 | 89.1 | 41.783
| 22.3458 | 329.167 | 425.786 | 88.601 | 30.364 | 89.193 | 41.781
| 22.3472 | 328.733 | 426.231 | 88.591 | 30.366 | 89.168 | 41.785
| 22.3486 | 329.712 | 427.953 | 88.626 | 30.367 | 89.21 | 41.786
| 22.35 | 330.484 | 428.123 | 88.678 | 30.368 | 89.252 | 41.786
| 22.3514 | 330.659 | 428.095 | 88.723 | 30.374 | 89.304 | 41.79
| 22.3528 | 329.888 | 427.176 | 88.76 | 30.378 | 89.334 | 41.788
| 22.3542 | 330.192 | 428.686 | 88.8 | 30.378 | 89.366 | 41.794
| 22.3556 | 329.599 | 427.373 | 88.841 | 30.384 | 89.388 | 41.792
| 22.3569 | 330.587 | 427.652 | 88.879 | 30.385 | 89.42 | 41.794
| 22.3583 | 330.595 | 427.949 | 88.925 | 30.389 | 89.451 | 41.797
| 22.3597 | 330.919 | 427.897 | 88.963 | 30.389 | 89.482 | 41.798
| 22.3611 | 330.893 | 428.849 | 88.998 | 30.394 | 89.506 | 41.796
| 22.3625 | 330.676 | 428.836 | 89.045 | 30.396 | 89.533 | 41.804
| 22.3639 | 330.546 | 428.672 | 89.083 | 30.403 | 89.557 | 41.804
| 22.3653 | 330.802 | 428.159 | 89.112 | 30.403 | 89.579 | 41.807
| 22.3667 | 330.837 | 429.192 | 89.152 | 30.407 | 89.604 | 41.804
| 22.3681 | 331.111 | 428.073 | 89.189 | 30.411 | 89.625 | 41.806
| 22.3694 | 330.47 | 427.939 | 89.216 | 30.413 | 89.629 | 41.809
| 22.3708 | 329.807 | 428.414 | 89.242 | 30.418 | 89.634 | 41.814
| 22.3722 | 330.112 | 427.948 | 89.27 | 30.42 | 89.644 | 41.814
| 22.3736 | 330.791 | 429.045 | 89.301 | 30.421 | 89.661 | 41.815
| 22.375 | 330.688 | 428.043 | 89.332 | 30.426 | 89.675 | 41.822
| 22.3764 | 330.001 | 429.015 | 89.365 | 30.429 | 89.69 | 41.823
| 22.3778 | 330.271 | 428.517 | 89.391 | 30.433 | 89.702 | 41.823
| 22.3792 | 331.288 | 428.735 | 89.423 | 30.436 | 89.721 | 41.825
| 22.3806 | 330.616 | 429.279 | 89.454 | 30.443 | 89.73 | 41.828
| 22.3819 | 330.475 | 429.02 | 89.48 | 30.446 | 89.739 | 41.831
| 22.3833 | 330.265 | 427.956 | 89.503 | 30.446 | 89.742 | 41.834
| 22.3847 | 330.086 | 427.757 | 89.52 | 30.447 | 89.75 | 41.838
| 22.3861 | 329.895 | 428.517 | 89.543 | 30.453 | 89.752 | 41.838
| 22.3875 | 329.975 | 428.831 | 89.561 | 30.458 | 89.746 | 41.842
| 22.3889 | 329.939 | 428.777 | 89.592 | 30.464 | 89.769 | 41.842
| 22.3903 | 331.563 | 429.248 | 89.623 | 30.462 | 89.79 | 41.851
| 22.3917 | 330.796 | 429.305 | 89.654 | 30.465 | 89.818 | 41.852
| 22.3931 | 324.955 | 429.592 | 89.571 | 30.468 | 89.834 | 41.855
| 22.3944 | 324.54 | 429.942 | 89.496 | 30.47 | 89.849 | 41.86
| 22.3958 | 324.113 | 429.381 | 89.442 | 30.476 | 89.857 | 41.859
| 22.3972 | 324.321 | 429.603 | 89.397 | 30.48 | 89.867 | 41.86
| 22.3986 | 325.11 | 428.624 | 89.359 | 30.479 | 89.877 | 41.866
| 22.4 | 323.94 | 428.938 | 89.321 | 30.483 | 89.874 | 41.868
| 22.4014 | 324.296 | 428.437 | 89.281 | 30.485 | 89.873 | 41.869
| 22.4028 | 323.717 | 427.529 | 89.243 | 30.486 | 89.862 | 41.874
| 22.4042 | 323.986 | 428.697 | 89.211 | 30.486 | 89.858 | 41.877
| 22.4056 | 324.066 | 429.194 | 89.178 | 30.493 | 89.856 | 41.881
| 22.4069 | 324.715 | 428.134 | 89.154 | 30.49 | 89.867 | 41.885
| 22.4083 | 324.132 | 428.982 | 89.131 | 30.493 | 89.889 | 41.884
| 22.4097 | 323.12 | 427.953 | 89.099 | 30.496 | 89.878 | 41.89
| 22.4111 | 323.379 | 428.545 | 89.06 | 30.495 | 89.864 | 41.896
| 22.4125 | 324.626 | 427.968 | 89.033 | 30.495 | 89.864 | 41.896
| 22.4139 | 322.939 | 427.806 | 89.005 | 30.502 | 89.862 | 41.901
| 22.4153 | 324.105 | 427.766 | 88.969 | 30.499 | 89.85 | 41.903
| 22.4167 | 323.449 | 427.94 | 88.942 | 30.495 | 89.844 | 41.906
| 22.4181 | 322.787 | 426.484 | 88.905 | 30.501 | 89.827 | 41.912
| 22.4194 | 322.963 | 427.531 | 88.861 | 30.501 | 89.797 | 41.913
| 22.4208 | 322.457 | 427.063 | 88.824 | 30.507 | 89.786 | 41.918
| 22.4222 | 322.266 | 426.197 | 88.793 | 30.502 | 89.776 | 41.92
| 22.4236 | 322.733 | 426.774 | 88.756 | 30.505 | 89.755 | 41.923
| 22.425 | 323.283 | 426.356 | 88.728 | 30.506 | 89.748 | 41.922
| 22.4264 | 322.515 | 425.583 | 88.696 | 30.502 | 89.737 | 41.927
| 22.4278 | 322.792 | 427.053 | 88.652 | 30.507 | 89.716 | 41.936
| 22.4292 | 323.441 | 426.236 | 88.625 | 30.503 | 89.702 | 41.934
| 22.4306 | 322.905 | 426.123 | 88.605 | 30.507 | 89.716 | 41.934
| 22.4319 | 323.342 | 427.366 | 88.583 | 30.505 | 89.717 | 41.94
| 22.4333 | 323.673 | 427.489 | 88.557 | 30.508 | 89.726 | 41.946
| 22.4347 | 323.275 | 427.127 | 88.547 | 30.506 | 89.732 | 41.948
| 22.4361 | 322.986 | 427.426 | 88.517 | 30.506 | 89.745 | 41.948
| 22.4375 | 323.146 | 426.733 | 88.492 | 30.511 | 89.745 | 41.951
| 22.4389 | 322.232 | 426.926 | 88.478 | 30.505 | 89.751 | 41.947
| 22.4403 | 323.044 | 427.926 | 88.462 | 30.504 | 89.756 | 41.957
| 22.4417 | 323.123 | 427.972 | 88.443 | 30.506 | 89.768 | 41.962
| 22.4431 | 322.613 | 427.306 | 88.422 | 30.508 | 89.762 | 41.959
| 22.4444 | 322.764 | 427.227 | 88.399 | 30.505 | 89.762 | 41.963
| 22.4458 | 323.793 | 427.06 | 88.376 | 30.506 | 89.757 | 41.964
| 22.4472 | 322.735 | 427.365 | 88.36 | 30.507 | 89.761 | 41.97
| 22.4486 | 323.004 | 426.547 | 88.342 | 30.508 | 89.768 | 41.972
| 22.45 | 323.213 | 425.85 | 88.322 | 30.505 | 89.765 | 41.977
| 22.4514 | 323.33 | 425.967 | 88.299 | 30.505 | 89.76 | 41.977
| 22.4528 | 322.626 | 426.029 | 88.272 | 30.505 | 89.754 | 41.984
| 22.4542 | 322.902 | 425.375 | 88.247 | 30.504 | 89.732 | 41.98
| 22.4556 | 322.91 | 425.595 | 88.216 | 30.503 | 89.723 | 41.985
| 22.4569 | 323.022 | 425.902 | 88.199 | 30.505 | 89.714 | 41.986
| 22.4583 | 321.719 | 425.878 | 88.174 | 30.5 | 89.703 | 41.989
| 22.4597 | 322.221 | 426.209 | 88.155 | 30.5 | 89.693 | 41.995
| 22.4611 | 322.537 | 425.924 | 88.139 | 30.5 | 89.697 | 41.998
| 22.4625 | 322.633 | 426.365 | 88.122 | 30.501 | 89.703 | 41.998
| 22.4639 | 322.203 | 426.331 | 88.106 | 30.5 | 89.706 | 42
| 22.4653 | 322.564 | 427.299 | 88.094 | 30.496 | 89.714 | 41.999
| 22.4667 | 323.233 | 426.036 | 88.085 | 30.5 | 89.729 | 42.006
| 22.4681 | 322.995 | 427.049 | 88.074 | 30.499 | 89.729 | 42.007
| 22.4694 | 323.372 | 426.182 | 88.053 | 30.496 | 89.734 | 42.008
| 22.4708 | 322.364 | 426.824 | 88.041 | 30.497 | 89.739 | 42.011
| 22.4722 | 323.086 | 426.292 | 88.026 | 30.497 | 89.732 | 42.014
| 22.4736 | 322.98 | 426.786 | 88.016 | 30.496 | 89.745 | 42.016
| 22.475 | 322.8 | 426.571 | 88.016 | 30.495 | 89.758 | 42.019
| 22.4764 | 322.891 | 427.336 | 87.997 | 30.495 | 89.756 | 42.02
| 22.4778 | 322.577 | 427.197 | 87.984 | 30.499 | 89.763 | 42.019
| 22.4792 | 322.456 | 426.404 | 87.98 | 30.496 | 89.762 | 42.025
| 22.4806 | 322.456 | 427.116 | 87.965 | 30.496 | 89.767 | 42.026
| 22.4819 | 323.123 | 425.682 | 87.956 | 30.497 | 89.763 | 42.029
| 22.4833 | 322.301 | 426.143 | 87.94 | 30.495 | 89.767 | 42.032
| 22.4847 | 322.126 | 426.031 | 87.924 | 30.495 | 89.763 | 42.031
| 22.4861 | 322.828 | 426.963 | 87.918 | 30.498 | 89.763 | 42.034
| 22.4875 | 322.32 | 426.988 | 87.912 | 30.493 | 89.774 | 42.038
| 22.4889 | 323.264 | 425.987 | 87.907 | 30.495 | 89.788 | 42.033
| 22.4903 | 322.448 | 426.707 | 87.897 | 30.496 | 89.791 | 42.038
| 22.4917 | 323.448 | 425.928 | 87.887 | 30.496 | 89.794 | 42.042
| 22.4931 | 323.682 | 426.341 | 87.884 | 30.497 | 89.811 | 42.045
| 22.4944 | 322.335 | 426.943 | 87.881 | 30.494 | 89.814 | 42.048
| 22.4958 | 323.535 | 426.796 | 87.878 | 30.498 | 89.83 | 42.047
| 22.4972 | 323.446 | 426.607 | 87.88 | 30.501 | 89.844 | 42.048
| 22.4986 | 323.668 | 426.266 | 87.882 | 30.496 | 89.854 | 42.053
| 22.5 | 323.511 | 428.282 | 87.881 | 30.49 | 89.871 | 42.056
| 22.5014 | 323.553 | 426.651 | 87.878 | 30.496 | 89.888 | 42.058
| 22.5028 | 323.02 | 427.339 | 87.872 | 30.494 | 89.892 | 42.058
| 22.5042 | 323.637 | 426.829 | 87.872 | 30.492 | 89.896 | 42.06
| 22.5056 | 324.209 | 427.178 | 87.87 | 30.495 | 89.903 | 42.059
| 22.5069 | 323.078 | 426.341 | 87.87 | 30.492 | 89.914 | 42.066
| 22.5083 | 323.041 | 427.707 | 87.867 | 30.494 | 89.914 | 42.068
| 22.5097 | 323.609 | 427.332 | 87.859 | 30.495 | 89.921 | 42.071
| 22.5111 | 323.521 | 427.961 | 87.867 | 30.498 | 89.942 | 42.076
| 22.5125 | 324.238 | 428.926 | 87.884 | 30.493 | 89.968 | 42.072
| 22.5139 | 325.049 | 429.926 | 87.896 | 30.497 | 90.003 | 42.078
| 22.5153 | 324.051 | 429.423 | 87.923 | 30.498 | 90.055 | 42.076
| 22.5167 | 324.251 | 429.425 | 87.927 | 30.497 | 90.078 | 42.078
| 22.5181 | 324.988 | 429.619 | 87.938 | 30.499 | 90.103 | 42.081
| 22.5194 | 321.88 | 424.612 | 87.905 | 30.5 | 90.059 | 42.085
| 22.5208 | 321.992 | 425.013 | 87.854 | 30.501 | 89.983 | 42.087
| 22.5222 | 322.112 | 424.917 | 87.828 | 30.499 | 89.932 | 42.087
| 22.5236 | 321.503 | 425.98 | 87.808 | 30.498 | 89.905 | 42.089
| 22.525 | 321.496 | 424.347 | 87.784 | 30.5 | 89.873 | 42.092
| 22.5264 | 320.29 | 424.333 | 87.749 | 30.5 | 89.83 | 42.093
| 22.5278 | 320.858 | 424.074 | 87.721 | 30.498 | 89.791 | 42.098
| 22.5292 | 321.65 | 424.049 | 87.694 | 30.499 | 89.756 | 42.104
| 22.5306 | 321.044 | 425.225 | 87.665 | 30.5 | 89.723 | 42.106
| 22.5319 | 320.862 | 424.412 | 87.646 | 30.499 | 89.704 | 42.105
| 22.5333 | 320.593 | 424.914 | 87.627 | 30.501 | 89.68 | 42.105
| 22.5347 | 320.693 | 425.146 | 87.603 | 30.501 | 89.667 | 42.107
| 22.5361 | 321.408 | 424.349 | 87.592 | 30.497 | 89.664 | 42.109
| 22.5375 | 321.755 | 424.462 | 87.575 | 30.501 | 89.665 | 42.11
| 22.5389 | 321.09 | 424.775 | 87.553 | 30.499 | 89.658 | 42.112
| 22.5403 | 320.514 | 424.805 | 87.54 | 30.5 | 89.639 | 42.119
| 22.5417 | 320.588 | 423.679 | 87.511 | 30.497 | 89.618 | 42.12
| 22.5431 | 321.251 | 423.68 | 87.49 | 30.499 | 89.603 | 42.124
| 22.5444 | 321.166 | 425.583 | 87.476 | 30.495 | 89.599 | 42.123
| 22.5458 | 321.401 | 423.797 | 87.461 | 30.496 | 89.597 | 42.123
| 22.5472 | 320.911 | 423.209 | 87.439 | 30.497 | 89.577 | 42.126
| 22.5486 | 320.519 | 424.85 | 87.417 | 30.494 | 89.556 | 42.13
| 22.55 | 320.817 | 424.491 | 87.402 | 30.499 | 89.554 | 42.132
| 22.5514 | 321.128 | 423.33 | 87.383 | 30.494 | 89.537 | 42.13
| 22.5528 | 320.93 | 423.622 | 87.364 | 30.494 | 89.531 | 42.131
| 22.5542 | 320.669 | 422.742 | 87.337 | 30.494 | 89.513 | 42.135
| 22.5556 | 320.573 | 422.769 | 87.314 | 30.496 | 89.487 | 42.134
| 22.5569 | 319.965 | 422.422 | 87.285 | 30.493 | 89.462 | 42.136
| 22.5583 | 319.927 | 422.331 | 87.261 | 30.488 | 89.443 | 42.142
| 22.5597 | 319.568 | 422.971 | 87.235 | 30.488 | 89.42 | 42.139
| 22.5611 | 319.547 | 422.294 | 87.212 | 30.487 | 89.396 | 42.142
| 22.5625 | 319.453 | 421.342 | 87.182 | 30.492 | 89.378 | 42.141
| 22.5639 | 319.225 | 423.031 | 87.159 | 30.489 | 89.347 | 42.147
| 22.5653 | 320.339 | 422.813 | 87.133 | 30.49 | 89.335 | 42.146
| 22.5667 | 319.693 | 423.649 | 87.116 | 30.49 | 89.328 | 42.145
| 22.5681 | 319.7 | 423.212 | 87.097 | 30.481 | 89.325 | 42.148
| 22.5694 | 319.627 | 423.204 | 87.08 | 30.484 | 89.307 | 42.15
| 22.5708 | 319.308 | 423.285 | 87.055 | 30.484 | 89.295 | 42.15
| 22.5722 | 319.564 | 423.594 | 87.038 | 30.484 | 89.296 | 42.149
| 22.5736 | 320.014 | 424.196 | 87.026 | 30.481 | 89.289 | 42.152
| 22.575 | 320.086 | 424.26 | 87.015 | 30.483 | 89.294 | 42.153
| 22.5764 | 320.784 | 422.926 | 87.006 | 30.482 | 89.304 | 42.155
| 22.5778 | 320.61 | 424.219 | 86.999 | 30.481 | 89.318 | 42.153
| 22.5792 | 320.375 | 423.963 | 86.99 | 30.48 | 89.321 | 42.158
| 22.5806 | 321.072 | 424.228 | 86.982 | 30.478 | 89.322 | 42.155
| 22.5819 | 320.403 | 424.1 | 86.978 | 30.475 | 89.328 | 42.154
| 22.5833 | 320.164 | 423.711 | 86.969 | 30.476 | 89.338 | 42.159
| 22.5847 | 320.456 | 424.888 | 86.959 | 30.477 | 89.339 | 42.159
| 22.5861 | 320.146 | 424.295 | 86.951 | 30.468 | 89.34 | 42.159
| 22.5875 | 320.437 | 422.532 | 86.943 | 30.476 | 89.339 | 42.16
| 22.5889 | 320.077 | 424.12 | 86.929 | 30.471 | 89.328 | 42.16
| 22.5903 | 319.863 | 424.006 | 86.919 | 30.475 | 89.326 | 42.158
| 22.5917 | 320.413 | 422.925 | 86.908 | 30.471 | 89.32 | 42.156
| 22.5931 | 320.666 | 425.009 | 86.907 | 30.469 | 89.328 | 42.159
| 22.5944 | 320.642 | 424.138 | 86.901 | 30.47 | 89.337 | 42.159
| 22.5958 | 321.466 | 423.976 | 86.902 | 30.47 | 89.351 | 42.163
| 22.5972 | 321.229 | 425.684 | 86.911 | 30.47 | 89.371 | 42.163
| 22.5986 | 320.522 | 425.129 | 86.909 | 30.468 | 89.396 | 42.165
| 22.6 | 321.084 | 423.627 | 86.911 | 30.467 | 89.405 | 42.165
| 22.6014 | 321.571 | 424.274 | 86.906 | 30.466 | 89.42 | 42.165
| 22.6028 | 321.616 | 425.765 | 86.913 | 30.466 | 89.434 | 42.165
| 22.6042 | 322.12 | 425.018 | 86.923 | 30.465 | 89.452 | 42.165
| 22.6056 | 321.46 | 424.958 | 86.918 | 30.466 | 89.457 | 42.165
| 22.6069 | 321.153 | 424.812 | 86.922 | 30.466 | 89.461 | 42.165
| 22.6083 | 321.736 | 424.636 | 86.914 | 30.464 | 89.465 | 42.17
| 22.6097 | 320.783 | 423.431 | 86.919 | 30.461 | 89.475 | 42.17
| 22.6111 | 321.662 | 424.79 | 86.928 | 30.467 | 89.487 | 42.171
| 22.6125 | 322.077 | 424.847 | 86.929 | 30.464 | 89.496 | 42.169
| 22.6139 | 321.294 | 425.762 | 86.935 | 30.462 | 89.507 | 42.172
| 22.6153 | 321.904 | 424.507 | 86.935 | 30.464 | 89.52 | 42.174
| 22.6167 | 321.093 | 424.588 | 86.936 | 30.464 | 89.509 | 42.172
| 22.6181 | 321.293 | 425.957 | 86.924 | 30.463 | 89.506 | 42.171
| 22.6194 | 321.828 | 425.063 | 86.933 | 30.462 | 89.521 | 42.174
| 22.6208 | 321.086 | 425.871 | 86.941 | 30.461 | 89.53 | 42.174
| 22.6222 | 321.449 | 425.102 | 86.944 | 30.462 | 89.539 | 42.175
| 22.6236 | 322.053 | 425.41 | 86.949 | 30.461 | 89.547 | 42.175
| 22.625 | 321.664 | 424.782 | 86.952 | 30.464 | 89.552 | 42.178
| 22.6264 | 321.355 | 425.951 | 86.948 | 30.46 | 89.55 | 42.177
| 22.6278 | 322.229 | 425.327 | 86.95 | 30.462 | 89.555 | 42.18
| 22.6292 | 322.148 | 425.819 | 86.953 | 30.467 | 89.562 | 42.179
| 22.6306 | 321.908 | 426.243 | 86.963 | 30.463 | 89.569 | 42.179
| 22.6319 | 320.695 | 425.281 | 86.967 | 30.461 | 89.576 | 42.182
| 22.6333 | 322.135 | 424.874 | 86.974 | 30.465 | 89.591 | 42.181
| 22.6347 | 322.767 | 426.191 | 86.978 | 30.465 | 89.601 | 42.181
| 22.6361 | 321.585 | 426.199 | 86.985 | 30.461 | 89.608 | 42.185
| 22.6375 | 321.59 | 426.508 | 86.989 | 30.462 | 89.615 | 42.184
| 22.6389 | 321.443 | 426.217 | 87 | 30.462 | 89.628 | 42.188
| 22.6403 | 322.342 | 425.122 | 86.996 | 30.465 | 89.625 | 42.189
| 22.6417 | 321.792 | 426.573 | 87.003 | 30.462 | 89.626 | 42.186
| 22.6431 | 322.221 | 425.04 | 87.001 | 30.466 | 89.627 | 42.19
| 22.6444 | 321.905 | 426.286 | 87.013 | 30.467 | 89.648 | 42.191
| 22.6458 | 322.408 | 425.514 | 87.02 | 30.464 | 89.654 | 42.189
| 22.6472 | 322.522 | 425.631 | 87.027 | 30.465 | 89.662 | 42.191
| 22.6486 | 322.072 | 427.274 | 87.042 | 30.467 | 89.683 | 42.195
| 22.65 | 322.456 | 426.818 | 87.05 | 30.464 | 89.693 | 42.197
| 22.6514 | 322.519 | 425.661 | 87.057 | 30.465 | 89.702 | 42.196
| 22.6528 | 322.872 | 426.149 | 87.065 | 30.466 | 89.714 | 42.196
| 22.6542 | 322.364 | 427.172 | 87.075 | 30.468 | 89.733 | 42.198
| 22.6556 | 323.338 | 427.005 | 87.096 | 30.464 | 89.754 | 42.198
| 22.6569 | 323.198 | 426.343 | 87.106 | 30.466 | 89.772 | 42.203
| 22.6583 | 322.628 | 427.942 | 87.122 | 30.471 | 89.793 | 42.199
| 22.6597 | 323.278 | 426.902 | 87.131 | 30.468 | 89.801 | 42.203
| 22.6611 | 323.244 | 427.455 | 87.136 | 30.469 | 89.812 | 42.207
| 22.6625 | 322.943 | 428.006 | 87.147 | 30.469 | 89.824 | 42.205
| 22.6639 | 323.031 | 428.383 | 87.169 | 30.468 | 89.849 | 42.209
| 22.6653 | 323.858 | 428.025 | 87.187 | 30.468 | 89.874 | 42.211
| 22.6667 | 323.644 | 427.902 | 87.204 | 30.471 | 89.891 | 42.212
| 22.6681 | 323.421 | 426.684 | 87.216 | 30.473 | 89.9 | 42.214
| 22.6694 | 323.827 | 427.253 | 87.22 | 30.471 | 89.915 | 42.216
| 22.6708 | 323.941 | 427.503 | 87.242 | 30.474 | 89.931 | 42.217
| 22.6722 | 323.019 | 428.334 | 87.256 | 30.473 | 89.95 | 42.219
| 22.6736 | 323.568 | 427.402 | 87.271 | 30.475 | 89.958 | 42.218
| 22.675 | 323.022 | 427.758 | 87.279 | 30.477 | 89.969 | 42.218
| 22.6764 | 323.791 | 427.363 | 87.29 | 30.475 | 89.978 | 42.226
| 22.6778 | 323.887 | 427.317 | 87.304 | 30.477 | 89.99 | 42.223
| 22.6792 | 323.426 | 427.751 | 87.322 | 30.476 | 90.01 | 42.226
| 22.6806 | 324.264 | 428.411 | 87.338 | 30.48 | 90.027 | 42.231
| 22.6819 | 324.532 | 427.907 | 87.355 | 30.478 | 90.045 | 42.232
| 22.6833 | 324.172 | 429.262 | 87.375 | 30.48 | 90.063 | 42.23
| 22.6847 | 324.279 | 428.648 | 87.395 | 30.481 | 90.084 | 42.236
| 22.6861 | 323.576 | 428.7 | 87.408 | 30.483 | 90.102 | 42.233
| 22.6875 | 324.393 | 428.132 | 87.419 | 30.486 | 90.111 | 42.239
| 22.6889 | 323.778 | 428.005 | 87.434 | 30.482 | 90.121 | 42.234
| 22.6903 | 324.365 | 428.341 | 87.448 | 30.486 | 90.135 | 42.238
| 22.6917 | 323.981 | 428.64 | 87.468 | 30.486 | 90.152 | 42.243
| 22.6931 | 324.394 | 428.316 | 87.478 | 30.486 | 90.168 | 42.248
| 22.6944 | 324.095 | 428.945 | 87.49 | 30.488 | 90.182 | 42.248
| 22.6958 | 324.396 | 428.009 | 87.505 | 30.494 | 90.196 | 42.252
| 22.6972 | 323.632 | 429.067 | 87.519 | 30.49 | 90.205 | 42.25
| 22.6986 | 324.222 | 427.731 | 87.525 | 30.491 | 90.208 | 42.253
| 22.7 | 323.73 | 429.006 | 87.529 | 30.493 | 90.207 | 42.255
| 22.7014 | 323.304 | 428.501 | 87.534 | 30.495 | 90.212 | 42.258
| 22.7028 | 323.429 | 426.896 | 87.531 | 30.492 | 90.194 | 42.258
| 22.7042 | 322.732 | 427.683 | 87.538 | 30.498 | 90.19 | 42.264
| 22.7056 | 322.809 | 426.733 | 87.54 | 30.497 | 90.187 | 42.264
| 22.7069 | 322.82 | 428.102 | 87.54 | 30.498 | 90.18 | 42.266
| 22.7083 | 323.09 | 427.648 | 87.541 | 30.5 | 90.179 | 42.271
| 22.7097 | 322.841 | 427.233 | 87.551 | 30.5 | 90.183 | 42.272
| 22.7111 | 322.998 | 427.873 | 87.553 | 30.504 | 90.175 | 42.275
| 22.7125 | 323.345 | 427.332 | 87.552 | 30.503 | 90.172 | 42.282
| 22.7139 | 322.733 | 427.386 | 87.56 | 30.503 | 90.174 | 42.28
| 22.7153 | 323.043 | 427.772 | 87.557 | 30.505 | 90.175 | 42.282
| 22.7167 | 323.714 | 426.672 | 87.56 | 30.502 | 90.175 | 42.281
| 22.7181 | 322.753 | 427.286 | 87.558 | 30.509 | 90.166 | 42.288
| 22.7194 | 323.532 | 426.46 | 87.553 | 30.508 | 90.161 | 42.288
| 22.7208 | 322.974 | 425.87 | 87.549 | 30.508 | 90.154 | 42.288
| 22.7222 | 321.919 | 425.465 | 87.534 | 30.51 | 90.127 | 42.289
| 22.7236 | 321.831 | 426.16 | 87.514 | 30.509 | 90.091 | 42.293
| 22.725 | 321.405 | 425.868 | 87.505 | 30.516 | 90.075 | 42.297
| 22.7264 | 321.371 | 425.821 | 87.487 | 30.512 | 90.057 | 42.297
| 22.7278 | 319.568 | 423.659 | 87.472 | 30.514 | 90.036 | 42.304
| 22.7292 | 318.511 | 422.281 | 87.413 | 30.514 | 89.947 | 42.301
| 22.7306 | 320.072 | 422.425 | 87.362 | 30.515 | 89.874 | 42.311
| 22.7319 | 325.218 | 423.294 | 87.351 | 30.519 | 89.817 | 42.307
| 22.7333 | 324.425 | 422.759 | 87.435 | 30.517 | 89.77 | 42.311
| 22.7347 | 328.908 | 427.517 | 87.546 | 30.517 | 89.809 | 42.313
| 22.7361 | 328.85 | 426.489 | 87.636 | 30.516 | 89.874 | 42.313
| 22.7375 | 328.425 | 427.418 | 87.715 | 30.517 | 89.912 | 42.319
| 22.7389 | 329.1 | 427.922 | 87.783 | 30.513 | 89.951 | 42.317
| 22.7403 | 329.2 | 427.262 | 87.845 | 30.518 | 89.98 | 42.323
| 22.7417 | 329.174 | 426.345 | 87.903 | 30.521 | 90.001 | 42.324
| 22.7431 | 329.307 | 426.634 | 87.954 | 30.518 | 90.025 | 42.324
| 22.7444 | 328.863 | 427.519 | 88.01 | 30.521 | 90.044 | 42.328
| 22.7458 | 329.01 | 427.061 | 88.056 | 30.525 | 90.048 | 42.328
| 22.7472 | 329.062 | 428.383 | 88.101 | 30.526 | 90.062 | 42.332
| 22.7486 | 327.9 | 427.496 | 88.148 | 30.526 | 90.082 | 42.331
| 22.75 | 329.258 | 427.015 | 88.184 | 30.53 | 90.082 | 42.335
| 22.7514 | 327.992 | 427.182 | 88.228 | 30.532 | 90.084 | 42.332
| 22.7528 | 329.426 | 427.255 | 88.268 | 30.531 | 90.098 | 42.34
| 22.7542 | 329.053 | 426.911 | 88.306 | 30.54 | 90.106 | 42.336
| 22.7556 | 328.598 | 428.357 | 88.355 | 30.543 | 90.116 | 42.339
| 22.7569 | 329.336 | 427.21 | 88.402 | 30.542 | 90.132 | 42.343
| 22.7583 | 329.186 | 428.58 | 88.441 | 30.542 | 90.145 | 42.347
| 22.7597 | 328.306 | 427.746 | 88.489 | 30.549 | 90.169 | 42.345
| 22.7611 | 329.708 | 427.205 | 88.53 | 30.552 | 90.183 | 42.349
| 22.7625 | 328.979 | 428.282 | 88.578 | 30.554 | 90.202 | 42.354
| 22.7639 | 329.735 | 429.898 | 88.625 | 30.555 | 90.234 | 42.348
| 22.7653 | 330.179 | 428.657 | 88.676 | 30.559 | 90.268 | 42.354
| 22.7667 | 329.791 | 428.957 | 88.717 | 30.563 | 90.287 | 42.354
| 22.7681 | 330.11 | 428.61 | 88.761 | 30.568 | 90.307 | 42.359
| 22.7694 | 330.195 | 427.909 | 88.806 | 30.571 | 90.328 | 42.358
| 22.7708 | 330.161 | 428.906 | 88.84 | 30.571 | 90.339 | 42.36
| 22.7722 | 329.726 | 428.969 | 88.891 | 30.574 | 90.355 | 42.36
| 22.7736 | 329.357 | 429.077 | 88.918 | 30.579 | 90.364 | 42.363
| 22.775 | 328.955 | 428.587 | 88.952 | 30.585 | 90.36 | 42.367
| 22.7764 | 329.834 | 428.231 | 88.982 | 30.585 | 90.367 | 42.369
| 22.7778 | 329.661 | 428.604 | 89.018 | 30.59 | 90.379 | 42.371
| 22.7792 | 330.1 | 428.369 | 89.053 | 30.596 | 90.39 | 42.373
| 22.7806 | 329.525 | 428.86 | 89.085 | 30.595 | 90.393 | 42.375
| 22.7819 | 329.106 | 428.647 | 89.111 | 30.601 | 90.394 | 42.375
| 22.7833 | 329.552 | 429.12 | 89.142 | 30.604 | 90.402 | 42.378
| 22.7847 | 329.553 | 428.447 | 89.181 | 30.609 | 90.415 | 42.381
| 22.7861 | 330.341 | 428.08 | 89.211 | 30.608 | 90.428 | 42.381
| 22.7875 | 329.708 | 428.84 | 89.234 | 30.618 | 90.432 | 42.382
| 22.7889 | 330.063 | 428.023 | 89.272 | 30.616 | 90.442 | 42.387
| 22.7903 | 330.826 | 428.759 | 89.306 | 30.617 | 90.466 | 42.388
| 22.7917 | 329.748 | 428.148 | 89.33 | 30.624 | 90.465 | 42.391
| 22.7931 | 330.369 | 428.108 | 89.356 | 30.623 | 90.47 | 42.392
| 22.7944 | 330.529 | 428.533 | 89.381 | 30.631 | 90.48 | 42.399
| 22.7958 | 330.622 | 428.517 | 89.41 | 30.632 | 90.486 | 42.399
| 22.7972 | 329.383 | 428.301 | 89.437 | 30.636 | 90.497 | 42.401
| 22.7986 | 330.283 | 428.229 | 89.467 | 30.637 | 90.514 | 42.403
| 22.8 | 330.788 | 429.763 | 89.5 | 30.642 | 90.534 | 42.408
| 22.8014 | 330.403 | 429.625 | 89.533 | 30.645 | 90.553 | 42.406
| 22.8028 | 330.317 | 428.831 | 89.559 | 30.649 | 90.57 | 42.409
| 22.8042 | 330.422 | 429.833 | 89.59 | 30.649 | 90.586 | 42.412
| 22.8056 | 325.019 | 428.891 | 89.57 | 30.655 | 90.614 | 42.413
| 22.8069 | 325.146 | 429.795 | 89.483 | 30.659 | 90.638 | 42.421
| 22.8083 | 325.017 | 429.251 | 89.432 | 30.663 | 90.66 | 42.424
| 22.8097 | 324.824 | 430.185 | 89.39 | 30.663 | 90.675 | 42.424
| 22.8111 | 324.986 | 430.844 | 89.363 | 30.67 | 90.703 | 42.422
| 22.8125 | 324.965 | 428.75 | 89.339 | 30.672 | 90.728 | 42.428
| 22.8139 | 325.678 | 429.706 | 89.313 | 30.672 | 90.744 | 42.424
| 22.8153 | 325.632 | 429.753 | 89.292 | 30.672 | 90.764 | 42.434
| 22.8167 | 325.569 | 429.796 | 89.279 | 30.678 | 90.788 | 42.435
| 22.8181 | 324.877 | 430.6 | 89.26 | 30.683 | 90.811 | 42.438
| 22.8194 | 325.463 | 431.57 | 89.243 | 30.682 | 90.828 | 42.444
| 22.8208 | 325.84 | 431.297 | 89.237 | 30.684 | 90.854 | 42.443
| 22.8222 | 325.484 | 430.183 | 89.227 | 30.686 | 90.886 | 42.446
| 22.8236 | 324.974 | 430.591 | 89.207 | 30.686 | 90.891 | 42.447
| 22.825 | 325.056 | 429.891 | 89.185 | 30.688 | 90.898 | 42.45
| 22.8264 | 325.57 | 430.137 | 89.18 | 30.689 | 90.912 | 42.451
| 22.8278 | 325.804 | 431.023 | 89.169 | 30.689 | 90.926 | 42.459
| 22.8292 | 325.45 | 431.009 | 89.155 | 30.691 | 90.942 | 42.455
| 22.8306 | 326.521 | 430.815 | 89.149 | 30.692 | 90.964 | 42.462
| 22.8319 | 321.589 | 426.578 | 89.14 | 30.692 | 90.977 | 42.469
| 22.8333 | 321.817 | 425.786 | 89.048 | 30.696 | 90.858 | 42.467
| 22.8347 | 321.632 | 426.451 | 88.985 | 30.699 | 90.778 | 42.471
| 22.8361 | 322.159 | 426.865 | 88.931 | 30.697 | 90.721 | 42.474
| 22.8375 | 322.099 | 426.309 | 88.893 | 30.701 | 90.68 | 42.479
| 22.8389 | 321.362 | 426.193 | 88.855 | 30.704 | 90.65 | 42.483
| 22.8403 | 323.038 | 426.443 | 88.82 | 30.695 | 90.626 | 42.485
| 22.8417 | 322.594 | 427.016 | 88.8 | 30.698 | 90.623 | 42.485
| 22.8431 | 322.075 | 426.843 | 88.765 | 30.698 | 90.602 | 42.49
| 22.8444 | 321.668 | 426.107 | 88.721 | 30.701 | 90.574 | 42.492
| 22.8458 | 322.429 | 426.359 | 88.689 | 30.7 | 90.551 | 42.494
| 22.8472 | 323.313 | 427.032 | 88.66 | 30.7 | 90.551 | 42.5
| 22.8486 | 322.871 | 427.237 | 88.649 | 30.701 | 90.577 | 42.503
| 22.85 | 322.892 | 428.161 | 88.633 | 30.702 | 90.597 | 42.507
| 22.8514 | 323.474 | 428.526 | 88.619 | 30.701 | 90.614 | 42.511
| 22.8528 | 323.782 | 428.867 | 88.613 | 30.697 | 90.644 | 42.512
| 22.8542 | 324.218 | 427.895 | 88.605 | 30.698 | 90.662 | 42.51
| 22.8556 | 323.222 | 428.964 | 88.589 | 30.698 | 90.677 | 42.516
| 22.8569 | 323.421 | 429.142 | 88.578 | 30.704 | 90.693 | 42.52
| 22.8583 | 323.665 | 428.333 | 88.566 | 30.702 | 90.706 | 42.519
| 22.8597 | 323.978 | 428.173 | 88.553 | 30.702 | 90.709 | 42.521
| 22.8611 | 324.088 | 427.788 | 88.538 | 30.702 | 90.712 | 42.522
| 22.8625 | 324.514 | 428.5 | 88.527 | 30.699 | 90.73 | 42.527
| 22.8639 | 323.553 | 428.983 | 88.52 | 30.7 | 90.74 | 42.53
| 22.8653 | 324.289 | 428.813 | 88.511 | 30.706 | 90.75 | 42.536
| 22.8667 | 324.026 | 429.39 | 88.507 | 30.707 | 90.773 | 42.533
| 22.8681 | 324.239 | 429.916 | 88.508 | 30.701 | 90.794 | 42.532
| 22.8694 | 324.448 | 430.087 | 88.512 | 30.702 | 90.816 | 42.541
| 22.8708 | 324.847 | 429.732 | 88.512 | 30.702 | 90.835 | 42.541
| 22.8722 | 324.905 | 428.813 | 88.513 | 30.703 | 90.857 | 42.543
| 22.8736 | 324.96 | 429.237 | 88.506 | 30.701 | 90.866 | 42.549
| 22.875 | 324.7 | 428.556 | 88.505 | 30.704 | 90.882 | 42.55
| 22.8764 | 325.463 | 429.341 | 88.503 | 30.706 | 90.898 | 42.555
| 22.8778 | 325.059 | 429.429 | 88.507 | 30.705 | 90.92 | 42.552
| 22.8792 | 324.977 | 429.619 | 88.516 | 30.706 | 90.941 | 42.556
| 22.8806 | 324.602 | 430.345 | 88.513 | 30.703 | 90.954 | 42.556
| 22.8819 | 325.182 | 430.476 | 88.513 | 30.709 | 90.971 | 42.561
| 22.8833 | 320.622 | 425.194 | 88.482 | 30.704 | 90.927 | 42.564
| 22.8847 | 321.313 | 425.053 | 88.414 | 30.707 | 90.828 | 42.565
| 22.8861 | 320.914 | 425.202 | 88.358 | 30.705 | 90.754 | 42.567
| 22.8875 | 320.765 | 424.887 | 88.32 | 30.706 | 90.694 | 42.57
| 22.8889 | 321.472 | 426.365 | 88.293 | 30.707 | 90.657 | 42.574
| 22.8903 | 321.342 | 426.301 | 88.261 | 30.705 | 90.625 | 42.577
| 22.8917 | 320.76 | 425.508 | 88.227 | 30.706 | 90.598 | 42.577
| 22.8931 | 321.692 | 424.73 | 88.203 | 30.704 | 90.577 | 42.583
| 22.8944 | 320.63 | 425.277 | 88.166 | 30.708 | 90.556 | 42.583
| 22.8958 | 321.017 | 425.323 | 88.138 | 30.703 | 90.529 | 42.585
| 22.8972 | 321.221 | 424.634 | 88.111 | 30.707 | 90.51 | 42.584
| 22.8986 | 321.102 | 425.126 | 88.089 | 30.705 | 90.497 | 42.589
| 22.9 | 321.532 | 424.14 | 88.055 | 30.707 | 90.482 | 42.594
| 22.9014 | 320.955 | 425.686 | 88.029 | 30.709 | 90.465 | 42.595
| 22.9028 | 321.074 | 424.716 | 88.004 | 30.703 | 90.449 | 42.595
| 22.9042 | 321.353 | 423.852 | 87.977 | 30.705 | 90.433 | 42.6
| 22.9056 | 320.321 | 424.177 | 87.947 | 30.702 | 90.414 | 42.6
| 22.9069 | 320.794 | 424.865 | 87.919 | 30.703 | 90.393 | 42.604
| 22.9083 | 321.383 | 424.4 | 87.899 | 30.703 | 90.393 | 42.608
| 22.9097 | 322.062 | 426.27 | 87.888 | 30.705 | 90.412 | 42.607
| 22.9111 | 320.811 | 425.286 | 87.882 | 30.702 | 90.423 | 42.609
| 22.9125 | 321.633 | 425.131 | 87.855 | 30.703 | 90.414 | 42.612
| 22.9139 | 321.274 | 425.975 | 87.838 | 30.704 | 90.412 | 42.614
| 22.9153 | 322.346 | 425.106 | 87.827 | 30.697 | 90.422 | 42.613
| 22.9167 | 322.077 | 425.842 | 87.817 | 30.701 | 90.433 | 42.618
| 22.9181 | 322.029 | 425.582 | 87.809 | 30.697 | 90.445 | 42.618
| 22.9194 | 322.188 | 426.05 | 87.801 | 30.701 | 90.459 | 42.62
| 22.9208 | 321.961 | 427.17 | 87.807 | 30.699 | 90.49 | 42.622
| 22.9222 | 322.902 | 426.543 | 87.8 | 30.696 | 90.504 | 42.623
| 22.9236 | 322.237 | 427.308 | 87.798 | 30.696 | 90.524 | 42.623
| 22.925 | 322.888 | 426.873 | 87.798 | 30.701 | 90.547 | 42.629
| 22.9264 | 322.759 | 426.165 | 87.794 | 30.697 | 90.558 | 42.627
| 22.9278 | 322.888 | 427.216 | 87.79 | 30.698 | 90.571 | 42.63
| 22.9292 | 322.874 | 426.128 | 87.794 | 30.697 | 90.587 | 42.632
| 22.9306 | 323.831 | 427.397 | 87.798 | 30.692 | 90.609 | 42.631
| 22.9319 | 323.068 | 428.221 | 87.806 | 30.694 | 90.643 | 42.632
| 22.9333 | 323.849 | 427.933 | 87.81 | 30.698 | 90.66 | 42.634
| 22.9347 | 323.988 | 428.414 | 87.817 | 30.695 | 90.681 | 42.636
| 22.9361 | 324.356 | 427.658 | 87.831 | 30.694 | 90.711 | 42.636
| 22.9375 | 324.658 | 428.15 | 87.845 | 30.695 | 90.741 | 42.639
| 22.9389 | 324.529 | 428.255 | 87.861 | 30.698 | 90.769 | 42.638
| 22.9403 | 324.658 | 428.439 | 87.875 | 30.696 | 90.807 | 42.644
| 22.9417 | 324.012 | 429.286 | 87.887 | 30.696 | 90.83 | 42.647
| 22.9431 | 323.975 | 429.222 | 87.903 | 30.694 | 90.858 | 42.644
| 22.9444 | 325.162 | 428.686 | 87.923 | 30.692 | 90.887 | 42.643
| 22.9458 | 324.275 | 428.765 | 87.939 | 30.694 | 90.916 | 42.651
| 22.9472 | 321.749 | 425.586 | 87.888 | 30.695 | 90.841 | 42.648
| 22.9486 | 321.93 | 425.804 | 87.858 | 30.698 | 90.791 | 42.651
| 22.95 | 322.077 | 426.72 | 87.846 | 30.694 | 90.757 | 42.652
| 22.9514 | 322.265 | 426.187 | 87.832 | 30.698 | 90.739 | 42.655
| 22.9528 | 322.457 | 427.51 | 87.827 | 30.701 | 90.739 | 42.657
| 22.9542 | 322.403 | 427.318 | 87.821 | 30.701 | 90.737 | 42.656
| 22.9556 | 322.159 | 427.329 | 87.818 | 30.699 | 90.739 | 42.66
| 22.9569 | 322.448 | 426.637 | 87.809 | 30.696 | 90.73 | 42.664
| 22.9583 | 322.572 | 427.816 | 87.804 | 30.698 | 90.735 | 42.665
| 22.9597 | 323.467 | 427.054 | 87.807 | 30.701 | 90.746 | 42.671
| 22.9611 | 323.195 | 426.934 | 87.803 | 30.699 | 90.753 | 42.668
| 22.9625 | 322.866 | 428.097 | 87.809 | 30.702 | 90.762 | 42.673
| 22.9639 | 323.387 | 427.26 | 87.812 | 30.698 | 90.772 | 42.672
| 22.9653 | 322.768 | 427.346 | 87.815 | 30.704 | 90.79 | 42.676
| 22.9667 | 323.797 | 427.291 | 87.814 | 30.699 | 90.798 | 42.677
| 22.9681 | 323.603 | 427.712 | 87.822 | 30.7 | 90.819 | 42.682
| 22.9694 | 323.723 | 427.436 | 87.829 | 30.707 | 90.832 | 42.682
| 22.9708 | 323.227 | 428.787 | 87.841 | 30.701 | 90.859 | 42.681
| 22.9722 | 324.408 | 430.09 | 87.863 | 30.701 | 90.894 | 42.68
| 22.9736 | 324.98 | 428.867 | 87.883 | 30.7 | 90.936 | 42.687
| 22.975 | 325.696 | 429.553 | 87.905 | 30.703 | 90.973 | 42.688
| 22.9764 | 324.687 | 429.82 | 87.925 | 30.701 | 91.006 | 42.694
| 22.9778 | 325.277 | 429.275 | 87.942 | 30.703 | 91.046 | 42.697
| 22.9792 | 321.356 | 424.406 | 87.906 | 30.706 | 90.984 | 42.698
| 22.9806 | 321.099 | 424.899 | 87.854 | 30.706 | 90.896 | 42.699
| 22.9819 | 321.714 | 424.711 | 87.828 | 30.708 | 90.847 | 42.698
| 22.9833 | 321.357 | 425.989 | 87.803 | 30.704 | 90.802 | 42.698
| 22.9847 | 321.29 | 424.64 | 87.788 | 30.704 | 90.769 | 42.702
| 22.9861 | 321.701 | 425.783 | 87.774 | 30.702 | 90.745 | 42.702
| 22.9875 | 322.047 | 425.301 | 87.762 | 30.706 | 90.732 | 42.704
| 22.9889 | 321.789 | 426.531 | 87.752 | 30.703 | 90.722 | 42.708
| 22.9903 | 322.029 | 425.413 | 87.74 | 30.705 | 90.719 | 42.712
| 22.9917 | 322.39 | 425.126 | 87.737 | 30.708 | 90.717 | 42.715
| 22.9931 | 321.727 | 426.387 | 87.729 | 30.71 | 90.715 | 42.715
| 22.9944 | 322.502 | 425.487 | 87.718 | 30.707 | 90.707 | 42.717
| 22.9958 | 321.601 | 426.226 | 87.704 | 30.708 | 90.697 | 42.718
| 22.9972 | 319.831 | 423.05 | 87.673 | 30.712 | 90.657 | 42.715
| 22.9986 | 319.442 | 423.537 | 87.623 | 30.711 | 90.583 | 42.722
| 23 | 319.683 | 422.418 | 87.585 | 30.706 | 90.525 | 42.728
| 23.0014 | 318.723 | 422.779 | 87.539 | 30.707 | 90.465 | 42.726
| 23.0028 | 318.69 | 422.484 | 87.503 | 30.707 | 90.414 | 42.728
| 23.0042 | 318.834 | 422.716 | 87.465 | 30.709 | 90.374 | 42.732
| 23.0056 | 318.47 | 422.18 | 87.432 | 30.71 | 90.336 | 42.73
| 23.0069 | 325.637 | 421.742 | 87.508 | 30.706 | 90.3 | 42.736
| 23.0083 | 325.502 | 422.399 | 87.575 | 30.703 | 90.279 | 42.733
| 23.0097 | 324.973 | 422.711 | 87.628 | 30.707 | 90.259 | 42.739
| 23.0111 | 325.824 | 422.18 | 87.668 | 30.707 | 90.251 | 42.736
| 23.0125 | 326.275 | 423.128 | 87.704 | 30.707 | 90.242 | 42.742
| 23.0139 | 326.836 | 423.477 | 87.754 | 30.704 | 90.26 | 42.742
| 23.0153 | 327.049 | 424.314 | 87.806 | 30.706 | 90.296 | 42.737
| 23.0167 | 326.841 | 425.427 | 87.85 | 30.705 | 90.311 | 42.745
| 23.0181 | 327.717 | 424.741 | 87.892 | 30.705 | 90.333 | 42.745
| 23.0194 | 327.344 | 425.226 | 87.939 | 30.703 | 90.357 | 42.742
| 23.0208 | 326.975 | 425.643 | 87.981 | 30.706 | 90.373 | 42.745
| 23.0222 | 326.702 | 425.081 | 88.017 | 30.709 | 90.376 | 42.75
| 23.0236 | 326.887 | 425.136 | 88.049 | 30.709 | 90.384 | 42.749
| 23.025 | 326.943 | 425.548 | 88.087 | 30.711 | 90.398 | 42.75
| 23.0264 | 327.447 | 425.001 | 88.127 | 30.709 | 90.412 | 42.748
| 23.0278 | 327.078 | 425.407 | 88.162 | 30.714 | 90.425 | 42.748
| 23.0292 | 327.7 | 425.053 | 88.202 | 30.714 | 90.449 | 42.752
| 23.0306 | 327.617 | 425.316 | 88.236 | 30.716 | 90.451 | 42.754
| 23.0319 | 327.705 | 425.303 | 88.267 | 30.717 | 90.458 | 42.754
| 23.0333 | 327.928 | 425.251 | 88.309 | 30.718 | 90.469 | 42.752
| 23.0347 | 327.79 | 425.604 | 88.339 | 30.721 | 90.478 | 42.753
| 23.0361 | 326.815 | 425.427 | 88.364 | 30.724 | 90.478 | 42.758
| 23.0375 | 326.397 | 424.885 | 88.38 | 30.727 | 90.464 | 42.757
| 23.0389 | 325.983 | 424.684 | 88.395 | 30.727 | 90.447 | 42.756
| 23.0403 | 326.433 | 423.821 | 88.411 | 30.727 | 90.433 | 42.755
| 23.0417 | 325.766 | 424.151 | 88.423 | 30.73 | 90.413 | 42.762
| 23.0431 | 325.811 | 424.132 | 88.437 | 30.732 | 90.394 | 42.763
| 23.0444 | 324.036 | 421.982 | 88.432 | 30.735 | 90.35 | 42.765
| 23.0458 | 324.138 | 422.027 | 88.412 | 30.734 | 90.28 | 42.761
| 23.0472 | 324.42 | 422.035 | 88.404 | 30.737 | 90.233 | 42.765
| 23.0486 | 324.618 | 421.237 | 88.401 | 30.74 | 90.198 | 42.759
| 23.05 | 324.789 | 420.797 | 88.4 | 30.742 | 90.162 | 42.761
| 23.0514 | 324.915 | 420.701 | 88.394 | 30.743 | 90.128 | 42.765
| 23.0528 | 324.732 | 421.099 | 88.395 | 30.747 | 90.103 | 42.768
| 23.0542 | 324.81 | 421.86 | 88.397 | 30.751 | 90.084 | 42.765
| 23.0556 | 325.636 | 421.813 | 88.399 | 30.754 | 90.075 | 42.77
| 23.0569 | 324.661 | 422.756 | 88.413 | 30.748 | 90.07 | 42.771
| 23.0583 | 326.019 | 422.225 | 88.428 | 30.752 | 90.08 | 42.772
| 23.0597 | 325.209 | 423.182 | 88.443 | 30.754 | 90.085 | 42.769
| 23.0611 | 325.333 | 421.885 | 88.449 | 30.754 | 90.088 | 42.771
| 23.0625 | 325.465 | 422.121 | 88.455 | 30.757 | 90.082 | 42.771
| 23.0639 | 325.372 | 423.251 | 88.462 | 30.755 | 90.087 | 42.772
| 23.0653 | 325.483 | 423.485 | 88.479 | 30.757 | 90.092 | 42.772
| 23.0667 | 325.602 | 423.422 | 88.493 | 30.757 | 90.1 | 42.774
| 23.0681 | 326.364 | 422.516 | 88.508 | 30.764 | 90.113 | 42.774
| 23.0694 | 325.536 | 422.711 | 88.517 | 30.766 | 90.114 | 42.775
| 23.0708 | 324.947 | 421.922 | 88.511 | 30.765 | 90.091 | 42.778
| 23.0722 | 324.916 | 422.104 | 88.507 | 30.769 | 90.07 | 42.779
| 23.0736 | 325.055 | 420.816 | 88.503 | 30.768 | 90.044 | 42.774
| 23.075 | 324.34 | 421.108 | 88.493 | 30.769 | 90.02 | 42.776
| 23.0764 | 324.769 | 420.403 | 88.484 | 30.773 | 89.989 | 42.778
| 23.0778 | 324.204 | 421.65 | 88.485 | 30.773 | 89.971 | 42.778
| 23.0792 | 324.904 | 421.097 | 88.484 | 30.776 | 89.965 | 42.776
| 23.0806 | 325.067 | 420.704 | 88.482 | 30.777 | 89.953 | 42.778
| 23.0819 | 324.106 | 421.544 | 88.482 | 30.775 | 89.938 | 42.777
| 23.0833 | 324.729 | 420.733 | 88.479 | 30.781 | 89.935 | 42.782
| 23.0847 | 324.951 | 421.274 | 88.482 | 30.781 | 89.927 | 42.78
| 23.0861 | 325.121 | 420.853 | 88.479 | 30.78 | 89.92 | 42.779
| 23.0875 | 324.757 | 421.076 | 88.482 | 30.786 | 89.919 | 42.781
| 23.0889 | 324.922 | 421.4 | 88.491 | 30.782 | 89.917 | 42.782
| 23.0903 | 325.014 | 421.406 | 88.482 | 30.786 | 89.913 | 42.782
| 23.0917 | 324.728 | 421.074 | 88.487 | 30.785 | 89.908 | 42.781
| 23.0931 | 324.517 | 421.651 | 88.487 | 30.785 | 89.905 | 42.783
| 23.0944 | 324.273 | 421.902 | 88.486 | 30.786 | 89.897 | 42.777
| 23.0958 | 324.731 | 422.659 | 88.488 | 30.79 | 89.9 | 42.781
| 23.0972 | 325.47 | 421.902 | 88.506 | 30.788 | 89.917 | 42.779
| 23.0986 | 325.651 | 422.144 | 88.508 | 30.79 | 89.919 | 42.781
| 23.1 | 324.907 | 422.659 | 88.518 | 30.79 | 89.927 | 42.778
| 23.1014 | 325.051 | 423.056 | 88.524 | 30.79 | 89.933 | 42.779
| 23.1028 | 325.113 | 422.593 | 88.535 | 30.792 | 89.941 | 42.777
| 23.1042 | 324.918 | 422.886 | 88.54 | 30.79 | 89.947 | 42.775
| 23.1056 | 325.542 | 422.597 | 88.543 | 30.794 | 89.952 | 42.783
| 23.1069 | 325.198 | 423.208 | 88.558 | 30.792 | 89.962 | 42.777
| 23.1083 | 326.172 | 422.453 | 88.568 | 30.797 | 89.971 | 42.777
| 23.1097 | 325.463 | 422.705 | 88.577 | 30.796 | 89.971 | 42.78
| 23.1111 | 325.161 | 423.293 | 88.578 | 30.802 | 89.969 | 42.777
| 23.1125 | 325.824 | 422.182 | 88.587 | 30.799 | 89.974 | 42.777
| 23.1139 | 325.289 | 423.278 | 88.588 | 30.803 | 89.976 | 42.781
| 23.1153 | 325.128 | 423.045 | 88.596 | 30.801 | 89.972 | 42.778
| 23.1167 | 325.505 | 422.935 | 88.602 | 30.805 | 89.977 | 42.781
| 23.1181 | 324.905 | 423.054 | 88.606 | 30.804 | 89.973 | 42.78
| 23.1194 | 325.143 | 422.619 | 88.615 | 30.806 | 89.974 | 42.778
| 23.1208 | 325.34 | 421.321 | 88.618 | 30.81 | 89.968 | 42.781
| 23.1222 | 324.887 | 422.423 | 88.613 | 30.811 | 89.957 | 42.777
| 23.1236 | 325.35 | 421.746 | 88.615 | 30.809 | 89.947 | 42.781
| 23.125 | 325.421 | 422.733 | 88.62 | 30.811 | 89.94 | 42.782
| 23.1264 | 325.614 | 422.008 | 88.628 | 30.815 | 89.953 | 42.781
| 23.1278 | 325.49 | 422.229 | 88.632 | 30.811 | 89.953 | 42.781
| 23.1292 | 325.726 | 422.322 | 88.631 | 30.819 | 89.95 | 42.785
| 23.1306 | 325.461 | 422.348 | 88.641 | 30.816 | 89.954 | 42.776
| 23.1319 | 325.436 | 422.011 | 88.643 | 30.817 | 89.952 | 42.778
| 23.1333 | 325.153 | 422.135 | 88.645 | 30.819 | 89.946 | 42.779
| 23.1347 | 324.92 | 422.499 | 88.646 | 30.819 | 89.936 | 42.784
| 23.1361 | 325.262 | 423.492 | 88.652 | 30.822 | 89.942 | 42.781
| 23.1375 | 325.995 | 422.226 | 88.659 | 30.819 | 89.95 | 42.783
| 23.1389 | 325.883 | 422.067 | 88.662 | 30.825 | 89.949 | 42.787
| 23.1403 | 325.099 | 422.185 | 88.668 | 30.825 | 89.948 | 42.783
| 23.1417 | 325.192 | 422.561 | 88.674 | 30.826 | 89.944 | 42.782
| 23.1431 | 324.891 | 422.85 | 88.674 | 30.83 | 89.943 | 42.783
| 23.1444 | 325.952 | 422.042 | 88.676 | 30.826 | 89.941 | 42.782
| 23.1458 | 325.62 | 422.262 | 88.681 | 30.829 | 89.945 | 42.787
| 23.1472 | 325.718 | 421.932 | 88.685 | 30.83 | 89.943 | 42.781
| 23.1486 | 325.08 | 422.952 | 88.685 | 30.832 | 89.94 | 42.784
| 23.15 | 325.12 | 422.763 | 88.693 | 30.834 | 89.939 | 42.782
| 23.1514 | 325.344 | 422.851 | 88.692 | 30.836 | 89.937 | 42.784
| 23.1528 | 325.598 | 422.042 | 88.698 | 30.837 | 89.938 | 42.786
| 23.1542 | 325.239 | 422.798 | 88.697 | 30.836 | 89.937 | 42.789
| 23.1556 | 325.919 | 422.416 | 88.709 | 30.836 | 89.936 | 42.784
| 23.1569 | 325.683 | 421.977 | 88.707 | 30.838 | 89.934 | 42.787
| 23.1583 | 325.155 | 422.798 | 88.706 | 30.839 | 89.93 | 42.786
| 23.1597 | 325.692 | 422.201 | 88.708 | 30.846 | 89.925 | 42.784
| 23.1611 | 324.821 | 422.948 | 88.706 | 30.84 | 89.923 | 42.784
| 23.1625 | 325.217 | 422.359 | 88.709 | 30.843 | 89.916 | 42.786
| 23.1639 | 325.437 | 422.929 | 88.718 | 30.849 | 89.921 | 42.79
| 23.1653 | 325.039 | 423.211 | 88.715 | 30.841 | 89.915 | 42.787
| 23.1667 | 325.372 | 422.571 | 88.721 | 30.852 | 89.916 | 42.79
| 23.1681 | 325.793 | 422.179 | 88.722 | 30.85 | 89.907 | 42.785
| 23.1694 | 325.487 | 422.146 | 88.719 | 30.848 | 89.909 | 42.792
| 23.1708 | 325.595 | 422.772 | 88.726 | 30.85 | 89.912 | 42.791
| 23.1722 | 325.548 | 421.749 | 88.724 | 30.853 | 89.909 | 42.792
| 23.1736 | 324.679 | 422.786 | 88.722 | 30.853 | 89.895 | 42.788
| 23.175 | 325.233 | 422.605 | 88.721 | 30.857 | 89.899 | 42.793
| 23.1764 | 325.247 | 422.442 | 88.725 | 30.854 | 89.89 | 42.788
| 23.1778 | 324.47 | 422.129 | 88.717 | 30.86 | 89.888 | 42.793
| 23.1792 | 325.654 | 421.809 | 88.718 | 30.858 | 89.883 | 42.791
| 23.1806 | 324.522 | 422.463 | 88.714 | 30.858 | 89.867 | 42.791
| 23.1819 | 325.132 | 421.558 | 88.704 | 30.857 | 89.856 | 42.79
| 23.1833 | 325.283 | 421.328 | 88.704 | 30.862 | 89.849 | 42.791
| 23.1847 | 324.796 | 422.5 | 88.706 | 30.858 | 89.848 | 42.794
| 23.1861 | 324.953 | 422.269 | 88.708 | 30.863 | 89.85 | 42.792
| 23.1875 | 325.594 | 421.814 | 88.714 | 30.863 | 89.853 | 42.792
| 23.1889 | 325.411 | 421.434 | 88.714 | 30.867 | 89.854 | 42.794
| 23.1903 | 325.424 | 421.801 | 88.709 | 30.865 | 89.852 | 42.791
| 23.1917 | 325.419 | 422.012 | 88.714 | 30.863 | 89.851 | 42.795
| 23.1931 | 325.244 | 422.667 | 88.72 | 30.868 | 89.864 | 42.797
| 23.1944 | 326.023 | 422.352 | 88.729 | 30.87 | 89.87 | 42.799
| 23.1958 | 325.322 | 422.38 | 88.731 | 30.868 | 89.875 | 42.796
| 23.1972 | 325.731 | 421.795 | 88.731 | 30.87 | 89.874 | 42.8
| 23.1986 | 325.994 | 421.946 | 88.732 | 30.87 | 89.876 | 42.799
| 23.2 | 324.821 | 422.899 | 88.737 | 30.876 | 89.882 | 42.798
| 23.2014 | 325.871 | 422.214 | 88.739 | 30.874 | 89.884 | 42.796
| 23.2028 | 324.908 | 422.991 | 88.744 | 30.877 | 89.885 | 42.797
| 23.2042 | 325.817 | 422.695 | 88.747 | 30.879 | 89.885 | 42.799
| 23.2056 | 325.907 | 422.375 | 88.752 | 30.878 | 89.894 | 42.797
| 23.2069 | 325.561 | 422.513 | 88.749 | 30.876 | 89.896 | 42.8
| 23.2083 | 325.214 | 422.974 | 88.765 | 30.881 | 89.897 | 42.803
| 23.2097 | 325.425 | 422.207 | 88.758 | 30.882 | 89.892 | 42.801
| 23.2111 | 325.62 | 421.744 | 88.76 | 30.883 | 89.893 | 42.802
| 23.2125 | 324.516 | 422.367 | 88.755 | 30.883 | 89.886 | 42.801
| 23.2139 | 325.293 | 421.266 | 88.756 | 30.886 | 89.875 | 42.806
| 23.2153 | 324.409 | 422.249 | 88.742 | 30.887 | 89.864 | 42.802
| 23.2167 | 324.687 | 422.809 | 88.75 | 30.883 | 89.867 | 42.805
| 23.2181 | 325.766 | 421.995 | 88.752 | 30.886 | 89.869 | 42.799
| 23.2194 | 324.695 | 422.657 | 88.757 | 30.889 | 89.867 | 42.802
| 23.2208 | 324.415 | 422.047 | 88.751 | 30.89 | 89.863 | 42.806
| 23.2222 | 324.401 | 421.497 | 88.743 | 30.887 | 89.846 | 42.807
| 23.2236 | 327.868 | 425.301 | 88.754 | 30.894 | 89.865 | 42.808
| 23.225 | 327.721 | 425.072 | 88.812 | 30.889 | 89.963 | 42.803
| 23.2264 | 327.474 | 425.022 | 88.845 | 30.896 | 90.035 | 42.808
| 23.2278 | 329.909 | 428.548 | 88.903 | 30.895 | 90.123 | 42.805
| 23.2292 | 329.194 | 428.457 | 88.967 | 30.898 | 90.221 | 42.806
| 23.2306 | 329.126 | 428.837 | 89.016 | 30.899 | 90.299 | 42.808
| 23.2319 | 329.749 | 428.032 | 89.061 | 30.899 | 90.359 | 42.807
| 23.2333 | 329.445 | 428.594 | 89.096 | 30.898 | 90.399 | 42.808
| 23.2347 | 328.95 | 428.328 | 89.132 | 30.901 | 90.448 | 42.81
| 23.2361 | 329.34 | 426.677 | 89.158 | 30.906 | 90.473 | 42.809
| 23.2375 | 329.158 | 427.042 | 89.187 | 30.904 | 90.487 | 42.81
| 23.2389 | 328.815 | 427.02 | 89.209 | 30.908 | 90.507 | 42.811
| 23.2403 | 328.99 | 427.81 | 89.236 | 30.91 | 90.527 | 42.813
| 23.2417 | 328.857 | 427.546 | 89.262 | 30.913 | 90.547 | 42.813
| 23.2431 | 328.298 | 427.607 | 89.28 | 30.912 | 90.556 | 42.816
| 23.2444 | 329.076 | 426.646 | 89.305 | 30.917 | 90.571 | 42.813
| 23.2458 | 328.363 | 427.389 | 89.331 | 30.919 | 90.584 | 42.815
| 23.2472 | 329.019 | 427.712 | 89.352 | 30.923 | 90.6 | 42.818
| 23.2486 | 328.101 | 427.477 | 89.377 | 30.924 | 90.612 | 42.818
| 23.25 | 328.365 | 426.163 | 89.394 | 30.922 | 90.615 | 42.821
| 23.2514 | 328.986 | 426.463 | 89.408 | 30.926 | 90.615 | 42.822
| 23.2528 | 328.095 | 426.442 | 89.42 | 30.932 | 90.612 | 42.823
| 23.2542 | 327.821 | 426.796 | 89.427 | 30.93 | 90.606 | 42.826
| 23.2556 | 327.88 | 426.426 | 89.431 | 30.935 | 90.604 | 42.825
| 23.2569 | 327.904 | 425.677 | 89.441 | 30.938 | 90.598 | 42.827
| 23.2583 | 330.605 | 428.739 | 89.459 | 30.935 | 90.604 | 42.827
| 23.2597 | 330.019 | 429.431 | 89.521 | 30.939 | 90.681 | 42.828
| 23.2611 | 329.904 | 428.884 | 89.558 | 30.945 | 90.726 | 42.833
| 23.2625 | 329.498 | 427.873 | 89.592 | 30.945 | 90.763 | 42.838
| 23.2639 | 328.067 | 427.179 | 89.604 | 30.944 | 90.767 | 42.835
| 23.2653 | 327.617 | 424.753 | 89.589 | 30.948 | 90.732 | 42.837
| 23.2667 | 326.285 | 424.87 | 89.569 | 30.95 | 90.682 | 42.843
| 23.2681 | 326.076 | 424.404 | 89.545 | 30.956 | 90.631 | 42.845
| 23.2694 | 326.457 | 423.417 | 89.531 | 30.956 | 90.583 | 42.846
| 23.2708 | 325.803 | 424.086 | 89.51 | 30.959 | 90.533 | 42.847
| 23.2722 | 329.526 | 428.003 | 89.555 | 30.964 | 90.585 | 42.85
| 23.2736 | 329.164 | 427.553 | 89.594 | 30.965 | 90.64 | 42.852
| 23.275 | 329.082 | 426.61 | 89.621 | 30.967 | 90.673 | 42.856
| 23.2764 | 329.226 | 427.019 | 89.638 | 30.968 | 90.694 | 42.858
| 23.2778 | 328.485 | 425.877 | 89.652 | 30.966 | 90.707 | 42.857
| 23.2792 | 328.081 | 425.785 | 89.656 | 30.973 | 90.705 | 42.859
| 23.2806 | 327.571 | 426.331 | 89.654 | 30.971 | 90.685 | 42.865
| 23.2819 | 327.565 | 424.396 | 89.645 | 30.976 | 90.667 | 42.865
| 23.2833 | 327.524 | 425.983 | 89.65 | 30.98 | 90.661 | 42.867
| 23.2847 | 327.525 | 425.106 | 89.646 | 30.976 | 90.642 | 42.869
| 23.2861 | 326.974 | 424.802 | 89.644 | 30.979 | 90.633 | 42.874
| 23.2875 | 326.782 | 424.229 | 89.632 | 30.983 | 90.605 | 42.876
| 23.2889 | 326.421 | 424.419 | 89.623 | 30.983 | 90.576 | 42.877
| 23.2903 | 326.503 | 424.168 | 89.609 | 30.986 | 90.548 | 42.879
| 23.2917 | 326.764 | 423.696 | 89.598 | 30.99 | 90.531 | 42.879
| 23.2931 | 325.614 | 423.547 | 89.578 | 30.987 | 90.503 | 42.887
| 23.2944 | 325.778 | 423.686 | 89.567 | 30.989 | 90.472 | 42.882
| 23.2958 | 325.68 | 422.637 | 89.548 | 30.994 | 90.442 | 42.883
| 23.2972 | 325.517 | 422.244 | 89.525 | 30.994 | 90.411 | 42.888
| 23.2986 | 324.733 | 421.988 | 89.504 | 30.998 | 90.375 | 42.893
| 23.3 | 324.735 | 421.72 | 89.48 | 30.998 | 90.335 | 42.891
| 23.3014 | 324.272 | 421.64 | 89.452 | 30.997 | 90.3 | 42.897
| 23.3028 | 328.355 | 426.796 | 89.451 | 31 | 90.306 | 42.901
| 23.3042 | 328.062 | 426.55 | 89.498 | 31.003 | 90.392 | 42.902
| 23.3056 | 326.979 | 425.432 | 89.521 | 31.003 | 90.434 | 42.904
| 23.3069 | 326.185 | 424.514 | 89.518 | 31.004 | 90.445 | 42.906
| 23.3083 | 328.459 | 427.355 | 89.523 | 31.004 | 90.462 | 42.904
| 23.3097 | 329.868 | 427.348 | 89.572 | 31.005 | 90.55 | 42.903
| 23.3111 | 328.815 | 428.001 | 89.611 | 31.004 | 90.615 | 42.909
| 23.3125 | 329.538 | 427.638 | 89.643 | 31.008 | 90.672 | 42.908
| 23.3139 | 329.908 | 427.652 | 89.669 | 31.011 | 90.711 | 42.915
| 23.3153 | 328.859 | 427.159 | 89.686 | 31.008 | 90.739 | 42.913
| 23.3167 | 328.426 | 426.795 | 89.697 | 31.011 | 90.753 | 42.916
| 23.3181 | 328.849 | 426.07 | 89.702 | 31.011 | 90.756 | 42.915
| 23.3194 | 328.672 | 426.631 | 89.71 | 31.017 | 90.759 | 42.914
| 23.3208 | 328.514 | 427.549 | 89.724 | 31.015 | 90.769 | 42.918
| 23.3222 | 329.444 | 426.715 | 89.737 | 31.019 | 90.779 | 42.921
| 23.3236 | 328.077 | 427.044 | 89.745 | 31.026 | 90.786 | 42.922
| 23.325 | 328.526 | 425.569 | 89.753 | 31.024 | 90.785 | 42.923
| 23.3264 | 328.433 | 425.322 | 89.753 | 31.028 | 90.781 | 42.926
| 23.3278 | 328.293 | 424.891 | 89.756 | 31.025 | 90.77 | 42.922
| 23.3292 | 328.364 | 425.096 | 89.758 | 31.026 | 90.766 | 42.929
| 23.3306 | 327.347 | 425.614 | 89.76 | 31.034 | 90.761 | 42.931
| 23.3319 | 327.992 | 424.667 | 89.764 | 31.031 | 90.756 | 42.932
| 23.3333 | 326.961 | 425.602 | 89.767 | 31.033 | 90.756 | 42.936
| 23.3347 | 327.135 | 425.449 | 89.764 | 31.034 | 90.751 | 42.937
| 23.3361 | 327.191 | 425.234 | 89.768 | 31.038 | 90.75 | 42.935
| 23.3375 | 327.307 | 425.47 | 89.769 | 31.038 | 90.739 | 42.938
| 23.3389 | 326.335 | 424.749 | 89.767 | 31.041 | 90.735 | 42.941
| 23.3403 | 326.38 | 424.855 | 89.756 | 31.038 | 90.71 | 42.939
| 23.3417 | 326.999 | 424.008 | 89.745 | 31.046 | 90.695 | 42.946
| 23.3431 | 326.495 | 424.122 | 89.745 | 31.047 | 90.687 | 42.945
| 23.3444 | 327.87 | 425.733 | 89.752 | 31.047 | 90.694 | 42.953
| 23.3458 | 329.503 | 427.265 | 89.767 | 31.046 | 90.709 | 42.951
| 23.3472 | 329.312 | 427.075 | 89.796 | 31.051 | 90.771 | 42.957
| 23.3486 | 328.111 | 427.267 | 89.815 | 31.05 | 90.806 | 42.951
| 23.35 | 328.085 | 426.469 | 89.83 | 31.048 | 90.831 | 42.953
| 23.3514 | 328.846 | 426.015 | 89.832 | 31.052 | 90.842 | 42.956
| 23.3528 | 327.987 | 426.59 | 89.838 | 31.05 | 90.846 | 42.963
| 23.3542 | 327.996 | 427.122 | 89.849 | 31.053 | 90.855 | 42.963
| 23.3556 | 328.408 | 426.623 | 89.855 | 31.056 | 90.859 | 42.962
| 23.3569 | 328.813 | 426.064 | 89.867 | 31.059 | 90.872 | 42.966
| 23.3583 | 327.861 | 426.995 | 89.867 | 31.061 | 90.877 | 42.969
| 23.3597 | 328.851 | 425.962 | 89.88 | 31.061 | 90.883 | 42.97
| 23.3611 | 328.353 | 425.49 | 89.89 | 31.061 | 90.894 | 42.975
| 23.3625 | 328.281 | 426.844 | 89.9 | 31.063 | 90.902 | 42.971
| 23.3639 | 327.749 | 426.605 | 89.907 | 31.068 | 90.907 | 42.975
| 23.3653 | 327.924 | 426.293 | 89.901 | 31.071 | 90.893 | 42.976
| 23.3667 | 328.178 | 425.302 | 89.913 | 31.073 | 90.895 | 42.979
| 23.3681 | 328.644 | 426.18 | 89.91 | 31.076 | 90.886 | 42.986
| 23.3694 | 328.522 | 425.955 | 89.916 | 31.072 | 90.896 | 42.982
| 23.3708 | 328.633 | 425.804 | 89.925 | 31.074 | 90.908 | 42.984
| 23.3722 | 328.856 | 425.913 | 89.935 | 31.081 | 90.914 | 42.988
| 23.3736 | 328.588 | 426.883 | 89.942 | 31.077 | 90.924 | 42.992
| 23.375 | 328.092 | 426.872 | 89.952 | 31.083 | 90.933 | 42.993
| 23.3764 | 327.982 | 426.616 | 89.961 | 31.082 | 90.944 | 42.991
| 23.3778 | 329.389 | 426.693 | 89.976 | 31.084 | 90.959 | 42.996
| 23.3792 | 330.175 | 427.788 | 89.997 | 31.085 | 90.987 | 42.998
| 23.3806 | 329.679 | 428.224 | 90.026 | 31.09 | 91.027 | 43.002
| 23.3819 | 328.905 | 426.805 | 90.04 | 31.085 | 91.055 | 43
| 23.3833 | 329.011 | 427.495 | 90.051 | 31.093 | 91.063 | 43.002
| 23.3847 | 329.06 | 426.974 | 90.057 | 31.095 | 91.068 | 43.002
| 23.3861 | 329.976 | 427.287 | 90.068 | 31.094 | 91.081 | 43.012
| 23.3875 | 329.523 | 427.465 | 90.082 | 31.097 | 91.095 | 43.01
| 23.3889 | 330.232 | 428.391 | 90.106 | 31.098 | 91.121 | 43.012
| 23.3903 | 330.841 | 428.547 | 90.135 | 31.099 | 91.158 | 43.012
| 23.3917 | 329.885 | 428.312 | 90.155 | 31.102 | 91.182 | 43.012
| 23.3931 | 329.602 | 428.387 | 90.18 | 31.102 | 91.206 | 43.019
| 23.3944 | 330.091 | 427.593 | 90.187 | 31.106 | 91.211 | 43.02
| 23.3958 | 329.825 | 429.265 | 90.199 | 31.106 | 91.218 | 43.024
| 23.3972 | 330.024 | 427.904 | 90.213 | 31.112 | 91.23 | 43.027
| 23.3986 | 329.282 | 428.719 | 90.229 | 31.111 | 91.248 | 43.026
| 23.4 | 329.526 | 428.22 | 90.24 | 31.114 | 91.247 | 43.028
| 23.4014 | 328.701 | 428.124 | 90.25 | 31.113 | 91.245 | 43.029
| 23.4028 | 329.103 | 427.856 | 90.253 | 31.116 | 91.248 | 43.034
| 23.4042 | 329.737 | 427.691 | 90.267 | 31.121 | 91.256 | 43.038
| 23.4056 | 329.031 | 428.456 | 90.278 | 31.121 | 91.268 | 43.04
| 23.4069 | 329.584 | 428.095 | 90.288 | 31.124 | 91.276 | 43.04
| 23.4083 | 329.548 | 428.382 | 90.307 | 31.125 | 91.287 | 43.041
| 23.4097 | 330.186 | 429.388 | 90.318 | 31.13 | 91.306 | 43.043
| 23.4111 | 329.983 | 427.703 | 90.337 | 31.127 | 91.32 | 43.05
| 23.4125 | 329.619 | 428.335 | 90.344 | 31.13 | 91.322 | 43.047
| 23.4139 | 329.491 | 427.848 | 90.348 | 31.135 | 91.323 | 43.051
| 23.4153 | 328.771 | 427.025 | 90.348 | 31.138 | 91.316 | 43.053
| 23.4167 | 328.6 | 427.817 | 90.355 | 31.136 | 91.31 | 43.055
| 23.4181 | 329.763 | 427.112 | 90.358 | 31.14 | 91.304 | 43.057
| 23.4194 | 329.759 | 427.361 | 90.367 | 31.144 | 91.317 | 43.06
| 23.4208 | 329.169 | 428.361 | 90.383 | 31.142 | 91.331 | 43.062
| 23.4222 | 329.559 | 427.104 | 90.379 | 31.148 | 91.327 | 43.066
| 23.4236 | 329.286 | 426.407 | 90.376 | 31.146 | 91.313 | 43.069
| 23.425 | 328.386 | 427.164 | 90.38 | 31.152 | 91.303 | 43.073
| 23.4264 | 329.144 | 427.378 | 90.381 | 31.151 | 91.303 | 43.075
| 23.4278 | 329.098 | 426.387 | 90.381 | 31.152 | 91.297 | 43.072
| 23.4292 | 328.745 | 427.008 | 90.383 | 31.156 | 91.299 | 43.079
| 23.4306 | 328.673 | 427.957 | 90.389 | 31.156 | 91.302 | 43.078
| 23.4319 | 329.044 | 428.047 | 90.4 | 31.16 | 91.316 | 43.084
| 23.4333 | 328.65 | 426.784 | 90.4 | 31.161 | 91.319 | 43.086
| 23.4347 | 328.835 | 428.171 | 90.404 | 31.161 | 91.326 | 43.089
| 23.4361 | 329.773 | 427.138 | 90.418 | 31.162 | 91.331 | 43.094
| 23.4375 | 329.791 | 427.415 | 90.422 | 31.165 | 91.342 | 43.097
| 23.4389 | 329.293 | 427.628 | 90.429 | 31.17 | 91.346 | 43.093
| 23.4403 | 329.257 | 426.286 | 90.433 | 31.169 | 91.352 | 43.097
| 23.4417 | 329.073 | 426.966 | 90.429 | 31.172 | 91.346 | 43.103
| 23.4431 | 329.306 | 426.82 | 90.43 | 31.174 | 91.348 | 43.106
| 23.4444 | 327.808 | 426.9 | 90.432 | 31.174 | 91.345 | 43.106
| 23.4458 | 328.986 | 426.438 | 90.434 | 31.179 | 91.344 | 43.106
| 23.4472 | 329.225 | 428.811 | 90.445 | 31.178 | 91.359 | 43.112
| 23.4486 | 328.676 | 428.003 | 90.45 | 31.178 | 91.371 | 43.117
| 23.45 | 328.546 | 427.619 | 90.452 | 31.184 | 91.363 | 43.117
| 23.4514 | 329.373 | 427.787 | 90.455 | 31.183 | 91.377 | 43.118
| 23.4528 | 329.114 | 426.178 | 90.453 | 31.188 | 91.37 | 43.123
| 23.4542 | 329.487 | 426.745 | 90.455 | 31.189 | 91.374 | 43.123
| 23.4556 | 329.239 | 426.575 | 90.457 | 31.188 | 91.376 | 43.122
| 23.4569 | 328.399 | 427.541 | 90.462 | 31.189 | 91.38 | 43.128
| 23.4583 | 328.811 | 426.808 | 90.466 | 31.194 | 91.385 | 43.131
| 23.4597 | 328.43 | 427.728 | 90.462 | 31.191 | 91.383 | 43.132
| 23.4611 | 328.312 | 427.135 | 90.466 | 31.195 | 91.375 | 43.136
| 23.4625 | 328.964 | 426.368 | 90.46 | 31.196 | 91.374 | 43.141
| 23.4639 | 328.816 | 426.429 | 90.46 | 31.198 | 91.368 | 43.138
| 23.4653 | 328.645 | 425.523 | 90.456 | 31.199 | 91.37 | 43.142
| 23.4667 | 329.262 | 426.201 | 90.451 | 31.205 | 91.361 | 43.145
| 23.4681 | 328.72 | 426.363 | 90.457 | 31.201 | 91.366 | 43.15
| 23.4694 | 328.474 | 425.933 | 90.446 | 31.205 | 91.364 | 43.147
| 23.4708 | 329.206 | 426.298 | 90.451 | 31.207 | 91.368 | 43.152
| 23.4722 | 328.614 | 427.336 | 90.458 | 31.21 | 91.378 | 43.156
| 23.4736 | 328.561 | 427.438 | 90.459 | 31.21 | 91.386 | 43.154
| 23.475 | 328.867 | 426.225 | 90.461 | 31.21 | 91.386 | 43.158
| 23.4764 | 328.337 | 427.403 | 90.457 | 31.214 | 91.377 | 43.159
| 23.4778 | 327.985 | 427.191 | 90.452 | 31.212 | 91.377 | 43.162
| 23.4792 | 328.801 | 427.6 | 90.448 | 31.214 | 91.368 | 43.166
| 23.4806 | 328.866 | 425.748 | 90.449 | 31.214 | 91.375 | 43.165
| 23.4819 | 328.493 | 427.105 | 90.454 | 31.218 | 91.385 | 43.168
| 23.4833 | 328.195 | 426.502 | 90.448 | 31.218 | 91.379 | 43.173
| 23.4847 | 328.885 | 425.787 | 90.446 | 31.22 | 91.377 | 43.176
| 23.4861 | 328.452 | 426.8 | 90.448 | 31.224 | 91.378 | 43.176
| 23.4875 | 327.936 | 426.799 | 90.45 | 31.226 | 91.39 | 43.177
| 23.4889 | 329.899 | 427.393 | 90.461 | 31.224 | 91.412 | 43.176
| 23.4903 | 328.934 | 428.11 | 90.476 | 31.225 | 91.424 | 43.181
| 23.4917 | 329.805 | 427.264 | 90.482 | 31.232 | 91.443 | 43.183
| 23.4931 | 329.073 | 427.471 | 90.492 | 31.23 | 91.46 | 43.187
| 23.4944 | 329.483 | 427.599 | 90.501 | 31.226 | 91.473 | 43.189
| 23.4958 | 328.984 | 428.298 | 90.507 | 31.232 | 91.486 | 43.192
| 23.4972 | 329.161 | 428.337 | 90.513 | 31.232 | 91.491 | 43.189
| 23.4986 | 329.375 | 428.782 | 90.524 | 31.235 | 91.505 | 43.196
| 23.5 | 330.041 | 427.472 | 90.53 | 31.236 | 91.515 | 43.194
| 23.5014 | 329.829 | 426.766 | 90.543 | 31.236 | 91.531 | 43.196
| 23.5028 | 329.52 | 427.766 | 90.551 | 31.239 | 91.542 | 43.197
| 23.5042 | 329.31 | 428.194 | 90.558 | 31.242 | 91.556 | 43.203
| 23.5056 | 329.824 | 427.736 | 90.564 | 31.245 | 91.571 | 43.208
| 23.5069 | 329.538 | 427.959 | 90.574 | 31.245 | 91.574 | 43.206
| 23.5083 | 330.405 | 427.786 | 90.583 | 31.247 | 91.588 | 43.209
| 23.5097 | 329.586 | 428.983 | 90.599 | 31.242 | 91.615 | 43.212
| 23.5111 | 330.88 | 428.239 | 90.62 | 31.251 | 91.639 | 43.208
| 23.5125 | 329.802 | 428.929 | 90.634 | 31.251 | 91.667 | 43.216
| 23.5139 | 330.806 | 429.793 | 90.657 | 31.253 | 91.688 | 43.216
| 23.5153 | 330.452 | 430.066 | 90.68 | 31.251 | 91.741 | 43.221
| 23.5167 | 330.714 | 429.405 | 90.699 | 31.258 | 91.759 | 43.223
| 23.5181 | 330.54 | 428.728 | 90.709 | 31.255 | 91.784 | 43.221
| 23.5194 | 329.817 | 429.53 | 90.717 | 31.259 | 91.792 | 43.223
| 23.5208 | 330.427 | 428.458 | 90.726 | 31.257 | 91.799 | 43.225
| 23.5222 | 330.39 | 429.808 | 90.747 | 31.262 | 91.819 | 43.23
| 23.5236 | 330.276 | 430.165 | 90.763 | 31.264 | 91.837 | 43.233
| 23.525 | 331.054 | 429.948 | 90.784 | 31.267 | 91.863 | 43.238
| 23.5264 | 330.572 | 430.533 | 90.803 | 31.265 | 91.89 | 43.236
| 23.5278 | 324.494 | 430.121 | 90.734 | 31.272 | 91.913 | 43.241
| 23.5292 | 324.118 | 429.29 | 90.636 | 31.268 | 91.917 | 43.242
| 23.5306 | 324.817 | 429.871 | 90.568 | 31.268 | 91.922 | 43.243
| 23.5319 | 323.629 | 429.266 | 90.516 | 31.275 | 91.94 | 43.248
| 23.5333 | 324.361 | 429.288 | 90.465 | 31.276 | 91.947 | 43.249
| 23.5347 | 324.348 | 429.34 | 90.421 | 31.279 | 91.942 | 43.248
| 23.5361 | 324.155 | 428.032 | 90.365 | 31.282 | 91.953 | 43.253
| 23.5375 | 324.086 | 428.746 | 90.331 | 31.282 | 91.957 | 43.261
| 23.5389 | 323.622 | 429.439 | 90.295 | 31.283 | 91.961 | 43.262
| 23.5403 | 324.386 | 428.881 | 90.252 | 31.28 | 91.962 | 43.261
| 23.5417 | 324.041 | 429.26 | 90.213 | 31.283 | 91.964 | 43.263
| 23.5431 | 323.938 | 428.215 | 90.172 | 31.278 | 91.959 | 43.271
| 23.5444 | 323.542 | 429.346 | 90.132 | 31.282 | 91.962 | 43.273
| 23.5458 | 324.289 | 428.936 | 90.097 | 31.28 | 91.959 | 43.272
| 23.5472 | 323.397 | 427.959 | 90.064 | 31.278 | 91.954 | 43.275
| 23.5486 | 323.115 | 428.09 | 90.019 | 31.286 | 91.942 | 43.281
| 23.55 | 323.865 | 428.454 | 89.979 | 31.281 | 91.938 | 43.28
| 23.5514 | 324.368 | 428.333 | 89.957 | 31.282 | 91.944 | 43.284
| 23.5528 | 324.849 | 428.95 | 89.928 | 31.28 | 91.956 | 43.292
| 23.5542 | 324.047 | 429.668 | 89.903 | 31.285 | 91.969 | 43.291
| 23.5556 | 323.726 | 429.477 | 89.882 | 31.283 | 91.977 | 43.291
| 23.5569 | 323.848 | 429.62 | 89.857 | 31.281 | 91.989 | 43.297
| 23.5583 | 323.887 | 429.468 | 89.826 | 31.283 | 91.993 | 43.304
| 23.5597 | 323.974 | 427.878 | 89.797 | 31.28 | 91.996 | 43.303
| 23.5611 | 323.639 | 429.02 | 89.768 | 31.281 | 92.001 | 43.305
| 23.5625 | 324.3 | 428.21 | 89.741 | 31.277 | 91.994 | 43.304
| 23.5639 | 322.958 | 428.305 | 89.712 | 31.28 | 91.995 | 43.313
| 23.5653 | 323.683 | 428.96 | 89.69 | 31.279 | 91.989 | 43.309
| 23.5667 | 324.045 | 429.08 | 89.665 | 31.277 | 91.995 | 43.311
| 23.5681 | 323.989 | 428.379 | 89.645 | 31.277 | 92.011 | 43.314
| 23.5694 | 324.334 | 428.473 | 89.626 | 31.282 | 92.019 | 43.315
| 23.5708 | 324.623 | 428.945 | 89.608 | 31.277 | 92.026 | 43.325
| 23.5722 | 324.007 | 427.604 | 89.585 | 31.276 | 92.028 | 43.33
| 23.5736 | 324.132 | 430.003 | 89.57 | 31.278 | 92.043 | 43.327
| 23.575 | 323.952 | 428.177 | 89.553 | 31.274 | 92.054 | 43.333
| 23.5764 | 323.252 | 428.552 | 89.531 | 31.27 | 92.061 | 43.334
| 23.5778 | 324.191 | 428.541 | 89.51 | 31.275 | 92.061 | 43.334
| 23.5792 | 325.006 | 428.961 | 89.496 | 31.273 | 92.069 | 43.339
| 23.5806 | 324.653 | 429.22 | 89.485 | 31.274 | 92.076 | 43.34
| 23.5819 | 324.846 | 430.575 | 89.476 | 31.268 | 92.097 | 43.348
| 23.5833 | 325.327 | 430.319 | 89.478 | 31.273 | 92.133 | 43.346
| 23.5847 | 325.185 | 430.727 | 89.475 | 31.271 | 92.165 | 43.349
| 23.5861 | 325.53 | 430.533 | 89.477 | 31.266 | 92.198 | 43.351
| 23.5875 | 324.757 | 430.414 | 89.47 | 31.271 | 92.213 | 43.357
| 23.5889 | 325.135 | 429.573 | 89.465 | 31.27 | 92.232 | 43.355
| 23.5903 | 321.691 | 424.361 | 89.381 | 31.273 | 92.126 | 43.357
| 23.5917 | 320.777 | 425.143 | 89.313 | 31.265 | 92.036 | 43.36
| 23.5931 | 321.552 | 425.178 | 89.259 | 31.269 | 91.966 | 43.363
| 23.5944 | 320.792 | 425.546 | 89.22 | 31.268 | 91.918 | 43.366
| 23.5958 | 321.32 | 426.108 | 89.184 | 31.264 | 91.885 | 43.37
| 23.5972 | 321.474 | 426.6 | 89.145 | 31.265 | 91.858 | 43.372
| 23.5986 | 321.672 | 424.683 | 89.107 | 31.263 | 91.838 | 43.374
| 23.6 | 321.551 | 425.187 | 89.076 | 31.262 | 91.822 | 43.378
| 23.6014 | 322.03 | 425.03 | 89.044 | 31.265 | 91.798 | 43.381
| 23.6028 | 321.456 | 425.915 | 89.008 | 31.263 | 91.787 | 43.384
| 23.6042 | 320.842 | 425.279 | 88.98 | 31.262 | 91.769 | 43.381
| 23.6056 | 320.874 | 425.052 | 88.94 | 31.258 | 91.747 | 43.388
| 23.6069 | 321.522 | 424.264 | 88.909 | 31.26 | 91.73 | 43.39
| 23.6083 | 320.879 | 424.713 | 88.875 | 31.254 | 91.717 | 43.395
| 23.6097 | 320.964 | 425.858 | 88.842 | 31.257 | 91.714 | 43.393
| 23.6111 | 322.254 | 425.435 | 88.821 | 31.255 | 91.706 | 43.395
| 23.6125 | 321.158 | 425.778 | 88.798 | 31.253 | 91.702 | 43.403
| 23.6139 | 321.29 | 425.341 | 88.772 | 31.25 | 91.695 | 43.403
| 23.6153 | 321.038 | 425.191 | 88.742 | 31.25 | 91.676 | 43.401
| 23.6167 | 321.376 | 425.254 | 88.713 | 31.246 | 91.667 | 43.408
| 23.6181 | 321.274 | 425.708 | 88.69 | 31.248 | 91.663 | 43.41
| 23.6194 | 321.942 | 425.316 | 88.668 | 31.247 | 91.662 | 43.407
| 23.6208 | 321.997 | 424.872 | 88.64 | 31.245 | 91.663 | 43.408
| 23.6222 | 321.288 | 426.008 | 88.627 | 31.242 | 91.667 | 43.412
| 23.6236 | 321.642 | 426.263 | 88.597 | 31.243 | 91.665 | 43.413
| 23.625 | 322.322 | 425.368 | 88.584 | 31.241 | 91.668 | 43.421
| 23.6264 | 321.428 | 426.434 | 88.562 | 31.243 | 91.658 | 43.421
| 23.6278 | 321.097 | 425.996 | 88.539 | 31.235 | 91.653 | 43.418
| 23.6292 | 322.616 | 425.832 | 88.531 | 31.237 | 91.673 | 43.424
| 23.6306 | 321.503 | 426.478 | 88.52 | 31.237 | 91.687 | 43.422
| 23.6319 | 321.979 | 426.811 | 88.517 | 31.231 | 91.702 | 43.427
| 23.6333 | 321.721 | 426.504 | 88.504 | 31.23 | 91.709 | 43.427
| 23.6347 | 321.693 | 426.492 | 88.488 | 31.233 | 91.713 | 43.425
| 23.6361 | 322.582 | 425.998 | 88.48 | 31.229 | 91.723 | 43.43
| 23.6375 | 321.808 | 424.538 | 88.462 | 31.228 | 91.721 | 43.428
| 23.6389 | 321.835 | 426.659 | 88.447 | 31.223 | 91.72 | 43.429
| 23.6403 | 322.215 | 425.976 | 88.438 | 31.227 | 91.719 | 43.437
| 23.6417 | 321.633 | 425.985 | 88.426 | 31.226 | 91.722 | 43.435
| 23.6431 | 322.408 | 425.678 | 88.417 | 31.224 | 91.728 | 43.437
| 23.6444 | 322.738 | 425.906 | 88.4 | 31.225 | 91.729 | 43.437
| 23.6458 | 321.754 | 426.032 | 88.391 | 31.226 | 91.727 | 43.439
| 23.6472 | 320.971 | 424.567 | 88.374 | 31.219 | 91.723 | 43.438
| 23.6486 | 322.453 | 425.389 | 88.369 | 31.222 | 91.732 | 43.439
| 23.65 | 321.428 | 425.691 | 88.357 | 31.221 | 91.735 | 43.447
| 23.6514 | 322.35 | 425.914 | 88.349 | 31.22 | 91.727 | 43.443
| 23.6528 | 322.427 | 427.033 | 88.347 | 31.216 | 91.744 | 43.45
| 23.6542 | 323.013 | 426.389 | 88.338 | 31.217 | 91.753 | 43.448
| 23.6556 | 322.43 | 427.459 | 88.344 | 31.214 | 91.774 | 43.448
| 23.6569 | 322.857 | 426.935 | 88.346 | 31.213 | 91.792 | 43.448
| 23.6583 | 323.365 | 427.138 | 88.344 | 31.216 | 91.805 | 43.455
| 23.6597 | 322.795 | 426.852 | 88.34 | 31.211 | 91.821 | 43.455
| 23.6611 | 323.378 | 426.596 | 88.339 | 31.212 | 91.822 | 43.454
| 23.6625 | 322.987 | 427.758 | 88.333 | 31.208 | 91.83 | 43.456
| 23.6639 | 322.677 | 426.553 | 88.323 | 31.21 | 91.83 | 43.454
| 23.6653 | 322.332 | 427.431 | 88.321 | 31.211 | 91.839 | 43.455
| 23.6667 | 322.714 | 426.577 | 88.313 | 31.21 | 91.837 | 43.457
| 23.6681 | 322.486 | 427.026 | 88.306 | 31.209 | 91.836 | 43.458
| 23.6694 | 322.669 | 427.741 | 88.308 | 31.21 | 91.845 | 43.461
| 23.6708 | 323.098 | 426.667 | 88.311 | 31.21 | 91.854 | 43.461
| 23.6722 | 322.965 | 428.23 | 88.309 | 31.208 | 91.855 | 43.468
| 23.6736 | 323.098 | 426.206 | 88.312 | 31.205 | 91.873 | 43.466
| 23.675 | 322.995 | 428.069 | 88.315 | 31.206 | 91.881 | 43.466
| 23.6764 | 322.745 | 427.447 | 88.31 | 31.206 | 91.89 | 43.466
| 23.6778 | 323.317 | 426.76 | 88.311 | 31.21 | 91.897 | 43.473
| 23.6792 | 323.079 | 426.907 | 88.315 | 31.205 | 91.904 | 43.471
| 23.6806 | 322.975 | 427.766 | 88.318 | 31.203 | 91.918 | 43.474
| 23.6819 | 323.09 | 428.217 | 88.324 | 31.206 | 91.933 | 43.475
| 23.6833 | 323.939 | 427.602 | 88.331 | 31.209 | 91.95 | 43.472
| 23.6847 | 323.659 | 427.302 | 88.341 | 31.204 | 91.974 | 43.481
| 23.6861 | 324.098 | 428.374 | 88.345 | 31.205 | 91.99 | 43.477
| 23.6875 | 323.665 | 428.85 | 88.356 | 31.207 | 92.003 | 43.48
| 23.6889 | 323.958 | 428.526 | 88.359 | 31.202 | 92.02 | 43.484
| 23.6903 | 323.407 | 429.059 | 88.367 | 31.205 | 92.04 | 43.487
| 23.6917 | 321.424 | 424.344 | 88.374 | 31.206 | 92.048 | 43.488
| 23.6931 | 321.119 | 425.99 | 88.334 | 31.203 | 91.995 | 43.487
| 23.6944 | 322.62 | 425.563 | 88.311 | 31.204 | 91.963 | 43.49
| 23.6958 | 321.622 | 424.702 | 88.29 | 31.208 | 91.941 | 43.492
| 23.6972 | 321.302 | 425.519 | 88.273 | 31.204 | 91.915 | 43.493
| 23.6986 | 321.893 | 425.25 | 88.251 | 31.206 | 91.883 | 43.494
| 23.7 | 321.485 | 425.739 | 88.234 | 31.206 | 91.868 | 43.497
| 23.7014 | 321.659 | 424.399 | 88.222 | 31.201 | 91.853 | 43.496
| 23.7028 | 321.054 | 425.22 | 88.205 | 31.203 | 91.83 | 43.497
| 23.7042 | 320.58 | 424.905 | 88.185 | 31.204 | 91.798 | 43.5
| 23.7056 | 321.116 | 423.812 | 88.16 | 31.203 | 91.77 | 43.498
| 23.7069 | 320.708 | 424.784 | 88.139 | 31.201 | 91.75 | 43.505
| 23.7083 | 320.7 | 425.038 | 88.122 | 31.199 | 91.734 | 43.508
| 23.7097 | 321.403 | 423.927 | 88.102 | 31.199 | 91.714 | 43.511
| 23.7111 | 321.214 | 423.756 | 88.083 | 31.202 | 91.697 | 43.51
| 23.7125 | 320.258 | 424.504 | 88.058 | 31.201 | 91.675 | 43.509
| 23.7139 | 320.542 | 424.838 | 88.04 | 31.201 | 91.662 | 43.514
| 23.7153 | 320.318 | 424.334 | 88.021 | 31.198 | 91.644 | 43.515
| 23.7167 | 320.264 | 423.739 | 87.997 | 31.2 | 91.619 | 43.514
| 23.7181 | 321.46 | 424.007 | 87.973 | 31.198 | 91.599 | 43.52
| 23.7194 | 320.046 | 422.725 | 87.957 | 31.198 | 91.589 | 43.518
| 23.7208 | 320.72 | 424.595 | 87.94 | 31.2 | 91.575 | 43.523
| 23.7222 | 319.922 | 422.326 | 87.919 | 31.197 | 91.555 | 43.526
| 23.7236 | 320.465 | 422.805 | 87.887 | 31.196 | 91.531 | 43.525
| 23.725 | 319.598 | 423.349 | 87.869 | 31.196 | 91.519 | 43.527
| 23.7264 | 319.498 | 423.436 | 87.846 | 31.202 | 91.504 | 43.526
| 23.7278 | 319.508 | 423.792 | 87.826 | 31.2 | 91.482 | 43.527
| 23.7292 | 319.368 | 422.814 | 87.799 | 31.193 | 91.456 | 43.53
| 23.7306 | 319.792 | 422.214 | 87.772 | 31.197 | 91.422 | 43.53
| 23.7319 | 319.247 | 422.448 | 87.734 | 31.194 | 91.39 | 43.534
| 23.7333 | 318.386 | 422.271 | 87.707 | 31.191 | 91.365 | 43.534
| 23.7347 | 316.052 | 418.167 | 87.653 | 31.19 | 91.303 | 43.534
| 23.7361 | 320.359 | 423.978 | 87.652 | 31.189 | 91.322 | 43.536
| 23.7375 | 319.813 | 424.379 | 87.656 | 31.188 | 91.353 | 43.537
| 23.7389 | 318.984 | 423.238 | 87.638 | 31.184 | 91.351 | 43.539
| 23.7403 | 322.626 | 427.429 | 87.626 | 31.185 | 91.347 | 43.538
| 23.7417 | 322.858 | 426.197 | 87.671 | 31.183 | 91.443 | 43.538
| 23.7431 | 322.407 | 427.19 | 87.688 | 31.181 | 91.503 | 43.537
| 23.7444 | 322.296 | 426.275 | 87.706 | 31.18 | 91.547 | 43.541
| 23.7458 | 321.799 | 426.87 | 87.717 | 31.181 | 91.581 | 43.542
| 23.7472 | 322.371 | 426.31 | 87.722 | 31.179 | 91.596 | 43.54
| 23.7486 | 322.232 | 427.164 | 87.726 | 31.176 | 91.625 | 43.544
| 23.75 | 321.973 | 425.642 | 87.731 | 31.177 | 91.637 | 43.544
| 23.7514 | 321.596 | 426.512 | 87.725 | 31.179 | 91.645 | 43.543
| 23.7528 | 322.316 | 425.549 | 87.728 | 31.178 | 91.657 | 43.548
| 23.7542 | 321.746 | 426.959 | 87.732 | 31.174 | 91.657 | 43.546
| 23.7556 | 322.633 | 426.1 | 87.731 | 31.176 | 91.672 | 43.543
| 23.7569 | 322.04 | 426.888 | 87.735 | 31.177 | 91.677 | 43.545
| 23.7583 | 321.27 | 426.336 | 87.732 | 31.174 | 91.684 | 43.547
| 23.7597 | 322.062 | 425.303 | 87.742 | 31.174 | 91.696 | 43.546
| 23.7611 | 322.301 | 425.659 | 87.747 | 31.173 | 91.707 | 43.55
| 23.7625 | 322.092 | 427.229 | 87.754 | 31.174 | 91.723 | 43.552
| 23.7639 | 322.182 | 427.011 | 87.764 | 31.171 | 91.746 | 43.549
| 23.7653 | 322.659 | 427.761 | 87.776 | 31.173 | 91.766 | 43.554
| 23.7667 | 322.652 | 427.391 | 87.782 | 31.172 | 91.783 | 43.553
| 23.7681 | 322.507 | 427.198 | 87.792 | 31.177 | 91.803 | 43.552
| 23.7694 | 322.405 | 427.687 | 87.798 | 31.174 | 91.804 | 43.55
| 23.7708 | 321.762 | 426.902 | 87.806 | 31.174 | 91.814 | 43.555
| 23.7722 | 322.898 | 427.469 | 87.806 | 31.174 | 91.823 | 43.558
| 23.7736 | 322.574 | 426.451 | 87.817 | 31.173 | 91.833 | 43.553
| 23.775 | 322.111 | 427.331 | 87.82 | 31.173 | 91.837 | 43.559
| 23.7764 | 323.268 | 426.63 | 87.821 | 31.173 | 91.836 | 43.563
| 23.7778 | 322.326 | 426.637 | 87.823 | 31.172 | 91.836 | 43.563
| 23.7792 | 322.315 | 427.16 | 87.831 | 31.172 | 91.839 | 43.565
| 23.7806 | 322.791 | 426.055 | 87.835 | 31.176 | 91.849 | 43.562
| 23.7819 | 322.897 | 426.198 | 87.835 | 31.173 | 91.851 | 43.565
| 23.7833 | 323.377 | 426.836 | 87.839 | 31.174 | 91.854 | 43.567
| 23.7847 | 322.875 | 426.633 | 87.85 | 31.176 | 91.864 | 43.569
| 23.7861 | 322.798 | 426.233 | 87.86 | 31.175 | 91.881 | 43.57
| 23.7875 | 323.172 | 426.215 | 87.863 | 31.173 | 91.884 | 43.568
| 23.7889 | 322.743 | 426.612 | 87.869 | 31.175 | 91.887 | 43.573
| 23.7903 | 322.21 | 426.808 | 87.87 | 31.175 | 91.892 | 43.572
| 23.7917 | 321.657 | 426.041 | 87.881 | 31.172 | 91.902 | 43.573
| 23.7931 | 323.016 | 427.149 | 87.884 | 31.178 | 91.907 | 43.578
| 23.7944 | 322.938 | 427.861 | 87.892 | 31.175 | 91.919 | 43.581
| 23.7958 | 322.957 | 427.884 | 87.907 | 31.178 | 91.935 | 43.577
| 23.7972 | 322.814 | 425.976 | 87.915 | 31.182 | 91.949 | 43.584
| 23.7986 | 323.921 | 427.951 | 87.931 | 31.177 | 91.97 | 43.583
| 23.8 | 323.194 | 427.601 | 87.944 | 31.175 | 91.992 | 43.584
| 23.8014 | 323.379 | 428.322 | 87.957 | 31.177 | 92.014 | 43.586
| 23.8028 | 323.773 | 427.702 | 87.97 | 31.178 | 92.024 | 43.586
| 23.8042 | 323.36 | 427.54 | 87.976 | 31.178 | 92.039 | 43.588
| 23.8056 | 323.003 | 427.766 | 87.992 | 31.179 | 92.058 | 43.593
| 23.8069 | 323.712 | 428.944 | 88.003 | 31.177 | 92.077 | 43.591
| 23.8083 | 323.001 | 427.552 | 88.017 | 31.178 | 92.093 | 43.593
| 23.8097 | 323.748 | 426.69 | 88.017 | 31.183 | 92.091 | 43.596
| 23.8111 | 323.394 | 427.491 | 88.025 | 31.178 | 92.089 | 43.599
| 23.8125 | 323.673 | 427.08 | 88.036 | 31.183 | 92.107 | 43.599
| 23.8139 | 323.656 | 427.188 | 88.042 | 31.186 | 92.118 | 43.601
| 23.8153 | 324.574 | 427.843 | 88.058 | 31.182 | 92.135 | 43.603
| 23.8167 | 323.992 | 429.023 | 88.078 | 31.183 | 92.158 | 43.606
| 23.8181 | 324.253 | 429.52 | 88.096 | 31.183 | 92.181 | 43.608
| 23.8194 | 323.892 | 429.253 | 88.116 | 31.184 | 92.208 | 43.609
| 23.8208 | 325.009 | 430.392 | 88.141 | 31.185 | 92.246 | 43.612
| 23.8222 | 325.477 | 429.393 | 88.169 | 31.183 | 92.286 | 43.611
| 23.8236 | 324.76 | 429.961 | 88.189 | 31.187 | 92.306 | 43.613
| 23.8377 | 321.413 | 424.711 | 88.162 | 31.199 | 92.144 | 43.637
| 23.8403 | 321.695 | 424.681 | 88.124 | 31.199 | 92.068 | 43.644
| 23.8472 | 322.058 | 417.549 | 88.046 | 31.201 | 91.262 | 43.654
| 23.8542 | 322.002 | 416.114 | 88.018 | 31.21 | 90.9 | 43.668
| 23.8611 | 322.19 | 416.476 | 87.972 | 31.205 | 90.645 | 43.676
| 23.8681 | 321.858 | 417.172 | 87.948 | 31.205 | 90.513 | 43.674
| 23.875 | 323.908 | 418.687 | 87.991 | 31.21 | 90.513 | 43.673
| 23.8819 | 323.526 | 419.203 | 88.079 | 31.207 | 90.585 | 43.666
| 23.8889 | 324.376 | 420.382 | 88.139 | 31.213 | 90.594 | 43.667
| 23.8958 | 323.263 | 419.252 | 88.176 | 31.214 | 90.561 | 43.658
| 23.9028 | 322.361 | 418.234 | 88.161 | 31.217 | 90.44 | 43.652
| 23.9097 | 323.229 | 418.563 | 88.143 | 31.226 | 90.352 | 43.643
| 23.9167 | 322.069 | 417.8 | 88.14 | 31.239 | 90.309 | 43.641
| 23.9236 | 322.4 | 418.38 | 88.137 | 31.233 | 90.264 | 43.63
| 23.9306 | 324.79 | 419.342 | 88.188 | 31.235 | 90.298 | 43.625
| 23.9375 | 324.845 | 420.417 | 88.285 | 31.233 | 90.414 | 43.617
| 23.9444 | 325.007 | 419.455 | 88.366 | 31.24 | 90.468 | 43.613
| 23.9514 | 325.35 | 421.135 | 88.448 | 31.244 | 90.524 | 43.61
| 23.9583 | 321.876 | 415.916 | 88.326 | 31.249 | 90.263 | 43.598
| 23.9653 | 322.053 | 415.56 | 88.269 | 31.259 | 90.117 | 43.591
| 23.9722 | 322.261 | 417.515 | 88.215 | 31.261 | 90.034 | 43.593
| 23.9792 | 323.225 | 417.65 | 88.231 | 31.26 | 90.08 | 43.585
| 23.9861 | 323.875 | 419.469 | 88.28 | 31.267 | 90.145 | 43.587
| 23.9931 | 322.729 | 417.714 | 88.217 | 31.262 | 90.023 | 43.577
| 24 | 322.919 | 417.516 | 88.207 | 31.271 | 90 | 43.574
| 24.0069 | 322.895 | 417.466 | 88.195 | 31.272 | 89.981 | 43.569
| 24.0139 | 324.431 | 419.458 | 88.213 | 31.271 | 90.005 | 43.566
| 24.0208 | 323.798 | 420.667 | 88.306 | 31.273 | 90.139 | 43.555
| 24.0278 | 324.773 | 411.422 | 88.387 | 31.28 | 90.096 | 43.555
| 24.0347 | 324.017 | 410.972 | 88.434 | 31.283 | 89.503 | 43.548
| 24.0417 | 323.968 | 409.909 | 88.435 | 31.298 | 89.229 | 43.546
| 24.0486 | 323.291 | 410.696 | 88.449 | 31.299 | 89.055 | 43.541
| 24.0556 | 324.326 | 410.144 | 88.476 | 31.305 | 88.961 | 43.537
| 24.0625 | 325.024 | 410.642 | 88.522 | 31.307 | 88.919 | 43.525
| 24.0694 | 321.874 | 414.372 | 88.521 | 31.31 | 88.822 | 43.51
| 24.0764 | 322.032 | 415.211 | 88.377 | 31.32 | 89.123 | 43.501
| 24.0833 | 321.292 | 415.154 | 88.285 | 31.322 | 89.213 | 43.488
| 24.0903 | 322.083 | 415.56 | 88.217 | 31.323 | 89.267 | 43.474
| 24.0972 | 321.944 | 415.679 | 88.169 | 31.322 | 89.307 | 43.463
| 24.1042 | 322.343 | 416.279 | 88.151 | 31.326 | 89.37 | 43.457
| 24.1111 | 322.518 | 415.414 | 88.137 | 31.321 | 89.407 | 43.446
| 24.1181 | 322.471 | 415.694 | 88.107 | 31.322 | 89.398 | 43.442
| 24.125 | 322.18 | 414.704 | 88.091 | 31.325 | 89.398 | 43.439
| 24.1319 | 322.208 | 415.451 | 88.067 | 31.328 | 89.396 | 43.436
| 24.1389 | 322.66 | 415.574 | 88.042 | 31.327 | 89.38 | 43.43
| 24.1458 | 322.211 | 414.948 | 88.041 | 31.332 | 89.41 | 43.427
| 24.1528 | 322.847 | 415.924 | 88.049 | 31.328 | 89.424 | 43.423
| 24.1597 | 321.998 | 415.223 | 88.015 | 31.333 | 89.388 | 43.418
| 24.1667 | 322.451 | 416.501 | 88.008 | 31.339 | 89.393 | 43.42
| 24.1736 | 322.521 | 416.311 | 88 | 31.336 | 89.393 | 43.415
| 24.1806 | 322.806 | 418.131 | 87.998 | 31.334 | 89.397 | 43.415
| 24.1875 | 322.632 | 418.463 | 88.051 | 31.338 | 89.486 | 43.409
| 24.1944 | 322.368 | 417.719 | 88.052 | 31.34 | 89.483 | 43.41
| 24.2014 | 321.845 | 417.211 | 88.056 | 31.343 | 89.475 | 43.407
| 24.2083 | 323.062 | 416.893 | 88.063 | 31.346 | 89.481 | 43.411
| 24.2153 | 322.912 | 417.509 | 88.075 | 31.351 | 89.502 | 43.404
| 24.2222 | 322.644 | 417.56 | 88.062 | 31.351 | 89.475 | 43.401
| 24.2292 | 322.248 | 416.663 | 88.054 | 31.356 | 89.483 | 43.401
| 24.2361 | 322.153 | 417.954 | 88.057 | 31.351 | 89.485 | 43.399
| 24.2431 | 322.621 | 416.847 | 88.066 | 31.356 | 89.5 | 43.394
| 24.25 | 321.717 | 417.188 | 88.062 | 31.358 | 89.503 | 43.399
| 24.2569 | 322.694 | 417.076 | 88.054 | 31.36 | 89.488 | 43.391
| 24.2639 | 321.95 | 416.348 | 88.034 | 31.366 | 89.461 | 43.393
| 24.2708 | 321.1 | 414.984 | 87.975 | 31.365 | 89.387 | 43.395
| 24.2778 | 320.703 | 415.432 | 87.895 | 31.367 | 89.283 | 43.394
| 24.2847 | 320.35 | 415.136 | 87.835 | 31.368 | 89.221 | 43.393
| 24.2917 | 320.048 | 413.86 | 87.744 | 31.367 | 89.122 | 43.392
| 24.2986 | 319.862 | 413.454 | 87.633 | 31.365 | 89.015 | 43.389
| 24.3056 | 324.394 | 412.191 | 87.573 | 31.365 | 88.897 | 43.385
| 24.3125 | 328.054 | 417.234 | 87.967 | 31.359 | 89.026 | 43.383
| 24.3194 | 328.558 | 417.348 | 88.287 | 31.366 | 89.2 | 43.376
| 24.3264 | 328.427 | 416.773 | 88.564 | 31.375 | 89.312 | 43.368
| 24.3333 | 328.035 | 417.896 | 88.793 | 31.383 | 89.349 | 43.364
| 24.3403 | 327.559 | 416.843 | 88.949 | 31.402 | 89.319 | 43.358
| 24.3472 | 329.286 | 418.24 | 89.163 | 31.413 | 89.419 | 43.356
| 24.3542 | 329.59 | 418.185 | 89.368 | 31.43 | 89.527 | 43.352
| 24.3611 | 329.989 | 418.817 | 89.557 | 31.448 | 89.6 | 43.353
| 24.3681 | 330 | 418.779 | 89.723 | 31.458 | 89.651 | 43.348
| 24.375 | 329.429 | 417.814 | 89.861 | 31.479 | 89.678 | 43.343
| 24.3819 | 328.029 | 418.111 | 89.967 | 31.494 | 89.675 | 43.351
| 24.3889 | 328.754 | 417.462 | 90.04 | 31.505 | 89.648 | 43.349
| 24.3958 | 328.502 | 417.319 | 90.116 | 31.522 | 89.639 | 43.347
| 24.4028 | 327.007 | 416.935 | 90.148 | 31.535 | 89.599 | 43.354
| 24.4097 | 326.949 | 416.211 | 90.161 | 31.546 | 89.534 | 43.354
| 24.4167 | 326.933 | 416.047 | 90.158 | 31.556 | 89.486 | 43.354
| 24.4236 | 327.248 | 415.255 | 90.174 | 31.567 | 89.468 | 43.353
| 24.4306 | 326.885 | 414.949 | 90.178 | 31.575 | 89.453 | 43.35
| 24.4375 | 325.508 | 414.891 | 90.134 | 31.582 | 89.372 | 43.354
| 24.4444 | 326.621 | 414.264 | 90.095 | 31.59 | 89.297 | 43.347
| 24.4514 | 324.751 | 414.096 | 90.039 | 31.597 | 89.228 | 43.351
| 24.4583 | 326.113 | 414.058 | 90.014 | 31.602 | 89.201 | 43.346
| 24.4653 | 325.655 | 414.734 | 89.992 | 31.606 | 89.191 | 43.343
| 24.4722 | 325.05 | 414.192 | 89.96 | 31.614 | 89.164 | 43.34
| 24.4792 | 324.98 | 413.712 | 89.955 | 31.615 | 89.132 | 43.336
| 24.4861 | 325.936 | 413.714 | 89.925 | 31.621 | 89.079 | 43.331
| 24.4931 | 321.126 | 417.282 | 89.64 | 31.627 | 89.01 | 43.327
| 24.5 | 321.766 | 417.291 | 89.484 | 31.624 | 89.255 | 43.315
| 24.5069 | 322.349 | 418.453 | 89.358 | 31.623 | 89.385 | 43.315
| 24.5139 | 322.723 | 417.322 | 89.263 | 31.617 | 89.49 | 43.304
| 24.5208 | 322.127 | 417.894 | 89.183 | 31.618 | 89.573 | 43.303
| 24.5278 | 321.609 | 416.689 | 89.067 | 31.611 | 89.557 | 43.301
| 24.5347 | 321.683 | 416.442 | 88.948 | 31.609 | 89.515 | 43.301
| 24.5417 | 322.506 | 416.97 | 88.859 | 31.603 | 89.522 | 43.301
| 24.5486 | 322.429 | 417.815 | 88.827 | 31.597 | 89.596 | 43.3
| 24.5556 | 322.755 | 418.247 | 88.772 | 31.594 | 89.619 | 43.295
| 24.5625 | 323.4 | 418.171 | 88.783 | 31.59 | 89.722 | 43.298
| 24.5694 | 322.505 | 418.63 | 88.772 | 31.589 | 89.766 | 43.303
| 24.5764 | 323.362 | 418.599 | 88.785 | 31.586 | 89.828 | 43.3
| 24.5833 | 323.31 | 419.316 | 88.796 | 31.585 | 89.884 | 43.303
| 24.5903 | 323.116 | 419.637 | 88.818 | 31.588 | 89.934 | 43.308
| 24.5972 | 324.869 | 420.027 | 88.851 | 31.589 | 90.012 | 43.306
| 24.6042 | 324.937 | 420.395 | 88.912 | 31.583 | 90.11 | 43.31
| 24.6111 | 323.841 | 420.645 | 88.952 | 31.587 | 90.152 | 43.317
| 24.6181 | 324.42 | 413.211 | 88.994 | 31.587 | 90.133 | 43.319
| 24.625 | 324.965 | 413.843 | 89.043 | 31.592 | 89.642 | 43.324
| 24.6319 | 324.602 | 413.793 | 89.099 | 31.594 | 89.471 | 43.33
| 24.6389 | 324.461 | 413.543 | 89.133 | 31.597 | 89.35 | 43.331
| 24.6458 | 324.97 | 414.636 | 89.189 | 31.605 | 89.314 | 43.333
| 24.6528 | 325.185 | 413.444 | 89.232 | 31.609 | 89.271 | 43.33
| 24.6597 | 324.987 | 413.925 | 89.268 | 31.615 | 89.239 | 43.325
| 24.6667 | 324.564 | 414.047 | 89.283 | 31.616 | 89.19 | 43.321
| 24.6736 | 324.793 | 414.246 | 89.312 | 31.62 | 89.162 | 43.317
| 24.6806 | 325.385 | 413.063 | 89.333 | 31.624 | 89.129 | 43.314
| 24.6875 | 325.587 | 413.26 | 89.355 | 31.624 | 89.111 | 43.308
| 24.6944 | 324.481 | 414.063 | 89.348 | 31.628 | 89.065 | 43.302
| 24.7014 | 323.751 | 413.288 | 89.333 | 31.633 | 89.01 | 43.298
| 24.7083 | 323.757 | 411.808 | 89.288 | 31.633 | 88.917 | 43.287
| 24.7153 | 322.64 | 411.459 | 89.206 | 31.636 | 88.794 | 43.286
| 24.7222 | 320.822 | 409.528 | 89.121 | 31.644 | 88.677 | 43.284
| 24.7292 | 321.651 | 409.392 | 88.978 | 31.638 | 88.499 | 43.272
| 24.7361 | 322.599 | 420.833 | 88.805 | 31.631 | 88.706 | 43.259
| 24.7431 | 324.831 | 413.375 | 88.952 | 31.626 | 88.777 | 43.251
| 24.75 | 325.038 | 412.59 | 88.996 | 31.628 | 88.728 | 43.241
| 24.7569 | 324.319 | 412.177 | 89.034 | 31.632 | 88.716 | 43.234
| 24.7639 | 325.068 | 412.277 | 89.054 | 31.634 | 88.689 | 43.223
| 24.7708 | 324.448 | 411.562 | 89.072 | 31.635 | 88.652 | 43.217
| 24.7778 | 324.823 | 413.128 | 89.088 | 31.636 | 88.63 | 43.208
| 24.7847 | 325.022 | 412.992 | 89.116 | 31.639 | 88.647 | 43.206
| 24.7917 | 324.901 | 413.362 | 89.165 | 31.639 | 88.677 | 43.198
| 24.7986 | 325.631 | 412.777 | 89.204 | 31.643 | 88.701 | 43.189
| 24.8056 | 326.379 | 415.479 | 89.265 | 31.647 | 88.745 | 43.183
| 24.8125 | 322.561 | 409.494 | 89.103 | 31.649 | 88.449 | 43.178
| 24.8194 | 322.027 | 410.653 | 89.011 | 31.651 | 88.312 | 43.169
| 24.8264 | 323.067 | 410.713 | 88.956 | 31.647 | 88.252 | 43.166
| 24.8333 | 323.303 | 410.065 | 88.907 | 31.652 | 88.223 | 43.158
| 24.8403 | 323.689 | 411.494 | 88.898 | 31.646 | 88.241 | 43.149
| 24.8472 | 324.763 | 412.204 | 88.909 | 31.648 | 88.273 | 43.141
| 24.8542 | 324.646 | 413.662 | 88.97 | 31.642 | 88.368 | 43.135
| 24.8611 | 321.178 | 416.117 | 88.821 | 31.647 | 88.556 | 43.125
| 24.8681 | 322.047 | 416.302 | 88.722 | 31.642 | 88.76 | 43.119
| 24.875 | 321.928 | 417.578 | 88.655 | 31.637 | 88.902 | 43.115
| 24.8819 | 322.834 | 417.089 | 88.625 | 31.637 | 89.038 | 43.111
| 24.8889 | 320.548 | 415.249 | 88.593 | 31.637 | 89.112 | 43.11
| 24.8958 | 324.288 | 413.784 | 88.372 | 31.635 | 88.841 | 43.11
| 24.9028 | 326.006 | 413.645 | 88.623 | 31.631 | 88.777 | 43.112
| 24.9097 | 325.385 | 413.204 | 88.727 | 31.63 | 88.722 | 43.109
| 24.9167 | 324.934 | 414.302 | 88.803 | 31.635 | 88.675 | 43.111
| 24.9236 | 325.295 | 414.41 | 88.907 | 31.644 | 88.711 | 43.115
| 24.9306 | 325.654 | 415.624 | 88.996 | 31.643 | 88.724 | 43.11
| 24.9375 | 325.353 | 415.097 | 89.067 | 31.651 | 88.722 | 43.105
| 24.9444 | 327.2 | 415.754 | 89.189 | 31.656 | 88.81 | 43.109
| 24.9514 | 327.099 | 417.449 | 89.311 | 31.666 | 88.901 | 43.107
| 24.9583 | 327.688 | 417.683 | 89.449 | 31.673 | 89.022 | 43.102
| 24.9653 | 327.654 | 418.103 | 89.576 | 31.676 | 89.091 | 43.103
| 24.9722 | 328.833 | 419.139 | 89.718 | 31.691 | 89.187 | 43.109
| 24.9792 | 329.902 | 418.921 | 89.903 | 31.695 | 89.339 | 43.11
| 24.9861 | 329.361 | 420.223 | 90.063 | 31.722 | 89.471 | 43.118
| 24.9931 | 329.939 | 419.656 | 90.205 | 31.721 | 89.529 | 43.109
| 25 | 329.882 | 420.568 | 90.348 | 31.733 | 89.632 | 43.119
| 25.0069 | 330.588 | 420.278 | 90.493 | 31.743 | 89.723 | 43.125
| 25.0139 | 330.341 | 421.226 | 90.613 | 31.76 | 89.79 | 43.135
| 25.0208 | 318.938 | 414.039 | 90.29 | 31.771 | 89.378 | 43.141
| 25.0278 | 328.968 | 418.713 | 90.278 | 31.779 | 89.344 | 43.154
| 25.0347 | 329.107 | 419.588 | 90.415 | 31.783 | 89.523 | 43.154
| 25.0417 | 328.148 | 418.508 | 90.459 | 31.791 | 89.555 | 43.164
| 25.0486 | 328.683 | 418.198 | 90.511 | 31.795 | 89.585 | 43.161
| 25.0556 | 329.099 | 418.927 | 90.596 | 31.809 | 89.671 | 43.172
| 25.0625 | 329.584 | 418.199 | 90.666 | 31.832 | 89.725 | 43.184
| 25.0694 | 329.19 | 419.619 | 90.734 | 31.818 | 89.763 | 43.183
| 25.0764 | 329.291 | 418.651 | 90.782 | 31.836 | 89.785 | 43.189
| 25.0833 | 329.473 | 419.261 | 90.845 | 31.853 | 89.832 | 43.201
| 25.0903 | 329.724 | 418.414 | 90.907 | 31.853 | 89.876 | 43.204
| 25.0972 | 330.914 | 420.119 | 90.991 | 31.863 | 89.948 | 43.206
| 25.1042 | 331.144 | 420.235 | 91.083 | 31.866 | 90.038 | 43.213
| 25.1111 | 331.027 | 412.374 | 91.171 | 31.877 | 89.74 | 43.218
| 25.1181 | 330.036 | 413.486 | 91.223 | 31.886 | 89.382 | 43.228
| 25.125 | 331.083 | 412.823 | 91.299 | 31.895 | 89.248 | 43.231
| 25.1319 | 331.235 | 412.845 | 91.371 | 31.898 | 89.182 | 43.236
| 25.1389 | 321.229 | 408.799 | 91.435 | 31.909 | 89.148 | 43.235
| 25.1458 | 321.64 | 408.99 | 90.826 | 31.918 | 88.753 | 43.233
| 25.1528 | 320.984 | 410.026 | 90.501 | 31.921 | 88.601 | 43.233
| 25.1597 | 321.679 | 409.019 | 90.22 | 31.918 | 88.5 | 43.226
| 25.1667 | 321.97 | 409.775 | 89.999 | 31.908 | 88.447 | 43.219
| 25.1736 | 322.024 | 409.762 | 89.797 | 31.9 | 88.395 | 43.21
| 25.1806 | 321.217 | 418.523 | 89.5 | 31.888 | 88.62 | 43.202
| 25.1875 | 321.498 | 418.964 | 89.391 | 31.876 | 89.163 | 43.194
| 25.1944 | 321.985 | 418.988 | 89.258 | 31.87 | 89.403 | 43.184
| 25.2014 | 321.145 | 419.181 | 89.138 | 31.859 | 89.542 | 43.179
| 25.2083 | 321.408 | 419.257 | 89.03 | 31.853 | 89.63 | 43.174
| 25.2153 | 322.046 | 418.295 | 88.933 | 31.841 | 89.692 | 43.172
| 25.2222 | 321.639 | 418.305 | 88.834 | 31.833 | 89.719 | 43.175
| 25.2292 | 321.162 | 418.282 | 88.746 | 31.821 | 89.768 | 43.181
| 25.2361 | 320.692 | 418.984 | 88.649 | 31.818 | 89.771 | 43.185
| 25.2431 | 320.594 | 419.081 | 88.558 | 31.808 | 89.768 | 43.189
| 25.25 | 320.773 | 418.657 | 88.5 | 31.802 | 89.818 | 43.192
| 25.2569 | 321.021 | 418.966 | 88.447 | 31.794 | 89.867 | 43.202
| 25.2639 | 320.539 | 417.088 | 88.362 | 31.79 | 89.843 | 43.208
| 25.2708 | 320.422 | 416.507 | 88.253 | 31.781 | 89.773 | 43.209
| 25.2778 | 319.877 | 417.614 | 88.168 | 31.773 | 89.755 | 43.215
| 25.2847 | 320.299 | 416.813 | 88.089 | 31.767 | 89.746 | 43.225
| 25.2917 | 319.697 | 417.367 | 88.022 | 31.758 | 89.755 | 43.225
| 25.2986 | 319.401 | 417.531 | 87.939 | 31.751 | 89.725 | 43.228
| 25.3056 | 319.169 | 415.837 | 87.862 | 31.747 | 89.7 | 43.234
| 25.3125 | 319.808 | 416.057 | 87.777 | 31.739 | 89.658 | 43.24
| 25.3194 | 318.549 | 416.681 | 87.696 | 31.73 | 89.621 | 43.244
| 25.3264 | 324.086 | 415.96 | 87.964 | 31.721 | 89.586 | 43.245
| 25.3333 | 324.025 | 416.243 | 88.127 | 31.718 | 89.57 | 43.246
| 25.3403 | 327.048 | 418.355 | 88.279 | 31.718 | 89.591 | 43.247
| 25.3472 | 325.437 | 418.123 | 88.517 | 31.72 | 89.765 | 43.251
| 25.3542 | 326.179 | 417.427 | 88.658 | 31.722 | 89.79 | 43.245
| 25.3611 | 326.245 | 417.663 | 88.784 | 31.728 | 89.811 | 43.249
| 25.3681 | 326.182 | 417.328 | 88.888 | 31.734 | 89.803 | 43.251
| 25.375 | 324.845 | 417.428 | 88.977 | 31.741 | 89.801 | 43.253
| 25.3819 | 324.924 | 417.998 | 89.052 | 31.749 | 89.801 | 43.253
| 25.3889 | 324.832 | 416.783 | 89.087 | 31.755 | 89.75 | 43.255
| 25.3958 | 324.16 | 415.327 | 89.078 | 31.759 | 89.649 | 43.258
| 25.4028 | 327.994 | 420.281 | 89.307 | 31.765 | 89.948 | 43.258
| 25.4097 | 326.68 | 419.493 | 89.421 | 31.776 | 90.037 | 43.262
| 25.4167 | 329.217 | 412.073 | 89.701 | 31.78 | 89.742 | 43.263
| 25.4236 | 328.886 | 412.295 | 89.871 | 31.797 | 89.344 | 43.265
| 25.4306 | 328.815 | 411.51 | 90.008 | 31.802 | 89.13 | 43.267
| 25.4375 | 327.876 | 411.054 | 90.095 | 31.815 | 88.955 | 43.268
| 25.4444 | 327.732 | 410.462 | 90.149 | 31.826 | 88.807 | 43.259
| 25.4514 | 327.139 | 410.345 | 90.189 | 31.84 | 88.679 | 43.26
| 25.4583 | 326.621 | 408.982 | 90.227 | 31.848 | 88.595 | 43.249
| 25.4653 | 326.928 | 409.043 | 90.249 | 31.857 | 88.499 | 43.241
| 25.4722 | 326.728 | 408.03 | 90.232 | 31.865 | 88.383 | 43.229
| 25.4792 | 325.835 | 416.205 | 90.186 | 31.866 | 88.756 | 43.215
| 25.4861 | 325.764 | 416.702 | 90.143 | 31.872 | 89.009 | 43.207
| 25.4931 | 328.792 | 420.821 | 90.293 | 31.875 | 89.411 | 43.192
| 25.5 | 328.865 | 419.456 | 90.371 | 31.884 | 89.589 | 43.185
| 25.5069 | 328.991 | 419.184 | 90.459 | 31.894 | 89.73 | 43.179
| 25.5139 | 328.589 | 419.076 | 90.508 | 31.898 | 89.783 | 43.177
| 25.5208 | 327.915 | 418.374 | 90.541 | 31.907 | 89.838 | 43.176
| 25.5278 | 327.545 | 419.247 | 90.593 | 31.912 | 89.901 | 43.178
| 25.5347 | 328.349 | 418.496 | 90.611 | 31.917 | 89.913 | 43.18
| 25.5417 | 327.974 | 418.399 | 90.645 | 31.925 | 89.97 | 43.185
| 25.5486 | 327.843 | 419.643 | 90.691 | 31.93 | 90.015 | 43.186
| 25.5556 | 328.236 | 419.741 | 90.731 | 31.933 | 90.063 | 43.197
| 25.5625 | 329.025 | 419.675 | 90.79 | 31.939 | 90.142 | 43.199
| 25.5694 | 328.746 | 420.233 | 90.86 | 31.949 | 90.234 | 43.206
| 25.5764 | 329.069 | 420.672 | 90.922 | 31.953 | 90.294 | 43.211
| 25.5833 | 329.393 | 421.769 | 90.975 | 31.96 | 90.361 | 43.216
| 25.5903 | 330.413 | 420.977 | 91.058 | 31.968 | 90.452 | 43.228
| 25.5972 | 330.116 | 414.215 | 91.129 | 31.974 | 89.878 | 43.239
| 25.6042 | 329.71 | 414.076 | 91.233 | 31.983 | 89.716 | 43.244
| 25.6111 | 330.732 | 413.568 | 91.305 | 31.989 | 89.618 | 43.254
| 25.6181 | 320.711 | 408.828 | 91.315 | 32.002 | 89.564 | 43.256
| 25.625 | 320.654 | 409.245 | 90.723 | 32.002 | 89.126 | 43.256
| 25.6319 | 321.441 | 409.704 | 90.4 | 32.005 | 88.959 | 43.253
| 25.6389 | 321.071 | 409.702 | 90.133 | 32.001 | 88.876 | 43.248
| 25.6458 | 321.029 | 409.937 | 89.904 | 31.989 | 88.806 | 43.249
| 25.6528 | 321.232 | 410.362 | 89.712 | 31.981 | 88.772 | 43.238
| 25.6597 | 321.073 | 411.54 | 89.557 | 31.967 | 88.761 | 43.227
| 25.6667 | 320.827 | 411.109 | 89.412 | 31.958 | 88.727 | 43.219
| 25.6736 | 320.265 | 410.515 | 89.267 | 31.949 | 88.653 | 43.208
| 25.6806 | 320.946 | 409.413 | 89.129 | 31.937 | 88.588 | 43.201
| 25.6875 | 320.842 | 409.188 | 89.007 | 31.931 | 88.533 | 43.192
| 25.6944 | 320.681 | 410.509 | 88.883 | 31.92 | 88.461 | 43.183
| 25.7014 | 320.344 | 409.771 | 88.789 | 31.908 | 88.432 | 43.166
| 25.7083 | 320.352 | 408.442 | 88.67 | 31.898 | 88.353 | 43.159
| 25.7153 | 319.335 | 415.817 | 88.533 | 31.889 | 88.686 | 43.145
| 25.7222 | 325.307 | 414.313 | 88.457 | 31.883 | 88.877 | 43.135
| 25.7292 | 325.817 | 417.02 | 88.644 | 31.872 | 88.88 | 43.132
| 25.7361 | 323.322 | 413.856 | 88.769 | 31.864 | 88.951 | 43.119
| 25.7431 | 323.217 | 413.952 | 88.803 | 31.864 | 88.881 | 43.121
| 25.75 | 324.034 | 414.594 | 88.88 | 31.859 | 88.923 | 43.119
| 25.7569 | 324.391 | 414.372 | 88.951 | 31.864 | 88.95 | 43.115
| 25.7639 | 324.341 | 413.381 | 88.993 | 31.864 | 88.925 | 43.113
| 25.7708 | 323.077 | 413.81 | 88.982 | 31.862 | 88.846 | 43.114
| 25.7778 | 324.181 | 415.251 | 89.027 | 31.862 | 88.877 | 43.116
| 25.7847 | 324.718 | 414.379 | 89.082 | 31.862 | 88.931 | 43.111
| 25.7917 | 324.92 | 414.492 | 89.147 | 31.862 | 88.98 | 43.112
| 25.7986 | 324.917 | 414.319 | 89.199 | 31.869 | 89.017 | 43.113
| 25.8056 | 325.603 | 415.971 | 89.272 | 31.871 | 89.076 | 43.117
| 25.8125 | 325.215 | 415.471 | 89.345 | 31.871 | 89.146 | 43.109
| 25.8194 | 325.238 | 415.046 | 89.401 | 31.876 | 89.181 | 43.119
| 25.8264 | 326.775 | 417.377 | 89.513 | 31.879 | 89.287 | 43.122
| 25.8333 | 326.466 | 416.568 | 89.59 | 31.886 | 89.351 | 43.123
| 25.8403 | 327.172 | 416.995 | 89.685 | 31.889 | 89.433 | 43.124
| 25.8472 | 327.558 | 418.157 | 89.78 | 31.899 | 89.51 | 43.132
| 25.8542 | 327.335 | 418.575 | 89.897 | 31.905 | 89.615 | 43.133
| 25.8611 | 327.84 | 419.357 | 90.021 | 31.911 | 89.731 | 43.143
| 25.8681 | 327.976 | 418.933 | 90.118 | 31.919 | 89.794 | 43.15
| 25.875 | 328.569 | 420.196 | 90.246 | 31.926 | 89.911 | 43.161
| 25.8819 | 329.732 | 420.663 | 90.399 | 31.934 | 90.045 | 43.172
| 25.8889 | 330.385 | 420.944 | 90.539 | 31.946 | 90.151 | 43.182
| 25.8958 | 329.087 | 419.167 | 90.618 | 31.956 | 90.189 | 43.193
| 25.9028 | 328.938 | 419.742 | 90.676 | 31.967 | 90.196 | 43.202
| 25.9097 | 329.17 | 419.961 | 90.758 | 31.974 | 90.245 | 43.217
| 25.9167 | 328.834 | 420.462 | 90.829 | 31.987 | 90.299 | 43.231
| 25.9236 | 329.853 | 420.631 | 90.917 | 32 | 90.39 | 43.245
| 25.9306 | 329.292 | 413.781 | 90.99 | 32.006 | 90.394 | 43.256
| 25.9375 | 325.805 | 407.619 | 90.997 | 32.016 | 89.739 | 43.275
| 25.9444 | 325.98 | 415.947 | 90.852 | 32.028 | 89.853 | 43.284
| 25.9514 | 326.531 | 417.549 | 90.779 | 32.032 | 89.9 | 43.295
| 25.9583 | 326.814 | 417.025 | 90.733 | 32.034 | 89.99 | 43.308
| 25.9653 | 326.936 | 419.364 | 90.738 | 32.039 | 90.087 | 43.312
| 25.9722 | 327.809 | 419.451 | 90.756 | 32.045 | 90.175 | 43.319
| 25.9792 | 328.839 | 419.994 | 90.829 | 32.051 | 90.307 | 43.326
| 25.9861 | 329.131 | 420.991 | 90.894 | 32.052 | 90.425 | 43.333
| 25.9931 | 330.037 | 421.242 | 90.963 | 32.06 | 90.523 | 43.342
| 26 | 327.347 | 417.835 | 90.88 | 32.069 | 90.386 | 43.36
| 26.0069 | 326.862 | 419.013 | 90.854 | 32.071 | 90.363 | 43.364
| 26.0139 | 328.424 | 419.707 | 90.875 | 32.074 | 90.41 | 43.379
| 26.0208 | 327.85 | 419.639 | 90.92 | 32.084 | 90.508 | 43.39
| 26.0278 | 329.059 | 419.776 | 90.968 | 32.092 | 90.592 | 43.4
| 26.0347 | 328.571 | 421.152 | 91.034 | 32.095 | 90.685 | 43.412
| 26.0417 | 327.89 | 419.599 | 91.027 | 32.102 | 90.661 | 43.419
| 26.0486 | 328.454 | 420.273 | 91.053 | 32.107 | 90.691 | 43.434
| 26.0556 | 328.898 | 420.173 | 91.082 | 32.119 | 90.737 | 43.442
| 26.0625 | 329.068 | 419.588 | 91.149 | 32.121 | 90.824 | 43.453
| 26.0694 | 328.909 | 421.169 | 91.203 | 32.129 | 90.892 | 43.468
| 26.0764 | 329.285 | 419.737 | 91.255 | 32.138 | 90.949 | 43.479
| 26.0833 | 328.823 | 420.796 | 91.281 | 32.144 | 90.958 | 43.489
| 26.0903 | 328.875 | 420.536 | 91.309 | 32.155 | 90.985 | 43.504
| 26.0972 | 329.909 | 420.534 | 91.352 | 32.155 | 91.013 | 43.519
| 26.1042 | 329.227 | 414.582 | 91.403 | 32.162 | 90.676 | 43.525
| 26.1111 | 329.394 | 413.822 | 91.42 | 32.167 | 90.375 | 43.539
| 26.1181 | 328.303 | 414.192 | 91.442 | 32.176 | 90.23 | 43.553
| 26.125 | 328.741 | 414.618 | 91.455 | 32.182 | 90.132 | 43.559
| 26.1319 | 328.989 | 414.824 | 91.481 | 32.185 | 90.077 | 43.564
| 26.1389 | 329.574 | 413.701 | 91.498 | 32.191 | 90.045 | 43.568
| 26.1458 | 329.391 | 414.58 | 91.519 | 32.202 | 90.011 | 43.565
| 26.1528 | 329.73 | 414.071 | 91.533 | 32.205 | 90.001 | 43.571
| 26.1597 | 329.04 | 414.354 | 91.571 | 32.213 | 90.008 | 43.57
| 26.1667 | 329.268 | 413.574 | 91.57 | 32.216 | 89.958 | 43.572
| 26.1736 | 329.206 | 413.246 | 91.58 | 32.223 | 89.934 | 43.574
| 26.1806 | 328.848 | 413.886 | 91.59 | 32.228 | 89.908 | 43.571
| 26.1875 | 328.838 | 412.867 | 91.576 | 32.236 | 89.855 | 43.568
| 26.1944 | 328.284 | 413.857 | 91.549 | 32.241 | 89.796 | 43.567
| 26.2014 | 328.299 | 412.495 | 91.513 | 32.249 | 89.729 | 43.566
| 26.2083 | 327.989 | 412.191 | 91.484 | 32.25 | 89.681 | 43.565
| 26.2153 | 326.761 | 411.949 | 91.418 | 32.255 | 89.594 | 43.56
| 26.2222 | 325.631 | 409.609 | 91.326 | 32.255 | 89.472 | 43.562
| 26.2292 | 324.8 | 409.366 | 91.16 | 32.259 | 89.252 | 43.555
| 26.2361 | 325.264 | 415.256 | 91.04 | 32.265 | 89.245 | 43.554
| 26.2431 | 323.924 | 413.838 | 90.887 | 32.259 | 89.508 | 43.549
| 26.25 | 326.103 | 416.243 | 90.748 | 32.256 | 89.605 | 43.542
| 26.2569 | 324.124 | 415.388 | 90.693 | 32.254 | 89.756 | 43.539
| 26.2639 | 323.432 | 412.662 | 90.572 | 32.254 | 89.735 | 43.534
| 26.2708 | 325.236 | 415.257 | 90.563 | 32.25 | 89.861 | 43.534
| 26.2778 | 324.937 | 415.308 | 90.463 | 32.249 | 89.812 | 43.532
| 26.2847 | 324.817 | 414.186 | 90.416 | 32.246 | 89.843 | 43.532
| 26.2917 | 326.984 | 419.349 | 90.355 | 32.241 | 89.822 | 43.531
| 26.2986 | 326.507 | 418.457 | 90.478 | 32.24 | 90.108 | 43.535
| 26.3056 | 325.452 | 416.455 | 90.507 | 32.242 | 90.165 | 43.535
| 26.3125 | 325.434 | 415.87 | 90.454 | 32.24 | 90.095 | 43.537
| 26.3194 | 324.473 | 414.741 | 90.4 | 32.244 | 90.034 | 43.543
| 26.3264 | 327.675 | 419.101 | 90.338 | 32.245 | 89.985 | 43.556
| 26.3333 | 329.36 | 420.566 | 90.488 | 32.242 | 90.263 | 43.55
| 26.3403 | 329.243 | 413.419 | 90.706 | 32.241 | 90.093 | 43.557
| 26.3472 | 328.978 | 412.782 | 90.839 | 32.249 | 89.902 | 43.558
| 26.3542 | 330.085 | 414.574 | 91.01 | 32.254 | 89.908 | 43.567
| 26.3611 | 329.846 | 412.713 | 91.128 | 32.264 | 89.867 | 43.567
| 26.3681 | 329.401 | 414.046 | 91.25 | 32.271 | 89.866 | 43.572
| 26.375 | 327.928 | 412.391 | 91.321 | 32.281 | 89.817 | 43.576
| 26.3819 | 329.944 | 414.033 | 91.395 | 32.291 | 89.795 | 43.579
| 26.3889 | 330.636 | 413.659 | 91.489 | 32.298 | 89.836 | 43.576
| 26.3958 | 330.832 | 414.241 | 91.616 | 32.304 | 89.912 | 43.582
| 26.4028 | 329.789 | 413.807 | 91.68 | 32.315 | 89.902 | 43.582
| 26.4097 | 328.902 | 413.267 | 91.716 | 32.328 | 89.851 | 43.583
| 26.4167 | 328.851 | 412.147 | 91.695 | 32.333 | 89.748 | 43.582
| 26.4236 | 328.278 | 412.803 | 91.689 | 32.342 | 89.696 | 43.583
| 26.4306 | 328.864 | 412.849 | 91.698 | 32.345 | 89.667 | 43.583
| 26.4375 | 330.261 | 413.343 | 91.759 | 32.357 | 89.735 | 43.585
| 26.4444 | 330.789 | 414.556 | 91.85 | 32.358 | 89.835 | 43.583
| 26.4514 | 330.47 | 413.731 | 91.907 | 32.364 | 89.882 | 43.579
| 26.4583 | 330.216 | 413.328 | 91.927 | 32.371 | 89.853 | 43.586
| 26.4653 | 329.741 | 414.009 | 91.978 | 32.379 | 89.875 | 43.584
| 26.4722 | 330.013 | 415.13 | 92.036 | 32.39 | 89.916 | 43.588
| 26.4792 | 330.825 | 414.656 | 92.108 | 32.394 | 89.968 | 43.594
| 26.4861 | 324.023 | 413.809 | 91.874 | 32.403 | 89.979 | 43.588
| 26.4931 | 323.803 | 414.984 | 91.631 | 32.411 | 89.968 | 43.589
| 26.5 | 323.312 | 414.243 | 91.448 | 32.415 | 89.965 | 43.589
| 26.5069 | 323.443 | 413.015 | 91.252 | 32.414 | 89.92 | 43.593
| 26.5139 | 324.393 | 414.894 | 91.077 | 32.408 | 89.883 | 43.592
| 26.5208 | 321.384 | 410.883 | 90.954 | 32.407 | 89.924 | 43.599
| 26.5278 | 320.473 | 410.339 | 90.657 | 32.402 | 89.645 | 43.596
| 26.5347 | 321.315 | 409.429 | 90.423 | 32.391 | 89.498 | 43.602
| 26.5417 | 321.019 | 409.591 | 90.206 | 32.387 | 89.396 | 43.6
| 26.5486 | 320.517 | 408.566 | 90.002 | 32.374 | 89.303 | 43.598
| 26.5556 | 320.159 | 415.924 | 89.799 | 32.367 | 89.596 | 43.6
| 26.5625 | 320.268 | 415.35 | 89.655 | 32.351 | 89.924 | 43.597
| 26.5694 | 320.76 | 417.837 | 89.534 | 32.336 | 90.109 | 43.59
| 26.5764 | 320.733 | 418.239 | 89.433 | 32.329 | 90.238 | 43.59
| 26.5833 | 320.905 | 416.759 | 89.345 | 32.319 | 90.328 | 43.59
| 26.5903 | 321.871 | 418.292 | 89.296 | 32.309 | 90.444 | 43.592
| 26.5972 | 322.504 | 418.325 | 89.281 | 32.297 | 90.579 | 43.597
| 26.6042 | 322.1 | 418.173 | 89.269 | 32.29 | 90.703 | 43.603
| 26.6111 | 323.033 | 419.165 | 89.279 | 32.29 | 90.809 | 43.609
| 26.6181 | 322.694 | 419.516 | 89.272 | 32.279 | 90.877 | 43.621
| 26.625 | 322.259 | 419.198 | 89.279 | 32.276 | 90.972 | 43.626
| 26.6319 | 322.323 | 420.155 | 89.283 | 32.271 | 91.024 | 43.64
| 26.6389 | 322.556 | 420.014 | 89.296 | 32.267 | 91.091 | 43.653
| 26.6458 | 322.162 | 418.346 | 89.279 | 32.264 | 91.111 | 43.667
| 26.6528 | 323.23 | 419.155 | 89.272 | 32.264 | 91.143 | 43.677
| 26.6597 | 322.439 | 419.429 | 89.274 | 32.263 | 91.2 | 43.689
| 26.6667 | 321.876 | 419.705 | 89.264 | 32.259 | 91.231 | 43.703
| 26.6736 | 322.215 | 419.759 | 89.261 | 32.258 | 91.261 | 43.715
| 26.6806 | 322.07 | 418.256 | 89.267 | 32.258 | 91.31 | 43.725
| 26.6875 | 322.311 | 419.476 | 89.256 | 32.252 | 91.34 | 43.74
| 26.6944 | 323.191 | 419.413 | 89.285 | 32.248 | 91.42 | 43.753
| 26.7014 | 323.42 | 421.455 | 89.325 | 32.249 | 91.509 | 43.764
| 26.7083 | 323.269 | 420.846 | 89.374 | 32.25 | 91.596 | 43.775
| 26.7153 | 322.92 | 418.865 | 89.382 | 32.252 | 91.611 | 43.79
| 26.7222 | 322.346 | 418.193 | 89.344 | 32.247 | 91.564 | 43.801
| 26.7292 | 321.576 | 419.302 | 89.322 | 32.248 | 91.542 | 43.812
| 26.7361 | 319.394 | 415.653 | 89.167 | 32.246 | 91.351 | 43.83
| 26.7431 | 324.818 | 413.948 | 89.177 | 32.245 | 91.161 | 43.839
| 26.75 | 328.723 | 420.767 | 89.51 | 32.241 | 91.318 | 43.844
| 26.7569 | 326.202 | 413.198 | 89.812 | 32.246 | 91.521 | 43.854
| 26.7639 | 321.043 | 409.534 | 89.637 | 32.252 | 90.837 | 43.865
| 26.7708 | 321.953 | 410.418 | 89.537 | 32.258 | 90.497 | 43.867
| 26.7778 | 322.134 | 408.698 | 89.467 | 32.26 | 90.313 | 43.875
| 26.7847 | 320.941 | 409.361 | 89.41 | 32.257 | 90.191 | 43.881
| 26.7917 | 322.743 | 409.594 | 89.391 | 32.253 | 90.16 | 43.873
| 26.7986 | 323.781 | 411.204 | 89.391 | 32.256 | 90.148 | 43.871
| 26.8056 | 322.956 | 409.987 | 89.444 | 32.256 | 90.195 | 43.868
| 26.8125 | 322.181 | 409.112 | 89.369 | 32.254 | 90.048 | 43.861
| 26.8194 | 321.678 | 409.617 | 89.294 | 32.254 | 89.916 | 43.85
| 26.8264 | 322.74 | 409.917 | 89.273 | 32.248 | 89.886 | 43.848
| 26.8333 | 322.536 | 411.169 | 89.289 | 32.248 | 89.906 | 43.839
| 26.8403 | 323.108 | 410.575 | 89.31 | 32.245 | 89.928 | 43.834
| 26.8472 | 323.853 | 412.965 | 89.353 | 32.253 | 89.98 | 43.819
| 26.8542 | 324.828 | 414.322 | 89.473 | 32.251 | 90.141 | 43.813
| 26.8611 | 322.992 | 412.201 | 89.507 | 32.253 | 90.134 | 43.807
| 26.8681 | 322.633 | 411.751 | 89.483 | 32.256 | 90.027 | 43.805
| 26.875 | 322.916 | 411.957 | 89.498 | 32.256 | 90.005 | 43.796
| 26.8819 | 324.594 | 412.131 | 89.542 | 32.258 | 90.029 | 43.787
| 26.8889 | 325.06 | 414.485 | 89.608 | 32.263 | 90.099 | 43.785
| 26.8958 | 324.784 | 412.149 | 89.67 | 32.267 | 90.143 | 43.782
| 26.9028 | 324.755 | 413.801 | 89.714 | 32.269 | 90.14 | 43.78
| 26.9097 | 320.76 | 409.174 | 89.614 | 32.271 | 89.924 | 43.777
| 26.9167 | 321.285 | 415.504 | 89.467 | 32.272 | 89.928 | 43.768
| 26.9236 | 321.248 | 417.919 | 89.4 | 32.272 | 90.337 | 43.765
| 26.9306 | 322.835 | 418.052 | 89.316 | 32.269 | 90.486 | 43.765
| 26.9375 | 323.051 | 418.363 | 89.371 | 32.27 | 90.764 | 43.762
| 26.9444 | 322.457 | 419.226 | 89.343 | 32.27 | 90.845 | 43.765
| 26.9514 | 323.331 | 420.116 | 89.35 | 32.273 | 90.937 | 43.766
| 26.9583 | 323.956 | 420.334 | 89.398 | 32.265 | 91.089 | 43.767
| 26.9653 | 324.644 | 420.661 | 89.459 | 32.27 | 91.204 | 43.774
| 26.9722 | 322.271 | 418.255 | 89.372 | 32.272 | 91.083 | 43.781
| 26.9792 | 323.252 | 419.799 | 89.392 | 32.277 | 91.165 | 43.791
| 26.9861 | 323.671 | 418.965 | 89.408 | 32.271 | 91.223 | 43.801
| 26.9931 | 323.804 | 420.322 | 89.423 | 32.274 | 91.267 | 43.802
| 27 | 322.687 | 419.603 | 89.437 | 32.276 | 91.305 | 43.817
| 27.0069 | 323.578 | 419.114 | 89.432 | 32.271 | 91.312 | 43.821
| 27.0139 | 324.7 | 420.99 | 89.44 | 32.275 | 91.346 | 43.834
| 27.0208 | 321.903 | 417.268 | 89.38 | 32.272 | 90.931 | 43.842
| 27.0278 | 321.126 | 417.523 | 89.306 | 32.28 | 91.03 | 43.852
| 27.0347 | 321.664 | 417.254 | 89.239 | 32.272 | 91.065 | 43.855
| 27.0417 | 319.824 | 416.284 | 89.137 | 32.272 | 90.998 | 43.866
| 27.0486 | 320.992 | 415.985 | 89.023 | 32.266 | 90.925 | 43.865
| 27.0556 | 320.586 | 417.59 | 88.941 | 32.265 | 90.907 | 43.871
| 27.0625 | 321.25 | 417.676 | 88.927 | 32.26 | 90.978 | 43.872
| 27.0694 | 321.345 | 417.202 | 88.906 | 32.257 | 91.016 | 43.878
| 27.0764 | 321.742 | 416.717 | 88.886 | 32.255 | 91.057 | 43.877
| 27.0833 | 321.299 | 416.942 | 88.848 | 32.249 | 91.032 | 43.879
| 27.0903 | 320.529 | 417.332 | 88.8 | 32.243 | 90.997 | 43.884
| 27.0972 | 321.584 | 417.753 | 88.771 | 32.243 | 91.006 | 43.885
| 27.1042 | 322.351 | 417.802 | 88.798 | 32.241 | 91.09 | 43.892
| 27.1111 | 322.242 | 418.597 | 88.807 | 32.237 | 91.124 | 43.892
| 27.1181 | 322.415 | 418.698 | 88.841 | 32.235 | 91.192 | 43.889
| 27.125 | 321.922 | 419.16 | 88.857 | 32.232 | 91.22 | 43.891
| 27.1319 | 322.623 | 418.551 | 88.863 | 32.237 | 91.23 | 43.896
| 27.1389 | 322.123 | 418.927 | 88.89 | 32.236 | 91.275 | 43.895
| 27.1458 | 322.645 | 418.656 | 88.9 | 32.232 | 91.292 | 43.905
| 27.1528 | 322.173 | 419.18 | 88.917 | 32.233 | 91.323 | 43.907
| 27.1597 | 322.621 | 419.822 | 88.965 | 32.232 | 91.395 | 43.909
| 27.1667 | 322.936 | 418.728 | 88.998 | 32.236 | 91.437 | 43.913
| 27.1736 | 322.451 | 419.606 | 89.013 | 32.236 | 91.466 | 43.916
| 27.1806 | 322.204 | 419.086 | 89.046 | 32.239 | 91.496 | 43.923
| 27.1875 | 322.884 | 418.336 | 89.041 | 32.237 | 91.496 | 43.925
| 27.1944 | 322.514 | 418.893 | 89.042 | 32.238 | 91.51 | 43.932
| 27.2014 | 322.832 | 418.764 | 89.056 | 32.242 | 91.542 | 43.938
| 27.2083 | 321.909 | 418.554 | 89.039 | 32.241 | 91.523 | 43.943
| 27.2153 | 321.725 | 418.663 | 89.012 | 32.24 | 91.492 | 43.949
| 27.2222 | 321.571 | 416.679 | 88.968 | 32.236 | 91.443 | 43.957
| 27.2292 | 321.029 | 415.937 | 88.876 | 32.234 | 91.328 | 43.957
| 27.2361 | 319.322 | 413.741 | 88.769 | 32.236 | 91.204 | 43.962
| 27.2431 | 325.715 | 414.637 | 88.671 | 32.23 | 91.079 | 43.966
| 27.25 | 324.111 | 414.483 | 88.928 | 32.223 | 90.942 | 43.968
| 27.2569 | 328.084 | 417.99 | 89.156 | 32.227 | 91.012 | 43.966
| 27.2639 | 325.153 | 415.788 | 89.368 | 32.234 | 91.114 | 43.965
| 27.2708 | 327.872 | 418.416 | 89.549 | 32.242 | 91.154 | 43.967
| 27.2778 | 328.564 | 417.997 | 89.765 | 32.25 | 91.264 | 43.96
| 27.2847 | 327.249 | 416.991 | 89.916 | 32.26 | 91.272 | 43.958
| 27.2917 | 326.68 | 415.509 | 89.991 | 32.272 | 91.182 | 43.963
| 27.2986 | 325.136 | 415.872 | 90.025 | 32.282 | 91.077 | 43.962
| 27.3056 | 325.106 | 413.432 | 90.004 | 32.287 | 90.924 | 43.961
| 27.3125 | 326.44 | 415.782 | 90.009 | 32.296 | 90.864 | 43.963
| 27.3194 | 325.18 | 413.964 | 90.031 | 32.303 | 90.845 | 43.964
| 27.3264 | 328.192 | 418.117 | 90.194 | 32.306 | 91.053 | 43.961
| 27.3333 | 327.801 | 419.1 | 90.322 | 32.31 | 91.179 | 43.959
| 27.3403 | 330.202 | 412.503 | 90.566 | 32.322 | 91.294 | 43.951
| 27.3472 | 323.725 | 413.238 | 90.512 | 32.329 | 90.901 | 43.954
| 27.3542 | 324.762 | 412.825 | 90.417 | 32.342 | 90.726 | 43.95
| 27.3611 | 324.161 | 413.383 | 90.339 | 32.346 | 90.611 | 43.952
| 27.3681 | 324.855 | 412.283 | 90.287 | 32.348 | 90.543 | 43.949
| 27.375 | 324.178 | 413.567 | 90.246 | 32.352 | 90.5 | 43.952
| 27.3819 | 323.121 | 412.031 | 90.147 | 32.354 | 90.375 | 43.943
| 27.3889 | 324.543 | 412.708 | 90.116 | 32.356 | 90.362 | 43.94
| 27.3958 | 320.697 | 417.669 | 89.932 | 32.357 | 90.443 | 43.936
| 27.4028 | 320.651 | 415.258 | 89.719 | 32.355 | 90.648 | 43.929
| 27.4097 | 319.748 | 415.407 | 89.528 | 32.351 | 90.689 | 43.918
| 27.4167 | 319.75 | 416.251 | 89.356 | 32.343 | 90.705 | 43.919
| 27.4236 | 318.422 | 414.379 | 89.184 | 32.334 | 90.685 | 43.912
| 27.4306 | 325.397 | 415.271 | 89.385 | 32.328 | 90.636 | 43.913
| 27.4375 | 324.96 | 413.068 | 89.489 | 32.326 | 90.632 | 43.905
| 27.4444 | 324.915 | 413.171 | 89.57 | 32.327 | 90.614 | 43.908
| 27.4514 | 324.93 | 415.005 | 89.658 | 32.327 | 90.641 | 43.902
| 27.4583 | 328.025 | 417.322 | 89.826 | 32.329 | 90.806 | 43.898
| 27.4653 | 327.981 | 417.661 | 90.042 | 32.335 | 91.03 | 43.898
| 27.4722 | 327.395 | 417.294 | 90.185 | 32.344 | 91.107 | 43.901
| 27.4792 | 326.327 | 416.528 | 90.259 | 32.351 | 91.077 | 43.895
| 27.4861 | 326.79 | 415.383 | 90.308 | 32.363 | 91.037 | 43.898
| 27.4931 | 325.821 | 415.588 | 90.342 | 32.364 | 91.003 | 43.904
| 27.5 | 325.883 | 416.522 | 90.364 | 32.379 | 90.964 | 43.906
| 27.5069 | 327.632 | 416.807 | 90.446 | 32.382 | 91.036 | 43.909
| 27.5139 | 328.127 | 419.23 | 90.531 | 32.386 | 91.113 | 43.912
| 27.5208 | 329.411 | 419.134 | 90.689 | 32.393 | 91.318 | 43.917
| 27.5278 | 327.823 | 419.378 | 90.838 | 32.399 | 91.465 | 43.915
| 27.5347 | 329.155 | 420.109 | 90.943 | 32.409 | 91.53 | 43.922
| 27.5417 | 328.977 | 420.175 | 91.053 | 32.421 | 91.609 | 43.932
| 27.5486 | 328.087 | 418.854 | 91.144 | 32.43 | 91.646 | 43.935
| 27.5556 | 328.51 | 419.221 | 91.213 | 32.441 | 91.654 | 43.944
| 27.5625 | 328.511 | 418.033 | 91.246 | 32.446 | 91.634 | 43.95
| 27.5694 | 328.546 | 418.181 | 91.252 | 32.457 | 91.589 | 43.963
| 27.5764 | 327.738 | 419.166 | 91.291 | 32.468 | 91.604 | 43.967
| 27.5833 | 328.837 | 420.031 | 91.364 | 32.473 | 91.687 | 43.975
| 27.5903 | 330.119 | 419.986 | 91.438 | 32.474 | 91.767 | 43.984
| 27.5972 | 329.027 | 419.482 | 91.505 | 32.49 | 91.829 | 43.989
| 27.6042 | 328.859 | 419.213 | 91.54 | 32.494 | 91.83 | 44.001
| 27.6111 | 328.695 | 420.443 | 91.568 | 32.501 | 91.836 | 44.011
| 27.6181 | 328.546 | 419.543 | 91.62 | 32.511 | 91.89 | 44.018
| 27.625 | 330.178 | 420.233 | 91.708 | 32.52 | 91.984 | 44.027
| 27.6319 | 330.484 | 412.937 | 91.797 | 32.523 | 91.727 | 44.033
| 27.6389 | 330.157 | 413.055 | 91.849 | 32.532 | 91.372 | 44.044
| 27.6458 | 330.316 | 413.73 | 91.931 | 32.54 | 91.251 | 44.048
| 27.6528 | 329.718 | 412.663 | 91.971 | 32.545 | 91.139 | 44.055
| 27.6597 | 329.886 | 413.673 | 92.016 | 32.557 | 91.076 | 44.059
| 27.6667 | 330.152 | 414.317 | 92.082 | 32.562 | 91.069 | 44.055
| 27.6736 | 330.593 | 413.323 | 92.129 | 32.574 | 91.037 | 44.063
| 27.6806 | 331.242 | 414.433 | 92.192 | 32.581 | 91.048 | 44.057
| 27.6875 | 330.021 | 414.487 | 92.235 | 32.588 | 91.021 | 44.05
| 27.6944 | 330.567 | 415.054 | 92.3 | 32.6 | 91.051 | 44.054
| 27.7014 | 330.727 | 413.968 | 92.361 | 32.599 | 91.067 | 44.051
| 27.7083 | 320.313 | 409.81 | 92.172 | 32.617 | 91.006 | 44.053
| 27.7153 | 320.501 | 410.213 | 91.665 | 32.622 | 90.62 | 44.046
| 27.7222 | 319.222 | 415.346 | 91.243 | 32.621 | 90.789 | 44.05
| 27.7292 | 317.412 | 413.941 | 90.831 | 32.621 | 90.839 | 44.043
| 27.7361 | 327.502 | 416.605 | 91.051 | 32.607 | 91.053 | 44.04
| 27.7431 | 328.426 | 418.125 | 91.066 | 32.605 | 91.136 | 44.038
| 27.75 | 328.587 | 418.205 | 91.161 | 32.596 | 91.305 | 44.034
| 27.7569 | 328.649 | 419.541 | 91.256 | 32.602 | 91.443 | 44.029
| 27.7639 | 330.83 | 414.799 | 91.47 | 32.604 | 91.251 | 44.032
| 27.7708 | 321.009 | 409.995 | 91.273 | 32.609 | 90.851 | 44.038
| 27.7778 | 321.147 | 408.598 | 90.935 | 32.618 | 90.479 | 44.046
| 27.7847 | 321.537 | 408.562 | 90.709 | 32.62 | 90.303 | 44.043
| 27.7917 | 321.286 | 417.874 | 90.501 | 32.602 | 90.267 | 44.043
| 27.7986 | 322.173 | 417.134 | 90.34 | 32.597 | 90.749 | 44.032
| 27.8056 | 322.178 | 417.681 | 90.214 | 32.592 | 90.984 | 44.033
| 27.8125 | 321.629 | 417.49 | 90.111 | 32.58 | 91.115 | 44.029
| 27.8194 | 321.925 | 418.672 | 90.02 | 32.571 | 91.21 | 44.03
| 27.8264 | 323.11 | 418.388 | 89.956 | 32.565 | 91.3 | 44.026
| 27.8333 | 322.5 | 419.019 | 89.936 | 32.556 | 91.416 | 44.034
| 27.8403 | 324.168 | 420.077 | 89.948 | 32.553 | 91.549 | 44.032
| 27.8472 | 326.041 | 421.948 | 90.005 | 32.554 | 91.748 | 44.044
| 27.8542 | 321.858 | 415.756 | 89.924 | 32.55 | 91.264 | 44.049
| 27.8611 | 321.895 | 415.494 | 89.775 | 32.543 | 91.266 | 44.062
| 27.8681 | 321.2 | 416.574 | 89.681 | 32.543 | 91.276 | 44.06
| 27.875 | 322.603 | 417.733 | 89.659 | 32.533 | 91.371 | 44.068
| 27.8819 | 320.77 | 415.916 | 89.673 | 32.532 | 91.511 | 44.076
| 27.8889 | 319.565 | 415.014 | 89.456 | 32.525 | 91.227 | 44.086
| 27.8958 | 323.967 | 412.95 | 89.313 | 32.519 | 91.058 | 44.094
| 27.9028 | 325.072 | 414.024 | 89.521 | 32.517 | 90.959 | 44.102
| 27.9097 | 325.558 | 414.98 | 89.655 | 32.513 | 90.961 | 44.103
| 27.9167 | 326.072 | 414.842 | 89.802 | 32.508 | 91.008 | 44.104
| 27.9236 | 327.126 | 416.108 | 89.951 | 32.515 | 91.076 | 44.109
| 27.9306 | 326.934 | 417.698 | 90.097 | 32.522 | 91.139 | 44.109
| 27.9375 | 327.714 | 417.327 | 90.26 | 32.523 | 91.252 | 44.108
| 27.9444 | 327.683 | 418.355 | 90.439 | 32.534 | 91.362 | 44.114
| 27.9514 | 328.598 | 419.485 | 90.617 | 32.54 | 91.473 | 44.119
| 27.9583 | 329.915 | 420.38 | 90.835 | 32.55 | 91.666 | 44.122
| 27.9653 | 330.371 | 412.004 | 91.034 | 32.557 | 91.728 | 44.128
| 27.9722 | 327.324 | 418.362 | 91.032 | 32.567 | 91.364 | 44.14
| 27.9792 | 325.348 | 413.854 | 90.995 | 32.579 | 91.319 | 44.138
| 27.9861 | 325.937 | 415.455 | 90.96 | 32.59 | 91.23 | 44.15
| 27.9931 | 326.194 | 414.633 | 90.941 | 32.597 | 91.212 | 44.155
| 28 | 326.048 | 414.476 | 90.9 | 32.602 | 91.154 | 44.158
| 28.0069 | 325.289 | 415.06 | 90.876 | 32.605 | 91.128 | 44.169
| 28.0139 | 326.378 | 415.442 | 90.855 | 32.607 | 91.127 | 44.168
| 28.0208 | 326.367 | 415.628 | 90.871 | 32.617 | 91.181 | 44.174
| 28.0278 | 326.607 | 415.737 | 90.909 | 32.618 | 91.243 | 44.175
| 28.0347 | 324.793 | 414.694 | 90.921 | 32.621 | 91.249 | 44.172
| 28.0417 | 324.391 | 412.955 | 90.779 | 32.629 | 91.029 | 44.178
| 28.0486 | 327.429 | 418.088 | 90.792 | 32.628 | 91.069 | 44.181
| 28.0556 | 328.237 | 417.852 | 90.905 | 32.629 | 91.282 | 44.183
| 28.0625 | 328.042 | 417.561 | 91.023 | 32.634 | 91.428 | 44.19
| 28.0694 | 326.945 | 417.659 | 91.087 | 32.643 | 91.464 | 44.19
| 28.0764 | 327.226 | 416.949 | 91.12 | 32.647 | 91.473 | 44.196
| 28.0833 | 327.381 | 417.512 | 91.161 | 32.658 | 91.485 | 44.201
| 28.0903 | 328.489 | 417.895 | 91.245 | 32.659 | 91.572 | 44.201
| 28.0972 | 329.139 | 418.507 | 91.32 | 32.666 | 91.649 | 44.21
| 28.1042 | 328.221 | 418.317 | 91.403 | 32.678 | 91.72 | 44.217
| 28.1111 | 328.493 | 418.742 | 91.481 | 32.679 | 91.794 | 44.227
| 28.1181 | 328.486 | 418.662 | 91.554 | 32.694 | 91.86 | 44.234
| 28.125 | 328.645 | 417.945 | 91.6 | 32.702 | 91.887 | 44.24
| 28.1319 | 327.951 | 418.7 | 91.653 | 32.704 | 91.924 | 44.249
| 28.1389 | 328.754 | 418.45 | 91.714 | 32.708 | 91.97 | 44.258
| 28.1458 | 328.281 | 419.26 | 91.785 | 32.717 | 92.064 | 44.265
| 28.1528 | 329.017 | 418.253 | 91.831 | 32.733 | 92.105 | 44.286
| 28.1597 | 327.722 | 417.485 | 91.845 | 32.733 | 92.082 | 44.287
| 28.1667 | 327.482 | 418.412 | 91.851 | 32.744 | 92.059 | 44.302
| 28.1736 | 327.579 | 417.482 | 91.87 | 32.742 | 92.069 | 44.306
| 28.1806 | 328.148 | 417.096 | 91.857 | 32.76 | 92.054 | 44.32
| 28.1875 | 327.532 | 418.347 | 91.871 | 32.769 | 92.084 | 44.334
| 28.1944 | 328.725 | 417.936 | 91.897 | 32.763 | 92.113 | 44.339
| 28.2014 | 327.978 | 418.641 | 91.905 | 32.772 | 92.137 | 44.353
| 28.2083 | 327.683 | 417.938 | 91.915 | 32.78 | 92.155 | 44.359
| 28.2153 | 327.788 | 418.233 | 91.921 | 32.786 | 92.154 | 44.367
| 28.2222 | 327.014 | 416.427 | 91.906 | 32.79 | 92.138 | 44.377
| 28.2292 | 326.358 | 415.306 | 91.803 | 32.797 | 92.017 | 44.379
| 28.2361 | 324.635 | 413.245 | 91.691 | 32.802 | 91.866 | 44.392
| 28.2431 | 324.364 | 412.098 | 91.524 | 32.802 | 91.658 | 44.399
| 28.25 | 328.17 | 417.206 | 91.59 | 32.806 | 91.861 | 44.408
| 28.2569 | 327.323 | 418.009 | 91.61 | 32.804 | 91.952 | 44.409
| 28.2639 | 328.791 | 412.382 | 91.822 | 32.801 | 92.059 | 44.417
| 28.2708 | 325.603 | 409.589 | 91.752 | 32.81 | 91.544 | 44.419
| 28.2778 | 329.43 | 418.776 | 91.743 | 32.814 | 91.654 | 44.42
| 28.2847 | 329.402 | 419.805 | 91.887 | 32.82 | 92.034 | 44.425
| 28.2917 | 328.816 | 419.671 | 91.984 | 32.819 | 92.214 | 44.432
| 28.2986 | 328.782 | 418.038 | 92.026 | 32.83 | 92.254 | 44.432
| 28.3056 | 326.848 | 416.218 | 92.011 | 32.837 | 92.189 | 44.441
| 28.3125 | 326.118 | 414.324 | 91.908 | 32.843 | 92.047 | 44.45
| 28.3194 | 328.811 | 419.52 | 91.774 | 32.848 | 91.859 | 44.45
| 28.3264 | 329.574 | 420.275 | 91.964 | 32.852 | 92.215 | 44.454
| 28.3333 | 328.97 | 419.539 | 92.075 | 32.852 | 92.399 | 44.458
| 28.3403 | 330.949 | 420.637 | 92.182 | 32.859 | 92.532 | 44.47
| 28.3472 | 321.008 | 416.673 | 91.849 | 32.863 | 92.016 | 44.477
| 28.3542 | 319.748 | 415.47 | 91.455 | 32.865 | 92.106 | 44.486
| 28.3611 | 319.736 | 415.567 | 91.156 | 32.861 | 92.107 | 44.49
| 28.3681 | 320.502 | 415.698 | 90.905 | 32.861 | 92.11 | 44.498
| 28.375 | 319.903 | 415.328 | 90.671 | 32.852 | 92.103 | 44.505
| 28.3819 | 320.025 | 416.861 | 90.489 | 32.849 | 92.139 | 44.51
| 28.3889 | 320.217 | 416.95 | 90.318 | 32.837 | 92.152 | 44.52
| 28.3958 | 319.268 | 414.579 | 90.146 | 32.827 | 92.123 | 44.521
| 28.4028 | 326.003 | 417.028 | 90.363 | 32.816 | 92.134 | 44.522
| 28.4097 | 325.097 | 414.732 | 90.453 | 32.81 | 92.095 | 44.532
| 28.4167 | 324.153 | 414.063 | 90.457 | 32.811 | 91.964 | 44.537
| 28.4236 | 323.411 | 413.121 | 90.464 | 32.81 | 91.873 | 44.534
| 28.4306 | 323.929 | 412.769 | 90.45 | 32.808 | 91.797 | 44.54
| 28.4375 | 327.387 | 418.445 | 90.614 | 32.805 | 92.018 | 44.533
| 28.4444 | 326.786 | 418.164 | 90.786 | 32.809 | 92.21 | 44.543
| 28.4514 | 326.966 | 417.258 | 90.899 | 32.81 | 92.277 | 44.539
| 28.4583 | 326.413 | 416.488 | 90.965 | 32.817 | 92.262 | 44.546
| 28.4653 | 327.615 | 419.102 | 91.062 | 32.821 | 92.314 | 44.55
| 28.4722 | 326.98 | 416.758 | 91.157 | 32.819 | 92.381 | 44.552
| 28.4792 | 327.819 | 418.116 | 91.238 | 32.829 | 92.431 | 44.558
| 28.4861 | 327 | 417.161 | 91.313 | 32.839 | 92.475 | 44.562
| 28.4931 | 326.845 | 417.271 | 91.37 | 32.845 | 92.477 | 44.563
| 28.5 | 326.782 | 415.828 | 91.392 | 32.847 | 92.457 | 44.576
| 28.5069 | 327.09 | 417.445 | 91.416 | 32.85 | 92.441 | 44.585
| 28.5139 | 328.032 | 417.774 | 91.487 | 32.855 | 92.516 | 44.586
| 28.5208 | 327.955 | 419.755 | 91.584 | 32.862 | 92.642 | 44.596
| 28.5278 | 327.848 | 419.164 | 91.662 | 32.87 | 92.726 | 44.602
| 28.5347 | 328.768 | 419.197 | 91.746 | 32.873 | 92.785 | 44.606
| 28.5417 | 327.786 | 419.093 | 91.845 | 32.877 | 92.887 | 44.617
| 28.5486 | 328.467 | 418.629 | 91.886 | 32.888 | 92.884 | 44.624
| 28.5556 | 327.039 | 416.509 | 91.895 | 32.897 | 92.847 | 44.633
| 28.5625 | 327.611 | 417.342 | 91.888 | 32.9 | 92.804 | 44.64
| 28.5694 | 327.27 | 416.87 | 91.863 | 32.908 | 92.753 | 44.649
| 28.5764 | 328.088 | 418.706 | 91.895 | 32.914 | 92.797 | 44.658
| 28.5833 | 327.638 | 419.111 | 91.946 | 32.92 | 92.886 | 44.663
| 28.5903 | 327.789 | 419.229 | 91.995 | 32.922 | 92.945 | 44.67
| 28.5972 | 328.358 | 418.057 | 92.02 | 32.929 | 92.953 | 44.68
| 28.6042 | 329.203 | 419.868 | 92.099 | 32.936 | 93.056 | 44.686
| 28.6111 | 329.035 | 421.023 | 92.183 | 32.94 | 93.151 | 44.696
| 28.6181 | 328.717 | 419.91 | 92.243 | 32.945 | 93.197 | 44.702
| 28.625 | 327.96 | 419.309 | 92.253 | 32.953 | 93.169 | 44.714
| 28.6319 | 328.591 | 419.269 | 92.282 | 32.96 | 93.193 | 44.721
| 28.6389 | 328.647 | 419.785 | 92.307 | 32.963 | 93.201 | 44.73
| 28.6458 | 327.468 | 418.664 | 92.348 | 32.969 | 93.242 | 44.736
| 28.6528 | 327.147 | 417.424 | 92.278 | 32.975 | 93.117 | 44.747
| 28.6597 | 325.845 | 416.66 | 92.208 | 32.983 | 93.015 | 44.753
| 28.6667 | 326.68 | 416.166 | 92.129 | 32.989 | 92.932 | 44.765
| 28.6736 | 325.948 | 417.006 | 92.097 | 32.989 | 92.925 | 44.772
| 28.6806 | 326.465 | 417.776 | 92.083 | 32.991 | 92.951 | 44.777
| 28.6875 | 327.269 | 418.506 | 92.078 | 32.991 | 92.985 | 44.784
| 28.6944 | 327.044 | 418.003 | 92.082 | 32.991 | 93.026 | 44.781
| 28.7014 | 328.204 | 418.567 | 92.129 | 32.991 | 93.108 | 44.786
| 28.7083 | 328.565 | 418.885 | 92.166 | 32.998 | 93.169 | 44.795
| 28.7153 | 328.511 | 418.361 | 92.207 | 33.003 | 93.215 | 44.796
| 28.7222 | 327.404 | 418.61 | 92.196 | 33.007 | 93.179 | 44.804
| 28.7292 | 325.645 | 414.858 | 92.138 | 33.01 | 93.092 | 44.807
| 28.7361 | 323.712 | 413.956 | 91.996 | 33.014 | 92.882 | 44.816
| 28.7431 | 323.074 | 413.228 | 91.821 | 33.017 | 92.67 | 44.82
| 28.75 | 326.47 | 415.87 | 91.723 | 33.014 | 92.613 | 44.822
| 28.7569 | 325.463 | 416.416 | 91.737 | 33.015 | 92.734 | 44.824
| 28.7639 | 327.05 | 417.318 | 91.755 | 33.012 | 92.827 | 44.83
| 28.7708 | 327.1 | 416.554 | 91.792 | 33.016 | 92.922 | 44.822
| 28.7778 | 327.696 | 417.497 | 91.833 | 33.016 | 92.987 | 44.823
| 28.7847 | 327.017 | 418.4 | 91.898 | 33.016 | 93.072 | 44.828
| 28.7917 | 327.405 | 417.979 | 91.982 | 33.021 | 93.18 | 44.834
| 28.7986 | 328.633 | 420.602 | 92.048 | 33.024 | 93.241 | 44.829
| 28.8056 | 327.275 | 417.742 | 92.115 | 33.031 | 93.295 | 44.835
| 28.8125 | 327.808 | 419.671 | 92.165 | 33.03 | 93.306 | 44.838
| 28.8194 | 327.755 | 418.153 | 92.181 | 33.036 | 93.31 | 44.849
| 28.8264 | 328.444 | 418.618 | 92.214 | 33.046 | 93.334 | 44.852
| 28.8333 | 327.328 | 419.112 | 92.241 | 33.049 | 93.345 | 44.857
| 28.8403 | 328.681 | 418.626 | 92.265 | 33.049 | 93.37 | 44.86
| 28.8472 | 329.141 | 420.43 | 92.339 | 33.05 | 93.466 | 44.868
| 28.8542 | 328.729 | 412.747 | 92.436 | 33.067 | 93.382 | 44.876
| 28.8611 | 328.872 | 413.138 | 92.51 | 33.068 | 92.948 | 44.881
| 28.8681 | 329.812 | 413.384 | 92.586 | 33.079 | 92.779 | 44.889
| 28.875 | 326.503 | 417.044 | 92.455 | 33.085 | 92.743 | 44.896
| 28.8819 | 326.71 | 416.19 | 92.385 | 33.085 | 92.945 | 44.895
| 28.8889 | 326.403 | 416.945 | 92.323 | 33.095 | 93.031 | 44.898
| 28.8958 | 325.247 | 416.496 | 92.253 | 33.109 | 93.096 | 44.908
| 28.9028 | 326.12 | 416.196 | 92.181 | 33.114 | 93.083 | 44.907
| 28.9097 | 325.944 | 417.416 | 92.136 | 33.094 | 93.073 | 44.898
| 28.9167 | 327.302 | 418.554 | 92.193 | 33.104 | 93.241 | 44.906
| 28.9236 | 327.977 | 419.657 | 92.248 | 33.097 | 93.368 | 44.897
| 28.9306 | 328.08 | 412.439 | 92.329 | 33.097 | 93.441 | 44.901
| 28.9375 | 328.197 | 413.078 | 92.367 | 33.114 | 93.03 | 44.907
| 28.9444 | 325.675 | 409.696 | 92.228 | 33.112 | 92.588 | 44.915
| 28.9514 | 327.316 | 419.249 | 92.221 | 33.117 | 92.969 | 44.911
| 28.9583 | 327.95 | 421.246 | 92.269 | 33.118 | 93.289 | 44.917
| 28.9653 | 329.251 | 413.193 | 92.357 | 33.111 | 93.43 | 44.909
| 28.9722 | 330.245 | 415.513 | 92.431 | 33.117 | 93.039 | 44.918
| 28.9792 | 325.691 | 411.037 | 92.407 | 33.127 | 92.774 | 44.914
| 28.9861 | 326.957 | 412.679 | 92.346 | 33.139 | 92.517 | 44.928
| 28.9931 | 327.677 | 411.974 | 92.342 | 33.135 | 92.423 | 44.937
| 29 | 325.78 | 409.244 | 92.203 | 33.135 | 92.154 | 44.921
| 29.0069 | 325.927 | 410.286 | 92.133 | 33.137 | 92.028 | 44.922
| 29.0139 | 326.401 | 412.45 | 92.105 | 33.125 | 91.983 | 44.906
| 29.0208 | 326.787 | 411.105 | 92.094 | 33.134 | 91.983 | 44.899
| 29.0278 | 325.164 | 410.111 | 92.039 | 33.134 | 91.904 | 44.894
| 29.0347 | 325.271 | 409.619 | 91.963 | 33.136 | 91.793 | 44.883
| 29.0417 | 325.596 | 409.122 | 91.897 | 33.136 | 91.72 | 44.876
| 29.0486 | 325.882 | 409.346 | 91.853 | 33.129 | 91.679 | 44.862
| 29.0556 | 325.178 | 409.656 | 91.793 | 33.128 | 91.613 | 44.85
| 29.0625 | 326.327 | 410.119 | 91.795 | 33.131 | 91.644 | 44.84
| 29.0694 | 325.865 | 410.748 | 91.781 | 33.134 | 91.634 | 44.829
| 29.0764 | 326.339 | 411.104 | 91.785 | 33.129 | 91.615 | 44.818
| 29.0833 | 326.723 | 410.025 | 91.788 | 33.129 | 91.612 | 44.807
| 29.0903 | 326.115 | 411.19 | 91.802 | 33.132 | 91.612 | 44.795
| 29.0972 | 327.709 | 411.372 | 91.845 | 33.136 | 91.674 | 44.789
| 29.1042 | 328.277 | 412.326 | 91.937 | 33.134 | 91.777 | 44.776
| 29.1111 | 328.02 | 412.54 | 92.019 | 33.147 | 91.862 | 44.777
| 29.1181 | 328.233 | 413.051 | 92.094 | 33.146 | 91.918 | 44.764
| 29.125 | 327.815 | 413.181 | 92.139 | 33.148 | 91.925 | 44.756
| 29.1319 | 327.523 | 412.698 | 92.194 | 33.156 | 91.948 | 44.75
| 29.1389 | 328.752 | 412.459 | 92.25 | 33.15 | 91.965 | 44.748
| 29.1458 | 328.27 | 413.083 | 92.318 | 33.164 | 92.023 | 44.743
| 29.1528 | 327.138 | 412.571 | 92.333 | 33.168 | 91.997 | 44.745
| 29.1597 | 327.498 | 413.117 | 92.373 | 33.168 | 91.996 | 44.737
| 29.1667 | 328.703 | 412.483 | 92.407 | 33.172 | 92.015 | 44.74
| 29.1736 | 328.077 | 413.734 | 92.453 | 33.192 | 92.053 | 44.738
| 29.1806 | 328.225 | 412.026 | 92.479 | 33.189 | 92.052 | 44.729
| 29.1875 | 328.193 | 411.95 | 92.493 | 33.206 | 92.073 | 44.742
| 29.1944 | 328.213 | 412.379 | 92.503 | 33.188 | 92.019 | 44.73
| 29.2014 | 328.731 | 412.886 | 92.518 | 33.191 | 92.015 | 44.73
| 29.2083 | 328.253 | 412.662 | 92.517 | 33.198 | 91.996 | 44.729
| 29.2153 | 327.828 | 412.337 | 92.519 | 33.209 | 91.978 | 44.734
| 29.2222 | 326.542 | 411.715 | 92.494 | 33.203 | 91.922 | 44.723
| 29.2292 | 326.533 | 409.897 | 92.402 | 33.207 | 91.801 | 44.724
| 29.2361 | 326.202 | 410.506 | 92.333 | 33.204 | 91.699 | 44.723
| 29.2431 | 325.419 | 408.539 | 92.236 | 33.207 | 91.585 | 44.716
| 29.25 | 324.298 | 414.966 | 92.091 | 33.204 | 91.753 | 44.71
| 29.2569 | 326.902 | 418.899 | 92.049 | 33.207 | 92.085 | 44.708
| 29.2639 | 326.559 | 416.714 | 92.152 | 33.202 | 92.5 | 44.698
| 29.2708 | 324.315 | 415.118 | 91.996 | 33.198 | 92.383 | 44.702
| 29.2778 | 325.218 | 415.573 | 91.95 | 33.202 | 92.411 | 44.704
| 29.2847 | 325.624 | 416.004 | 91.879 | 33.198 | 92.402 | 44.705
| 30.7223 | 325.917 | 416.965 | 92.901 | 33.491 | 95.183 | 45.501
| 30.7292 | 314.503 | 403.008 | 92.396 | 33.489 | 94.446 | 45.497
| 30.7361 | 314.508 | 403.29 | 91.792 | 33.482 | 93.636 | 45.493
| 30.7431 | 315.863 | 404.054 | 91.26 | 33.471 | 93.125 | 45.487
| 30.75 | 318.933 | 408.288 | 90.989 | 33.449 | 93.075 | 45.467
| 30.7569 | 318.383 | 408.023 | 90.796 | 33.426 | 93.095 | 45.45
| 30.7639 | 318.67 | 409.782 | 90.624 | 33.408 | 93.104 | 45.428
| 30.7708 | 318.592 | 408.622 | 90.464 | 33.395 | 93.051 | 45.401
| 30.7778 | 319.344 | 408.258 | 90.311 | 33.371 | 92.972 | 45.386
| 30.7847 | 318.783 | 408.065 | 90.168 | 33.356 | 92.878 | 45.357
| 30.7917 | 318.106 | 408.582 | 90.039 | 33.338 | 92.788 | 45.328
| 30.7986 | 318.525 | 408.061 | 89.927 | 33.326 | 92.719 | 45.309
| 30.8056 | 320.464 | 409.67 | 89.876 | 33.308 | 92.73 | 45.284
| 30.8125 | 316.185 | 404.462 | 89.776 | 33.297 | 92.639 | 45.263
| 30.8194 | 317.432 | 406.298 | 89.553 | 33.285 | 92.338 | 45.242
| 30.8264 | 316.143 | 406.283 | 89.38 | 33.263 | 92.161 | 45.218
| 30.8333 | 316.795 | 407.022 | 89.256 | 33.249 | 92.08 | 45.195
| 30.8403 | 315.324 | 404.267 | 89.11 | 33.233 | 91.961 | 45.172
| 30.8472 | 317.045 | 405.725 | 88.962 | 33.216 | 91.816 | 45.155
| 30.8542 | 316.899 | 407.246 | 88.889 | 33.197 | 91.812 | 45.127
| 30.8611 | 317.077 | 407.166 | 88.844 | 33.187 | 91.812 | 45.102
| 30.8681 | 315.953 | 406.155 | 88.72 | 33.172 | 91.688 | 45.083
| 30.875 | 316.851 | 405.194 | 88.63 | 33.155 | 91.604 | 45.056
| 30.8819 | 316.787 | 405.459 | 88.583 | 33.143 | 91.592 | 45.029
| 30.8889 | 317.827 | 406.393 | 88.543 | 33.124 | 91.571 | 45.013
| 30.8958 | 315.561 | 404.477 | 88.455 | 33.115 | 91.474 | 44.982
| 30.9028 | 315.745 | 404.257 | 88.362 | 33.103 | 91.362 | 44.967
| 30.9097 | 316.057 | 404.674 | 88.287 | 33.085 | 91.294 | 44.943
| 30.9167 | 316.508 | 406.682 | 88.261 | 33.084 | 91.305 | 44.925
| 30.9236 | 317.836 | 406.467 | 88.279 | 33.06 | 91.362 | 44.899
| 30.9306 | 318.206 | 409.044 | 88.311 | 33.05 | 91.412 | 44.876
| 30.9375 | 319.051 | 408.06 | 88.386 | 33.041 | 91.514 | 44.859
| 30.9444 | 319.424 | 410.494 | 88.468 | 33.036 | 91.601 | 44.84
| 30.9514 | 313.563 | 402.738 | 88.217 | 33.026 | 91.162 | 44.825
| 30.9583 | 314.44 | 403.672 | 88.064 | 33.016 | 90.962 | 44.806
| 30.9653 | 315.122 | 402.962 | 87.983 | 33.002 | 90.888 | 44.789
| 30.9722 | 315.427 | 405.832 | 87.898 | 32.991 | 90.828 | 44.774
| 30.9792 | 316.057 | 406.348 | 87.917 | 32.979 | 90.916 | 44.758
| 30.9861 | 317.206 | 406.375 | 87.934 | 32.967 | 90.966 | 44.738
| 30.9931 | 315.329 | 403.559 | 87.903 | 32.956 | 90.903 | 44.72
| 31 | 315.983 | 404.587 | 87.843 | 32.952 | 90.802 | 44.704
| 31.0069 | 315.553 | 404.835 | 87.793 | 32.944 | 90.74 | 44.684
| 31.0139 | 314.575 | 404.647 | 87.668 | 32.93 | 90.575 | 44.664
| 31.0208 | 315.948 | 404.672 | 87.663 | 32.925 | 90.598 | 44.65
| 31.0278 | 316.296 | 405.862 | 87.679 | 32.911 | 90.653 | 44.635
| 31.0347 | 317.061 | 405.456 | 87.689 | 32.903 | 90.667 | 44.611
| 31.0417 | 315.968 | 403.944 | 87.647 | 32.894 | 90.586 | 44.601
| 31.0486 | 315.244 | 405.105 | 87.607 | 32.887 | 90.508 | 44.588
| 31.0556 | 315.789 | 404.941 | 87.601 | 32.877 | 90.497 | 44.566
| 31.0625 | 315.745 | 405.911 | 87.599 | 32.865 | 90.499 | 44.556
| 31.0694 | 316.361 | 405.778 | 87.623 | 32.859 | 90.535 | 44.539
| 31.0764 | 317.017 | 406.185 | 87.644 | 32.855 | 90.568 | 44.526
| 31.0833 | 317.059 | 407.625 | 87.69 | 32.847 | 90.615 | 44.511
| 31.0903 | 317.667 | 406.454 | 87.758 | 32.848 | 90.697 | 44.494
| 31.0972 | 317.925 | 407.965 | 87.822 | 32.841 | 90.762 | 44.487
| 31.1042 | 318.184 | 408.472 | 87.897 | 32.831 | 90.825 | 44.471
| 31.1111 | 318.311 | 408.627 | 87.964 | 32.835 | 90.879 | 44.464
| 31.1181 | 318.65 | 408.093 | 88.039 | 32.833 | 90.92 | 44.456
| 31.125 | 318.018 | 408.478 | 88.09 | 32.831 | 90.947 | 44.444
| 31.1319 | 318.914 | 407.691 | 88.14 | 32.828 | 90.968 | 44.439
| 31.1389 | 317.913 | 408.617 | 88.172 | 32.837 | 90.981 | 44.436
| 31.1458 | 318.706 | 408.996 | 88.215 | 32.822 | 90.99 | 44.427
| 31.1528 | 319.439 | 409.486 | 88.287 | 32.823 | 91.073 | 44.419
| 31.1597 | 319.287 | 408.712 | 88.354 | 32.828 | 91.129 | 44.422
| 31.1667 | 319.629 | 409.002 | 88.412 | 32.83 | 91.165 | 44.419
| 31.1736 | 319.12 | 409.877 | 88.459 | 32.823 | 91.176 | 44.406
| 31.1806 | 318.659 | 409.089 | 88.489 | 32.829 | 91.176 | 44.411
| 31.1875 | 319.366 | 408.33 | 88.529 | 32.825 | 91.194 | 44.4
| 31.1944 | 319.268 | 408.491 | 88.541 | 32.827 | 91.175 | 44.403
| 31.2014 | 319.23 | 408.098 | 88.563 | 32.828 | 91.187 | 44.402
| 31.2083 | 318.884 | 409.5 | 88.588 | 32.832 | 91.223 | 44.402
| 31.2153 | 318.565 | 408.855 | 88.592 | 32.821 | 91.211 | 44.4
| 31.2222 | 317.911 | 408.956 | 88.603 | 32.823 | 91.196 | 44.395
| 31.2292 | 318.249 | 408.941 | 88.599 | 32.829 | 91.2 | 44.4
| 31.2361 | 319.116 | 408.321 | 88.584 | 32.832 | 91.165 | 44.399
| 31.2431 | 318.024 | 407.956 | 88.578 | 32.827 | 91.154 | 44.394
| 31.25 | 317.87 | 407.026 | 88.54 | 32.82 | 91.099 | 44.391
| 31.2569 | 318.019 | 406.537 | 88.493 | 32.822 | 91.045 | 44.39
| 31.2639 | 317.917 | 407.121 | 88.451 | 32.818 | 90.999 | 44.392
| 31.2708 | 316.378 | 405.531 | 88.354 | 32.815 | 90.883 | 44.384
| 31.2778 | 316.414 | 406.192 | 88.257 | 32.81 | 90.768 | 44.376
| 31.2847 | 315.371 | 405.223 | 88.173 | 32.799 | 90.691 | 44.375
| 31.2917 | 314.842 | 404.45 | 88.067 | 32.794 | 90.582 | 44.365
| 31.2986 | 314.947 | 404.558 | 87.958 | 32.786 | 90.489 | 44.366
| 31.3056 | 314.257 | 402.856 | 87.84 | 32.782 | 90.386 | 44.351
| 31.3125 | 313.301 | 402.777 | 87.7 | 32.768 | 90.27 | 44.347
| 31.3194 | 313.303 | 401.902 | 87.535 | 32.762 | 90.105 | 44.338
| 31.3264 | 312.867 | 402.206 | 87.403 | 32.75 | 90.001 | 44.324
| 31.3333 | 312.976 | 401.972 | 87.279 | 32.74 | 89.913 | 44.314
| 31.3403 | 318.033 | 406.585 | 87.323 | 32.726 | 90.075 | 44.304
| 31.3472 | 319.448 | 409.281 | 87.547 | 32.72 | 90.496 | 44.287
| 31.3542 | 318.732 | 407.927 | 87.655 | 32.717 | 90.599 | 44.271
| 31.3611 | 318.195 | 408.485 | 87.728 | 32.711 | 90.631 | 44.263
| 31.3681 | 318.333 | 407.196 | 87.798 | 32.71 | 90.648 | 44.256
| 31.375 | 317.385 | 406.945 | 87.808 | 32.711 | 90.597 | 44.248
| 31.3819 | 317.003 | 405.121 | 87.791 | 32.705 | 90.513 | 44.243
| 31.3889 | 316.728 | 407.165 | 87.771 | 32.704 | 90.46 | 44.239
| 31.3958 | 316.485 | 405.171 | 87.715 | 32.709 | 90.372 | 44.232
| 31.4028 | 315.318 | 404.49 | 87.667 | 32.702 | 90.299 | 44.227
| 31.4097 | 315.284 | 404.021 | 87.595 | 32.696 | 90.214 | 44.22
| 31.4167 | 318.04 | 407.133 | 87.613 | 32.691 | 90.265 | 44.216
| 31.4236 | 317.749 | 407.985 | 87.696 | 32.683 | 90.425 | 44.207
| 31.4306 | 318.96 | 407.858 | 87.755 | 32.691 | 90.495 | 44.198
| 31.4375 | 317.163 | 407.771 | 87.798 | 32.69 | 90.515 | 44.194
| 31.4444 | 318.462 | 407.601 | 87.826 | 32.685 | 90.527 | 44.182
| 31.4514 | 318.036 | 407.358 | 87.89 | 32.684 | 90.595 | 44.182
| 31.4583 | 317.858 | 406.741 | 87.904 | 32.681 | 90.569 | 44.174
| 31.4653 | 316.682 | 406.44 | 87.887 | 32.683 | 90.501 | 44.171
| 31.4722 | 317.147 | 405.997 | 87.848 | 32.68 | 90.423 | 44.172
| 31.4792 | 316.497 | 406.862 | 87.835 | 32.683 | 90.411 | 44.167
| 31.4861 | 317.069 | 405.3 | 87.799 | 32.681 | 90.381 | 44.163
| 31.4931 | 317.128 | 405.961 | 87.78 | 32.67 | 90.354 | 44.166
| 31.5 | 316.612 | 405.85 | 87.746 | 32.669 | 90.312 | 44.154
| 31.5069 | 316.926 | 405.786 | 87.708 | 32.666 | 90.266 | 44.147
| 31.5139 | 317.014 | 406.317 | 87.691 | 32.66 | 90.265 | 44.142
| 31.5208 | 317.014 | 405.906 | 87.677 | 32.659 | 90.27 | 44.138
| 31.5278 | 316.209 | 406.29 | 87.647 | 32.658 | 90.255 | 44.134
| 31.5347 | 316.591 | 405.625 | 87.623 | 32.654 | 90.221 | 44.128
| 31.5417 | 315.708 | 405.806 | 87.585 | 32.646 | 90.187 | 44.122
| 31.5486 | 316.498 | 406.847 | 87.598 | 32.641 | 90.204 | 44.116
| 31.5556 | 317.55 | 405.995 | 87.599 | 32.636 | 90.216 | 44.11
| 31.5625 | 317.107 | 407.448 | 87.63 | 32.638 | 90.273 | 44.106
| 31.5694 | 318.277 | 407.17 | 87.67 | 32.632 | 90.322 | 44.099
| 31.5764 | 317.968 | 407.65 | 87.728 | 32.628 | 90.392 | 44.09
| 31.5833 | 318.205 | 408.668 | 87.78 | 32.628 | 90.439 | 44.086
| 31.5903 | 317.909 | 408.604 | 87.834 | 32.629 | 90.487 | 44.084
| 31.5972 | 318.959 | 409.832 | 87.933 | 32.63 | 90.596 | 44.078
| 31.6042 | 319.536 | 409.354 | 88.008 | 32.629 | 90.668 | 44.082
| 31.6111 | 319.205 | 409.231 | 88.068 | 32.631 | 90.701 | 44.075
| 31.6181 | 320.178 | 409.369 | 88.15 | 32.631 | 90.765 | 44.077
| 31.625 | 320.341 | 410.263 | 88.235 | 32.637 | 90.843 | 44.074
| 31.6319 | 320.221 | 410.012 | 88.307 | 32.639 | 90.878 | 44.08
| 31.6389 | 315.447 | 405.005 | 88.082 | 32.659 | 90.498 | 44.092
| 31.6458 | 315.972 | 405.509 | 87.981 | 32.652 | 90.34 | 44.094
| 31.6528 | 315.275 | 405.366 | 87.896 | 32.648 | 90.274 | 44.093
| 31.6597 | 316.509 | 404.957 | 87.814 | 32.643 | 90.21 | 44.093
| 31.6667 | 315.404 | 405.723 | 87.747 | 32.638 | 90.165 | 44.086
| 31.6736 | 315.887 | 405.985 | 87.684 | 32.636 | 90.121 | 44.084
| 31.6806 | 315.623 | 405.862 | 87.628 | 32.633 | 90.085 | 44.076
| 31.6875 | 315.443 | 404.904 | 87.56 | 32.627 | 90.038 | 44.074
| 31.6944 | 315.758 | 404.529 | 87.5 | 32.624 | 90.014 | 44.07
| 31.7014 | 315.442 | 405.223 | 87.455 | 32.617 | 89.984 | 44.059
| 31.7083 | 315.487 | 403.983 | 87.387 | 32.607 | 89.919 | 44.052
| 31.7153 | 314.794 | 404.797 | 87.317 | 32.6 | 89.853 | 44.045
| 31.7222 | 314.438 | 402.943 | 87.23 | 32.596 | 89.768 | 44.039
| 31.7292 | 317.072 | 407.523 | 87.191 | 32.589 | 89.764 | 44.034
| 31.7361 | 314.142 | 404.561 | 87.219 | 32.58 | 89.878 | 44.027
| 31.7431 | 314.942 | 403.35 | 87.091 | 32.565 | 89.684 | 44.006
| 31.75 | 313.956 | 403.283 | 87.022 | 32.559 | 89.624 | 43.995
| 31.7569 | 314.433 | 404.319 | 86.954 | 32.554 | 89.582 | 43.989
| 31.7639 | 313.93 | 404.274 | 86.893 | 32.546 | 89.558 | 43.98
| 31.7708 | 318.434 | 409.196 | 86.952 | 32.536 | 89.714 | 43.971
| 31.7778 | 317.819 | 408.989 | 87.115 | 32.533 | 89.994 | 43.964
| 31.7847 | 317.943 | 408.829 | 87.212 | 32.533 | 90.087 | 43.962
| 31.7917 | 318.517 | 408.09 | 87.317 | 32.529 | 90.166 | 43.947
| 31.7986 | 319.123 | 410.049 | 87.432 | 32.529 | 90.254 | 43.95
| 31.8056 | 319.62 | 409.555 | 87.549 | 32.531 | 90.337 | 43.946
| 31.8125 | 319.663 | 408.893 | 87.669 | 32.537 | 90.421 | 43.948
| 31.8194 | 320.535 | 410.521 | 87.773 | 32.539 | 90.487 | 43.947
| 31.8264 | 320.333 | 411.487 | 87.907 | 32.543 | 90.581 | 43.949
| 31.8333 | 316.554 | 406.33 | 87.811 | 32.545 | 90.066 | 43.952
| 31.8403 | 316.997 | 406.806 | 87.75 | 32.555 | 90.071 | 43.955
| 31.8472 | 318.583 | 407.976 | 87.738 | 32.552 | 90.11 | 43.954
| 31.8542 | 314.849 | 404.393 | 87.736 | 32.556 | 90.141 | 43.96
| 31.8611 | 315.528 | 405.973 | 87.583 | 32.561 | 89.929 | 43.96
| 31.8681 | 315.285 | 405.136 | 87.516 | 32.552 | 89.882 | 43.957
| 31.875 | 315.561 | 406.276 | 87.451 | 32.547 | 89.842 | 43.959
| 31.8819 | 317.151 | 406.233 | 87.419 | 32.542 | 89.847 | 43.956
| 31.8889 | 315.417 | 406.106 | 87.392 | 32.539 | 89.856 | 43.956
| 31.8958 | 314.5 | 404.854 | 87.283 | 32.537 | 89.743 | 43.954
| 31.9028 | 314.882 | 405.265 | 87.221 | 32.533 | 89.692 | 43.943
| 31.9097 | 315.62 | 406.348 | 87.179 | 32.529 | 89.697 | 43.946
| 31.9167 | 315.643 | 406.306 | 87.163 | 32.519 | 89.718 | 43.938
| 31.9236 | 316.819 | 406.028 | 87.178 | 32.518 | 89.782 | 43.935
| 31.9306 | 317.332 | 407.474 | 87.215 | 32.518 | 89.847 | 43.936
| 31.9375 | 317.238 | 407.567 | 87.241 | 32.511 | 89.893 | 43.927
| 31.9444 | 317.291 | 408.169 | 87.294 | 32.516 | 89.968 | 43.927
| 31.9514 | 318.135 | 409.556 | 87.366 | 32.507 | 90.049 | 43.922
| 31.9583 | 319.297 | 408.956 | 87.466 | 32.513 | 90.188 | 43.921
| 31.9653 | 319.066 | 410.124 | 87.564 | 32.513 | 90.27 | 43.922
| 31.9722 | 319.923 | 411.035 | 87.668 | 32.516 | 90.349 | 43.918
| 31.9792 | 318.27 | 408.004 | 87.703 | 32.521 | 90.315 | 43.922
| 31.9861 | 318.353 | 407.516 | 87.721 | 32.524 | 90.272 | 43.927
| 31.9931 | 318.388 | 408.829 | 87.762 | 32.524 | 90.289 | 43.928
| 32 | 319.445 | 409.149 | 87.827 | 32.522 | 90.348 | 43.929
| 32.0069 | 316.557 | 406.655 | 87.817 | 32.534 | 90.298 | 43.931
| 32.0139 | 316.89 | 406.689 | 87.707 | 32.528 | 90.096 | 43.934
| 32.0208 | 316.692 | 407.327 | 87.68 | 32.533 | 90.072 | 43.939
| 32.0278 | 316.749 | 407.053 | 87.651 | 32.527 | 90.069 | 43.94
| 32.0347 | 317.417 | 406.974 | 87.641 | 32.533 | 90.088 | 43.944
| 32.0417 | 315.96 | 406.672 | 87.588 | 32.528 | 90.048 | 43.94
| 32.0486 | 316.393 | 407.352 | 87.554 | 32.527 | 90.024 | 43.938
| 32.0556 | 319.031 | 410.449 | 87.662 | 32.526 | 90.209 | 43.939
| 32.0625 | 320.251 | 403.562 | 87.795 | 32.521 | 90.323 | 43.945
| 32.0694 | 316.695 | 405.667 | 87.65 | 32.527 | 89.909 | 43.938
| 32.0764 | 316.057 | 406.986 | 87.588 | 32.525 | 89.918 | 43.942
| 32.0833 | 316.254 | 406.299 | 87.553 | 32.527 | 89.945 | 43.941
| 32.0903 | 316.429 | 407.499 | 87.535 | 32.523 | 89.967 | 43.939
| 32.0972 | 317.826 | 407.793 | 87.524 | 32.518 | 89.996 | 43.934
| 32.1042 | 318.08 | 408.544 | 87.577 | 32.518 | 90.102 | 43.938
| 32.1111 | 317.596 | 409.191 | 87.611 | 32.516 | 90.165 | 43.933
| 32.1181 | 319.007 | 408.87 | 87.667 | 32.52 | 90.243 | 43.929
| 32.125 | 318.303 | 410.196 | 87.731 | 32.521 | 90.332 | 43.935
| 32.1319 | 318.315 | 409.27 | 87.792 | 32.521 | 90.409 | 43.929
| 32.1389 | 318.374 | 409.88 | 87.819 | 32.526 | 90.428 | 43.932
| 32.1458 | 318.827 | 410.405 | 87.886 | 32.526 | 90.508 | 43.936
| 32.1528 | 319.564 | 409.074 | 87.94 | 32.532 | 90.545 | 43.934
| 32.1597 | 319.6 | 409.109 | 87.999 | 32.537 | 90.59 | 43.941
| 32.1667 | 319.475 | 409.069 | 88.032 | 32.535 | 90.603 | 43.944
| 32.1736 | 318.756 | 409.504 | 88.062 | 32.539 | 90.618 | 43.946
| 32.1806 | 319.638 | 409.104 | 88.086 | 32.538 | 90.62 | 43.95
| 32.1875 | 319.641 | 409.522 | 88.129 | 32.545 | 90.659 | 43.96
| 32.1944 | 319.733 | 409.496 | 88.17 | 32.547 | 90.707 | 43.966
| 32.2014 | 319.387 | 410.102 | 88.212 | 32.547 | 90.743 | 43.967
| 32.2083 | 319.188 | 409.761 | 88.231 | 32.553 | 90.749 | 43.969
| 32.2153 | 319.403 | 409.277 | 88.241 | 32.552 | 90.74 | 43.98
| 32.2222 | 319.699 | 409.609 | 88.254 | 32.56 | 90.736 | 43.985
| 32.2292 | 319.375 | 409.107 | 88.264 | 32.561 | 90.745 | 43.988
| 32.2361 | 319.255 | 408.64 | 88.263 | 32.563 | 90.721 | 43.993
| 32.2431 | 318.326 | 408.709 | 88.248 | 32.564 | 90.689 | 43.992
| 32.25 | 318.526 | 409.511 | 88.233 | 32.565 | 90.673 | 43.999
| 32.2569 | 319.017 | 408.473 | 88.223 | 32.57 | 90.675 | 43.999
| 32.2639 | 318.582 | 408.224 | 88.199 | 32.569 | 90.649 | 44.008
| 32.2708 | 317.657 | 408.455 | 88.143 | 32.574 | 90.584 | 44.002
| 32.2778 | 317.858 | 407.985 | 88.094 | 32.569 | 90.522 | 44.007
| 32.2847 | 318.167 | 407.643 | 88.058 | 32.567 | 90.496 | 44.005
| 32.2917 | 317.75 | 406.828 | 88.012 | 32.568 | 90.458 | 44.007
| 32.2986 | 316.927 | 407.503 | 87.949 | 32.562 | 90.403 | 44.006
| 32.3056 | 316.171 | 406.252 | 87.874 | 32.56 | 90.326 | 44.009
| 32.3125 | 316.508 | 406.494 | 87.791 | 32.556 | 90.255 | 44.006
| 32.3194 | 316.571 | 407.195 | 87.736 | 32.558 | 90.226 | 44.005
| 32.3264 | 316.503 | 405.973 | 87.662 | 32.553 | 90.171 | 44.003
| 32.3333 | 315.583 | 406.083 | 87.597 | 32.547 | 90.124 | 43.997
| 32.3403 | 317.965 | 408.774 | 87.571 | 32.54 | 90.147 | 43.992
| 32.3472 | 318.116 | 407.937 | 87.647 | 32.537 | 90.307 | 43.988
| 32.3542 | 317.787 | 407.236 | 87.642 | 32.533 | 90.307 | 43.979
| 32.3611 | 317.531 | 408.085 | 87.644 | 32.535 | 90.294 | 43.976
| 32.3681 | 317.302 | 406.55 | 87.612 | 32.534 | 90.248 | 43.968
| 32.375 | 316.64 | 407.376 | 87.574 | 32.528 | 90.185 | 43.962
| 32.3819 | 316.684 | 406.325 | 87.533 | 32.527 | 90.131 | 43.963
| 32.3889 | 315.009 | 405.055 | 87.453 | 32.52 | 90.035 | 43.959
| 32.3958 | 316.071 | 404.631 | 87.375 | 32.516 | 89.943 | 43.955
| 32.4028 | 315.004 | 404.909 | 87.28 | 32.512 | 89.843 | 43.95
| 32.4097 | 315.209 | 403.767 | 87.196 | 32.506 | 89.766 | 43.945
| 32.4167 | 314.593 | 404.256 | 87.095 | 32.496 | 89.677 | 43.934
| 32.4236 | 314.467 | 403.268 | 86.997 | 32.494 | 89.584 | 43.926
| 32.4306 | 314.104 | 402.624 | 86.887 | 32.484 | 89.498 | 43.917
| 32.4375 | 317.301 | 406.515 | 86.964 | 32.477 | 89.704 | 43.903
| 32.4444 | 316.017 | 407.2 | 87.003 | 32.475 | 89.801 | 43.897
| 32.4514 | 315.682 | 406.344 | 87.026 | 32.469 | 89.836 | 43.885
| 32.4583 | 317.261 | 408.639 | 87.123 | 32.466 | 89.978 | 43.877
| 32.4653 | 318.336 | 407.779 | 87.196 | 32.465 | 90.057 | 43.868
| 32.4722 | 317.453 | 406.923 | 87.253 | 32.462 | 90.089 | 43.863
| 32.4792 | 316.522 | 407.442 | 87.276 | 32.461 | 90.067 | 43.857
| 32.4861 | 316.779 | 407.779 | 87.295 | 32.461 | 90.053 | 43.852
| 32.4931 | 316.506 | 406.319 | 87.285 | 32.46 | 90.005 | 43.852
| 32.5 | 316.275 | 406.483 | 87.279 | 32.462 | 89.98 | 43.848
| 32.5069 | 316.436 | 406.45 | 87.252 | 32.455 | 89.942 | 43.84
| 32.5139 | 317.132 | 406.426 | 87.263 | 32.457 | 89.967 | 43.841
| 32.5208 | 316.102 | 406.309 | 87.257 | 32.454 | 89.973 | 43.833
| 32.5278 | 316.628 | 406.554 | 87.262 | 32.449 | 90.001 | 43.827
| 32.5347 | 317.492 | 406.524 | 87.279 | 32.453 | 90.016 | 43.826
| 32.5417 | 317.133 | 406.096 | 87.278 | 32.444 | 90.005 | 43.824
| 32.5486 | 316.534 | 405.528 | 87.269 | 32.444 | 89.979 | 43.816
| 32.5556 | 316.094 | 406.089 | 87.222 | 32.439 | 89.907 | 43.815
| 32.5625 | 316.333 | 406.961 | 87.236 | 32.441 | 89.943 | 43.813
| 32.5694 | 317.37 | 406.261 | 87.248 | 32.438 | 89.975 | 43.806
| 32.5764 | 317.013 | 407.006 | 87.287 | 32.438 | 90.036 | 43.802
| 32.5833 | 317.54 | 406.443 | 87.294 | 32.432 | 90.047 | 43.806
| 32.5903 | 318.262 | 407.749 | 87.343 | 32.428 | 90.118 | 43.793
| 32.5972 | 317.207 | 407.291 | 87.362 | 32.431 | 90.14 | 43.792
| 32.6042 | 317.337 | 407.485 | 87.395 | 32.428 | 90.182 | 43.79
| 32.6111 | 317.546 | 408.12 | 87.406 | 32.428 | 90.181 | 43.783
| 32.6181 | 317.888 | 408.257 | 87.43 | 32.423 | 90.189 | 43.786
| 32.625 | 317.816 | 408.576 | 87.475 | 32.424 | 90.26 | 43.783
| 32.6319 | 318.318 | 409.308 | 87.528 | 32.424 | 90.301 | 43.78
| 32.6389 | 318.307 | 408.865 | 87.565 | 32.424 | 90.329 | 43.783
| 32.6458 | 317.647 | 408.654 | 87.591 | 32.427 | 90.332 | 43.782
| 32.6528 | 318.331 | 408.4 | 87.609 | 32.424 | 90.325 | 43.782
| 32.6597 | 317.954 | 408.788 | 87.632 | 32.426 | 90.332 | 43.78
| 32.6667 | 317.64 | 408.907 | 87.647 | 32.428 | 90.336 | 43.786
| 32.6736 | 318.78 | 408.586 | 87.678 | 32.423 | 90.363 | 43.786
| 32.6806 | 317.689 | 409.17 | 87.684 | 32.427 | 90.356 | 43.787
| 32.6875 | 317.743 | 409.019 | 87.699 | 32.425 | 90.359 | 43.786
| 32.6944 | 318.391 | 408.224 | 87.686 | 32.421 | 90.349 | 43.786
| 32.7014 | 317.735 | 409.269 | 87.69 | 32.426 | 90.352 | 43.788
| 32.7083 | 316.901 | 408.026 | 87.688 | 32.426 | 90.346 | 43.791
| 32.7153 | 317.182 | 408.393 | 87.674 | 32.425 | 90.324 | 43.789
| 32.7222 | 317.641 | 406.852 | 87.642 | 32.423 | 90.278 | 43.792
| 32.7292 | 316.397 | 405.957 | 87.544 | 32.42 | 90.136 | 43.789
| 32.7361 | 316.075 | 405.395 | 87.521 | 32.416 | 90.149 | 43.791
| 32.7431 | 314.919 | 405.541 | 87.398 | 32.412 | 90.028 | 43.788
| 32.75 | 314.805 | 404.552 | 87.283 | 32.413 | 89.905 | 43.79
| 32.7569 | 314.298 | 403.562 | 87.16 | 32.403 | 89.804 | 43.783
| 32.7639 | 313.927 | 403.242 | 87.026 | 32.4 | 89.681 | 43.783
| 32.7708 | 313.362 | 401.8 | 86.896 | 32.394 | 89.576 | 43.782
| 32.7778 | 313.614 | 402.222 | 86.783 | 32.397 | 89.515 | 43.78
| 32.7847 | 313.569 | 403.928 | 86.676 | 32.378 | 89.44 | 43.77
| 32.7917 | 313.758 | 403.11 | 86.612 | 32.368 | 89.425 | 43.76
| 32.7986 | 317.951 | 407.421 | 86.636 | 32.373 | 89.565 | 43.761
| 32.8056 | 318.6 | 410.199 | 86.835 | 32.356 | 89.91 | 43.747
| 32.8125 | 319.008 | 409.303 | 86.989 | 32.35 | 90.104 | 43.74
| 32.8194 | 319.167 | 410.484 | 87.133 | 32.357 | 90.256 | 43.736
| 32.8264 | 320.259 | 410.005 | 87.292 | 32.356 | 90.388 | 43.738
| 32.8333 | 319.67 | 410.524 | 87.4 | 32.356 | 90.442 | 43.73
| 32.8403 | 319.925 | 409.927 | 87.51 | 32.361 | 90.486 | 43.73
| 32.8472 | 319.248 | 404.132 | 87.615 | 32.367 | 90.341 | 43.736
| 32.8542 | 316.231 | 399.988 | 87.614 | 32.371 | 89.854 | 43.738
| 32.8611 | 317.188 | 400.073 | 87.524 | 32.371 | 89.445 | 43.734
| 32.8681 | 316.792 | 400.933 | 87.489 | 32.374 | 89.269 | 43.739
| 32.875 | 317.788 | 403.075 | 87.494 | 32.368 | 89.209 | 43.742
| 32.8819 | 318.23 | 403.206 | 87.533 | 32.367 | 89.226 | 43.729
| 32.8889 | 318.978 | 402.959 | 87.578 | 32.374 | 89.26 | 43.726
| 32.8958 | 316.087 | 400.701 | 87.552 | 32.374 | 89.177 | 43.72
| 32.9028 | 316.282 | 401.534 | 87.496 | 32.367 | 89.055 | 43.709
| 32.9097 | 316.65 | 401.586 | 87.449 | 32.371 | 88.972 | 43.702
| 32.9167 | 316.601 | 401.746 | 87.413 | 32.367 | 88.909 | 43.689
| 32.9236 | 316.84 | 400.752 | 87.401 | 32.364 | 88.893 | 43.681
| 32.9306 | 316.629 | 402.146 | 87.357 | 32.358 | 88.808 | 43.666
| 32.9375 | 316.07 | 401.058 | 87.334 | 32.369 | 88.773 | 43.662
| 32.9444 | 317.085 | 401.369 | 87.322 | 32.36 | 88.762 | 43.647
| 32.9514 | 317.643 | 403.144 | 87.338 | 32.356 | 88.78 | 43.636
| 32.9583 | 318.35 | 402.922 | 87.385 | 32.354 | 88.863 | 43.619
| 32.9653 | 318.565 | 403.443 | 87.451 | 32.354 | 88.936 | 43.609
| 32.9722 | 320.277 | 404.783 | 87.528 | 32.356 | 88.988 | 43.602
| 32.9792 | 316.262 | 399.403 | 87.573 | 32.359 | 89.003 | 43.599
| 32.9861 | 316.648 | 399.51 | 87.456 | 32.362 | 88.736 | 43.586
| 32.9931 | 316.05 | 401.027 | 87.403 | 32.353 | 88.644 | 43.579
| 33 | 316.993 | 402.102 | 87.387 | 32.359 | 88.624 | 43.573
| 33.0069 | 317.591 | 402.045 | 87.381 | 32.35 | 88.614 | 43.565
| 33.0139 | 318.316 | 403.885 | 87.415 | 32.351 | 88.662 | 43.553
| 33.0208 | 319.142 | 402.92 | 87.486 | 32.349 | 88.746 | 43.546
| 33.0278 | 318.775 | 403.624 | 87.535 | 32.36 | 88.783 | 43.536
| 33.0347 | 318.919 | 403.721 | 87.59 | 32.358 | 88.805 | 43.529
| 33.0417 | 318.379 | 401.761 | 87.572 | 32.359 | 88.737 | 43.52
| 33.0486 | 318.389 | 402.344 | 87.575 | 32.358 | 88.681 | 43.51
| 33.0556 | 318.435 | 403.785 | 87.569 | 32.356 | 88.641 | 43.505
| 33.0625 | 318.749 | 404.101 | 87.637 | 32.352 | 88.706 | 43.5
| 33.0694 | 319.046 | 403.674 | 87.669 | 32.359 | 88.716 | 43.497
| 33.0764 | 319.333 | 402.75 | 87.693 | 32.361 | 88.708 | 43.482
| 33.0833 | 318.665 | 403.876 | 87.716 | 32.36 | 88.7 | 43.48
| 33.0903 | 319.331 | 403.877 | 87.737 | 32.367 | 88.7 | 43.475
| 33.0972 | 316.095 | 404.966 | 87.623 | 32.37 | 88.568 | 43.469
| 33.1042 | 315.492 | 405.76 | 87.491 | 32.371 | 88.792 | 43.462
| 33.1111 | 313.017 | 402.002 | 87.234 | 32.363 | 88.644 | 43.455
| 33.1181 | 312.912 | 401.651 | 87.012 | 32.352 | 88.527 | 43.446
| 33.125 | 312.396 | 402.27 | 86.831 | 32.346 | 88.477 | 43.446
| 33.1319 | 312.746 | 402.652 | 86.677 | 32.335 | 88.447 | 43.44
| 33.1389 | 313.186 | 401.626 | 86.533 | 32.335 | 88.429 | 43.437
| 33.1458 | 312.243 | 402.006 | 86.409 | 32.328 | 88.398 | 43.427
| 33.1528 | 316.253 | 406.868 | 86.426 | 32.308 | 88.572 | 43.424
| 33.1597 | 316.741 | 406.147 | 86.498 | 32.298 | 88.783 | 43.41
| 33.1667 | 316.155 | 406.077 | 86.542 | 32.292 | 88.879 | 43.406
| 33.1736 | 316.439 | 406.986 | 86.583 | 32.293 | 88.944 | 43.4
| 33.1806 | 315.906 | 406.762 | 86.606 | 32.29 | 88.971 | 43.404
| 33.1875 | 315.957 | 405.417 | 86.602 | 32.284 | 88.955 | 43.397
| 33.1944 | 315.488 | 405.799 | 86.591 | 32.289 | 88.936 | 43.403
| 33.2014 | 315.832 | 405.027 | 86.568 | 32.277 | 88.905 | 43.394
| 33.2083 | 315.405 | 405.347 | 86.557 | 32.267 | 88.902 | 43.39
| 33.2153 | 315.002 | 404.474 | 86.515 | 32.266 | 88.862 | 43.393
| 33.2222 | 313.752 | 403.292 | 86.443 | 32.264 | 88.785 | 43.39
| 33.2292 | 314.73 | 403.713 | 86.407 | 32.26 | 88.792 | 43.39
| 33.2361 | 313.535 | 404.063 | 86.341 | 32.254 | 88.73 | 43.388
| 33.2431 | 313.521 | 403.434 | 86.269 | 32.248 | 88.675 | 43.382
| 33.25 | 314.419 | 403.383 | 86.201 | 32.237 | 88.625 | 43.377
| 33.2569 | 314.295 | 403.789 | 86.164 | 32.232 | 88.629 | 43.379
| 33.2639 | 313.596 | 403.638 | 86.103 | 32.221 | 88.591 | 43.374
| 33.2708 | 314.976 | 403.738 | 86.111 | 32.221 | 88.681 | 43.368
| 33.2778 | 315.863 | 405.438 | 86.149 | 32.212 | 88.802 | 43.361
| 33.2847 | 315.808 | 406.168 | 86.234 | 32.21 | 88.941 | 43.361
| 33.2917 | 316.246 | 404.914 | 86.266 | 32.207 | 88.97 | 43.356
| 33.2986 | 314.327 | 403.955 | 86.23 | 32.206 | 88.895 | 43.357
| 33.3056 | 317.436 | 406.752 | 86.311 | 32.202 | 89.006 | 43.35
| 33.3125 | 315.267 | 405.459 | 86.31 | 32.199 | 89.006 | 43.35
| 33.3194 | 316.965 | 406.989 | 86.303 | 32.199 | 88.967 | 43.346
| 33.3264 | 316.403 | 407.169 | 86.413 | 32.194 | 89.114 | 43.353
| 33.3333 | 315.49 | 406.004 | 86.406 | 32.195 | 89.066 | 43.349
| 33.3403 | 317.388 | 408.627 | 86.534 | 32.192 | 89.226 | 43.347
| 33.3472 | 316.17 | 406.093 | 86.594 | 32.196 | 89.269 | 43.348
| 33.3542 | 316.402 | 405.151 | 86.582 | 32.196 | 89.209 | 43.352
| 33.3611 | 316.318 | 406.19 | 86.591 | 32.194 | 89.189 | 43.354
| 33.3681 | 316.151 | 404.988 | 86.584 | 32.196 | 89.149 | 43.353
| 33.375 | 316.61 | 405.566 | 86.581 | 32.192 | 89.15 | 43.353
| 33.3819 | 316.234 | 407.037 | 86.616 | 32.194 | 89.198 | 43.357
| 33.3889 | 316.889 | 408.112 | 86.653 | 32.199 | 89.254 | 43.358
| 33.3958 | 318.067 | 407.584 | 86.728 | 32.192 | 89.363 | 43.358
| 33.4028 | 317.345 | 406.464 | 86.778 | 32.193 | 89.4 | 43.36
| 33.4097 | 317.254 | 407.116 | 86.799 | 32.196 | 89.393 | 43.361
| 33.4167 | 318.039 | 407.318 | 86.815 | 32.195 | 89.391 | 43.361
| 33.4236 | 315.851 | 406.452 | 86.808 | 32.202 | 89.363 | 43.365
| 33.4306 | 315.756 | 406.377 | 86.776 | 32.197 | 89.306 | 43.368
| 33.4375 | 316.914 | 406.547 | 86.776 | 32.197 | 89.325 | 43.37
| 33.4444 | 317.608 | 408.465 | 86.803 | 32.196 | 89.379 | 43.37
| 33.4514 | 317.658 | 407.584 | 86.835 | 32.2 | 89.437 | 43.369
| 33.4583 | 316.692 | 407.677 | 86.84 | 32.194 | 89.433 | 43.371
| 33.4653 | 316.374 | 407.171 | 86.843 | 32.197 | 89.42 | 43.375
| 33.4722 | 317.505 | 407.068 | 86.846 | 32.197 | 89.422 | 43.375
| 33.4792 | 317.435 | 406.69 | 86.871 | 32.195 | 89.457 | 43.378
| 33.4861 | 317.327 | 407.838 | 86.884 | 32.196 | 89.478 | 43.37
| 33.4931 | 318.62 | 408.21 | 86.937 | 32.195 | 89.552 | 43.377
| 33.5 | 318.463 | 408.918 | 86.998 | 32.196 | 89.63 | 43.377
| 33.5069 | 318.259 | 407.595 | 87.024 | 32.194 | 89.639 | 43.38
| 33.5139 | 319.332 | 410.4 | 87.12 | 32.201 | 89.759 | 43.382
| 33.5208 | 316.063 | 404.941 | 87.095 | 32.201 | 89.695 | 43.385
| 33.5278 | 315.435 | 404.333 | 86.978 | 32.203 | 89.503 | 43.383
| 33.5347 | 315.416 | 404.997 | 86.862 | 32.201 | 89.351 | 43.388
| 33.5417 | 314.973 | 403.966 | 86.764 | 32.193 | 89.27 | 43.388
| 33.5486 | 314.74 | 405.096 | 86.667 | 32.188 | 89.202 | 43.388
| 33.5556 | 313.879 | 404.278 | 86.584 | 32.187 | 89.149 | 43.38
| 33.5625 | 314.715 | 403.297 | 86.503 | 32.173 | 89.103 | 43.379
| 33.5694 | 315.131 | 404.43 | 86.452 | 32.173 | 89.106 | 43.373
| 33.5764 | 315.872 | 406.44 | 86.455 | 32.169 | 89.165 | 43.371
| 33.5833 | 316.374 | 405.571 | 86.462 | 32.159 | 89.217 | 43.364
| 33.5903 | 316.664 | 405.773 | 86.494 | 32.155 | 89.274 | 43.361
| 33.5972 | 316.311 | 407.428 | 86.499 | 32.153 | 89.284 | 43.364
| 33.6042 | 315.409 | 405.993 | 86.51 | 32.148 | 89.306 | 43.355
| 33.6111 | 316.023 | 405.789 | 86.472 | 32.15 | 89.259 | 43.35
| 33.6181 | 315.804 | 406.734 | 86.499 | 32.146 | 89.303 | 43.348
| 33.625 | 316.736 | 406.072 | 86.518 | 32.142 | 89.347 | 43.344
| 33.6319 | 315.748 | 406.852 | 86.542 | 32.145 | 89.369 | 43.342
| 33.6389 | 316.393 | 407.114 | 86.554 | 32.137 | 89.377 | 43.334
| 33.6458 | 314.021 | 404.227 | 86.484 | 32.134 | 89.259 | 43.336
| 33.6528 | 314.398 | 404.548 | 86.425 | 32.133 | 89.187 | 43.326
| 33.7014 | 252.165 | 370.963 | 72.288 | 31.496 | 80.966 | 42.7
| 33.7083 | 273.331 | 358.913 | 73.314 | 31.379 | 80.526 | 42.61
| 33.7153 | 273.682 | 359.69 | 73.322 | 31.287 | 79.984 | 42.533
| 33.7222 | 273.389 | 358.072 | 73.237 | 31.214 | 79.62 | 42.453
| 33.7292 | 272.342 | 357.892 | 73.102 | 31.152 | 79.272 | 42.375
| 33.7361 | 271.525 | 357.295 | 72.959 | 31.091 | 78.974 | 42.298
| 33.7431 | 273.162 | 357.736 | 72.833 | 31.04 | 78.749 | 42.215
| 33.75 | 273.993 | 360.517 | 72.718 | 30.987 | 78.56 | 42.14
| 33.7569 | 274.801 | 360.714 | 72.749 | 30.939 | 78.568 | 42.058
| 33.7639 | 274.845 | 361.499 | 72.738 | 30.9 | 78.494 | 41.981
| 33.7708 | 274.653 | 360.876 | 72.722 | 30.86 | 78.401 | 41.903
| 33.7778 | 274.665 | 351.817 | 72.69 | 30.827 | 78.264 | 41.836
| 33.7847 | 274.67 | 351.858 | 72.657 | 30.777 | 77.564 | 41.759
| 33.7917 | 274.058 | 352.24 | 72.616 | 30.75 | 77.216 | 41.688
| 33.7986 | 268.497 | 352.844 | 72.284 | 30.711 | 76.978 | 41.62
| 33.8056 | 269.378 | 352.374 | 72.052 | 30.673 | 76.809 | 41.546
| 33.8125 | 269.224 | 344.551 | 71.868 | 30.63 | 76.286 | 41.476
| 33.8194 | 268.028 | 341.75 | 71.639 | 30.596 | 75.76 | 41.403
| 33.8264 | 268.272 | 342.599 | 71.429 | 30.555 | 75.376 | 41.33
| 33.8333 | 260.199 | 341.47 | 70.863 | 30.514 | 75.075 | 41.254
| 33.8403 | 259.889 | 330.859 | 70.432 | 30.465 | 74.727 | 41.175
| 33.8472 | 250.58 | 331.825 | 70.036 | 30.418 | 73.983 | 41.097
| 33.8542 | 250.983 | 331.613 | 69.236 | 30.368 | 73.547 | 41.015
| 33.8611 | 250.712 | 321.487 | 68.644 | 30.307 | 72.669 | 40.932
| 33.8681 | 241.767 | 313.016 | 67.743 | 30.249 | 71.964 | 40.847
| 33.875 | 235.123 | 313.46 | 66.949 | 30.185 | 71.222 | 40.756
| 33.8819 | 235.245 | 303.55 | 66.009 | 30.111 | 70.395 | 40.661
| 33.8889 | 228.519 | 303.666 | 65.06 | 30.046 | 69.767 | 40.565
| 33.8958 | 226.903 | 292.28 | 64.11 | 29.956 | 68.76 | 40.463
| 33.9028 | 218.881 | 292.737 | 63.171 | 29.866 | 68.102 | 40.348
| 33.9097 | 219.292 | 283.292 | 62.172 | 29.782 | 67.206 | 40.238
| 33.9167 | 215.964 | 279.4 | 61.373 | 29.683 | 66.584 | 40.116
| 33.9236 | 210.48 | 275.424 | 60.266 | 29.599 | 65.7 | 39.996
| 33.9306 | 209.295 | 273.037 | 59.364 | 29.489 | 65.077 | 39.862
| 33.9375 | 200.514 | 260.986 | 58.267 | 29.394 | 64.103 | 39.733
| 33.9444 | 200.242 | 253.501 | 57.343 | 29.284 | 63.365 | 39.594
| 33.9514 | 192.704 | 254.392 | 56.331 | 29.17 | 62.537 | 39.449
| 33.9583 | 193.605 | 244.144 | 55.435 | 29.064 | 61.738 | 39.306
| 33.9653 | 183.056 | 241.49 | 54.305 | 28.955 | 60.923 | 39.16
| 33.9722 | 183.654 | 234.007 | 53.374 | 28.843 | 60.221 | 39.008
| 33.9792 | 174.731 | 232.306 | 52.349 | 28.725 | 59.482 | 38.857
| 33.9861 | 173.628 | 213.071 | 51.4 | 28.608 | 58.406 | 38.695
| 33.9931 | 174.273 | 224.857 | 50.573 | 28.486 | 57.954 | 38.535
| 34 | 165.172 | 215.738 | 49.571 | 28.373 | 57.169 | 38.37
| 34.0069 | 164.953 | 215.832 | 48.735 | 28.255 | 56.599 | 38.204
| 34.0139 | 157.591 | 205.159 | 47.943 | 28.137 | 55.828 | 38.038
| 34.0208 | 158.073 | 205.836 | 47.082 | 28.019 | 55.243 | 37.869
| 34.0278 | 158.064 | 205.834 | 46.359 | 27.907 | 54.75 | 37.698
| 34.0347 | 157.446 | 197.536 | 45.709 | 27.792 | 54.174 | 37.528
| 34.0417 | 148.755 | 196.448 | 45.033 | 27.684 | 53.565 | 37.354
| 34.0486 | 149.027 | 196.969 | 44.307 | 27.563 | 53.081 | 37.18
| 34.0556 | 149.271 | 196.597 | 43.697 | 27.455 | 52.669 | 37.014
| 34.0625 | 148.873 | 187.796 | 43.145 | 27.343 | 51.997 | 36.843
| 34.0694 | 141.577 | 187.476 | 42.462 | 27.236 | 51.525 | 36.673
| 34.0764 | 141.631 | 187.298 | 41.886 | 27.133 | 51.117 | 36.506
| 34.0833 | 141.534 | 177.948 | 41.372 | 27.03 | 50.544 | 36.34
| 34.0903 | 141.566 | 178.248 | 40.903 | 26.932 | 50.055 | 36.174
| 34.0972 | 141.408 | 178.263 | 40.49 | 26.829 | 49.656 | 36.008
| 34.1042 | 134.655 | 178.17 | 39.943 | 26.728 | 49.288 | 35.839
| 34.1111 | 134.683 | 178.158 | 39.489 | 26.637 | 48.967 | 35.677
| 34.1181 | 134.769 | 178.014 | 39.084 | 26.534 | 48.641 | 35.515
| 34.125 | 134.594 | 177.952 | 38.714 | 26.445 | 48.34 | 35.356
| 34.1319 | 134.502 | 178.377 | 38.382 | 26.352 | 48.05 | 35.197
| 34.1389 | 134.627 | 177.942 | 38.08 | 26.264 | 47.778 | 35.039
| 34.1458 | 134.335 | 178.13 | 37.807 | 26.183 | 47.502 | 34.886
| 34.1528 | 134.014 | 168.497 | 37.552 | 26.091 | 47.043 | 34.732
| 34.1597 | 133.888 | 168.673 | 37.316 | 26.01 | 46.651 | 34.59
| 34.1667 | 133.902 | 168.651 | 37.104 | 25.933 | 46.335 | 34.445
| 34.1736 | 134.216 | 168.308 | 36.903 | 25.857 | 46.067 | 34.292
| 34.1806 | 134.385 | 177.33 | 36.725 | 25.782 | 45.882 | 34.156
| 34.1875 | 134.254 | 177.617 | 36.557 | 25.705 | 45.825 | 34.01
| 34.1944 | 134.248 | 177.947 | 36.405 | 25.634 | 45.68 | 33.871
| 34.2014 | 134.532 | 177.67 | 36.262 | 25.568 | 45.512 | 33.733
| 34.2083 | 140.763 | 186.939 | 36.279 | 25.508 | 45.583 | 33.601
| 34.2153 | 152.466 | 200.644 | 36.366 | 25.433 | 45.637 | 33.466
| 34.2222 | 163.415 | 215.281 | 36.661 | 25.375 | 45.905 | 33.345
| 34.2292 | 166.501 | 218.945 | 37.211 | 25.324 | 46.465 | 33.218
| 34.2361 | 175.281 | 231.178 | 37.926 | 25.286 | 47.112 | 33.1
| 34.2431 | 185.013 | 243.596 | 38.79 | 25.255 | 47.836 | 32.988
| 34.25 | 197.757 | 259.444 | 39.838 | 25.23 | 48.694 | 32.894
| 34.2569 | 208.206 | 281.783 | 41.032 | 25.225 | 49.666 | 32.806
| 34.2639 | 219.569 | 282.192 | 42.363 | 25.228 | 50.642 | 32.724
| 34.2708 | 230.093 | 302.499 | 43.823 | 25.242 | 51.946 | 32.655
| 34.2778 | 242.429 | 318.282 | 45.449 | 25.273 | 53.132 | 32.601
| 34.2847 | 252.955 | 331.439 | 47.188 | 25.32 | 54.386 | 32.566
| 34.2917 | 264.38 | 341.054 | 49.04 | 25.368 | 56.003 | 32.535
| 34.2986 | 263.96 | 353.365 | 51.023 | 25.436 | 57.491 | 32.528
| 34.3056 | 274.315 | 360.759 | 53.237 | 25.525 | 59.1 | 32.534
| 34.3125 | 286.723 | 382.005 | 55.584 | 25.616 | 61.005 | 32.557
| 34.3194 | 302.24 | 396.467 | 58.267 | 25.729 | 63.171 | 32.595
| 34.3264 | 308.645 | 405.296 | 60.898 | 25.858 | 65.049 | 32.654
| 34.3333 | 321.633 | 421.69 | 63.667 | 26.002 | 67.1 | 32.733
| 34.3403 | 323.019 | 424.054 | 66.313 | 26.153 | 68.947 | 32.833
| 34.3472 | 321.773 | 423.982 | 68.539 | 26.32 | 70.114 | 32.953
| 34.3542 | 321.061 | 421.917 | 70.447 | 26.493 | 70.979 | 33.089
| 34.3611 | 320.666 | 420.255 | 72.104 | 26.662 | 71.67 | 33.242
| 34.3681 | 320.668 | 422.137 | 73.57 | 26.82 | 72.314 | 33.403
| 34.375 | 320.939 | 420.2 | 74.873 | 26.972 | 72.92 | 33.571
| 34.3819 | 320.41 | 420.526 | 76.007 | 27.126 | 73.474 | 33.74
| 34.3889 | 321.297 | 413.13 | 77.038 | 27.268 | 73.557 | 33.912
| 34.3958 | 314.951 | 414.125 | 77.949 | 27.407 | 73.852 | 34.083
| 34.4028 | 315.612 | 413.714 | 78.424 | 27.536 | 74.208 | 34.248
| 34.4097 | 315.199 | 414.74 | 78.951 | 27.656 | 74.6 | 34.413
| 34.4167 | 314.301 | 406.343 | 79.429 | 27.771 | 74.739 | 34.562
| 34.4236 | 314.564 | 405.462 | 79.834 | 27.876 | 74.683 | 34.719
| 34.4306 | 306.103 | 397.457 | 79.805 | 27.974 | 74.748 | 34.868
| 34.4375 | 306.438 | 396.682 | 79.775 | 28.063 | 74.364 | 35.003
| 34.4444 | 306.31 | 398.156 | 79.791 | 28.139 | 74.345 | 35.135
| 34.4514 | 297.368 | 388.017 | 79.287 | 28.206 | 73.83 | 35.262
| 34.4583 | 296.479 | 387.002 | 78.944 | 28.263 | 73.639 | 35.37
| 34.4653 | 288.542 | 377.69 | 78.593 | 28.309 | 73.135 | 35.472
| 34.4722 | 288.873 | 378.705 | 77.867 | 28.351 | 72.824 | 35.571
| 34.4792 | 288.54 | 369.173 | 77.38 | 28.374 | 72.387 | 35.653
| 34.4861 | 281.265 | 369.513 | 76.545 | 28.393 | 71.943 | 35.731
| 34.4931 | 280.92 | 360.224 | 75.888 | 28.408 | 71.588 | 35.795
| 34.5 | 273.191 | 360.227 | 75.278 | 28.414 | 71.025 | 35.844
| 34.5069 | 273.128 | 361.506 | 74.369 | 28.405 | 70.805 | 35.89
| 34.5139 | 273.883 | 353.228 | 73.699 | 28.397 | 70.148 | 35.927
| 34.5208 | 274.048 | 352.84 | 73.14 | 28.382 | 69.858 | 35.957
| 34.5278 | 272.994 | 352.193 | 72.646 | 28.364 | 69.661 | 35.976
| 34.5347 | 266.295 | 352.633 | 72.172 | 28.345 | 69.505 | 35.985
| 34.5417 | 266.68 | 353.025 | 71.388 | 28.33 | 69.414 | 35.996
| 34.5486 | 266.125 | 352.959 | 70.799 | 28.307 | 69.306 | 35.995
| 34.5556 | 266.573 | 343.636 | 70.286 | 28.28 | 68.997 | 35.996
| 34.5625 | 265.667 | 344.326 | 69.854 | 28.254 | 68.54 | 35.995
| 34.5694 | 265.495 | 343.543 | 69.45 | 28.225 | 68.255 | 35.989
| 34.5764 | 265.74 | 343.165 | 69.097 | 28.2 | 68.068 | 35.976
| 34.5833 | 265.638 | 344.186 | 68.789 | 28.17 | 67.923 | 35.964
| 34.5903 | 258.502 | 342.395 | 68.175 | 28.145 | 67.803 | 35.951
| 34.5972 | 259.381 | 344.24 | 67.693 | 28.117 | 67.699 | 35.931
| 34.6042 | 259.238 | 343.609 | 67.295 | 28.08 | 67.63 | 35.909
| 34.6111 | 258.992 | 342.917 | 66.934 | 28.049 | 67.54 | 35.889
| 34.6181 | 264.833 | 344.206 | 66.783 | 28.016 | 67.479 | 35.867
| 34.625 | 264.475 | 343.914 | 66.751 | 27.985 | 67.43 | 35.841
| 34.6319 | 264.145 | 343.859 | 66.692 | 27.962 | 67.375 | 35.818
| 34.6389 | 265.048 | 350.2 | 66.644 | 27.942 | 67.608 | 35.794
| 34.6458 | 265.75 | 352.188 | 66.612 | 27.923 | 67.791 | 35.774
| 34.6528 | 265.602 | 351.406 | 66.591 | 27.902 | 67.88 | 35.754
| 34.6597 | 273.347 | 351.116 | 66.71 | 27.887 | 67.906 | 35.738
| 34.6667 | 273.585 | 351.698 | 67.024 | 27.873 | 67.951 | 35.717
| 34.6736 | 270.896 | 360.41 | 67.094 | 27.871 | 68.3 | 35.709
| 34.6806 | 270.297 | 360.813 | 67.197 | 27.862 | 68.633 | 35.695
| 34.6875 | 270.85 | 360.016 | 67.264 | 27.859 | 68.78 | 35.681
| 34.6944 | 271.23 | 361.681 | 67.354 | 27.857 | 68.92 | 35.675
| 34.7014 | 271.585 | 360.882 | 67.419 | 27.851 | 68.999 | 35.674
| 34.7083 | 270.757 | 361.847 | 67.512 | 27.844 | 69.106 | 35.667
| 34.7153 | 271.794 | 361.277 | 67.579 | 27.847 | 69.177 | 35.672
| 34.7222 | 271.013 | 360.402 | 67.618 | 27.842 | 69.201 | 35.675
| 34.7292 | 270.458 | 359.728 | 67.614 | 27.837 | 69.176 | 35.682
| 34.7361 | 276.961 | 358.844 | 67.69 | 27.836 | 69.141 | 35.686
| 34.7431 | 275.292 | 357.648 | 67.981 | 27.835 | 69.082 | 35.691
| 34.75 | 276.829 | 359.348 | 68.217 | 27.838 | 69.114 | 35.698
| 34.7569 | 277.411 | 360.737 | 68.446 | 27.842 | 69.177 | 35.703
| 34.7639 | 277.942 | 360.948 | 68.645 | 27.848 | 69.232 | 35.707
| 34.7708 | 272.715 | 360.372 | 68.763 | 27.857 | 69.298 | 35.711
| 34.7778 | 272.244 | 353.204 | 68.657 | 27.865 | 69.33 | 35.716
| 34.7847 | 272.222 | 353.146 | 68.573 | 27.866 | 68.855 | 35.718
| 34.7917 | 272.684 | 352.631 | 68.528 | 27.865 | 68.703 | 35.731
| 34.7986 | 272.363 | 352.444 | 68.494 | 27.87 | 68.611 | 35.729
| 34.8056 | 264.343 | 353.247 | 68.123 | 27.868 | 68.539 | 35.734
| 34.8125 | 263.948 | 342.977 | 67.801 | 27.86 | 68.048 | 35.726
| 34.8194 | 265.582 | 344.603 | 67.566 | 27.846 | 67.738 | 35.724
| 34.8264 | 265.929 | 344.07 | 67.376 | 27.832 | 67.589 | 35.718
| 34.8333 | 265.695 | 345.163 | 67.218 | 27.82 | 67.492 | 35.708
| 34.8403 | 256.844 | 335.473 | 66.697 | 27.805 | 66.981 | 35.696
| 34.8472 | 256.941 | 326.659 | 66.254 | 27.784 | 66.622 | 35.679
| 34.8542 | 248.168 | 327.365 | 65.629 | 27.762 | 65.968 | 35.667
| 34.8611 | 248.008 | 319.264 | 64.991 | 27.729 | 65.388 | 35.647
| 34.8681 | 240.128 | 318.871 | 64.316 | 27.692 | 64.841 | 35.62
| 34.875 | 237.419 | 305.703 | 63.499 | 27.65 | 64.017 | 35.586
| 34.8819 | 230.282 | 306.419 | 62.775 | 27.607 | 63.371 | 35.549
| 34.8889 | 230.867 | 298.489 | 61.807 | 27.549 | 62.718 | 35.502
| 34.8958 | 230.182 | 298.801 | 61.063 | 27.496 | 62.171 | 35.455
| 34.9028 | 221.646 | 287.384 | 60.058 | 27.437 | 61.311 | 35.399
| 34.9097 | 214.267 | 280.22 | 59.187 | 27.367 | 60.7 | 35.333
| 34.9167 | 214.78 | 280.988 | 58.228 | 27.293 | 59.993 | 35.266
| 34.9236 | 213.883 | 270.349 | 57.404 | 27.223 | 59.267 | 35.196
| 34.9306 | 206.571 | 271.431 | 56.369 | 27.146 | 58.636 | 35.113
| 34.9375 | 199.287 | 262.548 | 55.447 | 27.059 | 57.863 | 35.032
| 34.9444 | 199.269 | 252.86 | 54.501 | 26.979 | 57.243 | 34.943
| 34.9514 | 190.007 | 253.465 | 53.703 | 26.898 | 56.499 | 34.851
| 34.9583 | 189.64 | 243.919 | 52.622 | 26.809 | 55.751 | 34.749
| 34.9653 | 187.303 | 241.391 | 51.694 | 26.716 | 54.992 | 34.643
| 34.9722 | 179.158 | 241.233 | 50.794 | 26.62 | 54.461 | 34.542
| 34.9792 | 178.85 | 229.395 | 49.87 | 26.531 | 53.698 | 34.429
| 34.9861 | 169.716 | 228.231 | 49.065 | 26.43 | 53.083 | 34.315
| 34.9931 | 169.644 | 218.794 | 48.048 | 26.334 | 52.383 | 34.199
| 35 | 170.063 | 218.621 | 47.236 | 26.233 | 51.774 | 34.077
| 35.0069 | 160.078 | 209.39 | 46.248 | 26.134 | 51.026 | 33.952
| 35.0139 | 160.793 | 209.804 | 45.422 | 26.033 | 50.49 | 33.831
| 35.0208 | 160.533 | 200.093 | 44.707 | 25.93 | 50.076 | 33.701
| 35.0278 | 160.35 | 201.161 | 44.061 | 25.829 | 49.397 | 33.563
| 35.0347 | 152.74 | 200.442 | 43.273 | 25.736 | 48.934 | 33.435
| 35.0417 | 152.433 | 199.946 | 42.605 | 25.639 | 48.526 | 33.302
| 35.0486 | 151.977 | 190.345 | 42.014 | 25.537 | 48.113 | 33.164
| 35.0556 | 144.193 | 190.5 | 41.495 | 25.447 | 47.531 | 33.034
| 35.0625 | 143.978 | 190.789 | 40.789 | 25.356 | 47.109 | 32.9
| 35.0694 | 144.551 | 191.053 | 40.233 | 25.259 | 46.765 | 32.763
| 35.0764 | 143.99 | 181.368 | 39.74 | 25.171 | 46.207 | 32.631
| 35.0833 | 136.052 | 181.175 | 39.125 | 25.081 | 45.774 | 32.495
| 35.0903 | 136.156 | 181.44 | 38.586 | 24.994 | 45.422 | 32.365
| 35.0972 | 136.679 | 182.123 | 38.12 | 24.898 | 45.121 | 32.233
| 35.1042 | 136.673 | 181.921 | 37.703 | 24.819 | 44.845 | 32.099
| 35.1111 | 136.619 | 173.899 | 37.329 | 24.733 | 44.504 | 31.966
| 35.1181 | 136.396 | 173.816 | 36.991 | 24.652 | 44.076 | 31.836
| 35.125 | 136.423 | 173.145 | 36.686 | 24.574 | 43.744 | 31.706
| 35.1319 | 136.402 | 173.753 | 36.406 | 24.497 | 43.46 | 31.581
| 35.1389 | 136.529 | 173.563 | 36.156 | 24.424 | 43.203 | 31.456
| 35.1458 | 136.554 | 173.506 | 35.927 | 24.354 | 42.959 | 31.328
| 35.1528 | 136.737 | 173.62 | 35.72 | 24.284 | 42.73 | 31.205
| 35.1597 | 136.717 | 174.058 | 35.537 | 24.217 | 42.52 | 31.088
| 35.1667 | 128.894 | 173.614 | 35.162 | 24.149 | 42.301 | 30.965
| 35.1736 | 129.118 | 173.511 | 34.873 | 24.08 | 42.094 | 30.849
| 35.1806 | 128.72 | 173.412 | 34.625 | 24.016 | 41.897 | 30.731
| 35.1875 | 135.296 | 173.641 | 34.504 | 23.946 | 41.707 | 30.618
| 35.1944 | 135.135 | 181.913 | 34.405 | 23.887 | 41.674 | 30.505
| 35.2014 | 135.401 | 181.653 | 34.304 | 23.829 | 41.628 | 30.397
| 35.2083 | 143.298 | 181.74 | 34.312 | 23.771 | 41.523 | 30.289
| 35.2153 | 151.976 | 193.392 | 34.478 | 23.72 | 41.69 | 30.186
| 35.2222 | 162.989 | 206.905 | 34.79 | 23.674 | 42.053 | 30.082
| 35.2292 | 163.401 | 220.963 | 35.282 | 23.634 | 42.576 | 29.987
| 35.2361 | 175.336 | 236.496 | 36.02 | 23.603 | 43.233 | 29.899
| 35.2431 | 185.143 | 251.672 | 36.905 | 23.579 | 44.006 | 29.807
| 35.25 | 197.817 | 265.88 | 37.976 | 23.573 | 44.849 | 29.732
| 35.2569 | 207.912 | 278.899 | 39.173 | 23.572 | 45.723 | 29.664
| 35.2639 | 218.986 | 287.529 | 40.535 | 23.584 | 46.94 | 29.602
| 35.2708 | 229.787 | 301.534 | 42.033 | 23.612 | 48.078 | 29.56
| 35.2778 | 242.712 | 318.09 | 43.719 | 23.648 | 49.377 | 29.523
| 35.2847 | 248.402 | 326.04 | 45.547 | 23.695 | 50.786 | 29.504
| 35.2917 | 258.88 | 347.241 | 47.473 | 23.766 | 52.204 | 29.498
| 35.2986 | 269.587 | 348.627 | 49.54 | 23.842 | 53.681 | 29.51
| 35.3056 | 279.812 | 368.377 | 51.719 | 23.932 | 55.566 | 29.534
| 35.3125 | 286.255 | 382.24 | 54.042 | 24.038 | 57.214 | 29.578
| 35.3194 | 300.478 | 394.37 | 56.645 | 24.155 | 59.265 | 29.634
| 35.3264 | 309.507 | 404.63 | 59.282 | 24.294 | 61.231 | 29.706
| 35.3333 | 322.924 | 423.346 | 62.071 | 24.442 | 63.288 | 29.801
| 35.3403 | 322.798 | 421.189 | 64.726 | 24.607 | 65.088 | 29.913
| 35.3472 | 321.965 | 422.11 | 66.988 | 24.782 | 66.307 | 30.047
| 35.3542 | 323.051 | 421.66 | 68.984 | 24.959 | 67.268 | 30.198
| 35.3611 | 322.709 | 421.825 | 70.706 | 25.13 | 68.045 | 30.366
| 35.3681 | 322.034 | 421.652 | 72.221 | 25.306 | 68.732 | 30.535
| 35.375 | 321.978 | 419.806 | 73.543 | 25.469 | 69.334 | 30.714
| 35.3819 | 322.401 | 420.55 | 74.733 | 25.628 | 69.914 | 30.9
| 35.3889 | 322.001 | 413.184 | 75.787 | 25.783 | 69.957 | 31.08
| 35.3958 | 316.349 | 413.211 | 76.47 | 25.929 | 70.216 | 31.259
| 35.4028 | 315.757 | 412.752 | 77.062 | 26.063 | 70.54 | 31.44
| 35.4097 | 316.392 | 411.582 | 77.603 | 26.191 | 70.887 | 31.619
| 35.4167 | 316.238 | 411.893 | 78.065 | 26.314 | 71.209 | 31.785
| 35.4236 | 308.22 | 401.808 | 78.347 | 26.429 | 71.363 | 31.95
| 35.4306 | 308.114 | 401.632 | 78.282 | 26.531 | 71.141 | 32.111
| 35.4375 | 307.915 | 401.685 | 78.315 | 26.619 | 71.195 | 32.263
| 35.4444 | 306.46 | 392.733 | 78.315 | 26.705 | 70.688 | 32.407
| 35.4514 | 297.99 | 391.889 | 77.837 | 26.775 | 70.571 | 32.543
| 35.4583 | 297.835 | 384.373 | 77.495 | 26.84 | 70.184 | 32.67
| 35.4653 | 289.911 | 384.663 | 76.891 | 26.891 | 70.01 | 32.787
| 35.4722 | 289.956 | 373.811 | 76.357 | 26.931 | 69.489 | 32.892
| 35.4792 | 282.173 | 373.325 | 75.669 | 26.963 | 69.086 | 32.991
| 35.4861 | 282.223 | 364.527 | 74.961 | 26.987 | 68.671 | 33.081
| 35.4931 | 282.999 | 364.927 | 74.373 | 27.001 | 68.214 | 33.161
| 35.5 | 273.607 | 354.558 | 73.511 | 27.009 | 67.937 | 33.224
| 35.5069 | 274.078 | 354.767 | 72.744 | 27.014 | 67.271 | 33.281
| 35.5139 | 274.117 | 356.557 | 72.11 | 27.008 | 66.992 | 33.329
| 35.5208 | 274.584 | 355.725 | 71.588 | 26.998 | 66.859 | 33.367
| 35.5278 | 274.317 | 355.486 | 71.135 | 26.99 | 66.769 | 33.399
| 35.5347 | 266.359 | 347.847 | 70.671 | 26.981 | 66.617 | 33.428
| 35.5417 | 266.64 | 349.961 | 69.907 | 26.966 | 66.162 | 33.446
| 35.5486 | 266.066 | 347.555 | 69.301 | 26.945 | 65.89 | 33.459
| 35.5556 | 265.724 | 348.766 | 68.8 | 26.924 | 65.732 | 33.473
| 35.5625 | 265.39 | 348.24 | 68.366 | 26.905 | 65.626 | 33.478
| 35.5694 | 265.719 | 348.413 | 67.97 | 26.879 | 65.52 | 33.483
| 35.5764 | 266.242 | 347.936 | 67.632 | 26.855 | 65.439 | 33.487
| 35.5833 | 265.714 | 339.931 | 67.328 | 26.835 | 64.847 | 33.481
| 35.5903 | 265.894 | 338.716 | 67.061 | 26.812 | 64.565 | 33.48
| 35.5972 | 265.419 | 339.637 | 66.831 | 26.792 | 64.38 | 33.474
| 35.6042 | 266.043 | 340.02 | 66.643 | 26.773 | 64.277 | 33.461
| 35.6111 | 265.735 | 340.352 | 66.464 | 26.756 | 64.149 | 33.446
| 35.6181 | 266.484 | 349.287 | 66.34 | 26.735 | 64.376 | 33.429
| 35.625 | 266.457 | 347.602 | 66.222 | 26.718 | 64.64 | 33.415
| 35.6319 | 266.409 | 348.906 | 66.115 | 26.706 | 64.73 | 33.399
| 35.6389 | 266.343 | 349.031 | 66.039 | 26.688 | 64.8 | 33.382
| 35.6458 | 268.18 | 350.34 | 66.002 | 26.678 | 64.872 | 33.37
| 35.6528 | 267.316 | 350.451 | 65.973 | 26.67 | 64.919 | 33.365
| 35.6597 | 267.813 | 350.384 | 65.937 | 26.657 | 64.935 | 33.353
| 35.6667 | 268.018 | 351.191 | 65.928 | 26.648 | 64.966 | 33.349
| 35.6736 | 268.117 | 360.362 | 65.931 | 26.64 | 65.403 | 33.339
| 35.6806 | 268.919 | 360.424 | 65.941 | 26.632 | 65.748 | 33.334
| 35.6875 | 268.186 | 360.255 | 65.957 | 26.625 | 65.942 | 33.338
| 35.6944 | 268.877 | 361.166 | 65.976 | 26.622 | 66.079 | 33.342
| 35.7014 | 269.057 | 361.429 | 65.998 | 26.616 | 66.189 | 33.343
| 35.7083 | 274.372 | 356.796 | 66.047 | 26.614 | 66.262 | 33.35
| 35.7153 | 273.581 | 357.832 | 66.3 | 26.608 | 66.094 | 33.361
| 35.7222 | 272.015 | 354.381 | 66.418 | 26.611 | 65.993 | 33.373
| 35.7292 | 270.917 | 353.347 | 66.455 | 26.61 | 65.853 | 33.381
| 35.7361 | 274.666 | 358.833 | 66.643 | 26.614 | 65.999 | 33.393
| 35.7431 | 272.892 | 356.878 | 66.75 | 26.613 | 66.035 | 33.402
| 35.75 | 274.063 | 357.725 | 66.796 | 26.62 | 65.98 | 33.41
| 35.7569 | 272.42 | 355.524 | 66.858 | 26.624 | 65.99 | 33.419
| 35.7639 | 272.231 | 356.063 | 66.885 | 26.63 | 65.95 | 33.428
| 35.7708 | 272.485 | 355.017 | 66.899 | 26.632 | 65.931 | 33.432
| 35.7778 | 272.196 | 356.167 | 66.911 | 26.631 | 65.925 | 33.44
| 35.8125 | 266.936 | 348.654 | 66.516 | 26.635 | 65.209 | 33.468
| 35.8194 | 267.276 | 348.418 | 66.384 | 26.629 | 65.167 | 33.471
| 35.8264 | 268.305 | 340.491 | 66.285 | 26.623 | 64.847 | 33.474
| 35.8333 | 260.762 | 340.644 | 65.814 | 26.618 | 64.536 | 33.472
| 35.8403 | 261.047 | 340.627 | 65.495 | 26.604 | 64.369 | 33.463
| 35.8472 | 251.828 | 331.618 | 65.074 | 26.583 | 63.384 | 33.455
| 35.8542 | 250.977 | 322.856 | 64.443 | 26.57 | 63.249 | 33.452
| 35.8611 | 250.938 | 323.117 | 63.933 | 26.534 | 62.619 | 33.426
| 35.8681 | 242.577 | 313.584 | 63.082 | 26.504 | 62.013 | 33.407
| 35.875 | 235.497 | 313.416 | 62.314 | 26.467 | 61.464 | 33.381
| 35.8819 | 231.964 | 300.377 | 61.451 | 26.426 | 60.683 | 33.355
| 35.8889 | 232.462 | 300.513 | 60.645 | 26.366 | 60.018 | 33.309
| 35.8958 | 224.17 | 299.08 | 59.733 | 26.315 | 59.567 | 33.265
| 35.9028 | 223.592 | 289.46 | 58.854 | 26.253 | 58.714 | 33.216
| 35.9097 | 215.382 | 280.506 | 57.967 | 26.187 | 58.055 | 33.167
| 35.9167 | 215.883 | 281.592 | 57.051 | 26.119 | 57.433 | 33.1
| 35.9236 | 208.112 | 272.493 | 56.063 | 26.045 | 56.732 | 33.029
| 35.9306 | 209.257 | 274.022 | 55.184 | 25.972 | 56.211 | 32.958
| 35.9375 | 201.963 | 262.866 | 54.164 | 25.89 | 55.367 | 32.883
| 35.9444 | 199.781 | 260.831 | 53.266 | 25.811 | 54.759 | 32.801
| 35.9514 | 192.833 | 250.766 | 52.277 | 25.719 | 53.973 | 32.71
| 35.9583 | 184.814 | 241.498 | 51.416 | 25.632 | 53.407 | 32.621
| 35.9653 | 184.623 | 242.532 | 50.365 | 25.544 | 52.616 | 32.523
| 35.9722 | 185.287 | 233.469 | 49.524 | 25.451 | 51.935 | 32.422
| 35.9792 | 176.874 | 234.318 | 48.544 | 25.354 | 51.322 | 32.318
| 35.9861 | 176.807 | 224.034 | 47.7 | 25.257 | 50.583 | 32.207
| 35.9931 | 167.698 | 215.32 | 46.767 | 25.164 | 50.012 | 32.098
| 36 | 166.179 | 212.596 | 45.897 | 25.069 | 49.252 | 31.986
| 36.0069 | 166.2 | 212.807 | 45.096 | 24.962 | 48.68 | 31.861
| 36.0139 | 158.802 | 212.656 | 44.208 | 24.862 | 48.237 | 31.743
| 36.0208 | 158.452 | 203.832 | 43.437 | 24.765 | 47.615 | 31.612
| 36.0278 | 158.946 | 203.894 | 42.777 | 24.666 | 47.132 | 31.491
| 36.0347 | 158.574 | 203.212 | 42.165 | 24.568 | 46.72 | 31.364
| 36.0417 | 149.127 | 194.075 | 41.391 | 24.472 | 46.208 | 31.235
| 36.0486 | 149.603 | 194.122 | 40.742 | 24.379 | 45.697 | 31.108
| 36.0556 | 149.534 | 194.856 | 40.18 | 24.283 | 45.316 | 30.979
| 36.0625 | 142.039 | 186.449 | 39.682 | 24.188 | 44.824 | 30.853
| 36.0694 | 142.283 | 186.968 | 39.028 | 24.1 | 44.39 | 30.722
| 36.0764 | 142.122 | 187.135 | 38.494 | 24.013 | 44.039 | 30.588
| 36.0833 | 142.012 | 177.587 | 38.013 | 23.922 | 43.492 | 30.464
| 36.0903 | 141.84 | 177.812 | 37.591 | 23.832 | 43.079 | 30.334
| 36.0972 | 134.515 | 177.677 | 37.078 | 23.75 | 42.748 | 30.207
| 36.1042 | 134.977 | 177.846 | 36.604 | 23.67 | 42.461 | 30.082
| 36.1111 | 134.682 | 178.413 | 36.187 | 23.581 | 42.192 | 29.952
| 36.1181 | 134.588 | 178.428 | 35.814 | 23.502 | 41.938 | 29.83
| 36.125 | 134.611 | 178.287 | 35.479 | 23.421 | 41.695 | 29.704
| 36.1319 | 134.755 | 178.292 | 35.177 | 23.35 | 41.469 | 29.583
| 36.1389 | 134.987 | 178.341 | 34.919 | 23.274 | 41.253 | 29.466
| 36.1458 | 135.015 | 178.242 | 34.664 | 23.201 | 41.033 | 29.345
| 36.1528 | 134.518 | 170.105 | 34.438 | 23.13 | 40.635 | 29.227
| 36.1597 | 134.625 | 170.386 | 34.232 | 23.07 | 40.345 | 29.116
| 36.1667 | 134.747 | 170.041 | 34.044 | 22.997 | 40.08 | 29.001
| 36.1736 | 134.505 | 170.152 | 33.87 | 22.937 | 39.861 | 28.889
| 36.1806 | 134.645 | 170.484 | 33.707 | 22.875 | 39.655 | 28.78
| 36.1875 | 134.913 | 177.648 | 33.564 | 22.813 | 39.64 | 28.665
| 36.1944 | 134.519 | 177.867 | 33.43 | 22.75 | 39.554 | 28.559
| 36.2014 | 134.725 | 177.427 | 33.301 | 22.693 | 39.428 | 28.455
| 36.2083 | 140.988 | 186.678 | 33.349 | 22.638 | 39.541 | 28.35
| 36.2153 | 151.189 | 198.719 | 33.475 | 22.588 | 39.672 | 28.248
| 36.2222 | 162.335 | 213.055 | 33.792 | 22.54 | 40.004 | 28.152
| 36.2292 | 173.887 | 227.434 | 34.285 | 22.5 | 40.485 | 28.06
| 36.2361 | 173.309 | 227.053 | 34.96 | 22.471 | 41.058 | 27.975
| 36.2431 | 184.32 | 243.004 | 35.848 | 22.451 | 41.895 | 27.891
| 36.25 | 195.256 | 257.052 | 36.903 | 22.441 | 42.775 | 27.819
| 36.2569 | 209.42 | 282.384 | 38.147 | 22.437 | 43.869 | 27.756
| 36.2639 | 218.981 | 293.188 | 39.527 | 22.456 | 44.926 | 27.705
| 36.2708 | 228.744 | 299.403 | 41.004 | 22.483 | 46.121 | 27.663
| 36.2778 | 242.584 | 312.076 | 42.681 | 22.523 | 47.354 | 27.637
| 36.2847 | 251.523 | 331.128 | 44.496 | 22.571 | 48.842 | 27.622
| 36.2917 | 263.115 | 345.181 | 46.365 | 22.631 | 50.154 | 27.621
| 36.2986 | 274.7 | 359.594 | 48.348 | 22.714 | 51.547 | 27.638
| 36.3056 | 272.742 | 358.477 | 50.456 | 22.804 | 53.116 | 27.664
| 36.3125 | 288.369 | 377.004 | 52.98 | 22.909 | 55.131 | 27.712
| 36.3194 | 296.013 | 394.109 | 55.43 | 23.034 | 57.095 | 27.768
| 36.3264 | 307.784 | 403.577 | 58.071 | 23.164 | 59.063 | 27.846
| 36.3333 | 321.718 | 420.794 | 60.942 | 23.316 | 61.249 | 27.949
| 36.3403 | 321.226 | 420.476 | 63.502 | 23.479 | 62.887 | 28.062
| 36.3472 | 321.262 | 420.365 | 65.697 | 23.657 | 64.019 | 28.2
| 36.3542 | 321.001 | 419.731 | 67.608 | 23.833 | 64.901 | 28.354
| 36.3611 | 320.655 | 418.343 | 69.27 | 24.007 | 65.628 | 28.525
| 36.3681 | 320.525 | 418.735 | 70.73 | 24.172 | 66.3 | 28.7
| 36.375 | 320.851 | 418.397 | 72.019 | 24.336 | 66.921 | 28.877
| 36.3819 | 319.799 | 418.42 | 73.179 | 24.491 | 67.506 | 29.064
| 36.3889 | 320.288 | 418.45 | 74.177 | 24.646 | 67.997 | 29.25
| 36.3958 | 321.087 | 410.104 | 75.133 | 24.791 | 68.375 | 29.432
| 36.4028 | 313.823 | 409.691 | 75.643 | 24.928 | 68.399 | 29.615
| 36.4097 | 313.569 | 409.278 | 76.084 | 25.061 | 68.601 | 29.792
| 36.4167 | 315.373 | 413.011 | 76.624 | 25.177 | 69.055 | 29.967
| 36.4236 | 307.977 | 402.256 | 76.867 | 25.289 | 69.152 | 30.135
| 36.4306 | 308.273 | 403.307 | 76.902 | 25.392 | 69.029 | 30.295
| 36.4375 | 300.518 | 391.593 | 76.932 | 25.486 | 69.067 | 30.453
| 36.4444 | 300.423 | 391.835 | 76.589 | 25.566 | 68.612 | 30.605
| 36.4514 | 300.025 | 393.281 | 76.402 | 25.637 | 68.547 | 30.74
| 36.4583 | 293.035 | 383.276 | 76.012 | 25.701 | 68.01 | 30.876
| 36.4653 | 292.409 | 383.459 | 75.517 | 25.753 | 67.825 | 30.994
| 36.4722 | 291.715 | 375.265 | 75.114 | 25.804 | 67.348 | 31.105
| 36.4792 | 283.347 | 374.92 | 74.436 | 25.838 | 67.077 | 31.211
| 36.4861 | 282.637 | 365.471 | 73.796 | 25.865 | 66.645 | 31.301
| 36.4931 | 276.204 | 365.994 | 73.058 | 25.886 | 66.201 | 31.383
| 36.5 | 276.58 | 354.895 | 72.296 | 25.893 | 65.844 | 31.454
| 36.5069 | 276.978 | 355.547 | 71.7 | 25.901 | 65.28 | 31.516
| 36.5139 | 275.505 | 353.271 | 71.083 | 25.9 | 64.865 | 31.572
| 36.5208 | 275.595 | 354.51 | 70.601 | 25.893 | 64.681 | 31.615
| 36.5278 | 268.234 | 354.283 | 69.813 | 25.889 | 64.558 | 31.652
| 36.5347 | 269.226 | 354.118 | 69.205 | 25.876 | 64.481 | 31.681
| 36.5417 | 268.303 | 354.559 | 68.69 | 25.858 | 64.418 | 31.706
| 36.5486 | 267.708 | 345.489 | 68.202 | 25.839 | 63.984 | 31.725
| 36.5556 | 267.546 | 344.415 | 67.768 | 25.822 | 63.606 | 31.744
| 36.5625 | 266.903 | 344.632 | 67.391 | 25.807 | 63.385 | 31.75
| 36.5694 | 267.135 | 344.744 | 67.057 | 25.786 | 63.225 | 31.763
| 36.5764 | 267.11 | 343.272 | 66.72 | 25.77 | 63.054 | 31.77
| 36.5833 | 259.853 | 343.012 | 66.173 | 25.75 | 62.903 | 31.771
| 36.5903 | 258.8 | 343.352 | 65.626 | 25.729 | 62.767 | 31.767
| 36.5972 | 259.864 | 342.94 | 65.174 | 25.702 | 62.685 | 31.765
| 36.6042 | 258.38 | 342.818 | 64.786 | 25.674 | 62.613 | 31.757
| 36.6111 | 259.19 | 343.167 | 64.43 | 25.647 | 62.528 | 31.751
| 36.6181 | 259.162 | 343.781 | 64.144 | 25.619 | 62.481 | 31.742
| 36.625 | 266.414 | 343.632 | 64.097 | 25.594 | 62.456 | 31.733
| 36.6319 | 292.144 | 382.99 | 64.792 | 25.575 | 63.463 | 31.727
| 36.6389 | 291.738 | 382.094 | 65.982 | 25.568 | 65.145 | 31.717
| 36.6458 | 293.084 | 382.638 | 66.896 | 25.585 | 65.967 | 31.712
| 36.6528 | 293.188 | 382.563 | 67.674 | 25.615 | 66.468 | 31.72
| 36.6597 | 293.665 | 383.214 | 68.404 | 25.649 | 66.898 | 31.74
| 36.6667 | 293.764 | 391.413 | 69.045 | 25.687 | 67.442 | 31.769
| 36.6736 | 294.178 | 392.816 | 69.601 | 25.728 | 68.072 | 31.805
| 36.6806 | 294.418 | 392.389 | 70.096 | 25.767 | 68.487 | 31.851
| 36.6875 | 294.956 | 393.405 | 70.588 | 25.808 | 68.887 | 31.899
| 36.6944 | 302.358 | 393.708 | 71.223 | 25.846 | 69.173 | 31.955
| 36.7014 | 302.948 | 394.367 | 71.929 | 25.889 | 69.46 | 32.009
| 36.7083 | 301.495 | 393.437 | 72.506 | 25.94 | 69.689 | 32.072
| 36.7153 | 302.524 | 394.169 | 73.003 | 25.984 | 69.881 | 32.141
| 36.7222 | 302.212 | 402.214 | 73.442 | 26.038 | 70.474 | 32.204
| 36.7292 | 302.21 | 402.014 | 73.807 | 26.087 | 70.999 | 32.265
| 36.7361 | 301.003 | 402.318 | 74.144 | 26.135 | 71.365 | 32.339
| 36.7431 | 301.224 | 391.815 | 74.395 | 26.179 | 71.082 | 32.409
| 36.75 | 296.771 | 387.889 | 74.524 | 26.222 | 70.847 | 32.48
| 36.7569 | 297.877 | 387.889 | 74.559 | 26.264 | 70.671 | 32.549
| 36.7639 | 291.35 | 380.146 | 74.406 | 26.297 | 70.302 | 32.621
| 36.7708 | 290.85 | 378.804 | 74.181 | 26.322 | 69.977 | 32.681
| 36.7778 | 283.638 | 370.856 | 73.891 | 26.347 | 69.687 | 32.737
| 36.7847 | 283.458 | 371.039 | 73.351 | 26.364 | 69.166 | 32.793
| 36.7917 | 283.759 | 370.727 | 72.954 | 26.368 | 68.935 | 32.838
| 36.7986 | 274.875 | 363.367 | 72.353 | 26.377 | 68.289 | 32.874
| 36.8056 | 276.148 | 363.63 | 71.723 | 26.371 | 68.023 | 32.912
| 36.8125 | 269.094 | 354.002 | 71.125 | 26.366 | 67.402 | 32.936
| 36.8194 | 268.607 | 354.732 | 70.346 | 26.346 | 66.984 | 32.957
| 36.8264 | 269.637 | 347.086 | 69.765 | 26.328 | 66.459 | 32.961
| 36.8333 | 261.701 | 345.707 | 68.863 | 26.296 | 65.997 | 32.971
| 36.8403 | 260.561 | 345.745 | 68.122 | 26.268 | 65.658 | 32.969
| 36.8472 | 260.424 | 336.26 | 67.483 | 26.228 | 64.942 | 32.964
| 36.8542 | 253.435 | 337.412 | 66.647 | 26.197 | 64.522 | 32.955
| 36.8611 | 252.807 | 326.311 | 65.898 | 26.147 | 63.883 | 32.931
| 36.8681 | 253.176 | 325.566 | 65.224 | 26.1 | 63.273 | 32.916
| 36.875 | 244.352 | 318.787 | 64.259 | 26.055 | 62.739 | 32.884
| 36.8819 | 244.675 | 319.265 | 63.496 | 25.995 | 62.185 | 32.854
| 36.8889 | 236.728 | 306.978 | 62.539 | 25.935 | 61.354 | 32.808
| 36.8958 | 236.027 | 307.287 | 61.686 | 25.88 | 60.727 | 32.764
| 36.9028 | 226.642 | 295.185 | 60.722 | 25.81 | 59.962 | 32.711
| 36.9097 | 227.129 | 296.117 | 59.787 | 25.739 | 59.247 | 32.649
| 36.9167 | 217.276 | 285.531 | 58.632 | 25.668 | 58.398 | 32.586
| 36.9236 | 207.368 | 272.989 | 57.371 | 25.58 | 57.346 | 32.519
| 36.9306 | 208.08 | 273.034 | 56.241 | 25.497 | 56.568 | 32.439
| 36.9375 | 198.406 | 264.532 | 55.084 | 25.409 | 55.664 | 32.362
| 36.9444 | 198.463 | 256.915 | 53.959 | 25.309 | 54.765 | 32.266
| 36.9514 | 188.279 | 246.334 | 52.685 | 25.212 | 53.802 | 32.169
| 36.9583 | 178.5 | 236.337 | 51.549 | 25.106 | 52.862 | 32.074
| 36.9653 | 178.816 | 237.156 | 50.281 | 25 | 52.135 | 31.963
| 36.9722 | 179.403 | 237.679 | 49.236 | 24.887 | 51.591 | 31.841
| 36.9792 | 179.006 | 228.11 | 48.336 | 24.777 | 50.825 | 31.725
| 36.9861 | 171.793 | 228.51 | 47.477 | 24.666 | 50.268 | 31.599
| 36.9931 | 170.372 | 225.685 | 46.528 | 24.561 | 49.77 | 31.47
| 37 | 169.291 | 225.006 | 45.676 | 24.454 | 49.278 | 31.343
| 37.0069 | 169.386 | 215.919 | 44.94 | 24.349 | 48.708 | 31.212
| 37.0139 | 169.326 | 216.053 | 44.289 | 24.24 | 48.138 | 31.079
| 37.0208 | 160.911 | 216.239 | 43.496 | 24.142 | 47.713 | 30.946
| 37.0278 | 160.744 | 207.409 | 42.808 | 24.039 | 47.335 | 30.814
| 37.0347 | 159.888 | 206.008 | 42.174 | 23.946 | 46.688 | 30.686
| 37.0417 | 154.509 | 208.078 | 41.53 | 23.843 | 46.272 | 30.553
| 37.0486 | 154.345 | 199.934 | 40.892 | 23.749 | 45.828 | 30.417
| 37.0556 | 154.396 | 200.248 | 40.337 | 23.643 | 45.312 | 30.286
| 37.0625 | 154.564 | 200.763 | 39.855 | 23.557 | 44.942 | 30.155
| 37.0694 | 154.883 | 200.358 | 39.425 | 23.465 | 44.616 | 30.028
| 37.0764 | 144.724 | 189.979 | 38.912 | 23.377 | 44.168 | 29.893
| 37.0833 | 144.979 | 190.229 | 38.344 | 23.291 | 43.659 | 29.764
| 37.0903 | 145.264 | 189.988 | 37.867 | 23.205 | 43.288 | 29.636
| 37.0972 | 145.49 | 190.623 | 37.444 | 23.119 | 42.972 | 29.504
| 37.1042 | 145.719 | 190.711 | 37.077 | 23.034 | 42.704 | 29.381
| 37.1111 | 145.651 | 191.246 | 36.741 | 22.953 | 42.449 | 29.244
| 37.1181 | 145.819 | 191.206 | 36.446 | 22.875 | 42.214 | 29.13
| 37.125 | 145.742 | 190.736 | 36.175 | 22.8 | 41.971 | 29.004
| 37.1319 | 145.98 | 191.026 | 35.927 | 22.726 | 41.748 | 28.881
| 37.1389 | 145.555 | 190.985 | 35.705 | 22.654 | 41.526 | 28.761
| 37.1458 | 145.243 | 190.931 | 35.501 | 22.585 | 41.319 | 28.645
| 37.1528 | 145.766 | 190.867 | 35.313 | 22.523 | 41.12 | 28.535
| 37.1597 | 151.943 | 200.796 | 35.282 | 22.46 | 41.167 | 28.42
| 37.1667 | 160.068 | 211.922 | 35.408 | 22.398 | 41.392 | 28.305
| 37.1736 | 159.646 | 212.225 | 35.531 | 22.348 | 41.517 | 28.206
| 37.1806 | 170.114 | 223.914 | 35.928 | 22.292 | 41.898 | 28.097
| 37.1875 | 178.686 | 245.937 | 36.316 | 22.252 | 42.32 | 27.998
| 37.1944 | 185.703 | 245.71 | 36.832 | 22.217 | 42.737 | 27.908
| 37.2014 | 186.015 | 245.246 | 37.437 | 22.193 | 43.132 | 27.819
| 37.2083 | 196.153 | 258.26 | 38.119 | 22.166 | 43.603 | 27.741
| 37.2153 | 202.892 | 267.88 | 38.923 | 22.16 | 44.19 | 27.675
| 37.2222 | 211.285 | 278.891 | 39.811 | 22.153 | 44.844 | 27.608
| 37.2292 | 219.063 | 288.522 | 40.776 | 22.16 | 45.564 | 27.554
| 37.2361 | 231.014 | 298.223 | 41.84 | 22.175 | 46.591 | 27.515
| 37.2431 | 238.168 | 313.063 | 43.408 | 22.195 | 47.706 | 27.478
| 37.25 | 250.806 | 331.134 | 45.009 | 22.23 | 49.252 | 27.45
| 37.2569 | 260.784 | 342.554 | 46.948 | 22.282 | 50.824 | 27.44
| 37.2639 | 270.43 | 359.427 | 48.998 | 22.353 | 52.566 | 27.443
| 37.2708 | 290.615 | 382.738 | 51.234 | 22.438 | 54.293 | 27.459
| 37.2778 | 295.805 | 389.588 | 53.843 | 22.537 | 56.421 | 27.49
| 37.2847 | 309.281 | 407.249 | 56.472 | 22.654 | 58.629 | 27.546
| 37.2917 | 322.796 | 420.431 | 59.286 | 22.795 | 60.85 | 27.62
| 37.2986 | 333.117 | 431.551 | 62.297 | 22.95 | 63.215 | 27.716
| 37.3056 | 341.964 | 450.233 | 65.279 | 23.121 | 65.386 | 27.836
| 37.3125 | 341.688 | 447.605 | 68.421 | 23.31 | 67.557 | 27.978
| 37.3194 | 348.005 | 459.262 | 71.52 | 23.511 | 69.82 | 28.147
| 37.3264 | 347.048 | 458.166 | 74.111 | 23.72 | 71.27 | 28.332
| 37.3333 | 349.091 | 452.209 | 76.456 | 23.94 | 72.385 | 28.537
| 37.3403 | 346.642 | 452.036 | 78.532 | 24.154 | 72.869 | 28.76
| 37.3472 | 342.707 | 450.535 | 79.856 | 24.366 | 73.473 | 28.993
| 37.3542 | 342.279 | 450.272 | 81.115 | 24.558 | 74.072 | 29.221
| 37.3611 | 341.686 | 448.739 | 82.196 | 24.743 | 74.603 | 29.46
| 37.3681 | 343.082 | 443.035 | 83.304 | 24.918 | 74.787 | 29.693
| 37.375 | 335.134 | 442.154 | 83.916 | 25.086 | 75.06 | 29.92
| 37.3819 | 336.001 | 442.186 | 84.425 | 25.242 | 75.445 | 30.147
| 37.3889 | 335.809 | 443.573 | 84.932 | 25.386 | 75.889 | 30.363
| 37.3958 | 336.234 | 433.074 | 85.418 | 25.526 | 75.732 | 30.578
| 37.4028 | 328.245 | 432.766 | 85.431 | 25.678 | 75.805 | 30.804
| 37.4097 | 328.242 | 433.609 | 85.458 | 25.801 | 76.018 | 31.016
| 37.4167 | 327.618 | 424.571 | 85.49 | 25.912 | 75.61 | 31.196
| 37.4236 | 319.991 | 424.703 | 85.061 | 26.003 | 75.601 | 31.376
| 37.4306 | 320.524 | 416.872 | 84.784 | 26.077 | 75.125 | 31.533
| 37.4375 | 312.437 | 415.53 | 84.531 | 26.15 | 75.048 | 31.693
| 37.4444 | 312.511 | 407.066 | 83.868 | 26.215 | 74.626 | 31.834
| 37.4514 | 312.356 | 407.246 | 83.408 | 26.269 | 74.349 | 31.968
| 37.4583 | 303.237 | 405.77 | 82.728 | 26.312 | 74.205 | 32.098
| 37.4653 | 302.902 | 397.638 | 81.929 | 26.346 | 73.543 | 32.209
| 37.4722 | 303.029 | 397.933 | 81.304 | 26.374 | 73.228 | 32.317
| 37.4792 | 295.147 | 388.817 | 80.457 | 26.392 | 72.711 | 32.408
| 37.4861 | 295.902 | 388.92 | 79.677 | 26.411 | 72.318 | 32.495
| 37.4931 | 295.736 | 389.484 | 78.992 | 26.411 | 72.086 | 32.568
| 37.5 | 296.479 | 389.152 | 78.439 | 26.412 | 72.002 | 32.638
| 37.5069 | 296.528 | 379.878 | 77.944 | 26.382 | 71.452 | 32.667
| 37.5139 | 289.369 | 381.762 | 77.258 | 26.378 | 71.117 | 32.714
| 37.5208 | 289.112 | 380.864 | 76.627 | 26.371 | 70.97 | 32.754
| 37.5278 | 288.989 | 379.179 | 76.055 | 26.358 | 70.805 | 32.795
| 37.5347 | 288.823 | 379.932 | 75.56 | 26.346 | 70.685 | 32.825
| 37.5417 | 281.313 | 371.01 | 75.079 | 26.331 | 70.148 | 32.856
| 37.5486 | 281.559 | 371.518 | 74.279 | 26.315 | 69.732 | 32.874
| 37.5556 | 281.08 | 370.964 | 73.7 | 26.296 | 69.516 | 32.894
| 37.5625 | 281.813 | 370.207 | 73.159 | 26.271 | 69.312 | 32.909
| 37.5694 | 281.29 | 369.987 | 72.695 | 26.246 | 69.169 | 32.916
| 37.5764 | 280.996 | 370.246 | 72.287 | 26.223 | 69.056 | 32.919
| 37.5833 | 281.299 | 371.442 | 71.952 | 26.2 | 68.983 | 32.921
| 37.5903 | 282.415 | 371.209 | 71.69 | 26.176 | 68.974 | 32.921
| 37.5972 | 279.375 | 368.488 | 71.438 | 26.158 | 68.911 | 32.917
| 37.6042 | 285.678 | 378.46 | 71.39 | 26.135 | 69.185 | 32.916
| 37.6111 | 285.515 | 378.204 | 71.366 | 26.117 | 69.374 | 32.916
| 37.6181 | 286.338 | 377.856 | 71.34 | 26.11 | 69.468 | 32.911
| 37.625 | 286.078 | 378.491 | 71.318 | 26.099 | 69.541 | 32.916
| 37.6319 | 286.744 | 378.545 | 71.312 | 26.09 | 69.611 | 32.918
| 37.6389 | 293.353 | 379.75 | 71.431 | 26.084 | 69.655 | 32.922
| 37.6458 | 294.637 | 389.294 | 71.807 | 26.078 | 69.821 | 32.933
| 37.6528 | 293.795 | 389.069 | 72.11 | 26.085 | 70.456 | 32.94
| 37.6597 | 294.559 | 390.014 | 72.363 | 26.096 | 70.76 | 32.947
| 37.6667 | 294.373 | 389.995 | 72.586 | 26.103 | 70.958 | 32.964
| 37.6736 | 294.507 | 388.488 | 72.754 | 26.121 | 71.058 | 32.98
| 37.6806 | 294.602 | 390.244 | 72.92 | 26.13 | 71.172 | 33.003
| 37.6875 | 295.489 | 389.676 | 73.081 | 26.147 | 71.299 | 33.025
| 37.6944 | 303.111 | 390.107 | 73.483 | 26.154 | 71.414 | 33.053
| 37.7014 | 303.727 | 399.6 | 73.987 | 26.177 | 71.805 | 33.08
| 37.7083 | 303.606 | 399.691 | 74.392 | 26.195 | 72.336 | 33.102
| 37.7153 | 303.152 | 399.075 | 74.744 | 26.224 | 72.634 | 33.139
| 37.7222 | 302.709 | 398.876 | 75.03 | 26.248 | 72.821 | 33.172
| 37.7292 | 302.44 | 397.505 | 75.268 | 26.275 | 72.944 | 33.207
| 37.7361 | 301.316 | 398.174 | 75.461 | 26.301 | 73.043 | 33.248
| 37.7431 | 300.9 | 396.134 | 75.578 | 26.326 | 73.049 | 33.289
| 37.75 | 299.443 | 386.176 | 75.644 | 26.354 | 72.971 | 33.333
| 37.7569 | 300.581 | 388.478 | 75.662 | 26.374 | 72.422 | 33.374
| 37.7639 | 293.175 | 388.311 | 75.316 | 26.394 | 72.318 | 33.412
| 37.7708 | 293.126 | 379.721 | 75.105 | 26.404 | 71.673 | 33.449
| 37.7778 | 285.78 | 378.495 | 74.563 | 26.413 | 71.375 | 33.48
| 37.7847 | 285.635 | 368.63 | 74.102 | 26.413 | 70.708 | 33.506
| 37.7917 | 278.457 | 368.543 | 73.448 | 26.401 | 70.261 | 33.53
| 37.7986 | 277.525 | 369.249 | 72.815 | 26.392 | 69.994 | 33.542
| 37.8056 | 278.318 | 358.226 | 72.294 | 26.373 | 69.205 | 33.556
| 37.8125 | 270.314 | 359.554 | 71.484 | 26.353 | 68.793 | 33.561
| 37.8194 | 271.369 | 352.848 | 70.84 | 26.323 | 68.204 | 33.557
| 37.8264 | 264.537 | 352.71 | 70.039 | 26.292 | 67.827 | 33.547
| 37.8333 | 264.084 | 343.816 | 69.277 | 26.249 | 67.04 | 33.534
| 37.8403 | 259.246 | 337.42 | 68.517 | 26.208 | 66.448 | 33.513
| 37.8472 | 259.375 | 339.024 | 67.766 | 26.162 | 65.895 | 33.479
| 37.8542 | 252.518 | 329.734 | 66.887 | 26.117 | 65.506 | 33.445
| 37.8611 | 252.974 | 330.3 | 66.119 | 26.06 | 64.777 | 33.41
| 37.8681 | 253.07 | 329.211 | 65.442 | 26.003 | 64.343 | 33.365
| 37.875 | 244.154 | 320.858 | 64.421 | 25.94 | 63.573 | 33.318
| 37.8819 | 243.276 | 312.455 | 63.637 | 25.881 | 62.993 | 33.266
| 37.8889 | 237.062 | 312.474 | 62.675 | 25.822 | 62.261 | 33.204
| 37.8958 | 235.996 | 312.504 | 61.832 | 25.744 | 61.79 | 33.138
| 37.9028 | 227.339 | 302.513 | 60.876 | 25.676 | 60.936 | 33.07
| 37.9097 | 227.324 | 294.176 | 59.933 | 25.592 | 60.013 | 32.995
| 37.9167 | 216.664 | 285.497 | 58.762 | 25.516 | 59.106 | 32.918
| 37.9236 | 207.617 | 272.98 | 57.702 | 25.422 | 58.05 | 32.831
| 37.9306 | 208.5 | 274.335 | 56.47 | 25.337 | 57.274 | 32.746
| 37.9375 | 200.474 | 264.635 | 55.189 | 25.239 | 56.303 | 32.647
| 37.9444 | 191.314 | 255.376 | 53.988 | 25.132 | 55.318 | 32.544
| 37.9514 | 190.86 | 242.549 | 52.781 | 25.031 | 54.506 | 32.429
| 37.9583 | 178.977 | 242.713 | 51.193 | 24.915 | 53.544 | 32.315
| 37.9653 | 179.062 | 232.4 | 50.118 | 24.807 | 52.673 | 32.197
| 37.9722 | 179.921 | 233.173 | 49.102 | 24.68 | 51.941 | 32.067
| 37.9792 | 177.841 | 230.635 | 48.179 | 24.559 | 51.338 | 31.933
| 37.9861 | 178.003 | 230.638 | 47.341 | 24.45 | 50.818 | 31.799
| 37.9931 | 177.688 | 221.228 | 46.6 | 24.336 | 50.124 | 31.66
| 38 | 171.446 | 221.368 | 45.801 | 24.228 | 49.534 | 31.522
| 38.0069 | 171.31 | 221.837 | 45.07 | 24.125 | 49.085 | 31.381
| 38.0139 | 163.288 | 221.601 | 44.2 | 24.011 | 48.669 | 31.233
| 38.0208 | 163.17 | 212.462 | 43.456 | 23.905 | 48.031 | 31.093
| 38.0278 | 163.838 | 212.683 | 42.809 | 23.803 | 47.543 | 30.951
| 38.0347 | 163.654 | 212.544 | 42.232 | 23.7 | 47.132 | 30.807
| 38.0417 | 154.767 | 201.875 | 41.458 | 23.605 | 46.583 | 30.67
| 38.0486 | 155.211 | 202.023 | 40.826 | 23.499 | 46.025 | 30.527
| 38.0556 | 155.365 | 202.4 | 40.28 | 23.397 | 45.611 | 30.384
| 38.0625 | 155.248 | 202.349 | 39.792 | 23.299 | 45.263 | 30.247
| 38.0694 | 155.198 | 193.975 | 39.349 | 23.203 | 44.769 | 30.103
| 38.0764 | 146.944 | 193.667 | 38.833 | 23.113 | 44.292 | 29.962
| 38.0833 | 147.387 | 193.472 | 38.304 | 23.025 | 43.918 | 29.828
| 38.0903 | 147.363 | 193.768 | 37.854 | 22.936 | 43.603 | 29.691
| 38.0972 | 146.467 | 193.096 | 37.444 | 22.845 | 43.295 | 29.553
| 38.1042 | 146.889 | 193.099 | 37.067 | 22.762 | 43.004 | 29.419
| 38.1111 | 146.773 | 193.448 | 36.729 | 22.676 | 42.732 | 29.283
| 38.1181 | 146.847 | 193.713 | 36.435 | 22.594 | 42.48 | 29.149
| 38.125 | 146.244 | 184.589 | 36.16 | 22.52 | 42.175 | 29.023
| 38.1319 | 146.475 | 184.485 | 35.9 | 22.448 | 41.722 | 28.898
| 38.1389 | 146.662 | 185.038 | 35.675 | 22.378 | 41.405 | 28.77
| 38.1458 | 146.651 | 184.666 | 35.463 | 22.308 | 41.131 | 28.645
| 38.1528 | 146.776 | 193.505 | 35.274 | 22.24 | 41.112 | 28.522
| 38.1597 | 154.378 | 202.562 | 35.163 | 22.168 | 41.235 | 28.4
| 38.1667 | 163.585 | 216.53 | 35.22 | 22.103 | 41.251 | 28.282
| 38.1736 | 163.956 | 216.642 | 35.492 | 22.044 | 41.623 | 28.166
| 38.1806 | 172.764 | 227.135 | 35.798 | 21.999 | 41.899 | 28.056
| 38.1875 | 172.68 | 237.765 | 36.136 | 21.953 | 42.269 | 27.951
| 38.1944 | 181.859 | 237.337 | 36.663 | 21.914 | 42.625 | 27.85
| 38.2014 | 191.81 | 248.265 | 37.134 | 21.884 | 43.042 | 27.759
| 38.2083 | 192.138 | 256.653 | 37.871 | 21.862 | 43.562 | 27.68
| 38.2153 | 202.878 | 268.341 | 38.619 | 21.844 | 44.164 | 27.597
| 38.2222 | 211.309 | 278.046 | 39.517 | 21.84 | 44.823 | 27.532
| 38.2292 | 219.08 | 288.71 | 40.508 | 21.843 | 45.514 | 27.471
| 38.2361 | 232.37 | 305.227 | 41.563 | 21.849 | 46.251 | 27.421
| 38.2431 | 232.01 | 312.7 | 42.989 | 21.873 | 47.677 | 27.376
| 38.25 | 245.055 | 323.769 | 44.646 | 21.905 | 49.024 | 27.35
| 38.2569 | 256.804 | 347.293 | 46.502 | 21.956 | 50.674 | 27.333
| 38.2639 | 270.134 | 356.368 | 48.564 | 22.021 | 52.377 | 27.325
| 38.2708 | 290.249 | 381.237 | 50.831 | 22.099 | 54.105 | 27.34
| 38.2778 | 289.963 | 389.124 | 53.227 | 22.2 | 56.243 | 27.368
| 38.2847 | 302.505 | 404.909 | 55.945 | 22.32 | 58.459 | 27.416
| 38.2917 | 315.081 | 416.63 | 58.838 | 22.453 | 60.652 | 27.485
| 38.2986 | 331.308 | 435.814 | 62.018 | 22.607 | 63.066 | 27.576
| 38.3056 | 341.535 | 442.463 | 64.859 | 22.78 | 65.244 | 27.694
| 38.3125 | 343.651 | 455.744 | 68.095 | 22.97 | 67.511 | 27.835
| 38.3194 | 343.08 | 454.224 | 70.743 | 23.169 | 69.329 | 27.993
| 38.3264 | 342.941 | 455.979 | 73.079 | 23.374 | 70.642 | 28.174
| 38.3333 | 344.022 | 457.556 | 75.273 | 23.577 | 71.918 | 28.377
| 38.3403 | 344.692 | 448.341 | 77.182 | 23.786 | 72.923 | 28.592
| 38.3472 | 342.934 | 447.995 | 78.817 | 23.987 | 73.073 | 28.818
| 38.3542 | 342.971 | 447.339 | 80.261 | 24.176 | 73.521 | 29.043
| 38.3611 | 342.14 | 446.936 | 81.531 | 24.363 | 74.04 | 29.272
| 38.3681 | 342.654 | 445.551 | 82.669 | 24.539 | 74.563 | 29.502
| 38.375 | 336.346 | 445.452 | 83.62 | 24.711 | 75.011 | 29.728
| 38.3819 | 335.363 | 445.223 | 84.046 | 24.872 | 75.472 | 29.946
| 38.3889 | 335.428 | 437.044 | 84.528 | 25.021 | 75.35 | 30.162
| 38.3958 | 334.595 | 437.384 | 84.977 | 25.159 | 75.518 | 30.371
| 38.4028 | 325.889 | 428.061 | 85.259 | 25.287 | 75.656 | 30.573
| 38.4097 | 325.557 | 428.469 | 85.064 | 25.407 | 75.376 | 30.764
| 38.4167 | 324.52 | 427.041 | 84.979 | 25.511 | 75.354 | 30.949
| 38.4236 | 325.655 | 417.413 | 84.967 | 25.607 | 75.185 | 31.119
| 38.4306 | 317.437 | 418.164 | 84.486 | 25.697 | 74.848 | 31.288
| 38.4375 | 316.927 | 417.717 | 84.137 | 25.766 | 74.779 | 31.437
| 38.4444 | 308.849 | 406.95 | 83.806 | 25.832 | 74.316 | 31.59
| 38.4514 | 309.301 | 408.356 | 83.048 | 25.889 | 74.005 | 31.717
| 38.4583 | 309.12 | 399.642 | 82.53 | 25.937 | 73.627 | 31.839
| 38.4653 | 301.328 | 399.364 | 81.902 | 25.974 | 73.222 | 31.956
| 38.4722 | 301.518 | 391.296 | 81.081 | 26.006 | 72.937 | 32.057
| 38.4792 | 301.253 | 390.202 | 80.44 | 26.023 | 72.329 | 32.15
| 38.4861 | 301.344 | 390.557 | 79.89 | 26.038 | 72.058 | 32.228
| 38.4931 | 293.046 | 390.333 | 78.963 | 26.045 | 71.888 | 32.304
| 38.5 | 294.224 | 383.078 | 78.248 | 26.047 | 71.625 | 32.365
| 38.5069 | 293.302 | 383.4 | 77.646 | 26.036 | 71.198 | 32.424
| 38.5139 | 294.272 | 383.863 | 77.136 | 26.035 | 71.01 | 32.474
| 38.5208 | 294.082 | 384.475 | 76.699 | 26.03 | 70.904 | 32.509
| 38.5278 | 286.261 | 374.826 | 75.91 | 26.021 | 70.308 | 32.55
| 38.5347 | 287.326 | 375.933 | 75.313 | 26.008 | 70.002 | 32.578
| 38.5417 | 287.178 | 375.937 | 74.812 | 25.992 | 69.84 | 32.604
| 38.5486 | 287.57 | 375.327 | 74.376 | 25.976 | 69.724 | 32.623
| 38.5556 | 287.247 | 376.938 | 74.012 | 25.958 | 69.643 | 32.642
| 38.5625 | 280.101 | 368.037 | 73.269 | 25.94 | 69.027 | 32.651
| 38.5694 | 280.863 | 367.651 | 72.727 | 25.918 | 68.733 | 32.66
| 38.5764 | 280.762 | 368.781 | 72.261 | 25.897 | 68.556 | 32.663
| 38.5833 | 280.836 | 368.663 | 71.873 | 25.869 | 68.429 | 32.664
| 38.5903 | 280.947 | 369.152 | 71.531 | 25.846 | 68.345 | 32.658
| 38.5972 | 284.9 | 376.934 | 71.291 | 25.822 | 68.409 | 32.652
| 38.6042 | 285.736 | 376.369 | 71.256 | 25.801 | 68.783 | 32.651
| 38.6111 | 285.413 | 376.93 | 71.181 | 25.786 | 68.912 | 32.648
| 38.6181 | 285.807 | 377.171 | 71.115 | 25.769 | 68.972 | 32.642
| 38.625 | 286.684 | 377.516 | 71.083 | 25.76 | 69.047 | 32.64
| 38.6319 | 285.853 | 377.128 | 71.039 | 25.748 | 69.062 | 32.639
| 38.6389 | 293.838 | 385.877 | 71.386 | 25.742 | 69.561 | 32.637
| 38.6458 | 292.596 | 385.069 | 71.638 | 25.742 | 69.849 | 32.643
| 38.6528 | 291.989 | 384.309 | 71.778 | 25.741 | 69.916 | 32.652
| 38.6597 | 291.773 | 383.646 | 71.897 | 25.752 | 69.965 | 32.657
| 38.6667 | 292.14 | 393.768 | 72.001 | 25.751 | 70.286 | 32.669
| 38.6736 | 299.214 | 392.925 | 72.219 | 25.762 | 70.75 | 32.691
| 38.6806 | 299.017 | 393.28 | 72.665 | 25.77 | 71.011 | 32.704
| 38.6875 | 298.98 | 392.103 | 72.969 | 25.783 | 71.147 | 32.725
| 38.6944 | 298.395 | 392.587 | 73.222 | 25.802 | 71.254 | 32.749
| 38.7014 | 299.152 | 392.567 | 73.452 | 25.818 | 71.353 | 32.777
| 38.7083 | 299.061 | 401.136 | 73.65 | 25.836 | 71.62 | 32.808
| 38.7153 | 298.841 | 400.181 | 73.825 | 25.854 | 72.149 | 32.834
| 38.7222 | 298.256 | 400.848 | 73.969 | 25.879 | 72.421 | 32.87
| 38.7292 | 302.898 | 405.168 | 74.28 | 25.892 | 72.895 | 32.906
| 38.7361 | 302.212 | 396.314 | 74.533 | 25.913 | 72.675 | 32.941
| 38.7431 | 300.537 | 395.682 | 74.713 | 25.934 | 72.567 | 32.984
| 38.75 | 299.387 | 393.92 | 74.808 | 25.956 | 72.461 | 33.024
| 38.7569 | 301.393 | 387.427 | 74.898 | 25.974 | 72.064 | 33.065
| 38.7639 | 290.144 | 383.381 | 74.419 | 25.994 | 71.638 | 33.102
| 38.7708 | 286.829 | 380.172 | 74.171 | 26.003 | 71.243 | 33.138
| 38.7778 | 285.404 | 371.036 | 73.686 | 26.007 | 70.817 | 33.171
| 38.7847 | 286.012 | 372.243 | 73.315 | 26.005 | 70.241 | 33.194
| 38.7917 | 278.669 | 372.031 | 72.707 | 25.998 | 69.975 | 33.218
| 38.7986 | 278.385 | 361.287 | 72.11 | 25.986 | 69.127 | 33.224
| 38.8056 | 274.826 | 356.035 | 71.44 | 25.971 | 68.476 | 33.235
| 38.8125 | 275.146 | 356.816 | 70.877 | 25.946 | 68.071 | 33.233
| 38.8194 | 266.501 | 349.611 | 70.083 | 25.919 | 67.741 | 33.227
| 38.8264 | 266.979 | 348.522 | 69.35 | 25.889 | 67.098 | 33.214
| 38.8333 | 267.712 | 349.586 | 68.75 | 25.848 | 66.755 | 33.197
| 38.8403 | 258.188 | 338.968 | 67.788 | 25.805 | 65.898 | 33.169
| 38.8472 | 258.632 | 339.377 | 67.051 | 25.755 | 65.418 | 33.14
| 38.8542 | 251.203 | 331.086 | 66.409 | 25.704 | 64.79 | 33.1
| 38.8611 | 250.967 | 332.256 | 65.476 | 25.661 | 64.324 | 33.067
| 38.8681 | 251.094 | 321.994 | 64.753 | 25.596 | 63.698 | 33.013
| 38.875 | 242.488 | 322.637 | 63.938 | 25.537 | 63.113 | 32.964
| 38.8819 | 242.362 | 313.85 | 63.071 | 25.484 | 62.577 | 32.914
| 38.8889 | 235.15 | 313.986 | 62.299 | 25.411 | 61.859 | 32.851
| 38.8958 | 235 | 305.359 | 61.326 | 25.342 | 61.129 | 32.788
| 38.9028 | 233.06 | 303.861 | 60.488 | 25.264 | 60.437 | 32.718
| 38.9097 | 222.474 | 291.716 | 59.33 | 25.188 | 59.45 | 32.645
| 38.9167 | 212.907 | 280.884 | 58.271 | 25.111 | 58.658 | 32.568
| 38.9236 | 212.967 | 273.076 | 57.116 | 25.019 | 57.743 | 32.479
| 38.9306 | 204.749 | 273.168 | 55.922 | 24.925 | 56.831 | 32.388
| 38.9375 | 204.753 | 264.433 | 54.837 | 24.828 | 55.858 | 32.291
| 38.9444 | 195.04 | 255.371 | 53.551 | 24.724 | 54.865 | 32.187
| 38.9514 | 184.13 | 240.293 | 52.362 | 24.617 | 54.022 | 32.079
| 38.9583 | 184.754 | 241.685 | 51.102 | 24.507 | 53.044 | 31.961
| 38.9653 | 176.698 | 231.957 | 49.877 | 24.398 | 52.168 | 31.84
| 38.9722 | 177.183 | 233.015 | 48.765 | 24.276 | 51.46 | 31.715
| 38.9792 | 177.777 | 233.524 | 47.812 | 24.163 | 50.951 | 31.584
| 38.9861 | 175.234 | 222.265 | 46.921 | 24.049 | 50.176 | 31.447
| 38.9931 | 175.519 | 222.248 | 46.119 | 23.933 | 49.566 | 31.309
| 39 | 175.345 | 223.03 | 45.419 | 23.82 | 49.077 | 31.165
| 39.0069 | 166.199 | 223.548 | 44.491 | 23.708 | 48.667 | 31.022
| 39.0139 | 166.015 | 214.177 | 43.735 | 23.605 | 48.004 | 30.881
| 39.0208 | 166.315 | 214.579 | 43.08 | 23.495 | 47.53 | 30.74
| 39.0278 | 157.561 | 212.372 | 42.294 | 23.387 | 47.082 | 30.593
| 39.0347 | 157.3 | 212.641 | 41.586 | 23.282 | 46.68 | 30.45
| 39.0417 | 156.627 | 202.953 | 40.94 | 23.179 | 46.036 | 30.309
| 39.0486 | 156.679 | 203.958 | 40.374 | 23.077 | 45.586 | 30.168
| 39.0556 | 157 | 204.119 | 39.874 | 22.981 | 45.214 | 30.03
| 39.0625 | 149.379 | 193.838 | 39.274 | 22.886 | 44.85 | 29.882
| 39.0694 | 149.681 | 194.301 | 38.721 | 22.793 | 44.256 | 29.748
| 39.0764 | 149.845 | 194.372 | 38.239 | 22.697 | 43.85 | 29.607
| 39.0833 | 149.683 | 194.873 | 37.805 | 22.602 | 43.509 | 29.474
| 39.0903 | 149.779 | 194.412 | 37.421 | 22.519 | 43.205 | 29.334
| 39.0972 | 149.567 | 195.006 | 37.077 | 22.431 | 42.917 | 29.198
| 39.1042 | 149.814 | 195.493 | 36.766 | 22.346 | 42.647 | 29.064
| 39.1111 | 149.593 | 194.922 | 36.484 | 22.27 | 42.396 | 28.934
| 39.1181 | 141.746 | 185.012 | 36.138 | 22.192 | 42.026 | 28.805
| 39.125 | 141.525 | 185.249 | 35.726 | 22.114 | 41.584 | 28.675
| 39.1319 | 141.72 | 185.588 | 35.375 | 22.038 | 41.263 | 28.551
| 39.1389 | 141.773 | 185.843 | 35.062 | 21.96 | 40.991 | 28.424
| 39.1458 | 142.067 | 186.03 | 34.791 | 21.891 | 40.747 | 28.303
| 39.1528 | 148.668 | 197.632 | 34.617 | 21.811 | 40.662 | 28.181
| 39.1597 | 155.905 | 198.796 | 34.598 | 21.746 | 40.714 | 28.058
| 39.1667 | 156.078 | 210.45 | 34.692 | 21.681 | 40.923 | 27.943
| 39.1736 | 166.85 | 220.281 | 34.935 | 21.626 | 41.235 | 27.831
| 39.1806 | 166.14 | 220.464 | 35.205 | 21.573 | 41.423 | 27.718
| 39.1875 | 176.123 | 233.797 | 35.686 | 21.534 | 41.869 | 27.615
| 39.1944 | 185.463 | 245.092 | 36.154 | 21.497 | 42.174 | 27.52
| 39.2014 | 185.533 | 245.86 | 36.752 | 21.468 | 42.621 | 27.43
| 39.2083 | 195.826 | 257.837 | 37.448 | 21.445 | 43.126 | 27.35
| 39.2153 | 196.19 | 267.81 | 38.118 | 21.436 | 43.747 | 27.275
| 39.2222 | 207.22 | 278.131 | 39.052 | 21.431 | 44.411 | 27.213
| 39.2292 | 215.014 | 289.212 | 40.084 | 21.432 | 45.098 | 27.155
| 39.2361 | 225.182 | 305.056 | 41.234 | 21.444 | 45.873 | 27.101
| 39.2431 | 237.365 | 313.423 | 42.626 | 21.465 | 47.299 | 27.065
| 39.25 | 251.184 | 330.941 | 44.242 | 21.499 | 48.598 | 27.036
| 39.2569 | 263.146 | 340.239 | 46.074 | 21.548 | 50.146 | 27.021
| 39.2639 | 276.408 | 364.981 | 48.063 | 21.618 | 51.889 | 27.024
| 39.2708 | 284.177 | 382.636 | 50.444 | 21.694 | 53.815 | 27.039
| 39.2778 | 295.796 | 382.865 | 52.897 | 21.8 | 55.578 | 27.068
| 39.2847 | 308.418 | 407.868 | 55.551 | 21.915 | 57.899 | 27.115
| 39.2917 | 322.086 | 425.015 | 58.386 | 22.052 | 60.275 | 27.19
| 39.2986 | 331.867 | 437.655 | 61.354 | 22.211 | 62.378 | 27.288
| 39.3056 | 341.583 | 449.617 | 64.283 | 22.376 | 64.413 | 27.402
| 39.3125 | 341.622 | 449.686 | 67.453 | 22.564 | 66.75 | 27.544
| 39.3194 | 349.565 | 460.546 | 70.593 | 22.773 | 69.015 | 27.706
| 39.3264 | 350.271 | 458.981 | 73.255 | 22.985 | 70.545 | 27.894
| 39.3333 | 345.049 | 451.031 | 75.562 | 23.203 | 71.671 | 28.097
| 39.3403 | 344.054 | 450.938 | 77.263 | 23.417 | 72.063 | 28.318
| 39.3472 | 341.703 | 448.667 | 78.785 | 23.625 | 72.586 | 28.543
| 39.3542 | 341.804 | 448.298 | 80.076 | 23.821 | 73.059 | 28.782
| 39.3611 | 340.323 | 446.392 | 81.185 | 24.006 | 73.521 | 29.017
| 39.3681 | 340.09 | 446.318 | 82.157 | 24.181 | 73.982 | 29.248
| 39.375 | 339.715 | 443.511 | 82.986 | 24.348 | 74.407 | 29.476
| 39.3819 | 338.984 | 444.531 | 83.721 | 24.508 | 74.846 | 29.7
| 39.3889 | 331.278 | 443.293 | 84.097 | 24.659 | 75.224 | 29.915
| 39.3958 | 333.875 | 437.464 | 84.377 | 24.801 | 75.155 | 30.129
| 39.4028 | 326.16 | 428.354 | 84.632 | 24.925 | 75.272 | 30.33
| 39.4097 | 324.657 | 427.201 | 84.435 | 25.042 | 74.923 | 30.533
| 39.4167 | 329.662 | 432.809 | 84.478 | 25.145 | 75.09 | 30.725
| 39.4236 | 319.209 | 419.595 | 84.019 | 25.24 | 74.541 | 30.904
| 39.4306 | 318.895 | 418.062 | 83.692 | 25.329 | 74.339 | 31.07
| 39.4375 | 318.548 | 409.77 | 83.421 | 25.396 | 74.201 | 31.228
| 39.4444 | 310.497 | 409.242 | 82.82 | 25.461 | 73.752 | 31.378
| 39.4514 | 309.8 | 408.624 | 82.222 | 25.516 | 73.563 | 31.518
| 39.4583 | 309.934 | 399.366 | 81.758 | 25.555 | 73.197 | 31.639
| 39.4653 | 302.887 | 398.615 | 80.949 | 25.596 | 72.741 | 31.761
| 39.4722 | 302.457 | 398.441 | 80.299 | 25.623 | 72.555 | 31.868
| 39.4792 | 300.913 | 389.002 | 79.718 | 25.644 | 71.998 | 31.962
| 39.4861 | 294.216 | 389.914 | 78.961 | 25.66 | 71.62 | 32.047
| 39.4931 | 294.964 | 389.809 | 78.23 | 25.668 | 71.458 | 32.126
| 39.5 | 293.738 | 389.627 | 77.619 | 25.671 | 71.35 | 32.198
| 39.5069 | 293.948 | 381.573 | 77.085 | 25.669 | 70.893 | 32.263
| 39.5139 | 294.235 | 381.381 | 76.592 | 25.672 | 70.557 | 32.314
| 39.5208 | 293.496 | 382.148 | 76.162 | 25.663 | 70.359 | 32.361
| 39.5278 | 287.43 | 381.384 | 75.426 | 25.658 | 70.283 | 32.402
| 39.5347 | 286.885 | 372.367 | 74.82 | 25.647 | 69.661 | 32.436
| 39.5417 | 287.093 | 374.162 | 74.34 | 25.637 | 69.359 | 32.471
| 39.5486 | 287.024 | 374.099 | 73.924 | 25.624 | 69.176 | 32.495
| 39.5556 | 288.077 | 373.409 | 73.571 | 25.61 | 69.06 | 32.519
| 39.5625 | 281.534 | 375.816 | 72.907 | 25.598 | 69.033 | 32.54
| 39.5694 | 281.302 | 375.413 | 72.414 | 25.577 | 68.999 | 32.548
| 39.5764 | 282.462 | 375.626 | 72 | 25.56 | 68.972 | 32.566
| 39.5833 | 278.295 | 371.861 | 71.456 | 25.536 | 68.683 | 32.57
| 39.5903 | 279.783 | 372.009 | 71.049 | 25.517 | 68.561 | 32.58
| 39.5972 | 279.767 | 372.92 | 70.718 | 25.492 | 68.498 | 32.59
| 39.6042 | 286.356 | 372.846 | 70.751 | 25.475 | 68.491 | 32.592
| 39.6111 | 287.169 | 374.081 | 70.779 | 25.46 | 68.522 | 32.599
| 39.6181 | 287.268 | 381.089 | 70.793 | 25.446 | 68.845 | 32.604
| 39.625 | 287.345 | 381.994 | 70.826 | 25.443 | 69.154 | 32.609
| 39.6319 | 287.157 | 382.538 | 70.869 | 25.439 | 69.319 | 32.617
| 39.6389 | 287.703 | 382.215 | 70.902 | 25.433 | 69.423 | 32.629
| 39.6458 | 294.923 | 381.91 | 71.003 | 25.436 | 69.475 | 32.64
| 39.6528 | 295.177 | 381.945 | 71.401 | 25.438 | 69.555 | 32.654
| 39.6597 | 294.68 | 390.691 | 71.663 | 25.447 | 69.948 | 32.676
| 39.6667 | 295.319 | 391.215 | 71.896 | 25.457 | 70.382 | 32.691
| 39.6736 | 295.234 | 391.176 | 72.099 | 25.471 | 70.621 | 32.708
| 39.6806 | 294.206 | 390.534 | 72.277 | 25.492 | 70.782 | 32.735
| 39.6875 | 300.66 | 390.222 | 72.686 | 25.504 | 70.838 | 32.766
| 39.6944 | 301.26 | 391.264 | 73.105 | 25.524 | 70.923 | 32.797
| 39.7014 | 301.414 | 399.549 | 73.469 | 25.547 | 71.544 | 32.826
| 39.7083 | 302.486 | 399.119 | 73.797 | 25.576 | 71.912 | 32.862
| 39.7153 | 301.183 | 398.887 | 74.065 | 25.603 | 72.125 | 32.9
| 39.7222 | 300.468 | 398.433 | 74.272 | 25.63 | 72.241 | 32.941
| 39.7292 | 298.804 | 396.098 | 74.357 | 25.659 | 72.211 | 32.98
| 39.7361 | 298.836 | 394.993 | 74.412 | 25.683 | 72.178 | 33.028
| 39.7431 | 297.608 | 394.155 | 74.456 | 25.707 | 72.181 | 33.075
| 39.75 | 295.275 | 388.323 | 74.581 | 25.726 | 71.934 | 33.118
| 39.7569 | 291.001 | 384.247 | 74.275 | 25.747 | 71.608 | 33.158
| 39.7639 | 288.797 | 379.005 | 74.065 | 25.76 | 71.325 | 33.196
| 39.7708 | 290.774 | 380.779 | 73.737 | 25.77 | 70.924 | 33.232
| 39.7778 | 287.272 | 378.165 | 73.409 | 25.771 | 70.647 | 33.267
| 39.7847 | 279.6 | 367.832 | 73.031 | 25.776 | 70.002 | 33.295
| 39.7917 | 279.57 | 369.927 | 72.361 | 25.778 | 69.578 | 33.316
| 39.7986 | 278.8 | 360.281 | 71.864 | 25.762 | 69.017 | 33.337
| 39.8056 | 271.876 | 360.083 | 71.227 | 25.744 | 68.479 | 33.343
| 39.8125 | 272.022 | 360.567 | 70.536 | 25.727 | 68.179 | 33.349
| 39.8194 | 271.292 | 349.18 | 69.959 | 25.7 | 67.446 | 33.344
| 39.8264 | 263.671 | 348.673 | 69.155 | 25.672 | 66.914 | 33.339
| 39.8333 | 263.548 | 349.48 | 68.401 | 25.632 | 66.581 | 33.322
| 39.8403 | 264.12 | 339.888 | 67.781 | 25.598 | 65.839 | 33.302
| 39.8472 | 255.505 | 340.44 | 66.875 | 25.553 | 65.412 | 33.282
| 39.8542 | 256.027 | 332.238 | 66.146 | 25.507 | 64.73 | 33.245
| 39.8611 | 256.206 | 331.884 | 65.516 | 25.456 | 64.234 | 33.209
| 39.8681 | 246.527 | 329.027 | 64.487 | 25.401 | 63.791 | 33.169
| 39.875 | 246.822 | 320.082 | 63.696 | 25.342 | 62.944 | 33.119
| 39.8819 | 238.939 | 320.191 | 62.908 | 25.281 | 62.442 | 33.072
| 39.8889 | 239.015 | 310.03 | 62 | 25.221 | 61.689 | 33.012
| 39.8958 | 238.574 | 309.96 | 61.249 | 25.152 | 61.112 | 32.953
| 39.9028 | 229.584 | 299.009 | 60.184 | 25.083 | 60.36 | 32.887
| 39.9097 | 219.988 | 289.71 | 59.169 | 25.013 | 59.475 | 32.821
| 39.9167 | 220.126 | 281.042 | 58.135 | 24.929 | 58.557 | 32.745
| 39.9236 | 211.199 | 280.396 | 56.952 | 24.854 | 57.686 | 32.663
| 39.9306 | 211.257 | 269.153 | 55.911 | 24.78 | 56.773 | 32.581
| 39.9375 | 201.644 | 259.084 | 54.639 | 24.672 | 55.767 | 32.484
| 39.9444 | 191.218 | 250.933 | 53.439 | 24.572 | 54.813 | 32.383
| 39.9514 | 191.209 | 241.483 | 52.234 | 24.47 | 53.869 | 32.274
| 39.9583 | 182.127 | 241.855 | 50.954 | 24.35 | 52.985 | 32.16
| 39.9653 | 179.747 | 229.598 | 49.783 | 24.242 | 52.055 | 32.04
| 39.9722 | 180.297 | 230.344 | 48.747 | 24.13 | 51.295 | 31.913
| 39.9792 | 180.36 | 230.797 | 47.86 | 24.02 | 50.761 | 31.786
| 39.9861 | 172.894 | 230.415 | 46.85 | 23.91 | 50.281 | 31.647
| 39.9931 | 172.481 | 221.604 | 45.976 | 23.798 | 49.612 | 31.511
| 40 | 172.735 | 221.664 | 45.208 | 23.688 | 49.039 | 31.366
| 40.0069 | 164.468 | 221.487 | 44.38 | 23.579 | 48.574 | 31.227
| 40.0139 | 164.858 | 221.637 | 43.594 | 23.47 | 48.177 | 31.086
| 40.0208 | 164.815 | 210.737 | 42.91 | 23.36 | 47.504 | 30.943
| 40.0278 | 157.449 | 211.214 | 42.278 | 23.263 | 46.995 | 30.808
| 40.0347 | 156.427 | 209.489 | 41.497 | 23.158 | 46.536 | 30.665
| 40.0417 | 155.999 | 208.763 | 40.842 | 23.055 | 46.137 | 30.526
| 40.0486 | 155.811 | 200.322 | 40.252 | 22.957 | 45.654 | 30.387
| 40.0556 | 155.868 | 200.545 | 39.718 | 22.864 | 45.121 | 30.249
| 40.0625 | 155.94 | 201.337 | 39.266 | 22.765 | 44.75 | 30.106
| 40.0694 | 148.372 | 200.989 | 38.712 | 22.672 | 44.406 | 29.968
| 40.0764 | 148.137 | 192.606 | 38.184 | 22.583 | 43.954 | 29.827
| 40.0833 | 148.398 | 192.503 | 37.721 | 22.493 | 43.499 | 29.694
| 40.0903 | 148.233 | 192.958 | 37.308 | 22.407 | 43.137 | 29.561
| 40.0972 | 148.34 | 192.917 | 36.937 | 22.32 | 42.83 | 29.426
| 40.1042 | 148.711 | 193.509 | 36.611 | 22.241 | 42.562 | 29.293
| 40.1111 | 148.648 | 193.316 | 36.319 | 22.164 | 42.31 | 29.162
| 40.1181 | 148.678 | 192.746 | 36.053 | 22.085 | 42.051 | 29.028
| 40.125 | 140.862 | 192.592 | 35.75 | 22.011 | 41.81 | 28.905
| 40.1319 | 141.199 | 193.549 | 35.347 | 21.937 | 41.574 | 28.776
| 40.1389 | 141.204 | 193.603 | 35.026 | 21.867 | 41.365 | 28.659
| 40.1458 | 141.441 | 193.221 | 34.728 | 21.789 | 41.154 | 28.532
| 40.1528 | 147.764 | 193.624 | 34.55 | 21.728 | 40.966 | 28.421
| 40.1597 | 156.134 | 200.723 | 34.524 | 21.654 | 40.95 | 28.303
| 40.1667 | 156.326 | 210.697 | 34.624 | 21.593 | 41.119 | 28.184
| 40.1736 | 166.264 | 211.346 | 34.867 | 21.537 | 41.186 | 28.078
| 40.1806 | 166.767 | 223.662 | 35.142 | 21.49 | 41.576 | 27.968
| 40.1875 | 175.432 | 237.926 | 35.6 | 21.446 | 41.89 | 27.869
| 40.1944 | 185.149 | 237.43 | 36.061 | 21.413 | 42.269 | 27.773
| 40.2014 | 185.166 | 248.664 | 36.656 | 21.383 | 42.736 | 27.684
| 40.2083 | 195.408 | 258.612 | 37.364 | 21.364 | 43.273 | 27.602
| 40.2153 | 195.388 | 267.283 | 38.035 | 21.356 | 43.85 | 27.531
| 40.2222 | 205.767 | 277.826 | 38.955 | 21.348 | 44.475 | 27.462
| 40.2292 | 214.538 | 287.404 | 39.977 | 21.353 | 45.165 | 27.404
| 40.2361 | 231.532 | 297.597 | 41.17 | 21.367 | 46.186 | 27.357
| 40.2431 | 233.113 | 312.824 | 42.587 | 21.39 | 47.329 | 27.318
| 40.25 | 244.86 | 330.244 | 44.233 | 21.433 | 48.833 | 27.294
| 40.2569 | 263.757 | 338.799 | 46.193 | 21.481 | 50.292 | 27.277
| 40.2639 | 272.138 | 357.316 | 48.31 | 21.556 | 51.902 | 27.276
| 40.2708 | 282.791 | 381.006 | 50.577 | 21.641 | 53.767 | 27.295
| 40.2778 | 297.033 | 392.293 | 53.01 | 21.744 | 55.849 | 27.325
| 40.2847 | 309.595 | 408.899 | 55.719 | 21.865 | 57.927 | 27.372
| 40.2917 | 321.973 | 423.635 | 58.607 | 21.997 | 60.138 | 27.444
| 40.2986 | 327.229 | 429.622 | 61.659 | 22.165 | 62.468 | 27.537
| 40.3056 | 335.011 | 450.224 | 64.66 | 22.344 | 64.682 | 27.655
| 40.3125 | 337.804 | 452.273 | 67.452 | 22.531 | 67.14 | 27.797
| 40.3194 | 349.373 | 459.939 | 70.583 | 22.736 | 69.003 | 27.955
| 40.3264 | 346.815 | 458.509 | 73.171 | 22.95 | 70.608 | 28.144
| 40.3333 | 349.101 | 450.823 | 75.469 | 23.165 | 71.668 | 28.352
| 40.3403 | 344.056 | 452.388 | 77.501 | 23.378 | 72.165 | 28.567
| 40.3472 | 342.769 | 452.828 | 78.906 | 23.587 | 72.868 | 28.8
| 40.3542 | 340.982 | 450.827 | 80.207 | 23.794 | 73.495 | 29.032
| 40.3611 | 342.016 | 451.308 | 81.371 | 23.981 | 74.091 | 29.271
| 40.3681 | 341.889 | 441.973 | 82.433 | 24.159 | 74.142 | 29.498
| 40.375 | 341.34 | 442.152 | 83.393 | 24.335 | 74.383 | 29.733
| 40.3819 | 333.939 | 442.436 | 83.891 | 24.494 | 74.729 | 29.958
| 40.3889 | 333.638 | 442.298 | 84.271 | 24.649 | 75.135 | 30.175
| 40.3958 | 332.502 | 430.292 | 84.616 | 24.787 | 75.204 | 30.384
| 40.4028 | 333.567 | 430.946 | 84.952 | 24.916 | 74.996 | 30.597
| 40.4097 | 325.041 | 429.509 | 84.815 | 25.038 | 74.973 | 30.789
| 40.4167 | 324.684 | 428.598 | 84.713 | 25.147 | 75.113 | 30.975
| 40.4236 | 324.933 | 419.412 | 84.628 | 25.243 | 74.918 | 31.152
| 40.4306 | 316.188 | 418.624 | 84.341 | 25.334 | 74.63 | 31.319
| 40.4375 | 316.119 | 411.128 | 83.809 | 25.412 | 74.423 | 31.482
| 40.4444 | 309.398 | 410.772 | 83.49 | 25.477 | 74.055 | 31.632
| 40.4514 | 309.084 | 412.542 | 82.7 | 25.536 | 73.949 | 31.774
| 40.4583 | 309.054 | 401.251 | 82.127 | 25.582 | 73.26 | 31.9
| 40.4653 | 300.119 | 401.881 | 81.444 | 25.62 | 72.985 | 32.018
| 40.4722 | 300.819 | 391.164 | 80.614 | 25.651 | 72.72 | 32.123
| 40.4792 | 299.712 | 392.03 | 79.962 | 25.671 | 72.129 | 32.224
| 40.4861 | 301.553 | 392.268 | 79.395 | 25.684 | 71.87 | 32.312
| 40.4931 | 293.118 | 391.515 | 78.68 | 25.696 | 71.745 | 32.385
| 40.5 | 292.018 | 383.422 | 77.861 | 25.701 | 71.138 | 32.454
| 40.5069 | 293.407 | 384.112 | 77.238 | 25.698 | 70.864 | 32.514
| 40.5139 | 293.765 | 384.094 | 76.704 | 25.693 | 70.719 | 32.567
| 40.5208 | 292.885 | 375.949 | 76.263 | 25.685 | 70.305 | 32.613
| 40.5278 | 284.893 | 375.11 | 75.625 | 25.682 | 69.888 | 32.655
| 40.5347 | 285.436 | 375.563 | 74.904 | 25.672 | 69.62 | 32.689
| 40.5417 | 285.544 | 376.015 | 74.329 | 25.659 | 69.47 | 32.714
| 40.5486 | 286.018 | 377.131 | 73.858 | 25.644 | 69.398 | 32.738
| 40.5556 | 285.781 | 375.464 | 73.429 | 25.629 | 69.302 | 32.755
| 40.5625 | 285.466 | 367.125 | 73.082 | 25.611 | 68.959 | 32.769
| 40.5694 | 286.577 | 366.837 | 72.765 | 25.595 | 68.497 | 32.786
| 40.5764 | 285.732 | 366.419 | 72.479 | 25.579 | 68.236 | 32.792
| 40.5833 | 286.309 | 366.849 | 72.264 | 25.569 | 68.095 | 32.807
| 40.5903 | 287.575 | 368.212 | 72.097 | 25.555 | 68.019 | 32.812
| 40.5972 | 287.654 | 375.764 | 71.978 | 25.545 | 68.351 | 32.809
| 40.6042 | 288.303 | 375.394 | 71.899 | 25.536 | 68.531 | 32.806
| 40.6111 | 288.463 | 375.801 | 71.817 | 25.531 | 68.59 | 32.809
| 40.6181 | 289.011 | 375.988 | 71.754 | 25.523 | 68.628 | 32.809
| 40.625 | 288.359 | 375.49 | 71.688 | 25.519 | 68.637 | 32.809
| 40.6319 | 284.566 | 380.625 | 71.553 | 25.516 | 68.789 | 32.815
| 40.6389 | 292.781 | 381.495 | 71.731 | 25.514 | 69.012 | 32.819
| 40.6458 | 292.913 | 381.217 | 71.876 | 25.513 | 69.155 | 32.826
| 40.6528 | 293.228 | 382.918 | 72.028 | 25.523 | 69.289 | 32.832
| 40.6597 | 292.71 | 382.432 | 72.186 | 25.529 | 69.418 | 32.842
| 40.6667 | 291.275 | 392.365 | 72.157 | 25.538 | 70.061 | 32.86
| 40.6736 | 291.938 | 392.313 | 72.205 | 25.544 | 70.447 | 32.877
| 40.6806 | 299.528 | 393.574 | 72.621 | 25.553 | 70.707 | 32.891
| 40.6875 | 299.302 | 391.814 | 72.944 | 25.565 | 70.837 | 32.916
| 40.6944 | 299.64 | 392.596 | 73.233 | 25.584 | 70.969 | 32.949
| 40.7014 | 300.181 | 392.997 | 73.51 | 25.603 | 71.139 | 32.976
| 40.7083 | 299.956 | 394.417 | 73.77 | 25.627 | 71.288 | 33.011
| 40.7153 | 300.217 | 394.081 | 73.991 | 25.65 | 71.4 | 33.041
| 40.7222 | 300.458 | 401.64 | 74.184 | 25.674 | 71.5 | 33.08
| 40.7292 | 299.155 | 401.393 | 74.32 | 25.7 | 72.126 | 33.112
| 40.7361 | 299.439 | 402.273 | 74.445 | 25.721 | 72.434 | 33.153
| 40.7431 | 299.159 | 392.309 | 74.531 | 25.74 | 72.134 | 33.194
| 40.75 | 300.309 | 385.417 | 74.629 | 25.761 | 71.925 | 33.237
| 40.7569 | 293.749 | 384.159 | 74.491 | 25.781 | 71.413 | 33.274
| 40.7639 | 293.478 | 385.724 | 74.312 | 25.798 | 71.208 | 33.318
| 40.7708 | 286.605 | 375.159 | 73.994 | 25.807 | 70.844 | 33.351
| 40.7778 | 286.353 | 376.259 | 73.552 | 25.817 | 70.374 | 33.376
| 40.7847 | 285.911 | 357.574 | 73.21 | 25.818 | 69.93 | 33.404
| 40.7917 | 279.559 | 368.892 | 72.607 | 25.812 | 69.259 | 33.426
| 40.7986 | 278.797 | 361.698 | 72.056 | 25.805 | 68.855 | 33.44
| 40.8056 | 272.368 | 361.411 | 71.396 | 25.785 | 68.424 | 33.449
| 40.8125 | 272.091 | 352.347 | 70.705 | 25.769 | 68.012 | 33.451
| 40.8194 | 265.27 | 352.309 | 70.055 | 25.737 | 67.384 | 33.444
| 40.8264 | 265.309 | 352.127 | 69.195 | 25.71 | 67.027 | 33.432
| 40.8333 | 264.12 | 342.988 | 68.481 | 25.665 | 66.197 | 33.419
| 40.8403 | 256.107 | 343.435 | 67.681 | 25.629 | 65.781 | 33.394
| 40.8472 | 257.535 | 333.333 | 66.837 | 25.579 | 65.295 | 33.363
| 40.8542 | 254.204 | 330.716 | 66.093 | 25.535 | 64.534 | 33.331
| 40.8611 | 253.983 | 330.457 | 65.389 | 25.479 | 64.004 | 33.291
| 40.8681 | 246.653 | 329.64 | 64.557 | 25.423 | 63.645 | 33.245
| 40.875 | 246.203 | 320.561 | 63.724 | 25.371 | 62.838 | 33.199
| 40.8819 | 238.435 | 319.521 | 62.904 | 25.309 | 62.348 | 33.147
| 40.8889 | 238.115 | 310.799 | 61.997 | 25.244 | 61.622 | 33.088
| 40.8958 | 236.949 | 309.532 | 61.205 | 25.173 | 61.017 | 33.025
| 40.9028 | 227.474 | 298.61 | 60.244 | 25.104 | 60.254 | 32.956
| 40.9097 | 227.559 | 290.383 | 59.315 | 25.034 | 59.382 | 32.882
| 40.9167 | 217.15 | 281.355 | 58.149 | 24.952 | 58.476 | 32.806
| 40.9236 | 207.702 | 272.963 | 57.115 | 24.867 | 57.601 | 32.717
| 40.9306 | 208.668 | 274.29 | 55.915 | 24.777 | 56.721 | 32.631
| 40.9375 | 202.061 | 263.625 | 54.664 | 24.679 | 55.707 | 32.531
| 40.9444 | 191.194 | 251.578 | 53.464 | 24.579 | 54.834 | 32.429
| 40.9514 | 189.169 | 249.19 | 52.221 | 24.475 | 53.908 | 32.325
| 40.9583 | 181.618 | 238.766 | 50.93 | 24.362 | 52.931 | 32.212
| 40.9653 | 181.91 | 238.953 | 49.813 | 24.251 | 52.228 | 32.09
| 40.9722 | 182.049 | 228.627 | 48.834 | 24.13 | 51.443 | 31.961
| 40.9792 | 174.673 | 229.817 | 47.756 | 24.021 | 50.768 | 31.827
| 40.9861 | 173.682 | 227.851 | 46.817 | 23.908 | 50.212 | 31.696
| 40.9931 | 173.138 | 227.893 | 45.974 | 23.789 | 49.718 | 31.553
| 41 | 173.267 | 219.142 | 45.23 | 23.681 | 49.074 | 31.415
| 41.0069 | 165.347 | 218.63 | 44.298 | 23.574 | 48.495 | 31.277
| 41.0139 | 164.822 | 218.437 | 43.538 | 23.459 | 48.043 | 31.129
| 41.0208 | 165.275 | 210.073 | 42.883 | 23.346 | 47.565 | 30.99
| 41.0278 | 158.062 | 209.74 | 42.262 | 23.247 | 46.969 | 30.845
| 41.0347 | 158.168 | 210.061 | 41.526 | 23.148 | 46.53 | 30.71
| 41.0417 | 158.116 | 209.839 | 40.914 | 23.045 | 46.145 | 30.565
| 41.0486 | 157.741 | 201.354 | 40.366 | 22.944 | 45.556 | 30.424
| 41.0556 | 156.714 | 199.938 | 39.84 | 22.848 | 45.067 | 30.283
| 41.0625 | 148.897 | 200.39 | 39.349 | 22.753 | 44.697 | 30.144
| 41.0694 | 149.163 | 200.129 | 38.73 | 22.664 | 44.352 | 30.005
| 41.0764 | 149.512 | 200.171 | 38.227 | 22.58 | 44.048 | 29.868
| 41.0833 | 149.219 | 192.296 | 37.773 | 22.479 | 43.513 | 29.731
| 41.0903 | 149.032 | 192.771 | 37.37 | 22.392 | 43.147 | 29.597
| 41.0972 | 149.44 | 192.671 | 37.019 | 22.305 | 42.824 | 29.463
| 41.1042 | 149.475 | 193.065 | 36.7 | 22.225 | 42.552 | 29.328
| 41.1111 | 149.534 | 193.584 | 36.418 | 22.144 | 42.295 | 29.199
| 41.1181 | 142.15 | 193.215 | 36.076 | 22.067 | 42.043 | 29.07
| 41.125 | 142.229 | 192.768 | 35.671 | 21.991 | 41.792 | 28.944
| 41.1319 | 141.954 | 192.93 | 35.335 | 21.914 | 41.559 | 28.815
| 41.1389 | 142.091 | 192.519 | 35.031 | 21.841 | 41.335 | 28.695
| 41.1458 | 142.054 | 193.286 | 34.752 | 21.772 | 41.121 | 28.574
| 41.1528 | 147.428 | 193.059 | 34.571 | 21.706 | 40.924 | 28.462
| 41.1597 | 155.992 | 200.789 | 34.542 | 21.631 | 40.922 | 28.34
| 41.1667 | 156.197 | 211.163 | 34.646 | 21.571 | 41.103 | 28.224
| 41.1736 | 166.201 | 211.143 | 34.891 | 21.529 | 41.187 | 28.126
| 41.1806 | 166.298 | 224.236 | 35.159 | 21.466 | 41.574 | 28.014
| 41.1875 | 175.168 | 236.006 | 35.631 | 21.424 | 41.877 | 27.913
| 41.1944 | 184.714 | 237.105 | 36.093 | 21.392 | 42.213 | 27.824
| 41.2014 | 185.261 | 248.27 | 36.681 | 21.365 | 42.692 | 27.733
| 41.2083 | 195.035 | 258.092 | 37.375 | 21.339 | 43.227 | 27.655
| 41.2153 | 203.19 | 267.666 | 38.184 | 21.334 | 43.821 | 27.574
| 41.2222 | 210.098 | 278.644 | 39.085 | 21.327 | 44.49 | 27.516
| 41.2292 | 218.711 | 288.433 | 40.05 | 21.325 | 45.171 | 27.458
| 41.2361 | 231.346 | 304.829 | 41.132 | 21.344 | 45.957 | 27.416
| 41.2431 | 230.906 | 303.609 | 42.494 | 21.364 | 47.058 | 27.379
| 41.25 | 247.39 | 333.651 | 44.196 | 21.402 | 48.776 | 27.349
| 41.2569 | 258.105 | 346.421 | 46.069 | 21.453 | 50.273 | 27.33
| 41.2639 | 269.784 | 365.375 | 48.126 | 21.524 | 52.086 | 27.331
| 41.2708 | 282.574 | 381.778 | 50.341 | 21.608 | 53.935 | 27.352
| 41.2778 | 295.175 | 389.941 | 52.812 | 21.709 | 55.95 | 27.384
| 41.2847 | 309.104 | 410.066 | 55.476 | 21.829 | 58.237 | 27.439
| 41.2917 | 321.658 | 422.885 | 58.34 | 21.968 | 60.369 | 27.516
| 41.2986 | 331.917 | 436.652 | 61.285 | 22.122 | 62.438 | 27.612
| 41.3056 | 341.118 | 450.004 | 64.226 | 22.299 | 64.504 | 27.731
| 41.3125 | 343.849 | 452.199 | 67.358 | 22.486 | 66.883 | 27.872
| 41.3194 | 351.616 | 461.451 | 70.288 | 22.699 | 69.088 | 28.048
| 41.3264 | 351.663 | 460.792 | 73.109 | 22.909 | 70.743 | 28.236
| 41.3333 | 345.922 | 451.304 | 75.199 | 23.126 | 71.373 | 28.437
| 41.3403 | 344.752 | 449.626 | 77.066 | 23.347 | 72.035 | 28.662
| 41.3472 | 343.585 | 450.505 | 78.679 | 23.551 | 72.661 | 28.893
| 41.3542 | 344.166 | 450.756 | 80.074 | 23.75 | 73.251 | 29.131
| 41.3611 | 344.177 | 448.88 | 81.349 | 23.943 | 73.893 | 29.36
| 41.3681 | 335.97 | 440.672 | 82.323 | 24.126 | 74.3 | 29.6
| 41.375 | 334.392 | 439.615 | 82.842 | 24.304 | 74.273 | 29.83
| 41.3819 | 334.917 | 439.563 | 83.404 | 24.457 | 74.547 | 30.055
| 41.3889 | 336.073 | 441.312 | 83.952 | 24.603 | 74.953 | 30.273
| 41.3958 | 337.494 | 433.158 | 84.5 | 24.743 | 74.843 | 30.488
| 41.4028 | 328.553 | 431.767 | 84.474 | 24.879 | 74.873 | 30.697
| 41.4097 | 326.951 | 431.874 | 84.503 | 24.998 | 75.039 | 30.885
| 41.4167 | 327.852 | 421.887 | 84.532 | 25.105 | 74.823 | 31.076
| 41.4236 | 318.969 | 421.944 | 84.275 | 25.209 | 74.634 | 31.252
| 41.4306 | 319.01 | 421.048 | 83.901 | 25.295 | 74.648 | 31.425
| 41.4375 | 318.795 | 412.515 | 83.628 | 25.372 | 74.172 | 31.586
| 41.4444 | 311.978 | 412.094 | 83.052 | 25.438 | 73.981 | 31.734
| 41.4514 | 311.671 | 403.923 | 82.53 | 25.496 | 73.586 | 31.871
| 41.4583 | 311.607 | 404.155 | 82.09 | 25.545 | 73.249 | 32.004
| 41.4653 | 301.911 | 394.246 | 81.189 | 25.585 | 72.869 | 32.121
| 41.4722 | 301.48 | 395.579 | 80.468 | 25.615 | 72.335 | 32.228
| 41.4792 | 294.226 | 386.078 | 79.881 | 25.639 | 72.145 | 32.324
| 41.4861 | 294.578 | 386.24 | 78.928 | 25.653 | 71.504 | 32.413
| 41.4931 | 294.218 | 387.135 | 78.212 | 25.66 | 71.231 | 32.491
| 41.5 | 293.999 | 387.117 | 77.585 | 25.663 | 71.062 | 32.56
| 41.5069 | 294.72 | 387.198 | 77.073 | 25.664 | 70.987 | 32.619
| 41.5139 | 294.941 | 379.052 | 76.635 | 25.66 | 70.922 | 32.671
| 41.5208 | 288.057 | 378.76 | 75.998 | 25.659 | 70.354 | 32.716
| 41.5278 | 287.629 | 379.354 | 75.337 | 25.65 | 70.087 | 32.757
| 41.5347 | 287.734 | 378.396 | 74.775 | 25.641 | 69.914 | 32.799
| 41.5417 | 287.802 | 367.883 | 74.318 | 25.632 | 69.666 | 32.831
| 41.5486 | 287.159 | 368.878 | 73.902 | 25.621 | 69.015 | 32.857
| 41.5556 | 287.507 | 369.458 | 73.558 | 25.607 | 68.716 | 32.879
| 41.5625 | 280.122 | 369.601 | 72.839 | 25.593 | 68.532 | 32.897
| 41.5694 | 280.518 | 368.753 | 72.296 | 25.578 | 68.37 | 32.907
| 41.5764 | 280.385 | 369.477 | 71.829 | 25.553 | 68.257 | 32.914
| 41.5833 | 280.303 | 369.741 | 71.458 | 25.54 | 68.19 | 32.919
| 41.5903 | 281.298 | 370.807 | 71.158 | 25.52 | 68.168 | 32.921
| 41.5972 | 282.363 | 370.815 | 70.915 | 25.497 | 68.166 | 32.925
| 41.6042 | 278.065 | 374.353 | 70.665 | 25.481 | 68.281 | 32.921
| 41.6111 | 286.556 | 375.197 | 70.683 | 25.466 | 68.386 | 32.925
| 41.6181 | 287.783 | 375.352 | 70.728 | 25.456 | 68.459 | 32.926
| 41.625 | 284.808 | 371.856 | 70.728 | 25.448 | 68.467 | 32.929
| 41.6319 | 291.935 | 384.473 | 71.045 | 25.442 | 69.041 | 32.936
| 41.6389 | 291.717 | 384.177 | 71.258 | 25.445 | 69.312 | 32.942
| 41.6458 | 292.113 | 384.216 | 71.425 | 25.454 | 69.458 | 32.949
| 41.6528 | 292.86 | 383.85 | 71.581 | 25.463 | 69.562 | 32.963
| 41.6597 | 291.989 | 384.515 | 71.721 | 25.472 | 69.664 | 32.981
| 41.6667 | 293.163 | 394.052 | 71.867 | 25.483 | 70.036 | 33.004
| 41.6736 | 293.866 | 393.24 | 72.026 | 25.493 | 70.53 | 33.023
| 41.6806 | 293.293 | 392.829 | 72.15 | 25.509 | 70.8 | 33.04
| 41.6875 | 301.74 | 394.114 | 72.627 | 25.521 | 71.02 | 33.071
| 41.6944 | 302.656 | 394.375 | 73.094 | 25.542 | 71.212 | 33.103
| 41.7014 | 302.667 | 394.225 | 73.489 | 25.567 | 71.372 | 33.14
| 41.7083 | 302.186 | 395.679 | 73.849 | 25.599 | 71.523 | 33.18
| 41.7153 | 299.184 | 401.738 | 74.073 | 25.63 | 71.666 | 33.216
| 41.7222 | 303.25 | 397.999 | 74.453 | 25.657 | 72.142 | 33.256
| 41.7292 | 303.488 | 397.621 | 74.705 | 25.686 | 72.217 | 33.296
| 41.7361 | 302.95 | 397.466 | 74.941 | 25.72 | 72.32 | 33.34
| 41.7431 | 302.221 | 396.228 | 75.125 | 25.745 | 72.395 | 33.388
| 41.75 | 302.592 | 387.017 | 75.239 | 25.781 | 72.269 | 33.435
| 41.7569 | 292.529 | 386.105 | 74.986 | 25.806 | 71.731 | 33.481
| 41.7639 | 293.238 | 385.157 | 74.705 | 25.833 | 71.487 | 33.525
| 41.7778 | 292.513 | 376.751 | 74.295 | 25.86 | 70.605 | 33.6
| 41.7847 | 281.343 | 376.152 | 73.692 | 25.86 | 70.31 | 33.628
| 41.7917 | 281.803 | 397.351 | 73.096 | 25.86 | 70.64 | 33.653
| 41.7986 | 274.786 | 396.389 | 72.452 | 25.857 | 71.641 | 33.674
| 41.8056 | 275.042 | 390.188 | 71.713 | 25.839 | 71.723 | 33.691
| 41.8125 | 267.535 | 381.913 | 71.119 | 25.823 | 71.765 | 33.715
| 41.8194 | 268.84 | 382.192 | 70.25 | 25.793 | 71.318 | 33.736
| 41.8264 | 269.111 | 383.573 | 69.598 | 25.774 | 71.186 | 33.765
| 41.8333 | 261.655 | 371.813 | 68.671 | 25.73 | 70.471 | 33.788
| 41.8403 | 261.92 | 372.741 | 67.926 | 25.688 | 70.1 | 33.81
| 41.8472 | 253.178 | 363.772 | 67.266 | 25.641 | 69.512 | 33.828
| 41.8542 | 251.14 | 361.299 | 66.241 | 25.593 | 68.983 | 33.838
| 41.8611 | 251.877 | 362.489 | 65.431 | 25.539 | 68.624 | 33.85
| 41.8681 | 250.44 | 350.302 | 64.687 | 25.48 | 67.803 | 33.843
| 41.875 | 241.928 | 350.323 | 63.938 | 25.428 | 67.313 | 33.84
| 41.8819 | 242.315 | 339.381 | 63.02 | 25.368 | 66.965 | 33.826
| 41.8889 | 241.292 | 339.468 | 62.258 | 25.303 | 66.08 | 33.809
| 41.8958 | 232.905 | 338.43 | 61.371 | 25.233 | 65.556 | 33.779
| 41.9028 | 233.082 | 329.051 | 60.481 | 25.168 | 64.705 | 33.75
| 41.9097 | 222.446 | 316.925 | 59.353 | 25.096 | 63.687 | 33.712
| 41.9167 | 213.053 | 308.714 | 58.38 | 25.015 | 62.699 | 33.671
| 41.9236 | 213.363 | 299.598 | 57.177 | 24.932 | 61.689 | 33.613
| 41.9306 | 204.3 | 290.547 | 56.011 | 24.84 | 60.674 | 33.561
| 41.9375 | 196.65 | 279.396 | 54.784 | 24.746 | 59.681 | 33.486
| 41.9444 | 196.614 | 271.013 | 53.592 | 24.648 | 58.636 | 33.41
| 41.9514 | 186.848 | 261.648 | 52.315 | 24.544 | 57.635 | 33.316
| 41.9583 | 184.699 | 259.934 | 51.174 | 24.434 | 56.617 | 33.223
| 41.9653 | 177.013 | 239.523 | 49.858 | 24.325 | 55.399 | 33.121
| 41.9722 | 178.048 | 251.858 | 48.789 | 24.211 | 54.678 | 33.011
| 41.9792 | 177.888 | 240.999 | 47.854 | 24.098 | 53.808 | 32.888
| 41.9861 | 177.509 | 228.652 | 47.023 | 23.983 | 53.119 | 32.761
| 41.9931 | 176.842 | 227.94 | 46.257 | 23.879 | 52.078 | 32.63
| 42 | 169.686 | 227.858 | 45.46 | 23.773 | 51.417 | 32.495
| 42.0069 | 170.742 | 240.727 | 44.696 | 23.662 | 51.313 | 32.351
| 42.0139 | 162.459 | 232.737 | 43.832 | 23.562 | 50.833 | 32.206
| 42.0208 | 162.531 | 233.241 | 43.074 | 23.457 | 50.395 | 32.063
| 42.0278 | 162.359 | 232.403 | 42.411 | 23.348 | 50.001 | 31.918
| 42.0347 | 162.208 | 222.287 | 41.809 | 23.24 | 49.444 | 31.775
| 42.0417 | 154.192 | 221.822 | 41.182 | 23.146 | 48.836 | 31.635
| 42.0486 | 154.234 | 221.94 | 40.512 | 23.043 | 48.385 | 31.499
| 42.0556 | 154.903 | 222.165 | 39.956 | 22.952 | 48.017 | 31.358
| 42.0625 | 154.717 | 212.591 | 39.46 | 22.858 | 47.483 | 31.22
| 42.0694 | 154.407 | 212.6 | 39.009 | 22.77 | 46.958 | 31.082
| 42.0764 | 146.166 | 212.497 | 38.523 | 22.679 | 46.563 | 30.95
| 42.0833 | 146.267 | 212.152 | 37.965 | 22.593 | 46.213 | 30.809
| 42.0903 | 146.408 | 212.452 | 37.498 | 22.501 | 45.907 | 30.679
| 42.0972 | 146.159 | 213.173 | 37.085 | 22.416 | 45.618 | 30.546
| 42.1042 | 146.585 | 213.3 | 36.716 | 22.325 | 45.366 | 30.413
| 42.1111 | 145.702 | 203.319 | 36.371 | 22.251 | 44.814 | 30.286
| 42.1181 | 145.567 | 203.419 | 36.063 | 22.176 | 44.412 | 30.161
| 42.125 | 145.48 | 203.175 | 35.78 | 22.093 | 44.083 | 30.034
| 42.1319 | 145.785 | 203.271 | 35.528 | 22.026 | 43.805 | 29.912
| 42.1389 | 145.911 | 202.761 | 35.293 | 21.954 | 43.543 | 29.789
| 42.1458 | 145.89 | 203.3 | 35.083 | 21.887 | 43.3 | 29.663
| 42.1528 | 146.325 | 215.312 | 34.897 | 21.818 | 43.151 | 29.542
| 42.1597 | 152.735 | 225.492 | 34.85 | 21.759 | 43.284 | 29.429
| 42.1667 | 160.06 | 225.724 | 34.954 | 21.693 | 43.604 | 29.313
| 42.1736 | 160.767 | 238.565 | 35.09 | 21.645 | 43.869 | 29.2
| 42.1806 | 170.414 | 248.811 | 35.455 | 21.595 | 44.309 | 29.095
| 42.1875 | 179.684 | 249.394 | 35.797 | 21.553 | 44.703 | 28.996
| 42.1944 | 179.719 | 262.99 | 36.318 | 21.522 | 45.233 | 28.906
| 42.2014 | 189.062 | 271.976 | 36.92 | 21.496 | 45.835 | 28.822
| 42.2083 | 189.705 | 280.627 | 37.503 | 21.48 | 46.446 | 28.746
| 42.2153 | 199.482 | 293.174 | 38.308 | 21.467 | 47.137 | 28.683
| 42.2222 | 207.774 | 302.877 | 39.231 | 21.463 | 47.927 | 28.627
| 42.2292 | 215.515 | 301.218 | 40.23 | 21.47 | 48.676 | 28.581
| 42.2361 | 226.257 | 324.212 | 41.394 | 21.484 | 50.066 | 28.545
| 42.2431 | 233.223 | 342.685 | 42.772 | 21.513 | 51.622 | 28.519
| 42.25 | 245.444 | 361.716 | 44.384 | 21.549 | 53.343 | 28.513
| 42.2569 | 258.45 | 371.433 | 46.207 | 21.602 | 55.176 | 28.518
| 42.2639 | 276.003 | 394.781 | 48.405 | 21.677 | 57.291 | 28.535
| 42.2708 | 285.003 | 408.235 | 50.667 | 21.764 | 59.383 | 28.581
| 42.2778 | 298.449 | 428.042 | 53.094 | 21.869 | 61.953 | 28.644
| 42.2847 | 312.045 | 444.746 | 55.737 | 21.992 | 64.337 | 28.732
| 42.2917 | 323.429 | 464.244 | 58.537 | 22.137 | 67.332 | 28.84
| 42.2986 | 327.226 | 468.236 | 61.61 | 22.294 | 70.244 | 28.982
| 42.3056 | 338.024 | 481.336 | 64.631 | 22.47 | 72.881 | 29.151
| 42.3125 | 346.812 | 493.671 | 67.712 | 22.668 | 75.871 | 29.349
| 42.3194 | 345.765 | 490.924 | 70.558 | 22.872 | 77.752 | 29.566
| 42.3264 | 346.359 | 490.089 | 73.017 | 23.086 | 79.111 | 29.815
| 42.3333 | 346.881 | 492.275 | 75.325 | 23.306 | 80.483 | 30.087
| 42.3403 | 346.211 | 489.94 | 77.319 | 23.517 | 81.592 | 30.369
| 42.3472 | 345.516 | 490.147 | 79.033 | 23.736 | 82.528 | 30.666
| 42.3542 | 345.06 | 488.75 | 80.512 | 23.936 | 83.333 | 30.972
| 42.3611 | 339.624 | 488.097 | 81.775 | 24.135 | 84.136 | 31.271
| 42.3681 | 339.621 | 488.064 | 82.579 | 24.32 | 84.888 | 31.578
| 42.375 | 338.531 | 478.235 | 83.363 | 24.496 | 85.158 | 31.88
| 42.3819 | 339.905 | 478.414 | 84.072 | 24.653 | 85.358 | 32.181
| 42.3889 | 331.546 | 479.474 | 84.527 | 24.814 | 85.784 | 32.474
| 42.3958 | 331.615 | 470.623 | 84.706 | 24.959 | 86.276 | 32.767
| 42.4028 | 331.482 | 469.553 | 84.921 | 25.091 | 86.137 | 33.038
| 42.4097 | 331.489 | 469.326 | 85.12 | 25.208 | 86.347 | 33.303
| 42.4167 | 323.551 | 459.493 | 84.782 | 25.323 | 85.896 | 33.559
| 42.4236 | 322.595 | 459.349 | 84.605 | 25.423 | 85.858 | 33.805
| 42.4306 | 315.241 | 447.582 | 84.377 | 25.51 | 85.844 | 34.032
| 42.4375 | 314.097 | 448.655 | 83.787 | 25.591 | 85.212 | 34.247
| 42.4444 | 315.471 | 448.447 | 83.389 | 25.653 | 85.086 | 34.453
| 42.4514 | 307.33 | 439.668 | 82.819 | 25.719 | 84.472 | 34.644
| 42.4583 | 306.551 | 437.983 | 82.079 | 25.763 | 84.142 | 34.818
| 42.4653 | 306.324 | 428.641 | 81.499 | 25.801 | 83.941 | 34.979
| 42.4722 | 299.496 | 430.099 | 80.709 | 25.836 | 83.267 | 35.129
| 42.4792 | 299.757 | 430.018 | 80.001 | 25.858 | 83.067 | 35.269
| 42.4861 | 298.829 | 420.039 | 79.389 | 25.874 | 82.258 | 35.393
| 42.4931 | 299.048 | 420.143 | 78.88 | 25.889 | 81.872 | 35.504
| 42.5 | 292.477 | 419.666 | 78.097 | 25.897 | 81.663 | 35.602
| 42.5069 | 291.052 | 418.901 | 77.406 | 25.898 | 81.529 | 35.693
| 42.5139 | 291.533 | 418.815 | 76.771 | 25.9 | 81.356 | 35.769
| 42.5208 | 292.585 | 410.719 | 76.28 | 25.892 | 80.739 | 35.854
| 42.5278 | 291.884 | 411.781 | 75.867 | 25.885 | 80.453 | 35.912
| 42.5347 | 284.907 | 411.605 | 75.155 | 25.881 | 80.273 | 35.968
| 42.5417 | 284.382 | 412.027 | 74.536 | 25.869 | 80.189 | 36.018
| 42.5486 | 284.612 | 402.61 | 74.009 | 25.858 | 79.417 | 36.066
| 42.5556 | 284.656 | 403.446 | 73.573 | 25.844 | 79.099 | 36.107
| 42.5625 | 284.883 | 402.207 | 73.166 | 25.831 | 78.861 | 36.141
| 42.5694 | 284.924 | 402.84 | 72.829 | 25.816 | 78.722 | 36.172
| 42.5764 | 284.874 | 402.328 | 72.522 | 25.801 | 78.593 | 36.199
| 42.5833 | 285.036 | 402.18 | 72.257 | 25.792 | 78.491 | 36.216
| 42.5903 | 284.017 | 401.523 | 72.009 | 25.774 | 78.4 | 36.236
| 42.5972 | 284.307 | 411.438 | 71.824 | 25.764 | 78.86 | 36.252
| 42.6042 | 284.971 | 411.853 | 71.669 | 25.758 | 79.161 | 36.266
| 42.6111 | 284.994 | 411.706 | 71.534 | 25.746 | 79.32 | 36.281
| 42.6181 | 284.309 | 410.648 | 71.405 | 25.743 | 79.377 | 36.302
| 42.625 | 284.664 | 411.411 | 71.31 | 25.732 | 79.454 | 36.321
| 42.6319 | 291.203 | 411.538 | 71.494 | 25.73 | 79.52 | 36.348
| 42.6389 | 291.435 | 411.65 | 71.655 | 25.732 | 79.6 | 36.375
| 42.6458 | 291.05 | 421.801 | 71.803 | 25.732 | 80.129 | 36.402
| 42.6528 | 291.795 | 422.45 | 71.928 | 25.743 | 80.603 | 36.427
| 42.6597 | 291.953 | 423.537 | 72.06 | 25.75 | 80.93 | 36.459
| 42.6667 | 291.729 | 422.533 | 72.175 | 25.764 | 81.143 | 36.495
| 42.6736 | 292.486 | 421.816 | 72.292 | 25.777 | 81.331 | 36.533
| 42.6806 | 292.483 | 424.278 | 72.415 | 25.789 | 81.535 | 36.578
| 42.6875 | 301.107 | 431.727 | 73.044 | 25.802 | 82.034 | 36.624
| 42.6944 | 301.251 | 432.604 | 73.465 | 25.821 | 82.585 | 36.672
| 42.7014 | 301.478 | 432.444 | 73.847 | 25.85 | 82.965 | 36.716
| 42.7083 | 300.731 | 431.044 | 74.154 | 25.882 | 83.196 | 36.776
| 42.7153 | 300.984 | 430.855 | 74.416 | 25.905 | 83.373 | 36.838
| 42.7222 | 301.399 | 432.674 | 74.652 | 25.938 | 83.541 | 36.896
| 42.7292 | 301.292 | 432.464 | 74.889 | 25.966 | 83.737 | 36.963
| 42.7361 | 301.767 | 432.649 | 75.09 | 25.997 | 83.914 | 37.026
| 42.7431 | 301.225 | 431.213 | 75.252 | 26.026 | 84.039 | 37.091
| 42.75 | 300.543 | 422.623 | 75.358 | 26.058 | 83.675 | 37.152
| 42.7569 | 294.031 | 420.421 | 75.223 | 26.085 | 83.314 | 37.218
| 42.7639 | 290.415 | 417.128 | 74.848 | 26.103 | 82.912 | 37.281
| 42.7708 | 292.864 | 407.156 | 74.602 | 26.117 | 82.503 | 37.342
| 42.7778 | 283.795 | 407.975 | 74.088 | 26.125 | 81.779 | 37.393
| 42.7847 | 284.775 | 407.449 | 73.612 | 26.131 | 81.458 | 37.444
| 42.7917 | 283.701 | 398.564 | 73.208 | 26.128 | 80.591 | 37.478
| 42.7986 | 276.927 | 398.189 | 72.503 | 26.119 | 80.149 | 37.507
| 42.8056 | 277.785 | 389.146 | 71.953 | 26.109 | 79.356 | 37.534
| 42.8125 | 269.865 | 390.5 | 71.186 | 26.094 | 78.887 | 37.545
| 42.8194 | 270.168 | 380.219 | 70.515 | 26.081 | 78.177 | 37.556
| 42.8264 | 269.97 | 380.86 | 69.93 | 26.039 | 77.517 | 37.554
| 42.8333 | 261.603 | 371.206 | 69.014 | 26.018 | 76.892 | 37.549
| 42.8403 | 259.832 | 368.814 | 68.268 | 25.969 | 76.13 | 37.526
| 42.8472 | 260.654 | 369.026 | 67.559 | 25.925 | 75.563 | 37.501
| 42.8542 | 251.761 | 358.044 | 66.716 | 25.882 | 74.788 | 37.476
| 42.8611 | 252.179 | 359.783 | 65.908 | 25.835 | 74.082 | 37.434
| 42.8681 | 252.081 | 348.976 | 65.233 | 25.78 | 73.375 | 37.389
| 42.875 | 240.999 | 345.033 | 64.256 | 25.721 | 72.498 | 37.329
| 42.8819 | 241.614 | 346.094 | 63.37 | 25.664 | 71.831 | 37.281
| 42.8889 | 241.534 | 335.566 | 62.616 | 25.602 | 71.023 | 37.215
| 42.8958 | 232.3 | 335.75 | 61.735 | 25.54 | 70.271 | 37.144
| 42.9028 | 232.496 | 322.905 | 60.842 | 25.465 | 69.463 | 37.063
| 42.9097 | 222.906 | 313.298 | 59.748 | 25.399 | 68.399 | 36.985
| 42.9167 | 212.661 | 302.72 | 58.775 | 25.318 | 67.31 | 36.893
| 42.9236 | 212.261 | 302.504 | 57.524 | 25.241 | 66.138 | 36.797
| 42.9306 | 204.162 | 290.392 | 56.347 | 25.145 | 65.071 | 36.695
| 42.9375 | 196.96 | 280.555 | 55.125 | 25.049 | 63.946 | 36.579
| 42.9444 | 196.306 | 272.537 | 53.939 | 24.947 | 62.836 | 36.463
| 42.9514 | 187.295 | 260.747 | 52.679 | 24.848 | 61.771 | 36.342
| 42.9583 | 187.395 | 262.345 | 51.565 | 24.742 | 60.622 | 36.201
| 42.9653 | 177.072 | 252.701 | 50.227 | 24.63 | 59.465 | 36.057
| 42.9722 | 177.015 | 244.258 | 49.139 | 24.515 | 58.53 | 35.904
| 42.9792 | 175.239 | 241.416 | 48.181 | 24.399 | 57.64 | 35.756
| 42.9861 | 175.218 | 229.72 | 47.269 | 24.29 | 56.831 | 35.593
| 42.9931 | 175.266 | 230.451 | 46.472 | 24.173 | 55.79 | 35.425
| 43 | 175.251 | 218.349 | 45.776 | 24.067 | 54.865 | 35.254
| 43.0069 | 165.893 | 239.893 | 44.88 | 23.964 | 54.718 | 35.079
| 43.0139 | 165.522 | 231.73 | 44.124 | 23.853 | 54.35 | 34.902
| 43.0208 | 164.898 | 230.764 | 43.447 | 23.748 | 53.699 | 34.729
| 43.0278 | 164.963 | 230.863 | 42.838 | 23.644 | 53.187 | 34.552
| 43.0347 | 157.796 | 230.075 | 42.08 | 23.549 | 52.731 | 34.383
| 43.0417 | 157.153 | 220.02 | 41.432 | 23.449 | 52.003 | 34.212
| 43.0486 | 157.484 | 220.871 | 40.871 | 23.351 | 51.458 | 34.043
| 43.0556 | 157.648 | 220.983 | 40.369 | 23.254 | 51.012 | 33.875
| 43.0625 | 148.98 | 213.171 | 39.786 | 23.161 | 50.455 | 33.714
| 43.0694 | 149.456 | 213.194 | 39.214 | 23.072 | 49.929 | 33.546
| 43.0764 | 149.156 | 213.615 | 38.714 | 22.983 | 49.5 | 33.388
| 43.0833 | 149.328 | 213.287 | 38.273 | 22.903 | 49.129 | 33.226
| 43.0903 | 148.942 | 213.489 | 37.871 | 22.806 | 48.775 | 33.058
| 43.0972 | 149.324 | 214.013 | 37.528 | 22.725 | 48.464 | 32.906
| 43.1042 | 149.255 | 204.61 | 37.202 | 22.647 | 47.87 | 32.75
| 43.1111 | 149.593 | 204.474 | 36.921 | 22.564 | 47.444 | 32.592
| 43.1181 | 141.746 | 204.544 | 36.61 | 22.488 | 47.094 | 32.443
| 43.125 | 141.61 | 204.417 | 36.187 | 22.417 | 46.754 | 32.291
| 43.1319 | 141.59 | 204.274 | 35.834 | 22.341 | 46.442 | 32.146
| 43.1389 | 141.695 | 204.724 | 35.529 | 22.267 | 46.18 | 32
| 43.1458 | 142.216 | 204.535 | 35.25 | 22.196 | 45.907 | 31.855
| 43.1528 | 149.249 | 216.109 | 35.05 | 22.128 | 45.733 | 31.714
| 43.1597 | 157.32 | 225.291 | 35.01 | 22.062 | 45.82 | 31.577
| 43.1667 | 157.643 | 225.869 | 35.174 | 22.004 | 46.069 | 31.442
| 43.1736 | 167.143 | 239.201 | 35.403 | 21.951 | 46.318 | 31.31
| 43.1806 | 167.346 | 248.31 | 35.687 | 21.905 | 46.721 | 31.186
| 43.1875 | 176.908 | 257.647 | 36.156 | 21.864 | 47.14 | 31.068
| 43.1944 | 186.063 | 267.071 | 36.554 | 21.831 | 47.577 | 30.958
| 43.2014 | 185.69 | 266.993 | 37.216 | 21.811 | 48.147 | 30.858
| 43.2083 | 195.908 | 277.121 | 37.883 | 21.791 | 48.781 | 30.766
| 43.2153 | 203.724 | 286.178 | 38.683 | 21.782 | 49.46 | 30.686
| 43.2222 | 211.679 | 298.276 | 39.563 | 21.774 | 50.278 | 30.613
| 43.2292 | 219.153 | 308.171 | 40.508 | 21.784 | 51.125 | 30.551
| 43.2361 | 219.351 | 324.327 | 41.623 | 21.798 | 52.207 | 30.501
| 43.2431 | 232.381 | 334.25 | 43.05 | 21.823 | 53.592 | 30.46
| 43.25 | 245.964 | 361.33 | 44.689 | 21.862 | 55.392 | 30.433
| 43.2569 | 258.861 | 379.268 | 46.549 | 21.917 | 57.389 | 30.424
| 43.2639 | 271.655 | 390.18 | 48.588 | 21.986 | 59.461 | 30.428
| 43.2708 | 288.155 | 411.696 | 50.889 | 22.075 | 61.529 | 30.452
| 43.2778 | 297.963 | 426.027 | 53.414 | 22.183 | 63.894 | 30.502
| 43.2847 | 304.186 | 448.137 | 56.095 | 22.306 | 66.687 | 30.578
| 43.2917 | 317.139 | 460.717 | 58.956 | 22.448 | 69.193 | 30.668
| 43.2986 | 327.766 | 471.228 | 61.942 | 22.608 | 72.218 | 30.791
| 43.3056 | 337.754 | 481.528 | 65.012 | 22.789 | 74.872 | 30.952
| 43.3125 | 341.683 | 494.975 | 67.99 | 22.983 | 78.05 | 31.133
| 43.3194 | 351.247 | 497.757 | 71.128 | 23.186 | 80.242 | 31.337
| 43.3264 | 349.416 | 492.989 | 73.844 | 23.403 | 81.865 | 31.578
| 43.3333 | 344.818 | 495.89 | 76.31 | 23.628 | 83.307 | 31.838
| 43.3403 | 343.969 | 494.33 | 77.959 | 23.856 | 84.405 | 32.117
| 43.3472 | 343.304 | 483.721 | 79.511 | 24.068 | 84.989 | 32.41
| 43.3542 | 342.683 | 481.504 | 80.869 | 24.271 | 85.293 | 32.709
| 43.3611 | 341.96 | 482.728 | 82.054 | 24.464 | 85.8 | 33.01
| 43.3681 | 342.811 | 481.766 | 83.109 | 24.646 | 86.392 | 33.308
| 43.375 | 341.714 | 481.971 | 84.033 | 24.823 | 86.969 | 33.596
| 43.3819 | 334.597 | 482.578 | 84.379 | 24.988 | 87.597 | 33.88
| 43.3889 | 335.13 | 474.89 | 84.843 | 25.141 | 88.021 | 34.154
| 43.3958 | 328.951 | 474.89 | 85.261 | 25.286 | 88.222 | 34.433
| 43.4028 | 327.915 | 475.693 | 85.213 | 25.42 | 88.598 | 34.696
| 43.4097 | 328.21 | 466.078 | 85.249 | 25.536 | 88.212 | 34.951
| 43.4167 | 328.34 | 465.484 | 85.306 | 25.648 | 88.293 | 35.2
| 43.4236 | 319.414 | 454.229 | 84.909 | 25.745 | 87.808 | 35.431
| 43.4306 | 319.212 | 456.357 | 84.61 | 25.833 | 87.635 | 35.647
| 43.4375 | 319.107 | 446.348 | 84.39 | 25.909 | 87.162 | 35.856
| 43.4444 | 312.721 | 447.316 | 83.732 | 25.98 | 86.858 | 36.05
| 43.4514 | 313.217 | 436.812 | 83.282 | 26.036 | 86.441 | 36.23
| 43.4583 | 303.342 | 436.446 | 82.693 | 26.087 | 85.904 | 36.391
| 43.4653 | 302.5 | 436.86 | 81.86 | 26.131 | 85.654 | 36.546
| 43.4722 | 301.927 | 427.894 | 81.198 | 26.158 | 85.093 | 36.684
| 43.4792 | 302.965 | 427.307 | 80.64 | 26.189 | 84.707 | 36.81
| 43.4861 | 294.636 | 417.715 | 79.721 | 26.204 | 84.225 | 36.921
| 43.4931 | 293.67 | 418.611 | 78.974 | 26.209 | 83.611 | 37.019
| 43.5 | 293.654 | 418.362 | 78.319 | 26.214 | 83.277 | 37.112
| 43.5069 | 294.37 | 418.262 | 77.766 | 26.214 | 83.108 | 37.195
| 43.5139 | 294.638 | 420.284 | 77.309 | 26.215 | 83.033 | 37.257
| 43.5208 | 294.609 | 412.804 | 76.931 | 26.212 | 82.518 | 37.324
| 43.5278 | 287.104 | 412.884 | 76.207 | 26.213 | 82.281 | 37.377
| 43.5347 | 286.809 | 412.875 | 75.603 | 26.206 | 82.087 | 37.428
| 43.5417 | 287.138 | 402.745 | 75.109 | 26.193 | 81.546 | 37.469
| 43.5486 | 287.451 | 402.901 | 74.665 | 26.181 | 81.072 | 37.505
| 43.5556 | 287.394 | 403.344 | 74.282 | 26.167 | 80.807 | 37.539
| 43.5625 | 287.076 | 403.806 | 73.95 | 26.157 | 80.624 | 37.564
| 43.5694 | 287.72 | 403.698 | 73.675 | 26.147 | 80.521 | 37.582
| 43.5764 | 287.682 | 404.109 | 73.448 | 26.141 | 80.45 | 37.597
| 43.5833 | 287.182 | 405.123 | 73.245 | 26.132 | 80.38 | 37.611
| 43.5903 | 288.341 | 406.681 | 73.101 | 26.124 | 80.375 | 37.626
| 43.5972 | 289.627 | 406.994 | 73.038 | 26.113 | 80.459 | 37.634
| 43.6042 | 287.743 | 405.435 | 72.928 | 26.117 | 80.426 | 37.642
| 43.6111 | 287.754 | 413.76 | 72.8 | 26.115 | 80.731 | 37.656
| 43.6181 | 288.232 | 414.449 | 72.708 | 26.11 | 81.064 | 37.665
| 43.625 | 289.065 | 414.519 | 72.666 | 26.11 | 81.313 | 37.678
| 43.6319 | 289.439 | 415.026 | 72.617 | 26.112 | 81.441 | 37.695
| 43.6389 | 289.052 | 413.896 | 72.582 | 26.108 | 81.545 | 37.715
| 43.6458 | 289.01 | 414.188 | 72.535 | 26.115 | 81.581 | 37.73
| 43.6528 | 289.366 | 414.506 | 72.512 | 26.112 | 81.647 | 37.752
| 43.6597 | 294.615 | 422.89 | 72.796 | 26.119 | 82.304 | 37.78
| 43.6667 | 294.698 | 423.913 | 73.001 | 26.124 | 82.676 | 37.808
| 43.6736 | 295.057 | 423.71 | 73.179 | 26.139 | 82.928 | 37.839
| 43.6806 | 294.951 | 425.228 | 73.349 | 26.15 | 83.14 | 37.869
| 43.6875 | 294.941 | 425.121 | 73.517 | 26.169 | 83.337 | 37.91
| 43.6944 | 295.77 | 426.2 | 73.662 | 26.183 | 83.515 | 37.95
| 43.7014 | 303.95 | 434.143 | 74.206 | 26.2 | 83.902 | 37.99
| 43.7083 | 299.893 | 428.597 | 74.515 | 26.223 | 84.361 | 38.038
| 43.7153 | 299.5 | 430.1 | 74.713 | 26.252 | 84.482 | 38.081
| 43.7222 | 299.894 | 429.639 | 74.921 | 26.274 | 84.658 | 38.133
| 43.7292 | 298.549 | 435.45 | 75.011 | 26.305 | 84.939 | 38.184
| 43.8264 | 293.789 | 408.647 | 76.761 | 26.621 | 86.99 | 38.957
| 43.8333 | 257.808 | 370.139 | 75.108 | 26.641 | 83.705 | 39.01
| 43.8403 | 255.273 | 368.052 | 73.316 | 26.64 | 81.211 | 39.062
| 43.8472 | 256.303 | 370.185 | 71.85 | 26.605 | 79.82 | 39.095
| 43.8542 | 256.352 | 358.733 | 70.649 | 26.558 | 78.472 | 39.108
| 43.8611 | 249.921 | 359.008 | 69.338 | 26.502 | 77.551 | 39.1
| 43.8681 | 249.791 | 351.549 | 68.161 | 26.443 | 76.63 | 39.068
| 43.875 | 248.817 | 351.54 | 67.16 | 26.372 | 75.83 | 39.027
| 43.8819 | 240.551 | 343.024 | 65.908 | 26.308 | 74.783 | 38.971
| 43.8889 | 241.341 | 334.196 | 64.879 | 26.225 | 73.978 | 38.899
| 43.8958 | 232.41 | 333.686 | 63.712 | 26.147 | 73.006 | 38.818
| 43.9028 | 231.476 | 324.695 | 62.631 | 26.067 | 71.989 | 38.73
| 43.9097 | 223.768 | 315.829 | 61.374 | 25.977 | 70.902 | 38.636
| 43.9167 | 213.78 | 305.919 | 60.202 | 25.897 | 69.806 | 38.538
| 43.9236 | 206.951 | 296.296 | 58.92 | 25.802 | 68.719 | 38.43
| 43.9306 | 206.959 | 285.915 | 57.614 | 25.699 | 67.573 | 38.304
| 43.9375 | 198.372 | 285.985 | 56.33 | 25.585 | 66.281 | 38.173
| 43.9444 | 198.065 | 278.458 | 55.112 | 25.475 | 65.125 | 38.042
| 43.9514 | 187.996 | 268.431 | 53.743 | 25.368 | 63.903 | 37.897
| 43.9583 | 178.606 | 256.194 | 52.496 | 25.253 | 62.672 | 37.749
| 43.9653 | 179.666 | 256.368 | 51.211 | 25.141 | 61.714 | 37.596
| 43.9722 | 179.2 | 248.515 | 50.12 | 25.005 | 60.606 | 37.421
| 43.9792 | 178.704 | 237.618 | 49.166 | 24.887 | 59.652 | 37.254
| 43.9861 | 179.265 | 238.094 | 48.312 | 24.777 | 58.731 | 37.082
| 43.9931 | 170.594 | 227.316 | 47.331 | 24.65 | 57.677 | 36.892
| 44 | 171.468 | 227.821 | 46.483 | 24.538 | 56.894 | 36.708
| 44.0069 | 169.15 | 237.468 | 45.735 | 24.418 | 56.703 | 36.518
| 44.0139 | 169.735 | 238.123 | 45.017 | 24.307 | 56.234 | 36.327
| 44.0208 | 159.986 | 229.697 | 44.133 | 24.204 | 55.696 | 36.136
| 44.0278 | 159.746 | 229.803 | 43.384 | 24.091 | 55.052 | 35.949
| 44.0347 | 159.385 | 229.592 | 42.701 | 23.978 | 54.518 | 35.765
| 44.0417 | 159.308 | 219.468 | 42.095 | 23.878 | 53.85 | 35.581
| 44.0486 | 159.538 | 219.934 | 41.554 | 23.78 | 53.214 | 35.399
| 44.0556 | 151.755 | 220.479 | 40.877 | 23.675 | 52.712 | 35.219
| 44.0625 | 151.989 | 212.74 | 40.306 | 23.578 | 52.246 | 35.042
| 44.0694 | 151.924 | 213.239 | 39.792 | 23.477 | 51.605 | 34.862
| 44.0764 | 152.005 | 212.662 | 39.336 | 23.378 | 51.131 | 34.686
| 44.0833 | 152.031 | 212.796 | 38.926 | 23.293 | 50.717 | 34.513
| 44.0903 | 152.011 | 213.181 | 38.558 | 23.207 | 50.347 | 34.343
| 44.0972 | 144.788 | 213.565 | 38.191 | 23.116 | 49.993 | 34.167
| 44.1042 | 145.013 | 213.259 | 37.702 | 23.034 | 49.68 | 34.001
| 44.1111 | 144.795 | 204.326 | 37.291 | 22.949 | 49.058 | 33.834
| 44.1181 | 144.68 | 204.606 | 36.94 | 22.866 | 48.635 | 33.675
| 44.125 | 144.455 | 203.927 | 36.609 | 22.789 | 48.264 | 33.512
| 44.1319 | 144.281 | 204.472 | 36.317 | 22.712 | 47.941 | 33.355
| 44.1389 | 144.794 | 204.168 | 36.052 | 22.635 | 47.627 | 33.197
| 44.1458 | 144.424 | 204.462 | 35.811 | 22.562 | 47.342 | 33.044
| 44.1528 | 145.078 | 213.578 | 35.598 | 22.493 | 47.214 | 32.889
| 44.1597 | 151.386 | 223.042 | 35.559 | 22.423 | 47.279 | 32.738
| 44.1667 | 159.704 | 233.08 | 35.688 | 22.362 | 47.467 | 32.591
| 44.1736 | 159.35 | 232.27 | 35.789 | 22.305 | 47.71 | 32.454
| 44.1806 | 169.651 | 242.676 | 36.197 | 22.254 | 48.118 | 32.317
| 44.1875 | 178.078 | 251.58 | 36.584 | 22.213 | 48.545 | 32.191
| 44.1944 | 178.224 | 260.106 | 37.021 | 22.174 | 48.996 | 32.065
| 44.2014 | 188.699 | 269.765 | 37.654 | 22.146 | 49.538 | 31.957
| 44.2083 | 188.355 | 279.441 | 38.208 | 22.126 | 50.114 | 31.85
| 44.2153 | 198.039 | 289.092 | 39.025 | 22.118 | 50.783 | 31.765
| 44.2222 | 206.534 | 301.825 | 39.952 | 22.106 | 51.536 | 31.679
| 44.2292 | 214.598 | 313.166 | 40.966 | 22.109 | 52.388 | 31.609
| 44.2361 | 226.608 | 324.058 | 42.175 | 22.128 | 53.659 | 31.548
| 44.2431 | 237.981 | 340.777 | 43.585 | 22.148 | 55.016 | 31.493
| 44.25 | 250.127 | 358.411 | 45.209 | 22.186 | 56.832 | 31.459
| 44.2569 | 263.003 | 377.257 | 47.021 | 22.239 | 58.764 | 31.437
| 44.2639 | 275.779 | 395.704 | 49.013 | 22.312 | 60.864 | 31.436
| 44.2708 | 282.46 | 412.909 | 51.338 | 22.39 | 63.006 | 31.453
| 44.2778 | 296.176 | 424.857 | 53.799 | 22.494 | 65.481 | 31.496
| 44.2847 | 308.276 | 440.323 | 56.476 | 22.614 | 67.818 | 31.56
| 44.2917 | 320.373 | 454.936 | 59.307 | 22.753 | 70.567 | 31.654
| 44.2986 | 332.038 | 476.637 | 62.236 | 22.911 | 73.473 | 31.775
| 44.3056 | 341.085 | 485.683 | 65.213 | 23.084 | 76.054 | 31.923
| 44.3125 | 339.533 | 483.662 | 68.206 | 23.279 | 78.52 | 32.097
| 44.3194 | 348.229 | 494.669 | 71.478 | 23.487 | 81.506 | 32.298
| 44.3264 | 348.55 | 497.066 | 74.08 | 23.703 | 83.133 | 32.531
| 44.3333 | 348.823 | 496.25 | 76.435 | 23.923 | 84.555 | 32.786
| 44.3403 | 348.985 | 496.261 | 78.493 | 24.143 | 85.747 | 33.059
| 44.3472 | 341.03 | 484.211 | 79.93 | 24.361 | 86.222 | 33.344
| 44.3542 | 340.186 | 483.089 | 81.065 | 24.56 | 86.547 | 33.634
| 44.3611 | 339.489 | 481.86 | 82.107 | 24.751 | 87.102 | 33.929
| 44.3681 | 339.714 | 482.849 | 83.041 | 24.926 | 87.712 | 34.219
| 44.375 | 338.226 | 482.247 | 83.9 | 25.093 | 88.396 | 34.502
| 44.3819 | 339.201 | 484.042 | 84.69 | 25.254 | 89.076 | 34.781
| 44.3889 | 332.152 | 474.866 | 85.095 | 25.403 | 88.928 | 35.054
| 44.3958 | 334.032 | 475.47 | 85.436 | 25.549 | 89.321 | 35.314
| 44.4028 | 332.188 | 464.738 | 85.736 | 25.674 | 89.509 | 35.571
| 44.4097 | 323.173 | 465.797 | 85.892 | 25.799 | 89.226 | 35.817
| 44.4167 | 323.854 | 464.882 | 85.559 | 25.911 | 89.338 | 36.053
| 44.4236 | 323.072 | 458.877 | 85.378 | 26.011 | 88.919 | 36.276
| 44.4306 | 322.722 | 458.231 | 85.247 | 26.095 | 88.904 | 36.485
| 44.4375 | 314.518 | 445.148 | 84.658 | 26.18 | 88.213 | 36.686
| 44.4444 | 314.896 | 445.871 | 84.203 | 26.246 | 87.885 | 36.871
| 44.4514 | 307.487 | 445.766 | 83.537 | 26.298 | 87.865 | 37.039
| 44.4583 | 306.385 | 436.105 | 82.865 | 26.342 | 87.17 | 37.2
| 44.4653 | 306.841 | 427.892 | 82.308 | 26.377 | 86.65 | 37.341
| 44.4722 | 297.664 | 429.042 | 81.68 | 26.411 | 86.064 | 37.474
| 44.4792 | 297.728 | 429.441 | 80.8 | 26.435 | 85.812 | 37.596
| 44.4861 | 297.807 | 420.955 | 80.144 | 26.448 | 85.279 | 37.701
| 44.4931 | 299.307 | 420.987 | 79.602 | 26.454 | 84.874 | 37.793
| 44.5 | 290.952 | 421.939 | 78.953 | 26.459 | 84.722 | 37.875
| 44.5069 | 291.576 | 414.081 | 78.203 | 26.466 | 84.484 | 37.954
| 44.5139 | 291.915 | 414.443 | 77.59 | 26.46 | 83.908 | 38.017
| 44.5208 | 292.08 | 416.108 | 77.12 | 26.45 | 83.735 | 38.072
| 44.5278 | 292.44 | 406.574 | 76.689 | 26.446 | 83.281 | 38.126
| 44.5347 | 284.66 | 407.258 | 75.886 | 26.436 | 82.743 | 38.166
| 44.5417 | 285.26 | 408.831 | 75.298 | 26.422 | 82.527 | 38.206
| 44.5486 | 285.661 | 407.472 | 74.783 | 26.399 | 82.349 | 38.233
| 44.5556 | 285.79 | 407.467 | 74.336 | 26.388 | 82.227 | 38.254
| 44.5625 | 281.867 | 394.037 | 73.871 | 26.369 | 81.657 | 38.281
| 44.5694 | 281.939 | 403.623 | 73.412 | 26.353 | 81.476 | 38.296
| 44.5764 | 282.237 | 402.069 | 73.011 | 26.336 | 81.349 | 38.309
| 44.5833 | 281.802 | 402.522 | 72.64 | 26.311 | 81.194 | 38.312
| 44.5903 | 282.474 | 404.016 | 72.362 | 26.295 | 81.142 | 38.32
| 44.5972 | 282.387 | 411.634 | 72.111 | 26.275 | 81.393 | 38.319
| 44.6042 | 283.045 | 411.775 | 71.923 | 26.263 | 81.828 | 38.321
| 44.6111 | 282.978 | 411.969 | 71.739 | 26.245 | 81.98 | 38.326
| 44.6181 | 288.466 | 410.551 | 71.824 | 26.232 | 82.033 | 38.332
| 44.625 | 288.678 | 412.425 | 71.918 | 26.224 | 82.07 | 38.338
| 44.6319 | 288.651 | 411.967 | 71.998 | 26.217 | 82.116 | 38.346
| 44.6389 | 289.493 | 413.62 | 72.085 | 26.221 | 82.183 | 38.361
| 44.6458 | 290.479 | 421.508 | 72.192 | 26.221 | 82.43 | 38.376
| 44.6528 | 291.347 | 422.448 | 72.302 | 26.22 | 83.072 | 38.391
| 44.6597 | 290.988 | 422.038 | 72.4 | 26.227 | 83.397 | 38.407
| 44.6667 | 290.253 | 422.768 | 72.49 | 26.232 | 83.628 | 38.43
| 44.6736 | 298.221 | 423.804 | 72.988 | 26.238 | 83.818 | 38.46
| 44.6806 | 298.439 | 423.872 | 73.349 | 26.256 | 83.949 | 38.489
| 44.6875 | 298.206 | 430.597 | 73.666 | 26.275 | 84.104 | 38.522
| 44.6944 | 298.314 | 431.377 | 73.916 | 26.295 | 84.837 | 38.555
| 44.7014 | 297.81 | 431.726 | 74.148 | 26.316 | 85.215 | 38.592
| 44.7083 | 298.734 | 431.23 | 74.378 | 26.343 | 85.531 | 38.635
| 44.7153 | 297.671 | 431.515 | 74.544 | 26.361 | 85.693 | 38.678
| 44.7222 | 305.013 | 430.481 | 74.981 | 26.386 | 85.803 | 38.728
| 44.7292 | 304.431 | 429.717 | 75.394 | 26.412 | 85.918 | 38.783
| 44.7361 | 304.077 | 430.455 | 75.727 | 26.44 | 86.016 | 38.831
| 44.7431 | 303.16 | 428.393 | 75.976 | 26.471 | 86.05 | 38.882
| 44.75 | 295.517 | 426.217 | 76.048 | 26.5 | 86.013 | 38.935
| 44.7569 | 293.481 | 416.772 | 75.78 | 26.526 | 85.876 | 38.988
| 44.7639 | 297.518 | 421.034 | 75.757 | 26.55 | 85.484 | 39.041
| 44.7708 | 287.597 | 409.816 | 75.196 | 26.569 | 84.51 | 39.089
| 44.7778 | 288.059 | 408.533 | 74.834 | 26.572 | 84.077 | 39.133
| 44.7847 | 279.294 | 398.411 | 74.375 | 26.576 | 83.624 | 39.168
| 44.7917 | 280.048 | 400.254 | 73.689 | 26.57 | 82.862 | 39.199
| 44.7986 | 278.6 | 397.626 | 73.119 | 26.563 | 82.391 | 39.219
| 44.8056 | 278.866 | 388.935 | 72.616 | 26.568 | 81.755 | 39.24
| 44.8125 | 270.563 | 389.61 | 71.782 | 26.531 | 81.104 | 39.237
| 44.8194 | 270.628 | 380.009 | 71.138 | 26.503 | 80.281 | 39.236
| 44.8264 | 262.434 | 380.32 | 70.572 | 26.465 | 79.732 | 39.221
| 44.8333 | 261.919 | 372.655 | 69.611 | 26.434 | 79.007 | 39.206
| 44.8403 | 262.739 | 374.168 | 68.929 | 26.392 | 78.427 | 39.177
| 44.8472 | 256.069 | 364.676 | 68.005 | 26.346 | 77.572 | 39.153
| 44.8542 | 256.676 | 356.822 | 67.27 | 26.295 | 76.943 | 39.106
| 44.8611 | 247.978 | 357.477 | 66.618 | 26.244 | 76.095 | 39.056
| 44.8681 | 247.337 | 357.197 | 65.625 | 26.193 | 75.549 | 39.003
| 44.875 | 244.416 | 343.948 | 64.856 | 26.128 | 74.607 | 38.941
| 44.8819 | 246.035 | 345.408 | 64.085 | 26.064 | 73.854 | 38.873
| 44.8889 | 236.88 | 336.916 | 63.106 | 26.006 | 72.949 | 38.798
| 44.8958 | 236.712 | 336.18 | 62.265 | 25.935 | 72.294 | 38.721
| 44.9028 | 226.652 | 324.59 | 61.267 | 25.866 | 71.374 | 38.635
| 44.9097 | 227.254 | 315.086 | 60.313 | 25.792 | 70.311 | 38.545
| 44.9167 | 217.746 | 305.852 | 59.145 | 25.711 | 69.237 | 38.45
| 44.9236 | 206.727 | 295.846 | 58.079 | 25.627 | 68.141 | 38.344
| 44.9306 | 205.989 | 286.468 | 56.821 | 25.536 | 67.04 | 38.233
| 44.9375 | 198.657 | 286.599 | 55.6 | 25.436 | 65.875 | 38.116
| 44.9444 | 198.413 | 278.12 | 54.459 | 25.333 | 64.732 | 37.982
| 44.9514 | 188.339 | 267.495 | 53.148 | 25.229 | 63.539 | 37.851
| 44.9583 | 179.115 | 256.663 | 51.966 | 25.125 | 62.389 | 37.707
| 44.9653 | 179.164 | 247.408 | 50.71 | 25.008 | 61.443 | 37.553
| 44.9722 | 179.687 | 248.474 | 49.661 | 24.892 | 60.381 | 37.395
| 44.9792 | 179.091 | 238.349 | 48.75 | 24.772 | 59.454 | 37.23
| 44.9861 | 172.062 | 238.934 | 47.846 | 24.661 | 58.573 | 37.063
| 44.9931 | 170.758 | 225.124 | 46.908 | 24.555 | 57.531 | 36.891
| 45 | 170.586 | 217.488 | 46.09 | 24.439 | 56.712 | 36.711
| 45.0069 | 171.627 | 238.715 | 45.383 | 24.332 | 56.221 | 36.526
| 45.0139 | 164.101 | 239.098 | 44.531 | 24.222 | 56.015 | 36.344
| 45.0208 | 163.033 | 229.587 | 43.792 | 24.114 | 55.391 | 36.154
| 45.0278 | 163.31 | 229.863 | 43.142 | 24.003 | 54.866 | 35.972
| 45.0347 | 155.611 | 229.506 | 42.569 | 23.905 | 54.413 | 35.792
| 45.0417 | 155.043 | 220.973 | 41.8 | 23.802 | 53.801 | 35.612
| 45.0486 | 155.372 | 221.938 | 41.191 | 23.701 | 53.235 | 35.427
| 45.0556 | 155.125 | 222.39 | 40.649 | 23.62 | 52.796 | 35.26
| 45.0625 | 154.882 | 212.437 | 40.158 | 23.512 | 52.12 | 35.081
| 45.0694 | 147.31 | 212.656 | 39.726 | 23.417 | 51.571 | 34.912
| 45.0764 | 147.739 | 212.47 | 39.112 | 23.323 | 51.115 | 34.743
| 45.0833 | 147.379 | 212.545 | 38.618 | 23.231 | 50.714 | 34.569
| 45.0903 | 147.769 | 212.709 | 38.19 | 23.14 | 50.363 | 34.401
| 45.0972 | 148.045 | 212.859 | 37.804 | 23.053 | 50.026 | 34.237
| 45.1042 | 148.212 | 210.732 | 37.474 | 22.973 | 49.723 | 34.074
| 45.1111 | 147.648 | 204.396 | 37.151 | 22.892 | 49.127 | 33.912
| 45.1181 | 147.749 | 204.503 | 36.867 | 22.807 | 48.713 | 33.749
| 45.125 | 147.67 | 204.771 | 36.612 | 22.743 | 48.365 | 33.597
| 45.1319 | 147.983 | 204.31 | 36.38 | 22.661 | 48.038 | 33.441
| 45.1389 | 147.961 | 204.708 | 36.166 | 22.592 | 47.753 | 33.289
| 45.1458 | 147.955 | 205.498 | 35.983 | 22.52 | 47.489 | 33.139
| 45.1528 | 146.778 | 209.853 | 35.807 | 22.457 | 47.332 | 32.988
| 45.1597 | 154.347 | 219.363 | 35.688 | 22.392 | 47.452 | 32.843
| 45.1667 | 163.185 | 232.303 | 35.741 | 22.331 | 47.503 | 32.701
| 45.1736 | 163.353 | 232.603 | 35.964 | 22.278 | 47.803 | 32.564
| 45.1806 | 172.25 | 242.625 | 36.268 | 22.231 | 48.22 | 32.43
| 45.1875 | 172.611 | 256.347 | 36.595 | 22.191 | 48.604 | 32.306
| 45.1944 | 181.263 | 256.908 | 37.127 | 22.15 | 49.006 | 32.191
| 45.2014 | 191.089 | 269.764 | 37.624 | 22.123 | 49.579 | 32.08
| 45.2083 | 191.405 | 278.776 | 38.317 | 22.102 | 50.192 | 31.982
| 45.2153 | 200.795 | 287.128 | 39.074 | 22.091 | 50.864 | 31.894
| 45.2222 | 210.74 | 301.946 | 39.958 | 22.086 | 51.619 | 31.808
| 45.2292 | 218.05 | 313.363 | 40.944 | 22.093 | 52.521 | 31.742
| 45.2361 | 230.97 | 329.667 | 42.042 | 22.102 | 53.773 | 31.68
| 45.2431 | 233.63 | 334.164 | 43.498 | 22.132 | 55.149 | 31.635
| 45.25 | 243.75 | 357.814 | 45.114 | 22.164 | 56.992 | 31.6
| 45.2569 | 256.296 | 376.011 | 46.958 | 22.223 | 58.96 | 31.585
| 45.2639 | 276.698 | 395.662 | 49.144 | 22.291 | 61.066 | 31.589
| 45.2708 | 289.248 | 413.418 | 51.305 | 22.374 | 63.285 | 31.61
| 45.2778 | 288.874 | 421.234 | 53.671 | 22.485 | 65.651 | 31.653
| 45.2847 | 302.282 | 441.487 | 56.394 | 22.605 | 68.31 | 31.722
| 45.2917 | 321.694 | 460.444 | 59.485 | 22.748 | 71.164 | 31.819
| 45.2986 | 330.709 | 468.863 | 62.431 | 22.911 | 73.892 | 31.945
| 45.3056 | 341.043 | 488.791 | 65.41 | 23.086 | 76.557 | 32.097
| 45.3125 | 341.007 | 486.346 | 68.495 | 23.284 | 79.193 | 32.281
| 45.3194 | 350.479 | 498.534 | 71.671 | 23.495 | 81.895 | 32.492
| 45.3264 | 351.708 | 491.895 | 74.462 | 23.709 | 83.606 | 32.723
| 45.3333 | 351.363 | 490.648 | 76.888 | 23.933 | 84.6 | 32.982
| 45.3403 | 345.107 | 490.428 | 78.663 | 24.159 | 85.562 | 33.258
| 45.3472 | 345.212 | 491.395 | 80.257 | 24.374 | 86.528 | 33.546
| 45.3542 | 344.815 | 489.912 | 81.668 | 24.583 | 87.41 | 33.849
| 45.3611 | 344.229 | 481.279 | 82.928 | 24.778 | 87.92 | 34.133
| 45.3681 | 336.841 | 479.9 | 83.849 | 24.963 | 88.133 | 34.431
| 45.375 | 335.207 | 480.275 | 84.366 | 25.139 | 88.558 | 34.721
| 45.3819 | 335.235 | 479.792 | 84.862 | 25.299 | 89.019 | 35.01
| 45.3889 | 335.272 | 478.527 | 85.309 | 25.443 | 89.503 | 35.28
| 45.3958 | 334.107 | 472.056 | 85.721 | 25.587 | 89.765 | 35.548
| 45.4028 | 330.492 | 477.616 | 85.952 | 25.717 | 89.896 | 35.802
| 45.4097 | 329.646 | 464.292 | 86.033 | 25.838 | 89.744 | 36.053
| 45.4167 | 322.063 | 463.119 | 85.769 | 25.951 | 89.646 | 36.29
| 45.4236 | 321.472 | 454.801 | 85.484 | 26.047 | 89.365 | 36.523
| 45.4306 | 320.987 | 454.209 | 85.272 | 26.136 | 89.107 | 36.735
| 45.4375 | 314.361 | 445.354 | 84.669 | 26.214 | 88.892 | 36.942
| 45.4444 | 313.047 | 444.915 | 84.151 | 26.275 | 88.368 | 37.121
| 45.4514 | 313.408 | 446.32 | 83.763 | 26.332 | 88.282 | 37.298
| 45.4583 | 305.473 | 435.343 | 82.863 | 26.377 | 87.506 | 37.457
| 45.4653 | 304.653 | 434.904 | 82.218 | 26.412 | 87.219 | 37.603
| 45.4722 | 304.257 | 426.209 | 81.637 | 26.438 | 86.479 | 37.741
| 45.4792 | 296.983 | 427.207 | 80.808 | 26.463 | 86.093 | 37.859
| 45.4861 | 297.837 | 427.328 | 80.117 | 26.477 | 85.956 | 37.967
| 45.4931 | 296.882 | 418.279 | 79.499 | 26.483 | 85.189 | 38.058
| 45.5 | 296.98 | 418.801 | 78.978 | 26.489 | 84.853 | 38.148
| 45.5069 | 290.473 | 418.545 | 78.413 | 26.491 | 84.711 | 38.22
| 45.5139 | 290.155 | 409.924 | 77.648 | 26.492 | 84.563 | 38.284
| 45.5208 | 290.391 | 410.339 | 77.041 | 26.479 | 83.899 | 38.339
| 45.5278 | 289.718 | 410.104 | 76.511 | 26.474 | 83.586 | 38.39
| 45.5347 | 289.321 | 410.154 | 76.037 | 26.463 | 83.353 | 38.432
| 45.5417 | 281.624 | 410.523 | 75.488 | 26.45 | 83.198 | 38.47
| 45.5486 | 281.885 | 400.183 | 74.736 | 26.435 | 83.023 | 38.502
| 45.5556 | 281.2 | 400.674 | 74.124 | 26.414 | 82.288 | 38.523
| 45.5625 | 281.722 | 402.319 | 73.632 | 26.401 | 81.982 | 38.548
| 45.5694 | 283.227 | 402.203 | 73.214 | 26.378 | 81.812 | 38.558
| 45.5764 | 283.713 | 403.014 | 72.896 | 26.355 | 81.769 | 38.573
| 45.5833 | 284.537 | 404.246 | 72.635 | 26.334 | 81.748 | 38.578
| 45.5903 | 285.181 | 405.268 | 72.446 | 26.316 | 81.766 | 38.585
| 45.5972 | 285.61 | 406.065 | 72.289 | 26.302 | 81.791 | 38.591
| 45.6042 | 281.8 | 410.677 | 72.037 | 26.291 | 81.864 | 38.594
| 45.6111 | 287.389 | 410.624 | 71.873 | 26.272 | 82.13 | 38.592
| 45.6181 | 287.354 | 410.305 | 71.937 | 26.266 | 82.233 | 38.603
| 45.625 | 287.788 | 411.888 | 71.964 | 26.259 | 82.335 | 38.606
| 45.6319 | 287.918 | 409.963 | 71.987 | 26.253 | 82.383 | 38.612
| 45.6389 | 288.547 | 421.941 | 72.009 | 26.249 | 83.15 | 38.626
| 45.6458 | 288.817 | 421.301 | 72.049 | 26.247 | 83.585 | 38.638
| 45.6528 | 296.184 | 422.199 | 72.384 | 26.25 | 83.844 | 38.652
| 45.6597 | 296.456 | 422.372 | 72.732 | 26.254 | 84.089 | 38.68
| 45.6667 | 296.068 | 422.447 | 73.006 | 26.268 | 84.261 | 38.704
| 45.6736 | 295.331 | 422.179 | 73.215 | 26.283 | 84.344 | 38.736
| 45.6806 | 296.141 | 422.152 | 73.403 | 26.302 | 84.456 | 38.774
| 45.6875 | 294.818 | 431.073 | 73.567 | 26.317 | 85.022 | 38.808
| 45.6944 | 302.904 | 430.497 | 73.998 | 26.334 | 85.482 | 38.846
| 45.7014 | 302.277 | 429.842 | 74.43 | 26.353 | 85.756 | 38.887
| 45.7083 | 302.375 | 429.685 | 74.785 | 26.379 | 85.947 | 38.931
| 45.7153 | 301.782 | 430.47 | 75.096 | 26.408 | 86.117 | 38.977
| 45.7222 | 302.81 | 430.197 | 75.383 | 26.439 | 86.282 | 39.028
| 45.7292 | 301.535 | 430.379 | 75.606 | 26.468 | 86.395 | 39.079
| 45.7361 | 301.619 | 428.906 | 75.79 | 26.494 | 86.476 | 39.132
| 45.7431 | 301.451 | 428.457 | 75.938 | 26.522 | 86.536 | 39.189
| 45.75 | 295.548 | 419.799 | 76.06 | 26.549 | 86.609 | 39.237
| 45.7569 | 294.464 | 418.179 | 75.778 | 26.573 | 85.971 | 39.294
| 45.7639 | 292.778 | 416.817 | 75.575 | 26.594 | 85.673 | 39.344
| 45.7708 | 292.163 | 407.182 | 75.345 | 26.61 | 85.055 | 39.393
| 45.7778 | 285.923 | 407.561 | 74.805 | 26.615 | 84.496 | 39.436
| 45.7847 | 284.879 | 399.279 | 74.377 | 26.618 | 84.043 | 39.473
| 45.7917 | 276.644 | 399.094 | 73.977 | 26.615 | 83.287 | 39.499
| 45.7986 | 276.907 | 398.816 | 73.164 | 26.609 | 82.874 | 39.523
| 45.8056 | 276.945 | 390.384 | 72.571 | 26.593 | 82.036 | 39.534
| 45.8125 | 269.208 | 390.754 | 71.907 | 26.566 | 81.618 | 39.536
| 45.8194 | 269.273 | 380.563 | 71.128 | 26.544 | 80.736 | 39.536
| 45.8264 | 262.145 | 381.619 | 70.515 | 26.515 | 80.208 | 39.531
| 45.8333 | 261.216 | 372.302 | 69.553 | 26.479 | 79.446 | 39.512
| 45.8403 | 262.17 | 373.451 | 68.853 | 26.435 | 78.845 | 39.49
| 45.8472 | 253.894 | 364.101 | 68.08 | 26.391 | 77.95 | 39.457
| 45.8542 | 254.927 | 365.373 | 67.252 | 26.342 | 77.411 | 39.41
| 45.8611 | 255.662 | 355.983 | 66.582 | 26.29 | 76.623 | 39.371
| 45.8681 | 246.919 | 355.437 | 65.705 | 26.238 | 75.94 | 39.315
| 45.875 | 246.656 | 344.873 | 64.902 | 26.181 | 75.18 | 39.258
| 45.8819 | 238.538 | 345.85 | 64.061 | 26.121 | 74.41 | 39.193
| 45.8889 | 238.966 | 334.821 | 63.152 | 26.054 | 73.744 | 39.126
| 45.8958 | 231.313 | 334.442 | 62.374 | 25.997 | 72.826 | 39.046
| 45.9028 | 231.839 | 324.234 | 61.376 | 25.928 | 71.844 | 38.966
| 45.9097 | 220.418 | 313.582 | 60.335 | 25.852 | 70.747 | 38.879
| 45.9167 | 220.389 | 305.866 | 59.29 | 25.779 | 69.67 | 38.789
| 45.9236 | 210.585 | 297.175 | 58.081 | 25.693 | 68.602 | 38.682
| 45.9306 | 201.474 | 285.986 | 57.016 | 25.594 | 67.535 | 38.565
| 45.9375 | 201.836 | 287.556 | 55.741 | 25.499 | 66.362 | 38.451
| 45.9444 | 192.082 | 274.769 | 54.5 | 25.408 | 65.085 | 38.327
| 45.9514 | 191.754 | 263.944 | 53.324 | 25.295 | 64.045 | 38.19
| 45.9583 | 182.417 | 255.409 | 52.027 | 25.194 | 62.954 | 38.05
| 45.9653 | 182.592 | 255.445 | 50.902 | 25.079 | 61.901 | 37.9
| 45.9722 | 182.127 | 244.071 | 49.914 | 24.956 | 60.844 | 37.74
| 45.9792 | 174.998 | 244.665 | 48.803 | 24.838 | 59.952 | 37.571
| 45.9861 | 172.72 | 230.547 | 47.819 | 24.74 | 58.831 | 37.418
| 45.9931 | 172.506 | 231.418 | 46.95 | 24.614 | 57.982 | 37.233
| 46 | 171.241 | 220.524 | 46.178 | 24.498 | 57.071 | 37.053
| 46.0069 | 171.95 | 237.911 | 45.473 | 24.403 | 56.663 | 36.882
| 46.0139 | 163.504 | 237.808 | 44.586 | 24.284 | 56.413 | 36.687
| 46.0208 | 163.865 | 230.251 | 43.875 | 24.175 | 55.962 | 36.5
| 46.0278 | 163.583 | 229.46 | 43.229 | 24.071 | 55.362 | 36.314
| 46.0347 | 155.92 | 228.938 | 42.646 | 23.968 | 54.865 | 36.135
| 46.0417 | 155.465 | 228.453 | 41.887 | 23.875 | 54.411 | 35.958
| 46.0486 | 155.183 | 219.598 | 41.27 | 23.765 | 53.656 | 35.781
| 46.0556 | 155.173 | 219.963 | 40.725 | 23.668 | 53.13 | 35.607
| 46.0625 | 155.645 | 210.902 | 40.258 | 23.575 | 52.645 | 35.435
| 46.0694 | 147.367 | 211.348 | 39.819 | 23.479 | 51.986 | 35.263
| 46.0764 | 147.528 | 211.062 | 39.197 | 23.389 | 51.494 | 35.092
| 46.0833 | 147.462 | 211.374 | 38.708 | 23.299 | 51.079 | 34.922
| 46.0903 | 147.681 | 211.403 | 38.275 | 23.206 | 50.707 | 34.756
| 46.0972 | 147.902 | 211.441 | 37.881 | 23.121 | 50.362 | 34.587
| 46.1042 | 148.165 | 211.578 | 37.544 | 23.043 | 50.053 | 34.426
| 46.1111 | 147.97 | 204.293 | 37.242 | 22.961 | 49.586 | 34.259
| 46.1181 | 147.757 | 204.117 | 36.952 | 22.882 | 49.128 | 34.103
| 46.125 | 147.656 | 204.372 | 36.697 | 22.812 | 48.765 | 33.944
| 46.1319 | 148.142 | 204.454 | 36.475 | 22.734 | 48.443 | 33.789
| 46.1389 | 147.91 | 204.536 | 36.266 | 22.666 | 48.14 | 33.637
| 46.1458 | 148.443 | 205.303 | 36.08 | 22.601 | 47.878 | 33.484
| 46.1528 | 149.015 | 212.498 | 35.916 | 22.533 | 47.741 | 33.335
| 46.1597 | 150.823 | 223.559 | 35.792 | 22.469 | 47.801 | 33.196
| 46.1667 | 158.721 | 224.17 | 35.874 | 22.417 | 47.955 | 33.053
| 46.1736 | 168.966 | 237.279 | 35.962 | 22.358 | 48.265 | 32.913
| 46.1806 | 169.059 | 247.251 | 36.326 | 22.309 | 48.671 | 32.775
| 46.1875 | 178.658 | 256.432 | 36.725 | 22.268 | 49.117 | 32.655
| 46.1944 | 178.54 | 256.896 | 37.168 | 22.235 | 49.455 | 32.536
| 46.2014 | 189.1 | 268.683 | 37.802 | 22.21 | 49.997 | 32.428
| 46.2083 | 197.888 | 279.693 | 38.364 | 22.193 | 50.653 | 32.334
| 46.2153 | 197.721 | 288.855 | 39.157 | 22.175 | 51.33 | 32.24
| 46.2222 | 206.36 | 301.607 | 40.068 | 22.176 | 52.103 | 32.156
| 46.2292 | 214.379 | 312.464 | 41.08 | 22.182 | 53.002 | 32.083
| 46.2361 | 230.009 | 329.911 | 42.662 | 22.193 | 54.254 | 32.033
| 46.2431 | 243.335 | 347.731 | 43.931 | 22.235 | 55.748 | 31.984
| 46.25 | 243.123 | 349.231 | 45.472 | 22.271 | 57.23 | 31.948
| 46.2569 | 256.905 | 376.711 | 47.3 | 22.333 | 59.297 | 31.935
| 46.2639 | 269.745 | 394.222 | 49.34 | 22.402 | 61.411 | 31.936
| 46.2708 | 281.899 | 414.503 | 51.568 | 22.487 | 63.628 | 31.958
| 46.2778 | 295.435 | 422.726 | 54.031 | 22.597 | 66.089 | 31.999
| 46.2847 | 308.552 | 441.593 | 56.71 | 22.728 | 68.743 | 32.076
| 46.2917 | 321.196 | 458.668 | 59.573 | 22.86 | 71.583 | 32.166
| 46.2986 | 330.432 | 467.477 | 62.535 | 23.016 | 74.283 | 32.286
| 46.3056 | 341.482 | 479.738 | 65.544 | 23.2 | 76.89 | 32.446
| 46.3125 | 341.101 | 492.124 | 68.598 | 23.386 | 79.573 | 32.616
| 46.3194 | 350.512 | 492.74 | 71.793 | 23.599 | 81.765 | 32.83
| 46.3264 | 353.037 | 495.73 | 74.674 | 23.813 | 83.696 | 33.063
| 46.3333 | 346.526 | 496.933 | 76.822 | 24.044 | 85.19 | 33.32
| 46.3403 | 346.757 | 494.852 | 78.752 | 24.268 | 86.436 | 33.592
| 46.3472 | 345.824 | 486.635 | 80.433 | 24.482 | 86.996 | 33.877
| 46.3542 | 345.545 | 484.622 | 81.846 | 24.692 | 87.412 | 34.174
| 46.3611 | 345.306 | 484.361 | 83.125 | 24.887 | 88.009 | 34.474
| 46.3681 | 337.692 | 483.971 | 83.805 | 25.072 | 88.673 | 34.769
| 46.375 | 337.487 | 483.498 | 84.477 | 25.246 | 89.346 | 35.057
| 46.3819 | 336.309 | 483.641 | 85.068 | 25.404 | 89.971 | 35.343
| 46.3889 | 336.366 | 473.194 | 85.552 | 25.555 | 89.774 | 35.618
| 46.3958 | 336.105 | 473.51 | 86.01 | 25.697 | 90.014 | 35.896
| 46.4028 | 328.745 | 474.294 | 85.984 | 25.828 | 90.396 | 36.15
| 46.4097 | 329.434 | 464.192 | 86.069 | 25.953 | 90.265 | 36.4
| 46.4167 | 328.091 | 464.327 | 86.139 | 26.064 | 90.253 | 36.643
| 46.4236 | 320.113 | 454.234 | 85.63 | 26.166 | 89.927 | 36.866
| 46.4306 | 319.953 | 454.532 | 85.325 | 26.252 | 89.624 | 37.081
| 46.4375 | 312.206 | 445.489 | 84.927 | 26.324 | 89.371 | 37.285
| 46.4444 | 312.985 | 444.685 | 84.329 | 26.393 | 88.844 | 37.475
| 46.4514 | 312.3 | 445.096 | 83.88 | 26.448 | 88.705 | 37.65
| 46.4583 | 304.277 | 435.657 | 83.177 | 26.495 | 87.946 | 37.804
| 46.4653 | 304 | 436.191 | 82.487 | 26.532 | 87.694 | 37.954
| 46.4722 | 303.742 | 427.487 | 81.9 | 26.558 | 87.003 | 38.087
| 46.4792 | 296.29 | 426.492 | 81.037 | 26.58 | 86.592 | 38.203
| 46.4861 | 296.587 | 427.477 | 80.275 | 26.595 | 86.38 | 38.31
| 46.4931 | 295.239 | 416.989 | 79.612 | 26.604 | 85.858 | 38.407
| 46.5 | 296.634 | 417.096 | 79.041 | 26.607 | 85.352 | 38.491
| 46.5069 | 296.218 | 418.351 | 78.558 | 26.605 | 85.109 | 38.562
| 46.5139 | 288.72 | 417.781 | 78.066 | 26.607 | 84.953 | 38.631
| 46.5208 | 288.14 | 417.879 | 77.271 | 26.603 | 84.861 | 38.685
| 46.5278 | 291.018 | 413.437 | 76.717 | 26.591 | 84.254 | 38.732
| 46.5347 | 284.303 | 413.68 | 76.142 | 26.578 | 84.172 | 38.776
| 46.5417 | 284.491 | 403.96 | 75.463 | 26.567 | 83.549 | 38.813
| 46.5486 | 284.055 | 405.038 | 74.903 | 26.551 | 83.137 | 38.843
| 46.5556 | 285.127 | 405.09 | 74.436 | 26.532 | 82.923 | 38.869
| 46.5625 | 286.107 | 406.44 | 74.081 | 26.512 | 82.859 | 38.888
| 46.5694 | 285.485 | 406.579 | 73.773 | 26.494 | 82.798 | 38.904
| 46.5764 | 282.51 | 401.129 | 73.352 | 26.483 | 82.467 | 38.918
| 46.5833 | 282.356 | 401.705 | 72.979 | 26.462 | 82.215 | 38.92
| 46.5903 | 282.473 | 402.557 | 72.671 | 26.447 | 82.078 | 38.93
| 46.5972 | 283.724 | 403.083 | 72.432 | 26.43 | 82.014 | 38.932
| 46.6042 | 284.459 | 411.347 | 72.257 | 26.413 | 82.563 | 38.936
| 46.6111 | 284.339 | 411.719 | 72.096 | 26.398 | 82.809 | 38.935
| 46.6181 | 283.942 | 410.946 | 71.966 | 26.383 | 82.951 | 38.94
| 46.625 | 289.981 | 413.237 | 72.072 | 26.374 | 83.05 | 38.95
| 46.6319 | 290.731 | 412.425 | 72.237 | 26.364 | 83.157 | 38.954
| 46.6389 | 290.387 | 413.486 | 72.358 | 26.37 | 83.211 | 38.964
| 46.6458 | 290.719 | 422.182 | 72.454 | 26.367 | 83.772 | 38.974
| 46.6528 | 291.245 | 421.478 | 72.549 | 26.372 | 84.133 | 38.991
| 46.6597 | 290.638 | 420.249 | 72.616 | 26.377 | 84.342 | 39.009
| 46.6667 | 291.239 | 420.936 | 72.695 | 26.386 | 84.52 | 39.034
| 46.6736 | 298.925 | 421.198 | 73.191 | 26.391 | 84.665 | 39.06
| 46.6806 | 296.988 | 428.078 | 73.531 | 26.404 | 84.931 | 39.089
| 46.6875 | 295.197 | 426.147 | 73.681 | 26.421 | 85.31 | 39.121
| 46.6944 | 295.518 | 425.878 | 73.822 | 26.439 | 85.515 | 39.15
| 46.7014 | 303.33 | 426.463 | 74.409 | 26.457 | 85.737 | 39.19
| 46.7083 | 303.155 | 436.394 | 74.822 | 26.48 | 86.484 | 39.232
| 46.7153 | 303.036 | 434.178 | 75.158 | 26.512 | 86.883 | 39.273
| 46.7222 | 302.14 | 433.088 | 75.418 | 26.536 | 87.118 | 39.316
| 46.7292 | 305.468 | 437.978 | 75.672 | 26.564 | 87.345 | 39.371
| 46.7361 | 305.32 | 429.584 | 76.061 | 26.595 | 87.472 | 39.429
| 46.7431 | 299.323 | 429.939 | 76.219 | 26.625 | 87.343 | 39.48
| 46.75 | 299.335 | 420.447 | 76.157 | 26.658 | 87.13 | 39.539
| 46.7569 | 297.01 | 419.661 | 76.105 | 26.681 | 86.518 | 39.595
| 46.7639 | 292.798 | 413.751 | 75.978 | 26.702 | 86.146 | 39.647
| 46.7708 | 289.376 | 418.985 | 75.621 | 26.715 | 85.93 | 39.696
| 46.7778 | 288.203 | 406.376 | 75.213 | 26.728 | 85.073 | 39.741
| 46.7847 | 279.86 | 406.196 | 74.743 | 26.731 | 84.617 | 39.771
| 46.7917 | 280.294 | 395.413 | 74.009 | 26.728 | 83.778 | 39.804
| 46.7986 | 280.191 | 395.7 | 73.468 | 26.713 | 83.222 | 39.82
| 46.8056 | 270.902 | 386.996 | 72.734 | 26.701 | 82.532 | 39.84
| 46.8125 | 271.779 | 386.981 | 71.966 | 26.68 | 81.866 | 39.843
| 46.8194 | 271.536 | 380.05 | 71.344 | 26.653 | 81.347 | 39.838
| 46.8264 | 262.951 | 380.717 | 70.486 | 26.618 | 80.657 | 39.821
| 46.8333 | 263.634 | 370.591 | 69.714 | 26.584 | 79.816 | 39.809
| 46.8403 | 264.173 | 371.334 | 69.068 | 26.536 | 79.143 | 39.772
| 46.8472 | 255.811 | 361.774 | 68.132 | 26.487 | 78.478 | 39.738
| 46.8542 | 255.794 | 362.957 | 67.389 | 26.445 | 77.745 | 39.7
| 46.8611 | 247.898 | 352.396 | 66.715 | 26.393 | 77.248 | 39.652
| 46.8681 | 247.703 | 353.916 | 65.73 | 26.341 | 76.315 | 39.595
| 46.875 | 248.663 | 354.458 | 64.999 | 26.288 | 75.826 | 39.536
| 46.8819 | 240.664 | 344.253 | 64.028 | 26.211 | 74.838 | 39.463
| 46.8889 | 238.091 | 340.697 | 63.121 | 26.151 | 74.029 | 39.395
| 46.8958 | 237.158 | 329.319 | 62.329 | 26.08 | 73.076 | 39.31
| 46.9028 | 228.689 | 331.892 | 61.401 | 26.012 | 72.434 | 39.225
| 46.9097 | 228.587 | 321.424 | 60.492 | 25.947 | 71.38 | 39.139
| 46.9167 | 217.391 | 310.562 | 59.296 | 25.856 | 70.155 | 39.043
| 46.9236 | 208.397 | 301.28 | 58.21 | 25.77 | 68.764 | 38.938
| 46.9306 | 208.231 | 292.298 | 57.026 | 25.671 | 67.768 | 38.823
| 46.9375 | 198.451 | 281.987 | 55.792 | 25.579 | 66.637 | 38.701
| 46.9444 | 198.216 | 273.783 | 54.648 | 25.481 | 65.507 | 38.574
| 46.9514 | 188.859 | 263.721 | 53.334 | 25.384 | 64.399 | 38.438
| 46.9583 | 178.814 | 255.7 | 52.148 | 25.272 | 63.328 | 38.291
| 46.9653 | 176.787 | 252.667 | 50.844 | 25.164 | 62.223 | 38.147
| 46.9722 | 177.471 | 253.171 | 49.735 | 25.044 | 61.387 | 37.987
| 46.9792 | 176.975 | 241.179 | 48.768 | 24.931 | 60.283 | 37.82
| 46.9861 | 177.022 | 231.397 | 47.914 | 24.799 | 59.362 | 37.642
| 46.9931 | 176.906 | 231.538 | 47.161 | 24.684 | 58.45 | 37.465
| 47 | 169.027 | 221.041 | 46.295 | 24.589 | 57.495 | 37.288
| 47.0069 | 170.265 | 239.362 | 45.531 | 24.476 | 57.118 | 37.102
| 47.0139 | 162.303 | 238.124 | 44.739 | 24.366 | 56.877 | 36.917
| 47.0208 | 161.226 | 228.353 | 43.937 | 24.255 | 56.351 | 36.728
| 47.0278 | 161.338 | 228.613 | 43.237 | 24.142 | 55.695 | 36.542
| 47.0347 | 161.147 | 228.573 | 42.616 | 24.035 | 55.187 | 36.361
| 47.0417 | 161.288 | 227.872 | 42.067 | 23.929 | 54.732 | 36.178
| 47.0486 | 152.404 | 218.249 | 41.432 | 23.834 | 53.977 | 35.999
| 47.0556 | 152.724 | 218.677 | 40.795 | 23.735 | 53.43 | 35.823
| 47.0625 | 153.076 | 219.577 | 40.258 | 23.635 | 53 | 35.649
| 47.0694 | 153.038 | 209.32 | 39.776 | 23.543 | 52.586 | 35.476
| 47.0764 | 152.734 | 209.805 | 39.336 | 23.45 | 51.901 | 35.301
| 47.0833 | 153.002 | 209.775 | 38.948 | 23.367 | 51.423 | 35.135
| 47.0903 | 145.597 | 209.889 | 38.521 | 23.271 | 51.018 | 34.961
| 47.0972 | 145.639 | 209.965 | 38.033 | 23.193 | 50.651 | 34.797
| 47.1042 | 145.752 | 209.84 | 37.621 | 23.105 | 50.309 | 34.629
| 47.1111 | 145.683 | 210.792 | 37.256 | 23.025 | 49.995 | 34.462
| 47.1181 | 144.493 | 209.011 | 36.905 | 22.944 | 49.643 | 34.302
| 47.125 | 144.578 | 209.059 | 36.588 | 22.865 | 49.327 | 34.143
| 47.1319 | 144.556 | 208.575 | 36.296 | 22.788 | 49.025 | 33.988
| 47.1389 | 144.627 | 209.243 | 36.047 | 22.715 | 48.75 | 33.834
| 47.1458 | 144.691 | 209.244 | 35.813 | 22.641 | 48.488 | 33.682
| 47.1528 | 144.973 | 208.842 | 35.608 | 22.576 | 48.231 | 33.535
| 47.1597 | 151.133 | 219.071 | 35.571 | 22.506 | 48.273 | 33.387
| 47.1667 | 159.488 | 228.514 | 35.7 | 22.447 | 48.477 | 33.248
| 47.1736 | 169.157 | 241.976 | 35.812 | 22.391 | 48.533 | 33.111
| 47.1806 | 169.434 | 241.903 | 36.218 | 22.353 | 48.963 | 32.985
| 47.1875 | 178.046 | 251.722 | 36.616 | 22.299 | 49.435 | 32.851
| 47.1944 | 178.271 | 265.616 | 37.055 | 22.268 | 49.82 | 32.737
| 47.2014 | 188.061 | 274.309 | 37.68 | 22.24 | 50.379 | 32.625
| 47.2083 | 198.038 | 284.351 | 38.225 | 22.215 | 50.903 | 32.522
| 47.2153 | 197.769 | 284.173 | 39.05 | 22.203 | 51.599 | 32.432
| 47.2222 | 205.881 | 295.403 | 39.982 | 22.201 | 52.414 | 32.351
| 47.2292 | 213.997 | 305.19 | 40.984 | 22.204 | 53.276 | 32.28
| 47.2361 | 224.028 | 330.297 | 42.144 | 22.217 | 54.459 | 32.221
| 47.2431 | 239.209 | 344.329 | 43.606 | 22.247 | 56.114 | 32.172
| 47.25 | 250.441 | 358.308 | 45.26 | 22.285 | 57.697 | 32.143
| 47.2569 | 262.616 | 369.187 | 47.104 | 22.339 | 59.534 | 32.119
| 47.2639 | 275.275 | 394.199 | 49.085 | 22.412 | 61.622 | 32.119
| 47.2708 | 281.938 | 413.351 | 51.385 | 22.496 | 63.875 | 32.141
| 47.2778 | 294.675 | 432.475 | 53.827 | 22.599 | 66.279 | 32.179
| 47.2847 | 307.658 | 439.443 | 56.504 | 22.724 | 68.927 | 32.251
| 47.2917 | 314.05 | 458.837 | 59.342 | 22.868 | 71.773 | 32.344
| 47.2986 | 325.823 | 473.5 | 62.347 | 23.028 | 74.611 | 32.468
| 47.3056 | 335.058 | 486.096 | 65.39 | 23.206 | 77.245 | 32.62
| 47.3125 | 344.096 | 492.633 | 68.461 | 23.402 | 80.056 | 32.807
| 47.3194 | 345.21 | 491.602 | 71.219 | 23.604 | 82.056 | 33.011
| 47.3264 | 344.873 | 491.26 | 73.736 | 23.823 | 83.716 | 33.251
| 47.3333 | 343.83 | 490.645 | 75.887 | 24.035 | 84.926 | 33.504
| 47.3403 | 348.482 | 495.806 | 77.751 | 24.251 | 85.934 | 33.781
| 47.3472 | 346.919 | 485.847 | 79.665 | 24.462 | 86.849 | 34.063
| 47.3542 | 346.764 | 486.052 | 81.242 | 24.668 | 87.461 | 34.358
| 47.3611 | 339.957 | 485.123 | 82.191 | 24.864 | 88.046 | 34.65
| 47.3681 | 342.465 | 488.561 | 83.313 | 25.048 | 88.986 | 34.945
| 47.375 | 335.735 | 481.07 | 83.905 | 25.223 | 88.351 | 35.234
| 47.3819 | 335.284 | 481.624 | 84.462 | 25.382 | 89.413 | 35.514
| 47.3889 | 336.146 | 481.866 | 84.986 | 25.533 | 90.137 | 35.787
| 47.3958 | 336.054 | 473.05 | 85.489 | 25.676 | 90.191 | 36.06
| 47.4028 | 327.489 | 472.252 | 85.455 | 25.812 | 90.483 | 36.313
| 47.4097 | 326.988 | 460.112 | 85.457 | 25.928 | 90.636 | 36.562
| 47.4167 | 326.297 | 460.275 | 85.466 | 26.039 | 90.109 | 36.805
| 47.4236 | 325.941 | 459.628 | 85.43 | 26.143 | 89.974 | 37.037
| 47.4306 | 317.554 | 457.78 | 84.867 | 26.231 | 89.964 | 37.251
| 47.4375 | 316.212 | 446.903 | 84.477 | 26.304 | 89.383 | 37.454
| 47.4444 | 311.002 | 438.903 | 83.911 | 26.373 | 89.283 | 37.645
| 47.4514 | 311.314 | 440.794 | 83.417 | 26.429 | 88.598 | 37.821
| 47.4583 | 311.065 | 439.148 | 82.997 | 26.471 | 88.378 | 37.982
| 47.4653 | 301.962 | 432.231 | 82.12 | 26.516 | 87.688 | 38.13
| 47.4722 | 302.248 | 432.505 | 81.47 | 26.544 | 87.394 | 38.266
| 47.4792 | 302.578 | 422.398 | 80.904 | 26.569 | 86.728 | 38.389
| 47.4861 | 293.963 | 423.074 | 80.093 | 26.584 | 86.286 | 38.501
| 47.5347 | 287.786 | 415.85 | 75.828 | 26.578 | 84.7 | 38.987
| 47.5417 | 283.39 | 400.329 | 75.221 | 26.562 | 83.445 | 39.03
| 47.5486 | 283.742 | 400.89 | 74.663 | 26.547 | 82.97 | 39.068
| 47.5556 | 284.218 | 400.253 | 74.216 | 26.529 | 82.706 | 39.096
| 47.5625 | 284.342 | 392.168 | 73.816 | 26.513 | 81.921 | 39.113
| 47.5694 | 281.427 | 388.105 | 73.31 | 26.499 | 81.243 | 39.126
| 47.5764 | 281.569 | 399.28 | 72.918 | 26.476 | 81.379 | 39.136
| 47.5833 | 281.463 | 397.79 | 72.588 | 26.464 | 81.46 | 39.131
| 47.5903 | 282.751 | 398.928 | 72.324 | 26.446 | 81.489 | 39.129
| 47.5972 | 283.65 | 401.906 | 72.12 | 26.427 | 81.503 | 39.119
| 47.6042 | 283.387 | 401.907 | 71.997 | 26.412 | 81.59 | 39.111
| 47.6111 | 281.677 | 398.231 | 71.835 | 26.401 | 81.526 | 39.104
| 47.6181 | 288.85 | 406.07 | 71.892 | 26.389 | 81.711 | 39.102
| 47.625 | 288.389 | 407.114 | 72.021 | 26.38 | 81.967 | 39.094
| 47.6319 | 289.187 | 407.854 | 72.108 | 26.38 | 82.087 | 39.095
| 47.6389 | 288.608 | 405.58 | 72.153 | 26.383 | 82.094 | 39.099
| 47.6458 | 292.078 | 411.785 | 72.388 | 26.389 | 82.427 | 39.103
| 47.6528 | 293.285 | 412.184 | 72.597 | 26.395 | 82.642 | 39.107
| 47.6597 | 292.595 | 411.192 | 72.782 | 26.402 | 82.807 | 39.119
| 47.6667 | 294.23 | 412.984 | 72.974 | 26.415 | 82.969 | 39.133
| 47.6736 | 293.697 | 414.19 | 73.142 | 26.429 | 83.079 | 39.145
| 47.6806 | 293.863 | 413.402 | 73.311 | 26.445 | 83.204 | 39.163
| 47.6875 | 301.596 | 423.358 | 73.778 | 26.457 | 83.746 | 39.181
| 47.6944 | 298.352 | 417.635 | 74.26 | 26.482 | 84.289 | 39.2
| 47.7014 | 298.637 | 418.995 | 74.428 | 26.506 | 84.225 | 39.228
| 47.7083 | 299.735 | 419.792 | 74.673 | 26.529 | 84.343 | 39.258
| 47.7153 | 298.659 | 427.631 | 74.832 | 26.555 | 84.499 | 39.295
| 47.7222 | 305.781 | 427.857 | 74.97 | 26.58 | 85.182 | 39.331
| 47.7292 | 305.005 | 428.524 | 75.55 | 26.604 | 85.527 | 39.368
| 47.7361 | 304.165 | 426.849 | 75.916 | 26.637 | 85.722 | 39.406
| 47.7431 | 303.33 | 416.838 | 76.142 | 26.669 | 85.548 | 39.448
| 47.75 | 295.596 | 409.548 | 76.323 | 26.703 | 85.145 | 39.493
| 47.7569 | 297.371 | 412.669 | 76.103 | 26.731 | 84.56 | 39.543
| 47.7639 | 294.818 | 408.541 | 75.939 | 26.753 | 84.222 | 39.583
| 47.7708 | 286.755 | 399.488 | 75.545 | 26.774 | 83.669 | 39.627
| 47.7778 | 286.629 | 399.173 | 75.024 | 26.781 | 83.06 | 39.652
| 47.7847 | 285.732 | 390.835 | 74.633 | 26.788 | 82.679 | 39.678
| 47.7917 | 277.545 | 390.847 | 73.954 | 26.783 | 81.926 | 39.705
| 47.7986 | 278.69 | 391.133 | 73.318 | 26.779 | 81.535 | 39.713
| 47.8056 | 277.912 | 382.097 | 72.786 | 26.76 | 80.712 | 39.715
| 47.8125 | 270.497 | 383.124 | 71.968 | 26.737 | 80.298 | 39.71
| 47.8194 | 270.836 | 373.833 | 71.31 | 26.712 | 79.568 | 39.696
| 47.8264 | 270.201 | 374.636 | 70.735 | 26.682 | 79.024 | 39.682
| 47.8333 | 261.678 | 362.585 | 69.745 | 26.659 | 78.213 | 39.662
| 47.8403 | 261.677 | 363.864 | 69.022 | 26.606 | 77.492 | 39.623
| 47.8472 | 253.751 | 354.001 | 68.26 | 26.573 | 76.882 | 39.587
| 47.8542 | 252.141 | 351.288 | 67.367 | 26.525 | 76.112 | 39.542
| 47.8611 | 252.37 | 352.221 | 66.544 | 26.466 | 75.469 | 39.484
| 47.8681 | 252.536 | 343.268 | 65.862 | 26.414 | 74.738 | 39.431
| 47.875 | 244.846 | 343.538 | 64.892 | 26.36 | 74.062 | 39.366
| 47.8819 | 243.566 | 333.401 | 64.07 | 26.289 | 73.344 | 39.291
| 47.8889 | 235.173 | 335.145 | 63.321 | 26.237 | 72.599 | 39.217
| 47.8958 | 234.288 | 323.876 | 62.327 | 26.165 | 71.704 | 39.138
| 47.9028 | 234.495 | 324.969 | 61.52 | 26.088 | 70.971 | 39.047
| 47.9097 | 223.397 | 313.657 | 60.362 | 26.015 | 69.909 | 38.951
| 47.9167 | 214.441 | 303.458 | 59.303 | 25.936 | 68.787 | 38.851
| 47.9236 | 214.729 | 294.956 | 58.192 | 25.862 | 67.709 | 38.758
| 47.9306 | 204.529 | 285.115 | 56.968 | 25.768 | 66.578 | 38.638
| 47.9375 | 204.535 | 278.014 | 55.874 | 25.664 | 65.513 | 38.52
| 47.9444 | 195.088 | 267.813 | 54.576 | 25.567 | 64.439 | 38.389
| 47.9514 | 184.85 | 258.419 | 53.382 | 25.466 | 63.343 | 38.256
| 47.9583 | 185.368 | 249.484 | 52.149 | 25.354 | 62.303 | 38.111
| 47.9653 | 174.501 | 247.27 | 50.859 | 25.24 | 61.17 | 37.96
| 47.9722 | 175.157 | 247.15 | 49.691 | 25.134 | 60.396 | 37.804
| 47.9792 | 175.615 | 238.42 | 48.692 | 25.003 | 59.419 | 37.637
| 47.9861 | 175.328 | 229.155 | 47.81 | 24.889 | 58.615 | 37.475
| 47.9931 | 175.029 | 229.305 | 47.03 | 24.77 | 57.751 | 37.293
| 48 | 174.156 | 219.52 | 46.319 | 24.659 | 56.844 | 37.123
| 48.0069 | 165.292 | 234.008 | 45.381 | 24.546 | 56.602 | 36.939
| 48.0139 | 165.728 | 233.769 | 44.628 | 24.443 | 56.228 | 36.764
| 48.0208 | 166.279 | 226.548 | 43.973 | 24.328 | 55.581 | 36.581
| 48.0278 | 157.803 | 226.447 | 43.359 | 24.225 | 55.055 | 36.394
| 48.0347 | 158.263 | 226.337 | 42.608 | 24.126 | 54.609 | 36.225
| 48.0417 | 157.178 | 216.842 | 41.978 | 24.015 | 53.844 | 36.045
| 48.0486 | 157.503 | 217.254 | 41.419 | 23.919 | 53.317 | 35.874
| 48.0556 | 157.608 | 217.393 | 40.931 | 23.822 | 52.879 | 35.703
| 48.0625 | 149.538 | 206.848 | 40.312 | 23.742 | 52.423 | 35.532
| 48.0694 | 149.822 | 207.1 | 39.757 | 23.637 | 51.737 | 35.359
| 48.0764 | 149.912 | 207.538 | 39.266 | 23.542 | 51.266 | 35.192
| 48.0833 | 150.077 | 207.574 | 38.828 | 23.456 | 50.859 | 35.027
| 48.0903 | 149.945 | 207.573 | 38.44 | 23.363 | 50.487 | 34.858
| 48.0972 | 150.17 | 208.076 | 38.098 | 23.266 | 50.146 | 34.688
| 48.1042 | 150.029 | 208.073 | 37.79 | 23.192 | 49.83 | 34.528
| 48.1111 | 150.091 | 198.4 | 37.501 | 23.11 | 49.359 | 34.368
| 48.1181 | 142.394 | 198.601 | 37.055 | 23.042 | 48.87 | 34.213
| 48.125 | 142.739 | 198.139 | 36.68 | 22.958 | 48.481 | 34.055
| 48.1319 | 142.27 | 198.492 | 36.347 | 22.882 | 48.143 | 33.903
| 48.1389 | 142.296 | 198.544 | 36.046 | 22.802 | 47.828 | 33.75
| 48.1458 | 142.364 | 198.254 | 35.774 | 22.735 | 47.54 | 33.6
| 48.1528 | 142.853 | 209.628 | 35.532 | 22.66 | 47.425 | 33.454
| 48.1597 | 151.677 | 220.928 | 35.525 | 22.594 | 47.545 | 33.308
| 48.1667 | 159.172 | 220.654 | 35.661 | 22.535 | 47.745 | 33.166
| 48.1736 | 159.549 | 233.403 | 35.785 | 22.477 | 48.029 | 33.028
| 48.1806 | 169.534 | 234.534 | 36.19 | 22.429 | 48.231 | 32.895
| 48.1875 | 177.686 | 247.028 | 36.593 | 22.382 | 48.696 | 32.773
| 48.1944 | 178.104 | 256.379 | 37.056 | 22.365 | 49.205 | 32.664
| 48.2014 | 188.944 | 266.216 | 37.697 | 22.327 | 49.764 | 32.55
| 48.2083 | 188.661 | 265.941 | 38.262 | 22.314 | 50.093 | 32.454
| 48.2153 | 198.705 | 279.809 | 39.119 | 22.296 | 50.839 | 32.36
| 48.2222 | 206.108 | 290.291 | 40.039 | 22.295 | 51.616 | 32.284
| 48.2292 | 214.97 | 302.668 | 41.071 | 22.299 | 52.509 | 32.209
| 48.2361 | 226.019 | 323.408 | 42.268 | 22.311 | 53.554 | 32.149
| 48.2431 | 235.801 | 331.651 | 43.639 | 22.337 | 54.979 | 32.105
| 48.25 | 244.407 | 350.944 | 45.259 | 22.38 | 56.696 | 32.074
| 48.2569 | 256.585 | 360.289 | 47.095 | 22.436 | 58.302 | 32.055
| 48.2639 | 276.97 | 387.412 | 49.25 | 22.511 | 60.327 | 32.054
| 48.2708 | 289.592 | 399.215 | 51.475 | 22.597 | 62.627 | 32.069
| 48.2778 | 288.93 | 412.694 | 53.849 | 22.7 | 64.727 | 32.109
| 48.2847 | 309.395 | 431.722 | 56.763 | 22.828 | 67.302 | 32.169
| 48.2917 | 321.83 | 452.427 | 59.594 | 22.978 | 70.061 | 32.26
| 48.2986 | 331.758 | 465.925 | 62.543 | 23.137 | 72.477 | 32.371
| 48.3056 | 334.345 | 477.586 | 65.698 | 23.319 | 75.281 | 32.515
| 48.3125 | 345.617 | 483.548 | 68.794 | 23.519 | 77.998 | 32.688
| 48.3194 | 348.527 | 486.211 | 71.746 | 23.727 | 80.146 | 32.891
| 48.3264 | 350.664 | 488.916 | 74.481 | 23.946 | 82.003 | 33.114
| 48.3333 | 348.857 | 487.469 | 76.812 | 24.171 | 83.312 | 33.358
| 48.3403 | 348.217 | 483.872 | 78.806 | 24.398 | 84.322 | 33.622
| 48.3472 | 348.462 | 483.873 | 80.577 | 24.619 | 85.232 | 33.9
| 48.3542 | 340.119 | 475.905 | 81.665 | 24.829 | 85.484 | 34.186
| 48.3611 | 340.075 | 473.636 | 82.671 | 25.024 | 85.88 | 34.469
| 48.3681 | 338.604 | 473.789 | 83.578 | 25.212 | 86.393 | 34.755
| 48.375 | 339.046 | 473.752 | 84.393 | 25.379 | 86.963 | 35.037
| 48.3819 | 339.283 | 473.205 | 85.097 | 25.541 | 87.504 | 35.309
| 48.3889 | 331.242 | 463.846 | 85.462 | 25.7 | 87.42 | 35.575
| 48.3958 | 332.471 | 466.215 | 85.696 | 25.839 | 87.761 | 35.832
| 48.4028 | 331.667 | 455.214 | 85.968 | 25.975 | 88.005 | 36.08
| 48.4097 | 323.53 | 454.2 | 86.121 | 26.094 | 87.649 | 36.319
| 48.4167 | 323.641 | 454.16 | 85.826 | 26.212 | 87.665 | 36.546
| 48.4236 | 322.706 | 444.895 | 85.68 | 26.31 | 87.434 | 36.764
| 48.4306 | 314.462 | 444.054 | 85.327 | 26.402 | 87.134 | 36.969
| 48.4375 | 315.404 | 443.805 | 84.82 | 26.476 | 87.112 | 37.165
| 48.4444 | 313.928 | 433.852 | 84.415 | 26.543 | 86.634 | 37.338
| 48.4514 | 308.837 | 435.695 | 83.795 | 26.603 | 86.359 | 37.512
| 48.4583 | 307.611 | 427.534 | 83.183 | 26.653 | 85.674 | 37.66
| 48.4653 | 306.241 | 426.208 | 82.643 | 26.692 | 85.36 | 37.803
| 48.4722 | 297.928 | 425.257 | 82.008 | 26.724 | 85.141 | 37.927
| 48.4792 | 298.671 | 415.783 | 81.153 | 26.75 | 84.537 | 38.047
| 48.4861 | 298.272 | 416.811 | 80.51 | 26.766 | 84.15 | 38.152
| 48.4931 | 298.691 | 416.57 | 79.952 | 26.78 | 83.948 | 38.246
| 48.5 | 298.24 | 407.473 | 79.454 | 26.789 | 83.582 | 38.328
| 48.5069 | 291.738 | 407.534 | 78.675 | 26.794 | 83.055 | 38.401
| 48.5139 | 292.001 | 408.042 | 78.037 | 26.792 | 82.819 | 38.467
| 48.5208 | 292.108 | 407.942 | 77.53 | 26.792 | 82.755 | 38.523
| 48.5278 | 292.742 | 402.419 | 77.12 | 26.783 | 82.228 | 38.571
| 48.5347 | 285.048 | 403.661 | 76.316 | 26.78 | 81.973 | 38.612
| 48.5417 | 284.77 | 395.01 | 75.696 | 26.767 | 81.695 | 38.65
| 48.5486 | 285.054 | 394.064 | 75.146 | 26.751 | 81.032 | 38.68
| 48.5556 | 284.924 | 394.722 | 74.711 | 26.733 | 80.767 | 38.706
| 48.5625 | 286.473 | 396.957 | 74.345 | 26.718 | 80.623 | 38.729
| 48.5694 | 285.275 | 395.675 | 74.044 | 26.701 | 80.534 | 38.739
| 48.5764 | 284.318 | 394.343 | 73.717 | 26.692 | 80.351 | 38.751
| 48.5833 | 285.567 | 396.29 | 73.456 | 26.675 | 80.249 | 38.757
| 48.5903 | 285.738 | 396.93 | 73.264 | 26.665 | 80.218 | 38.763
| 48.5972 | 286.735 | 397.772 | 73.123 | 26.652 | 80.222 | 38.764
| 48.6042 | 286.832 | 396.99 | 73.003 | 26.647 | 80.22 | 38.771
| 48.6111 | 286.796 | 405.188 | 72.894 | 26.641 | 80.584 | 38.772
| 48.6181 | 286.765 | 405.274 | 72.805 | 26.634 | 80.84 | 38.773
| 48.625 | 287.797 | 406.092 | 72.761 | 26.631 | 81.043 | 38.776
| 48.6319 | 284.31 | 400.385 | 72.647 | 26.626 | 81.026 | 38.785
| 48.6389 | 293.197 | 412.832 | 72.924 | 26.627 | 81.607 | 38.795
| 48.6458 | 292.828 | 412.497 | 73.089 | 26.63 | 81.923 | 38.807
| 48.6528 | 293.918 | 413.33 | 73.243 | 26.633 | 82.125 | 38.824
| 48.6597 | 293.545 | 413.579 | 73.397 | 26.653 | 82.32 | 38.847
| 48.6667 | 294.17 | 414.202 | 73.564 | 26.658 | 82.509 | 38.865
| 48.6736 | 293.775 | 413.856 | 73.689 | 26.672 | 82.638 | 38.898
| 48.6806 | 294.078 | 413.633 | 73.803 | 26.69 | 82.753 | 38.929
| 48.6875 | 300.761 | 422.607 | 74.224 | 26.7 | 82.905 | 38.961
| 48.6944 | 301.654 | 423.362 | 74.661 | 26.718 | 83.683 | 38.993
| 48.7014 | 301.507 | 424.329 | 75.042 | 26.743 | 84.108 | 39.028
| 48.7083 | 302.605 | 423.792 | 75.355 | 26.773 | 84.377 | 39.072
| 48.7153 | 302.609 | 423.789 | 75.627 | 26.803 | 84.578 | 39.114
| 48.7222 | 300.985 | 422.875 | 75.859 | 26.832 | 84.722 | 39.155
| 48.7292 | 301.534 | 422.688 | 76.061 | 26.858 | 84.843 | 39.208
| 48.7361 | 301.773 | 423.463 | 76.245 | 26.886 | 84.989 | 39.259
| 48.7431 | 301.381 | 422.641 | 76.373 | 26.919 | 85.049 | 39.312
| 48.75 | 300.475 | 412.053 | 76.492 | 26.945 | 84.974 | 39.362
| 48.7569 | 293.872 | 409.603 | 76.274 | 26.975 | 84.289 | 39.415
| 48.7639 | 293.865 | 411.924 | 75.958 | 26.988 | 83.845 | 39.461
| 48.7708 | 292.462 | 398.87 | 75.787 | 27.003 | 83.121 | 39.507
| 48.7778 | 283.041 | 397.609 | 75.373 | 27.017 | 82.613 | 39.545
| 48.7847 | 283.292 | 397.297 | 74.76 | 27.018 | 82.264 | 39.575
| 48.7917 | 276.81 | 389.122 | 74.348 | 27.023 | 81.672 | 39.6
| 48.7986 | 277.7 | 389.711 | 73.557 | 27.004 | 81.218 | 39.611
| 48.8056 | 276.773 | 378.255 | 72.991 | 26.996 | 80.605 | 39.627
| 48.8125 | 270.425 | 380.101 | 72.168 | 26.968 | 79.895 | 39.626
| 48.8194 | 271.319 | 371.407 | 71.516 | 26.939 | 79.417 | 39.623
| 48.8264 | 263.759 | 371.687 | 70.66 | 26.906 | 78.647 | 39.606
| 48.8333 | 263.518 | 373.39 | 69.896 | 26.881 | 78.266 | 39.588
| 48.8403 | 264.186 | 362.518 | 69.239 | 26.826 | 77.361 | 39.556
| 48.8472 | 255.596 | 360.866 | 68.283 | 26.783 | 76.761 | 39.519
| 48.8542 | 255.994 | 353.066 | 67.542 | 26.731 | 75.944 | 39.483
| 48.8611 | 253.066 | 349.111 | 66.794 | 26.684 | 75.198 | 39.433
| 48.8681 | 253.626 | 350.101 | 66.142 | 26.635 | 74.671 | 39.379
| 48.875 | 244.308 | 340.577 | 65.111 | 26.576 | 73.775 | 39.317
| 48.8819 | 244.299 | 340.58 | 64.311 | 26.517 | 73.229 | 39.251
| 48.8889 | 234.342 | 331.839 | 63.53 | 26.445 | 72.407 | 39.176
| 48.8958 | 233.76 | 330.983 | 62.497 | 26.373 | 71.762 | 39.099
| 48.9028 | 232.778 | 318.154 | 61.657 | 26.298 | 70.846 | 39.016
| 48.9097 | 223.754 | 309.63 | 60.517 | 26.225 | 69.801 | 38.925
| 48.9167 | 212.88 | 298.053 | 59.454 | 26.149 | 68.743 | 38.834
| 48.9236 | 213.857 | 289.837 | 58.31 | 26.06 | 67.64 | 38.727
| 48.9306 | 204.985 | 282.868 | 57.104 | 25.97 | 66.576 | 38.623
| 48.9375 | 205.826 | 282.13 | 56.036 | 25.873 | 65.497 | 38.503
| 48.9444 | 195.152 | 273.655 | 54.734 | 25.768 | 64.397 | 38.379
| 48.9514 | 185.124 | 264.255 | 53.538 | 25.662 | 63.312 | 38.246
| 48.9583 | 185.465 | 253.326 | 52.304 | 25.565 | 62.21 | 38.114
| 48.9653 | 175.494 | 250.602 | 51.038 | 25.444 | 61.287 | 37.96
| 48.9722 | 173.754 | 248.373 | 49.838 | 25.331 | 60.485 | 37.809
| 48.9792 | 173.814 | 237.863 | 48.8 | 25.203 | 59.46 | 37.643
| 48.9861 | 173.42 | 228.515 | 47.874 | 25.085 | 58.607 | 37.479
| 48.9931 | 173.034 | 228.932 | 47.044 | 24.967 | 57.731 | 37.314
| 49 | 172.459 | 228.132 | 46.312 | 24.859 | 57.066 | 37.14
| 49.0069 | 164.578 | 231.198 | 45.526 | 24.745 | 56.728 | 36.958
| 49.0139 | 165.027 | 231.276 | 44.749 | 24.632 | 56.201 | 36.782
| 49.0208 | 165.759 | 232.506 | 44.093 | 24.527 | 55.773 | 36.607
| 49.0278 | 157.358 | 221.702 | 43.456 | 24.409 | 55.063 | 36.423
| 49.0347 | 156.799 | 220.893 | 42.699 | 24.31 | 54.442 | 36.252
| 49.0417 | 156.976 | 220.321 | 42.066 | 24.206 | 53.935 | 36.079
| 49.0486 | 156.824 | 220.91 | 41.497 | 24.106 | 53.494 | 35.907
| 49.0556 | 156.587 | 212.885 | 40.995 | 24.008 | 52.855 | 35.737
| 49.0625 | 149.915 | 212.343 | 40.391 | 23.914 | 52.353 | 35.568
| 49.0694 | 149.686 | 212.946 | 39.845 | 23.821 | 51.933 | 35.398
| 49.0764 | 149.998 | 212.652 | 39.366 | 23.723 | 51.546 | 35.23
| 49.0833 | 149.355 | 203.302 | 38.928 | 23.637 | 51.047 | 35.063
| 49.0903 | 149.692 | 203.571 | 38.54 | 23.545 | 50.496 | 34.904
| 49.0972 | 149.585 | 204.25 | 38.197 | 23.464 | 50.085 | 34.741
| 49.1042 | 149.809 | 204.337 | 37.892 | 23.377 | 49.734 | 34.582
| 49.1111 | 148.234 | 201.506 | 37.6 | 23.299 | 49.387 | 34.42
| 49.1181 | 148.094 | 201.785 | 37.306 | 23.223 | 49.01 | 34.272
| 49.125 | 147.729 | 201.748 | 37.043 | 23.141 | 48.676 | 34.109
| 49.1319 | 147.75 | 201.508 | 36.79 | 23.07 | 48.365 | 33.956
| 49.1389 | 148.113 | 201.749 | 36.579 | 23.004 | 48.09 | 33.809
| 49.1458 | 147.947 | 201.715 | 36.382 | 22.93 | 47.824 | 33.662
| 49.1528 | 148.042 | 209.16 | 36.196 | 22.864 | 47.674 | 33.515
| 49.1597 | 155.056 | 220.419 | 36.097 | 22.806 | 47.726 | 33.375
| 49.1667 | 162.956 | 229.051 | 36.145 | 22.742 | 47.917 | 33.234
| 49.1736 | 163.221 | 229.758 | 36.35 | 22.69 | 48.175 | 33.099
| 49.1806 | 172.619 | 242.541 | 36.652 | 22.636 | 48.479 | 32.974
| 49.1875 | 173.158 | 250.567 | 36.993 | 22.602 | 48.897 | 32.852
| 49.1944 | 181.732 | 260.788 | 37.508 | 22.567 | 49.335 | 32.735
| 49.2014 | 191.884 | 270.16 | 38.001 | 22.532 | 49.822 | 32.63
| 49.2083 | 191.607 | 269.606 | 38.679 | 22.518 | 50.366 | 32.53
| 49.2153 | 202.293 | 279.801 | 39.432 | 22.506 | 51.02 | 32.445
| 49.2222 | 210.882 | 290.657 | 40.334 | 22.498 | 51.8 | 32.366
| 49.2292 | 218.072 | 300.946 | 41.306 | 22.502 | 52.605 | 32.302
| 49.2361 | 230.674 | 323.743 | 42.387 | 22.519 | 53.682 | 32.247
| 49.2431 | 230.564 | 332.893 | 43.705 | 22.545 | 55.129 | 32.196
| 49.25 | 247.057 | 346.16 | 45.478 | 22.578 | 56.728 | 32.164
| 49.2569 | 255.883 | 368.496 | 47.29 | 22.64 | 58.583 | 32.146
| 49.2639 | 275.763 | 387.378 | 49.444 | 22.711 | 60.582 | 32.148
| 49.2708 | 289.224 | 404.379 | 51.848 | 22.797 | 62.756 | 32.166
| 49.2778 | 295.256 | 412.751 | 54.303 | 22.906 | 64.803 | 32.208
| 49.2847 | 308.359 | 431.801 | 56.919 | 23.032 | 67.382 | 32.275
| 49.2917 | 321.552 | 451.259 | 59.766 | 23.177 | 70.144 | 32.359
| 49.2986 | 332.78 | 465.666 | 62.721 | 23.339 | 72.55 | 32.476
| 49.3056 | 341.793 | 477.746 | 65.708 | 23.517 | 75.004 | 32.621
| 49.3125 | 344.598 | 481.496 | 68.796 | 23.718 | 77.594 | 32.795
| 49.3194 | 346.816 | 491.873 | 71.687 | 23.928 | 80.501 | 32.995
| 49.3264 | 345.809 | 482.395 | 74.185 | 24.143 | 81.734 | 33.22
| 49.3333 | 345.1 | 481.425 | 76.365 | 24.363 | 82.787 | 33.466
| 49.3403 | 344.199 | 480.152 | 78.244 | 24.579 | 83.691 | 33.728
| 49.3472 | 343.878 | 479.066 | 79.885 | 24.786 | 84.498 | 34
| 49.3542 | 342.387 | 477.057 | 81.265 | 24.996 | 85.17 | 34.281
| 49.3611 | 342.106 | 476.384 | 82.481 | 25.187 | 85.82 | 34.56
| 49.3681 | 342.004 | 476.129 | 83.577 | 25.377 | 86.501 | 34.845
| 49.375 | 341.663 | 475.672 | 84.542 | 25.546 | 87.14 | 35.116
| 49.3819 | 334.923 | 466.675 | 85.063 | 25.721 | 87.238 | 35.393
| 49.3889 | 335.9 | 466.374 | 85.548 | 25.878 | 87.479 | 35.66
| 49.3958 | 329.305 | 467.162 | 85.836 | 26.024 | 87.925 | 35.922
| 49.4028 | 328.247 | 454.332 | 85.845 | 26.157 | 88.073 | 36.167
| 49.4097 | 327.96 | 454.952 | 85.89 | 26.279 | 87.693 | 36.413
| 49.4167 | 328.114 | 454.503 | 85.947 | 26.389 | 87.748 | 36.642
| 49.4236 | 318.514 | 445.786 | 85.679 | 26.49 | 87.516 | 36.863
| 49.4306 | 318.682 | 444.566 | 85.287 | 26.583 | 87.234 | 37.074
| 49.4375 | 318.094 | 436.636 | 85.032 | 26.659 | 87.093 | 37.264
| 49.4444 | 312.108 | 436.164 | 84.439 | 26.729 | 86.584 | 37.447
| 49.4514 | 311.228 | 437.305 | 83.952 | 26.788 | 86.5 | 37.615
| 49.4583 | 311.065 | 427.252 | 83.497 | 26.837 | 85.786 | 37.773
| 49.4653 | 302.444 | 425.67 | 82.622 | 26.885 | 85.497 | 37.912
| 49.4722 | 302.072 | 416.972 | 81.946 | 26.916 | 85.199 | 38.043
| 49.4792 | 295.359 | 416.772 | 81.36 | 26.935 | 84.623 | 38.159
| 49.4861 | 294.637 | 416.617 | 80.398 | 26.952 | 84.327 | 38.265
| 49.4931 | 295.106 | 417.31 | 79.676 | 26.962 | 84.175 | 38.358
| 49.5 | 294.26 | 407.849 | 79.018 | 26.963 | 83.486 | 38.446
| 49.5069 | 294.537 | 408.435 | 78.463 | 26.961 | 83.138 | 38.524
| 49.5139 | 295.176 | 409.458 | 78.006 | 26.962 | 82.978 | 38.589
| 49.5208 | 288.455 | 403.616 | 77.403 | 26.957 | 82.668 | 38.647
| 49.5278 | 288.275 | 403.797 | 76.804 | 26.953 | 82.332 | 38.696
| 49.5347 | 288.835 | 402.75 | 76.29 | 26.942 | 82.137 | 38.741
| 49.5417 | 288.891 | 393.825 | 75.843 | 26.932 | 81.856 | 38.776
| 49.5486 | 281.315 | 394.451 | 75.412 | 26.92 | 81.207 | 38.811
| 49.5556 | 280.691 | 395.226 | 74.63 | 26.909 | 80.889 | 38.834
| 49.5625 | 281.181 | 393.8 | 74.078 | 26.889 | 80.711 | 38.858
| 49.5694 | 280.841 | 395.32 | 73.583 | 26.87 | 80.552 | 38.877
| 49.5764 | 280.969 | 394.587 | 73.169 | 26.849 | 80.45 | 38.886
| 49.5833 | 281.465 | 394.721 | 72.807 | 26.827 | 80.366 | 38.895
| 49.5903 | 281.607 | 396.023 | 72.508 | 26.808 | 80.311 | 38.9
| 49.5972 | 281.93 | 396.388 | 72.256 | 26.787 | 80.274 | 38.904
| 49.6042 | 281.695 | 395.959 | 72.06 | 26.774 | 80.278 | 38.906
| 49.6111 | 288.474 | 404.573 | 71.965 | 26.761 | 80.726 | 38.909
| 49.6181 | 287.889 | 404.675 | 72.122 | 26.755 | 81.026 | 38.912
| 49.625 | 288.973 | 405.545 | 72.205 | 26.748 | 81.196 | 38.917
| 49.6319 | 288.469 | 405.978 | 72.297 | 26.743 | 81.317 | 38.925
| 49.6389 | 288.913 | 406.103 | 72.395 | 26.747 | 81.443 | 38.944
| 49.6458 | 289.228 | 405.936 | 72.454 | 26.748 | 81.501 | 38.956
| 49.6528 | 290.166 | 415.244 | 72.559 | 26.751 | 82.051 | 38.975
| 49.6597 | 289.863 | 416.676 | 72.679 | 26.761 | 82.534 | 38.995
| 49.6667 | 297.171 | 414.58 | 73.017 | 26.766 | 82.82 | 39.018
| 49.6736 | 297.391 | 415.821 | 73.403 | 26.779 | 82.948 | 39.045
| 49.6806 | 297.826 | 416.684 | 73.731 | 26.794 | 83.093 | 39.078
| 49.6875 | 297.881 | 415.876 | 74.015 | 26.819 | 83.224 | 39.111
| 49.6944 | 298.761 | 417.378 | 74.3 | 26.841 | 83.406 | 39.152
| 49.7014 | 295.871 | 422.045 | 74.55 | 26.87 | 84.163 | 39.189
| 49.7083 | 304.476 | 422.629 | 75.108 | 26.892 | 84.355 | 39.236
| 49.7153 | 302.496 | 420.562 | 75.465 | 26.921 | 84.374 | 39.277
| 49.7222 | 303.726 | 419.92 | 75.791 | 26.957 | 84.455 | 39.322
| 49.7292 | 303.29 | 419.836 | 76.081 | 26.992 | 84.56 | 39.366
| 49.7361 | 302.823 | 419.082 | 76.314 | 27.025 | 84.625 | 39.42
| 49.7431 | 302.343 | 418.56 | 76.504 | 27.056 | 84.665 | 39.466
| 49.75 | 294.59 | 418.709 | 76.526 | 27.087 | 84.66 | 39.519
| 49.7569 | 297.951 | 414.277 | 76.353 | 27.114 | 84.408 | 39.565
| 49.7639 | 289.077 | 404.182 | 76.041 | 27.135 | 83.862 | 39.615
| 49.7708 | 286.992 | 399.797 | 75.53 | 27.15 | 83.147 | 39.662
| 49.7778 | 288.115 | 402.561 | 75.177 | 27.157 | 82.848 | 39.697
| 49.7847 | 279.546 | 393.592 | 74.768 | 27.16 | 82.561 | 39.731
| 49.7917 | 279.131 | 392.898 | 74.072 | 27.156 | 81.886 | 39.757
| 49.7986 | 279.176 | 393.059 | 73.553 | 27.147 | 81.572 | 39.776
| 49.8056 | 279.354 | 381.648 | 73.087 | 27.133 | 80.617 | 39.794
| 49.8125 | 270.884 | 383.022 | 72.266 | 27.114 | 80.147 | 39.796
| 49.8194 | 270.682 | 374.011 | 71.609 | 27.09 | 79.383 | 39.796
| 49.8264 | 263.534 | 373.458 | 70.755 | 27.06 | 78.875 | 39.787
| 49.8333 | 263.132 | 363.663 | 69.969 | 27.021 | 78.148 | 39.771
| 49.8403 | 263.207 | 365.642 | 69.336 | 26.987 | 77.559 | 39.749
| 49.8472 | 255.701 | 353.083 | 68.406 | 26.94 | 76.899 | 39.72
| 49.8542 | 254.639 | 353.3 | 67.642 | 26.896 | 76.075 | 39.675
| 49.8611 | 254.902 | 352.898 | 66.948 | 26.846 | 75.518 | 39.635
| 49.8681 | 246.165 | 343.228 | 66.075 | 26.797 | 74.767 | 39.586
| 49.875 | 246.299 | 343.894 | 65.251 | 26.735 | 74.11 | 39.525
| 49.8819 | 238.481 | 333.978 | 64.427 | 26.672 | 73.482 | 39.463
| 49.8889 | 240.144 | 335.706 | 63.538 | 26.612 | 72.718 | 39.396
| 49.8958 | 236.769 | 322.761 | 62.702 | 26.542 | 72.046 | 39.32
| 49.9028 | 227.535 | 322.47 | 61.727 | 26.475 | 71.063 | 39.238
| 49.9097 | 227.317 | 312.712 | 60.795 | 26.408 | 70.013 | 39.161
| 49.9167 | 217.89 | 304.367 | 59.628 | 26.326 | 68.874 | 39.067
| 49.9236 | 207.977 | 295.974 | 58.584 | 26.237 | 67.851 | 38.968
| 49.9306 | 208.312 | 285.597 | 57.384 | 26.148 | 66.73 | 38.866
| 49.9375 | 195.544 | 273.931 | 56.157 | 26.057 | 65.634 | 38.752
| 49.9444 | 195.576 | 274.698 | 54.928 | 25.96 | 64.635 | 38.629
| 49.9514 | 185.546 | 256.17 | 53.728 | 25.851 | 63.26 | 38.498
| 49.9583 | 178.4 | 257.546 | 52.478 | 25.742 | 62.358 | 38.364
| 49.9653 | 178.887 | 245.051 | 51.22 | 25.629 | 61.333 | 38.219
| 49.9722 | 178.776 | 246.011 | 50.176 | 25.513 | 60.498 | 38.066
| 49.9792 | 178.665 | 234.955 | 49.256 | 25.397 | 59.638 | 37.907
| 49.9861 | 177.299 | 232.548 | 48.392 | 25.29 | 58.721 | 37.749
| 49.9931 | 177.47 | 222.847 | 47.637 | 25.172 | 57.969 | 37.574
| 50 | 169.132 | 222.439 | 46.79 | 25.068 | 57.07 | 37.403
| 50.0069 | 170.105 | 234.319 | 46.022 | 24.963 | 56.666 | 37.238
| 50.0139 | 162.847 | 234.271 | 45.237 | 24.856 | 56.388 | 37.055
| 50.0208 | 163.297 | 226.684 | 44.469 | 24.747 | 55.782 | 36.881
| 50.0278 | 163.493 | 226.963 | 43.814 | 24.638 | 55.286 | 36.702
| 50.0347 | 155.477 | 216.878 | 43.233 | 24.535 | 54.865 | 36.529
| 50.0417 | 155.017 | 217.269 | 42.459 | 24.436 | 54.106 | 36.358
| 50.0486 | 154.89 | 216.948 | 41.832 | 24.336 | 53.567 | 36.19
| 50.0556 | 155.411 | 217.09 | 41.289 | 24.236 | 53.131 | 36.019
| 50.0625 | 155.262 | 206.723 | 40.799 | 24.142 | 52.669 | 35.851
| 50.0694 | 147.502 | 206.64 | 40.36 | 24.054 | 51.996 | 35.692
| 50.0764 | 147.914 | 206.65 | 39.745 | 23.96 | 51.512 | 35.526
| 50.0833 | 147.969 | 206.938 | 39.255 | 23.875 | 51.101 | 35.366
| 50.0903 | 148.104 | 207.063 | 38.823 | 23.779 | 50.742 | 35.196
| 50.0972 | 147.879 | 207.066 | 38.437 | 23.697 | 50.403 | 35.039
| 50.1042 | 147.778 | 207.471 | 38.096 | 23.617 | 50.081 | 34.879
| 50.1111 | 147.988 | 206.868 | 37.776 | 23.533 | 49.768 | 34.726
| 50.1181 | 147.729 | 198.857 | 37.486 | 23.466 | 49.23 | 34.574
| 50.125 | 147.639 | 199.074 | 37.231 | 23.391 | 48.829 | 34.422
| 50.1319 | 147.65 | 199.183 | 36.995 | 23.308 | 48.482 | 34.266
| 50.1389 | 147.623 | 199.137 | 36.779 | 23.24 | 48.182 | 34.118
| 50.1458 | 148.04 | 199.217 | 36.588 | 23.174 | 47.9 | 33.979
| 50.1528 | 143.661 | 210.018 | 36.357 | 23.102 | 47.799 | 33.832
| 50.1597 | 151.712 | 220.256 | 36.296 | 23.054 | 47.922 | 33.695
| 50.1667 | 159.553 | 229.775 | 36.393 | 22.982 | 48.118 | 33.555
| 50.1736 | 159.094 | 229.18 | 36.493 | 22.929 | 48.385 | 33.416
| 50.1806 | 168.917 | 237.513 | 36.864 | 22.887 | 48.72 | 33.293
| 50.1875 | 178.358 | 247.248 | 37.258 | 22.84 | 49.159 | 33.17
| 50.1944 | 178.441 | 260.144 | 37.69 | 22.81 | 49.49 | 33.06
| 50.2014 | 188.049 | 269.542 | 38.29 | 22.783 | 50.02 | 32.957
| 50.2083 | 187.926 | 269.76 | 38.818 | 22.761 | 50.561 | 32.864
| 50.2153 | 198.368 | 280.177 | 39.667 | 22.749 | 51.274 | 32.773
| 50.2222 | 206.674 | 288.554 | 40.596 | 22.751 | 51.997 | 32.696
| 50.2292 | 214.255 | 300.36 | 41.603 | 22.752 | 52.851 | 32.63
| 50.2361 | 224.964 | 323.548 | 42.764 | 22.772 | 53.94 | 32.58
| 50.2431 | 236.631 | 323.865 | 44.133 | 22.801 | 55.096 | 32.53
| 50.25 | 244.008 | 349.716 | 45.752 | 22.841 | 56.908 | 32.501
| 50.2569 | 263.495 | 366.378 | 47.74 | 22.895 | 58.999 | 32.481
| 50.2639 | 275.977 | 387.053 | 49.727 | 22.97 | 60.868 | 32.487
| 50.2708 | 286.37 | 399.334 | 52.161 | 23.059 | 63.061 | 32.505
| 50.2778 | 295.958 | 413.466 | 54.615 | 23.17 | 65.104 | 32.551
| 50.2847 | 307.694 | 432.391 | 57.258 | 23.297 | 67.692 | 32.616
| 50.2917 | 321.625 | 452.576 | 60.086 | 23.441 | 70.442 | 32.709
| 50.2986 | 331.645 | 464.022 | 63.033 | 23.602 | 72.894 | 32.827
| 50.3056 | 340.913 | 477.268 | 66.05 | 23.79 | 75.308 | 32.975
| 50.3125 | 338.32 | 481.692 | 69.022 | 23.984 | 78.139 | 33.15
| 50.3194 | 355.778 | 489.018 | 72.59 | 24.197 | 80.896 | 33.353
| 50.3264 | 344.783 | 486.299 | 74.902 | 24.425 | 82.415 | 33.574
| 50.3333 | 345.208 | 485.944 | 77.013 | 24.644 | 83.625 | 33.823
| 50.3403 | 344.811 | 485.58 | 78.874 | 24.867 | 84.665 | 34.092
| 50.3472 | 344.7 | 483.584 | 80.509 | 25.081 | 85.606 | 34.378
| 50.3542 | 343.297 | 473.687 | 81.887 | 25.289 | 86 | 34.661
| 50.3611 | 344.157 | 475.651 | 83.226 | 25.485 | 86.487 | 34.949
| 50.3681 | 343.672 | 474.141 | 84.364 | 25.673 | 87.043 | 35.243
| 50.375 | 335.403 | 472.375 | 85.265 | 25.855 | 87.58 | 35.523
| 50.3819 | 336.996 | 475.063 | 85.638 | 26.028 | 88.116 | 35.803
| 50.3889 | 338.009 | 467.24 | 86.272 | 26.183 | 88.046 | 36.07
| 50.3958 | 330.977 | 467.178 | 86.327 | 26.33 | 88.368 | 36.333
| 50.4028 | 330.293 | 459.495 | 86.515 | 26.461 | 88.284 | 36.585
| 50.4097 | 329.778 | 457.614 | 86.635 | 26.587 | 88.315 | 36.828
| 50.4167 | 322.016 | 456.237 | 86.427 | 26.701 | 88.503 | 37.062
| 50.4236 | 321.686 | 447.003 | 86.16 | 26.801 | 87.95 | 37.272
| 50.4306 | 320.409 | 446.889 | 85.962 | 26.887 | 87.856 | 37.487
| 50.4375 | 312.024 | 434.417 | 85.635 | 26.974 | 87.692 | 37.677
| 50.4444 | 312.391 | 435.399 | 85.004 | 27.044 | 87.104 | 37.863
| 50.4514 | 312.411 | 435.572 | 84.543 | 27.099 | 86.935 | 38.029
| 50.4583 | 303.337 | 424.832 | 83.825 | 27.152 | 86.495 | 38.184
| 50.4653 | 303.075 | 424.492 | 83.039 | 27.192 | 85.999 | 38.328
| 50.4722 | 302.303 | 425.098 | 82.406 | 27.223 | 85.792 | 38.459
| 50.4792 | 295.953 | 416.216 | 81.804 | 27.244 | 85.188 | 38.576
| 50.4861 | 295.862 | 415.338 | 80.913 | 27.265 | 84.771 | 38.686
| 50.4931 | 295.285 | 415.402 | 80.24 | 27.269 | 84.563 | 38.782
| 50.5 | 294.983 | 405.919 | 79.659 | 27.273 | 84.174 | 38.868
| 50.5069 | 295.067 | 406.579 | 79.136 | 27.279 | 83.615 | 38.938
| 50.5139 | 288.397 | 407.835 | 78.683 | 27.278 | 83.409 | 39.004
| 50.5208 | 288.587 | 407.879 | 77.897 | 27.275 | 83.301 | 39.061
| 50.5278 | 287.727 | 398.726 | 77.307 | 27.265 | 82.897 | 39.114
| 50.5347 | 288.977 | 399.73 | 76.818 | 27.257 | 82.461 | 39.157
| 50.5417 | 288.436 | 401.205 | 76.385 | 27.248 | 82.24 | 39.19
| 50.5486 | 281.082 | 401.165 | 75.976 | 27.236 | 82.11 | 39.225
| 50.5556 | 281.472 | 400.493 | 75.232 | 27.224 | 82.039 | 39.248
| 50.5625 | 280.768 | 391.069 | 74.668 | 27.204 | 81.282 | 39.268
| 50.5694 | 280.493 | 391.374 | 74.172 | 27.183 | 80.896 | 39.286
| 50.5764 | 280.287 | 390.972 | 73.731 | 27.17 | 80.631 | 39.308
| 50.5833 | 281.116 | 400.168 | 73.345 | 27.147 | 80.499 | 39.315
| 50.5903 | 280.898 | 400.653 | 73.056 | 27.127 | 81.005 | 39.316
| 50.5972 | 281.157 | 399.99 | 72.786 | 27.11 | 81.166 | 39.316
| 50.6042 | 280.494 | 400.066 | 72.535 | 27.095 | 81.207 | 39.315
| 50.6111 | 287.331 | 400.123 | 72.643 | 27.077 | 81.203 | 39.316
| 50.6181 | 287.351 | 400.636 | 72.728 | 27.069 | 81.216 | 39.321
| 50.625 | 288.001 | 399.89 | 72.79 | 27.065 | 81.23 | 39.327
| 50.6319 | 287.983 | 410.846 | 72.864 | 27.063 | 81.907 | 39.335
| 50.6389 | 288.396 | 411.385 | 72.949 | 27.068 | 82.258 | 39.341
| 50.6458 | 289.178 | 410.708 | 73.021 | 27.065 | 82.47 | 39.354
| 50.6528 | 289.686 | 411.581 | 73.117 | 27.075 | 82.671 | 39.375
| 50.6597 | 295.863 | 411.239 | 73.477 | 27.083 | 82.844 | 39.393
| 50.6667 | 296.673 | 412.222 | 73.878 | 27.094 | 82.998 | 39.418
| 50.6736 | 297.824 | 413.668 | 74.237 | 27.111 | 83.18 | 39.449
| 50.6806 | 296.648 | 420.002 | 74.489 | 27.13 | 83.735 | 39.471
| 50.6875 | 297.328 | 420.676 | 74.743 | 27.155 | 84.16 | 39.505
| 50.6944 | 295.996 | 419.522 | 74.902 | 27.178 | 84.344 | 39.536
| 50.7014 | 296.511 | 420.197 | 75.084 | 27.2 | 84.55 | 39.574
| 50.7083 | 305.464 | 421.933 | 75.695 | 27.221 | 84.738 | 39.617
| 50.7153 | 305.327 | 420.804 | 76.189 | 27.247 | 84.934 | 39.659
| 50.7222 | 305.476 | 420.653 | 76.61 | 27.283 | 85.097 | 39.708
| 50.7292 | 304.334 | 421.411 | 76.964 | 27.32 | 85.218 | 39.752
| 50.7361 | 304.677 | 420.022 | 77.288 | 27.356 | 85.364 | 39.799
| 50.7431 | 304.087 | 419.449 | 77.525 | 27.397 | 85.401 | 39.852
| 50.75 | 297.611 | 410.718 | 77.376 | 27.434 | 85.27 | 39.896
| 50.7569 | 295.915 | 408.532 | 77.228 | 27.457 | 84.719 | 39.946
| 50.7639 | 292.503 | 405.755 | 77.038 | 27.478 | 84.377 | 39.987
| 50.7708 | 287.281 | 406.741 | 76.592 | 27.498 | 84.087 | 40.031
| 50.7778 | 285.512 | 397.489 | 76.063 | 27.505 | 83.379 | 40.069
| 50.7847 | 285.944 | 396.928 | 75.644 | 27.508 | 83.003 | 40.1
| 50.7917 | 276.506 | 385.542 | 75.231 | 27.501 | 82.715 | 40.122
| 50.7986 | 276.969 | 387.726 | 74.395 | 27.5 | 81.814 | 40.138
| 50.8056 | 278.318 | 388.494 | 73.844 | 27.481 | 81.466 | 40.155
| 50.8125 | 270.112 | 378.787 | 72.965 | 27.464 | 80.663 | 40.154
| 50.8194 | 270.776 | 378.867 | 72.262 | 27.434 | 80.174 | 40.147
| 50.8264 | 261.985 | 368.258 | 71.659 | 27.404 | 79.393 | 40.139
| 50.8333 | 262.185 | 369.566 | 70.7 | 27.378 | 78.804 | 40.127
| 50.8403 | 262.684 | 360.193 | 69.986 | 27.332 | 78.128 | 40.091
| 50.8472 | 255.241 | 360.745 | 69.056 | 27.29 | 77.479 | 40.057
| 50.8542 | 255.548 | 352.267 | 68.317 | 27.242 | 76.652 | 40.02
| 50.8611 | 247.337 | 351.685 | 67.629 | 27.183 | 76.031 | 39.963
| 50.8681 | 244.493 | 348.279 | 66.522 | 27.138 | 75.452 | 39.917
| 50.875 | 244.067 | 336.938 | 65.654 | 27.064 | 74.644 | 39.853
| 50.8819 | 244.869 | 337.899 | 64.892 | 27.004 | 73.857 | 39.784
| 50.8889 | 236.55 | 328.916 | 63.951 | 26.94 | 73.243 | 39.717
| 50.8958 | 236.403 | 327.529 | 63.098 | 26.863 | 72.333 | 39.633
| 50.9028 | 227.215 | 317.635 | 62.124 | 26.787 | 71.401 | 39.549
| 50.9097 | 227.693 | 309.733 | 61.206 | 26.713 | 70.409 | 39.462
| 50.9167 | 218.457 | 300.312 | 60.055 | 26.644 | 69.415 | 39.368
| 50.9236 | 210.425 | 290.916 | 58.851 | 26.542 | 68.37 | 39.257
| 50.9306 | 201.772 | 280.805 | 57.796 | 26.461 | 67.315 | 39.15
| 50.9375 | 202.385 | 282.712 | 56.554 | 26.354 | 66.211 | 39.03
| 50.9444 | 195.33 | 273.51 | 55.278 | 26.253 | 65.115 | 38.897
| 50.9514 | 184.831 | 260.238 | 54.041 | 26.142 | 63.876 | 38.764
| 50.9583 | 184.707 | 249.692 | 52.823 | 26.039 | 62.907 | 38.625
| 50.9653 | 178.295 | 250.432 | 51.597 | 25.93 | 61.887 | 38.476
| 50.9722 | 176.623 | 241.196 | 50.479 | 25.802 | 60.911 | 38.322
| 50.9792 | 176.944 | 241.591 | 49.516 | 25.682 | 60.115 | 38.158
| 50.9861 | 177.519 | 233.178 | 48.665 | 25.566 | 59.177 | 37.988
| 50.9931 | 177.02 | 223.091 | 47.918 | 25.449 | 58.403 | 37.816
| 51 | 168.991 | 222.668 | 47.06 | 25.338 | 57.488 | 37.637

## Experiment - Data - MF_III_CL
Electric Load and Cable Temperatures | [6 empty] | Soil Moisture | [7 empty] | Weather Station Data
|  |  | Silt | Sand | Fluidized Backfill | Loam |  |  | Silt | Silt (undisturbed) | Sand | Sand (undisturbed) | Loam | Loam (undisturbed)
Parameter | Time | Electrical load (IV) | Sheat Temperature | Sheat Temperature | Sheat Temperature | Sheat Temperature | Parameter | Time | Vol. Water Content | Vol. Water Content | Vol. Water Content | Vol. Water Content | Vol. Water Content | Vol. Water Content | Parameter | Time | Air Temperature | Soil Temperature [-0.8 m] | Time | Precipitation
Unit | d | A | °C | °C | °C | °C | Unit | d | % | % | % | % | % | % | Unit | d | °C | °C | d | mm/h
| 0 | 282.853 | 39.859 | 46.976 | 42.109 | 64.839 |  | 0 | 31.5999 | 28.7169 | 11.2285 | 13.0533 | 28.4121 | 28.7644 |  | 0 | 7.7 | 10 | 0 | 1.4
| 0.0069444 | 285.051 | 39.87 | 46.994 | 42.12 | 64.869 |  | 0.020833 | 31.5248 | 28.6555 | 11.1485 | 12.9819 | 28.344 | 28.6939 |  | 0.020833 | 7.6 | 10 | 0.041667 | 0
| 0.013889 | 283.076 | 39.903 | 47.027 | 42.147 | 64.925 |  | 0.041667 | 31.4977 | 28.6374 | 11.1308 | 12.9642 | 28.3238 | 28.6691 |  | 0.041667 | 7.7 | 10 | 0.083333 | 0
| 0.020833 | 283.029 | 39.909 | 47.04 | 42.153 | 64.944 |  | 0.0625 | 31.5021 | 28.6443 | 11.1153 | 12.9686 | 28.3417 | 28.6781 |  | 0.0625 | 7.8 | 10 | 0.125 | 0
| 0.027778 | 282.14 | 39.916 | 47.049 | 42.157 | 64.958 |  | 0.083333 | 31.4863 | 28.6307 | 11.1153 | 12.9486 | 28.335 | 28.6645 |  | 0.083333 | 7.8 | 10 | 0.16667 | 0
| 0.034722 | 282.486 | 39.913 | 47.055 | 42.165 | 64.959 |  | 0.10417 | 31.4817 | 28.6171 | 11.0778 | 12.9375 | 28.3238 | 28.6488 |  | 0.10417 | 7.7 | 10 | 0.20833 | 0
| 0.041667 | 282.215 | 39.917 | 47.066 | 42.171 | 64.959 |  | 0.125 | 31.4908 | 28.6284 | 11.0844 | 12.9442 | 28.3598 | 28.6488 |  | 0.125 | 7.7 | 10 | 0.25 | 0
| 0.048611 | 281.998 | 39.918 | 47.072 | 42.178 | 64.964 |  | 0.14583 | 31.5112 | 28.6239 | 11.0778 | 12.942 | 28.353 | 28.6533 |  | 0.14583 | 7.7 | 10 | 0.29167 | 0
| 0.055556 | 282.509 | 39.924 | 47.083 | 42.184 | 64.961 |  | 0.16667 | 31.5248 | 28.6239 | 11.0645 | 12.9375 | 28.3553 | 28.6488 |  | 0.16667 | 7.7 | 10 | 0.33333 | 0
| 0.0625 | 282.529 | 39.928 | 47.093 | 42.194 | 64.973 |  | 0.1875 | 31.5339 | 28.6284 | 11.0512 | 12.9375 | 28.353 | 28.6555 |  | 0.1875 | 7.6 | 10 | 0.375 | 0
| 0.069444 | 282.764 | 39.936 | 47.103 | 42.199 | 64.986 |  | 0.20833 | 31.5519 | 28.6374 | 11.0689 | 12.9331 | 28.371 | 28.6555 |  | 0.20833 | 7.7 | 10 | 0.41667 | 0
| 0.076389 | 282.473 | 39.937 | 47.117 | 42.211 | 65.003 |  | 0.22917 | 31.5678 | 28.633 | 11.0512 | 12.9242 | 28.3576 | 28.6488 |  | 0.22917 | 7.6 | 10 | 0.45833 | 0
| 0.083333 | 282.762 | 39.947 | 47.13 | 42.211 | 65.011 |  | 0.25 | 31.5973 | 28.6352 | 11.0556 | 12.9264 | 28.3734 | 28.6533 |  | 0.25 | 7.6 | 10 | 0.5 | 0
| 0.090278 | 282.904 | 39.953 | 47.139 | 42.222 | 65.023 |  | 0.27083 | 31.6289 | 28.651 | 11.0556 | 12.9397 | 28.3847 | 28.6691 |  | 0.27083 | 7.6 | 10 | 0.54167 | 0
| 0.097222 | 282.812 | 39.963 | 47.155 | 42.235 | 65.039 |  | 0.29167 | 31.6811 | 28.6714 | 11.08 | 12.9597 | 28.4524 | 28.7301 |  | 0.29167 | 7.5 | 10 | 0.58333 | 0
| 0.10417 | 282.837 | 39.972 | 47.166 | 42.243 | 65.054 |  | 0.3125 | 31.6403 | 28.6622 | 11.0313 | 12.9464 | 28.3756 | 28.6623 |  | 0.3125 | 7.6 | 10 | 0.625 | 0
| 0.11111 | 283.319 | 39.974 | 47.179 | 42.256 | 65.068 |  | 0.33333 | 31.6737 | 28.7317 | 11.0796 | 12.9659 | 28.4179 | 28.6889 |  | 0.33333 | 7.8 | 10 | 0.66667 | 0
| 0.11806 | 283.439 | 39.982 | 47.19 | 42.266 | 65.077 |  | 0.35417 | 31.6795 | 28.7509 | 11.0541 | 12.9711 | 28.4169 | 28.7081 |  | 0.35417 | 8.6 | 10 | 0.70833 | 0
| 0.125 | 283.818 | 39.986 | 47.202 | 42.277 | 65.092 |  | 0.375 | 31.6872 | 28.7607 | 11.0793 | 12.9806 | 28.4223 | 28.7113 |  | 0.375 | 9.6 | 10 | 0.75 | 0
| 0.13194 | 283.238 | 39.996 | 47.218 | 42.286 | 65.109 |  | 0.39583 | 31.6955 | 28.7645 | 11.0805 | 12.9817 | 28.4328 | 28.7149 |  | 0.39583 | 10.4 | 10.6 | 0.79167 | 0
| 0.13889 | 283.788 | 40.009 | 47.233 | 42.296 | 65.127 |  | 0.41667 | 31.6525 | 28.7261 | 11.0518 | 12.9438 | 28.3764 | 28.6878 |  | 0.41667 | 10.8 | 10.6 | 0.83333 | 0
| 0.14583 | 283.453 | 40.016 | 47.248 | 42.308 | 65.15 |  | 0.4375 | 31.7114 | 28.778 | 11.08 | 12.9922 | 28.4214 | 28.7284 |  | 0.4375 | 11.6 | 10.6 | 0.875 | 0
| 0.15278 | 283.175 | 40.027 | 47.261 | 42.318 | 65.162 |  | 0.45833 | 31.6954 | 28.7756 | 11.0644 | 12.9831 | 28.41 | 28.7191 |  | 0.45833 | 12.1 | 10.6 | 0.91667 | 0
| 0.15972 | 283.97 | 40.033 | 47.277 | 42.335 | 65.175 |  | 0.47917 | 31.7205 | 28.7914 | 11.0861 | 13.0071 | 28.4281 | 28.7418 |  | 0.47917 | 12.9 | 10.6 | 0.95833 | 0
| 0.16667 | 283.454 | 40.04 | 47.288 | 42.343 | 65.193 |  | 0.5 | 31.7291 | 28.7999 | 11.0898 | 13.0149 | 28.4366 | 28.7525 |  | 0.5 | 14.1 | 10.6 | 1 | 0
| 0.17361 | 283.416 | 40.048 | 47.3 | 42.354 | 65.203 |  | 0.52083 | 31.7102 | 28.772 | 11.0625 | 12.9782 | 28.3974 | 28.7425 |  | 0.52083 | 15.2 | 10.6 | 1.0417 | 0
| 0.18056 | 283.35 | 40.056 | 47.313 | 42.357 | 65.214 |  | 0.54167 | 31.7271 | 28.7932 | 11.0919 | 13.001 | 28.4164 | 28.7571 |  | 0.54167 | 15.6 | 10.6 | 1.0833 | 0
| 0.1875 | 283.494 | 40.057 | 47.323 | 42.366 | 65.228 |  | 0.5625 | 31.4349 | 28.5265 | 10.8271 | 12.7451 | 28.1885 | 28.5379 |  | 0.5625 | 16.1 | 10.6 | 1.125 | 0
| 0.19444 | 283.405 | 40.065 | 47.338 | 42.381 | 65.237 |  | 0.58333 | 31.7212 | 28.7915 | 11.0843 | 12.9849 | 28.4239 | 28.7532 |  | 0.58333 | 16.8 | 10.6 | 1.1667 | 0
| 0.20139 | 283.453 | 40.07 | 47.347 | 42.39 | 65.247 |  | 0.60417 | 31.7569 | 28.8226 | 11.1118 | 13.0282 | 28.4527 | 28.7887 |  | 0.60417 | 17.9 | 10.6 | 1.2083 | 0
| 0.20833 | 283.324 | 40.077 | 47.358 | 42.396 | 65.258 |  | 0.625 | 31.7609 | 28.8355 | 11.1262 | 13.0384 | 28.4657 | 28.813 |  | 0.625 | 18.7 | 10.6 | 1.25 | 0
| 0.21528 | 283.778 | 40.08 | 47.371 | 42.4 | 65.264 |  | 0.64583 | 31.7265 | 28.8011 | 11.0984 | 13.0086 | 28.4065 | 28.756 |  | 0.64583 | 19.2 | 10.6 | 1.2917 | 0
| 0.22222 | 283.604 | 40.085 | 47.374 | 42.412 | 65.272 |  | 0.66667 | 31.7737 | 28.8458 | 11.1239 | 13.0408 | 28.4578 | 28.8163 |  | 0.66667 | 19.6 | 10.6 | 1.3333 | 0
| 0.22917 | 283.589 | 40.092 | 47.387 | 42.423 | 65.276 |  | 0.6875 | 31.7646 | 28.8322 | 11.1106 | 13.0342 | 28.451 | 28.8027 |  | 0.6875 | 19.4 | 10.6 | 1.375 | 0
| 0.23611 | 283.033 | 40.096 | 47.4 | 42.43 | 65.283 |  | 0.70833 | 31.6543 | 28.7285 | 10.9997 | 12.9321 | 28.3695 | 28.6787 |  | 0.70833 | 19.3 | 10.6 | 1.4167 | 0
| 0.24306 | 283.852 | 40.099 | 47.406 | 42.436 | 65.287 |  | 0.72917 | 31.7269 | 28.8037 | 11.0737 | 13.0038 | 28.4113 | 28.7743 |  | 0.72917 | 19.4 | 10.6 | 1.4583 | 0
| 0.25 | 284.812 | 40.11 | 47.415 | 42.444 | 65.302 |  | 0.75 | 31.7609 | 28.8398 | 11.1181 | 13.035 | 28.4361 | 28.806 |  | 0.75 | 19.3 | 10.6 | 1.5 | 0
| 0.25694 | 284.369 | 40.124 | 47.437 | 42.456 | 65.332 |  | 0.77083 | 31.5899 | 28.6761 | 10.9422 | 12.8833 | 28.2726 | 28.6603 |  | 0.77083 | 19.1 | 10.6 | 1.5417 | 0
| 0.26389 | 284.696 | 40.138 | 47.452 | 42.474 | 65.355 |  | 0.79167 | 31.6378 | 28.724 | 10.9899 | 12.9286 | 28.3362 | 28.7038 |  | 0.79167 | 18.5 | 10.6 | 1.5833 | 0
| 0.27083 | 284.78 | 40.146 | 47.468 | 42.487 | 65.374 |  | 0.8125 | 31.684 | 28.768 | 11.01 | 12.9681 | 28.3575 | 28.7297 |  | 0.8125 | 17.9 | 10.6 | 1.625 | 0
| 0.27778 | 284.022 | 40.156 | 47.483 | 42.5 | 65.393 |  | 0.83333 | 31.7417 | 28.828 | 11.0984 | 13.0364 | 28.4106 | 28.7964 |  | 0.83333 | 17 | 10.6 | 1.6667 | 0
| 0.28472 | 284.321 | 40.166 | 47.497 | 42.505 | 65.407 |  | 0.85417 | 31.647 | 28.7405 | 11.0086 | 12.96 | 28.341 | 28.72 |  | 0.85417 | 16 | 10.6 | 1.7083 | 0
| 0.29167 | 284.462 | 40.176 | 47.51 | 42.517 | 65.423 |  | 0.875 | 31.5976 | 28.7139 | 10.9784 | 12.93 | 28.3799 | 28.7636 |  | 0.875 | 15.2 | 10.6 | 1.75 | 0
| 0.29861 | 284.074 | 40.174 | 47.526 | 42.524 | 65.429 |  | 0.89583 | 31.6965 | 28.8036 | 11.0514 | 13.0235 | 28.3818 | 28.7655 |  | 0.89583 | 14.4 | 10.6 | 1.7917 | 0
| 0.30556 | 283.704 | 40.182 | 47.535 | 42.537 | 65.444 |  | 0.91667 | 31.7083 | 28.8018 | 11.0692 | 13.046 | 28.3956 | 28.7748 |  | 0.91667 | 13 | 10.6 | 1.8333 | 0
| 0.3125 | 283.498 | 40.186 | 47.545 | 42.547 | 65.448 |  | 0.9375 | 31.658 | 28.7834 | 11.0693 | 13.0464 | 28.4043 | 28.7903 |  | 0.9375 | 12.1 | 10.6 | 1.875 | 0
| 0.31944 | 283.708 | 40.194 | 47.552 | 42.549 | 65.452 |  | 0.95833 | 31.5611 | 28.7592 | 11.1233 | 13.0429 | 28.3981 | 28.7683 |  | 0.95833 | 11.4 | 10.6 | 1.9167 | 0
| 0.32639 | 283.238 | 40.196 | 47.563 | 42.555 | 65.451 |  | 0.97917 | 31.5176 | 28.7272 | 11.0543 | 13.0071 | 28.3841 | 28.743 |  | 0.97917 | 10.6 | 10.6 | 1.9583 | 0
| 0.33333 | 283.33 | 40.194 | 47.57 | 42.563 | 65.45 |  | 1 | 31.5178 | 28.7298 | 11.0661 | 13.0101 | 28.398 | 28.7501 |  | 1 | 9.8 | 10.6 | 2 | 0
| 0.34028 | 283.054 | 40.196 | 47.573 | 42.569 | 65.455 |  | 1.0208 | 31.5372 | 28.7401 | 11.0786 | 13.0316 | 28.4061 | 28.7673 |  | 1.0208 | 9.2 | 10.6 | 2.0417 | 0
| 0.34722 | 283.353 | 40.195 | 47.577 | 42.572 | 65.45 |  | 1.0417 | 31.5031 | 28.7152 | 11.0342 | 12.9916 | 28.3721 | 28.7356 |  | 1.0417 | 9 | 10.6 | 2.0833 | 0
| 0.35417 | 282.795 | 40.198 | 47.578 | 42.581 | 65.442 |  | 1.0625 | 31.5212 | 28.7445 | 11.0652 | 13.0138 | 28.3947 | 28.7581 |  | 1.0625 | 8.8 | 10.6 | 2.125 | 0
| 0.36111 | 281.894 | 40.196 | 47.577 | 42.573 | 65.432 |  | 1.0833 | 31.4972 | 28.723 | 11.0354 | 12.9883 | 28.3708 | 28.7365 |  | 1.0833 | 9.2 | 10.6 | 2.1667 | 0
| 0.36806 | 282.279 | 40.194 | 47.582 | 42.578 | 65.417 |  | 1.1042 | 31.5267 | 28.7478 | 11.0531 | 13.0128 | 28.3888 | 28.7659 |  | 1.1042 | 8.8 | 10.6 | 2.2083 | 0
| 0.375 | 281.382 | 40.187 | 47.577 | 42.573 | 65.401 |  | 1.125 | 31.4965 | 28.7222 | 11.0326 | 12.9812 | 28.3722 | 28.7312 |  | 1.125 | 8.7 | 10.6 | 2.25 | 0
| 0.38194 | 280.932 | 40.184 | 47.573 | 42.57 | 65.381 |  | 1.1458 | 31.5395 | 28.7583 | 11.0657 | 13.0145 | 28.4084 | 28.7787 |  | 1.1458 | 8.3 | 10.6 | 2.2917 | 0
| 0.38889 | 280.737 | 40.175 | 47.562 | 42.564 | 65.366 |  | 1.1667 | 31.4894 | 28.7061 | 11.0191 | 12.9677 | 28.3517 | 28.722 |  | 1.1667 | 8.2 | 10.6 | 2.3333 | 0
| 0.39583 | 280.536 | 40.167 | 47.562 | 42.565 | 65.342 |  | 1.1875 | 31.5347 | 28.7536 | 11.0545 | 13.0011 | 28.3923 | 28.7717 |  | 1.1875 | 7.7 | 10.6 | 2.375 | 0
| 0.40278 | 279.798 | 40.164 | 47.551 | 42.558 | 65.315 |  | 1.2083 | 31.4982 | 28.7218 | 11.0234 | 12.9588 | 28.3515 | 28.74 |  | 1.2083 | 7 | 10.6 | 2.4167 | 0.2
| 0.40972 | 278.866 | 40.15 | 47.538 | 42.551 | 65.285 |  | 1.2292 | 31.5073 | 28.7286 | 11.0255 | 12.9677 | 28.3606 | 28.758 |  | 1.2292 | 6.7 | 10.6 | 2.4583 | 0.8
| 0.41667 | 281.772 | 40.147 | 47.536 | 42.545 | 65.264 |  | 1.25 | 31.5142 | 28.7422 | 11.0278 | 12.9699 | 28.3696 | 28.7625 |  | 1.25 | 6.6 | 10.6 | 2.5 | 0.4
| 0.42361 | 281.155 | 40.147 | 47.541 | 42.547 | 65.26 |  | 1.2708 | 31.5118 | 28.7376 | 11.0189 | 12.9632 | 28.3629 | 28.7513 |  | 1.2708 | 6.6 | 10.6 | 2.5417 | 0
| 0.43056 | 281.558 | 40.151 | 47.537 | 42.553 | 65.257 |  | 1.2917 | 31.5069 | 28.7259 | 11.0252 | 12.9583 | 28.3669 | 28.7553 |  | 1.2917 | 7.1 | 10.6 | 2.5833 | 0
| 0.4375 | 281.382 | 40.154 | 47.54 | 42.552 | 65.252 |  | 1.3125 | 31.5282 | 28.7493 | 11.0215 | 12.9633 | 28.3745 | 28.7719 |  | 1.3125 | 8.1 | 10.6 | 2.625 | 0
| 0.44444 | 280.424 | 40.152 | 47.532 | 42.552 | 65.24 |  | 1.3333 | 31.559 | 28.7686 | 11.0381 | 12.9887 | 28.4006 | 28.7957 |  | 1.3333 | 9.5 | 10.6 | 2.6667 | 0
| 0.45139 | 280.65 | 40.141 | 47.531 | 42.549 | 65.224 |  | 1.3542 | 31.7059 | 28.8833 | 11.084 | 13.0321 | 28.4656 | 28.8472 |  | 1.3542 | 10.8 | 10.6 | 2.7083 | 0
| 0.45833 | 279.617 | 40.14 | 47.525 | 42.539 | 65.209 |  | 1.375 | 31.7471 | 28.8858 | 11.0707 | 13.0362 | 28.4818 | 28.8476 |  | 1.375 | 12 | 10.6 | 2.75 | 0
| 0.46528 | 279.822 | 40.13 | 47.521 | 42.54 | 65.188 |  | 1.3958 | 31.7489 | 28.8829 | 11.0848 | 13.0435 | 28.4813 | 28.8379 |  | 1.3958 | 13.4 | 10.6 | 2.7917 | 0.2
| 0.47222 | 279.141 | 40.127 | 47.51 | 42.531 | 65.17 |  | 1.4167 | 31.7506 | 28.889 | 11.0774 | 13.0425 | 28.4851 | 28.8417 |  | 1.4167 | 14.6 | 10.6 | 2.8333 | 0
| 0.47917 | 279.57 | 40.121 | 47.503 | 42.53 | 65.147 |  | 1.4375 | 31.7535 | 28.8942 | 11.085 | 13.0455 | 28.4811 | 28.8399 |  | 1.4375 | 15.4 | 10.6 | 2.875 | 0
| 0.48611 | 279.434 | 40.117 | 47.496 | 42.519 | 65.123 |  | 1.4583 | 31.772 | 28.9081 | 11.0936 | 13.063 | 28.5017 | 28.8583 |  | 1.4583 | 17.1 | 10.6 | 2.9167 | 0
| 0.49306 | 278.428 | 40.107 | 47.487 | 42.515 | 65.104 |  | 1.4792 | 31.7469 | 28.8896 | 11.0732 | 13.0445 | 28.4791 | 28.8355 |  | 1.4792 | 17.7 | 10.6 | 2.9583 | 0
| 0.5 | 278.521 | 40.1 | 47.473 | 42.505 | 65.076 |  | 1.5 | 31.7566 | 28.8948 | 11.0825 | 13.0606 | 28.4888 | 28.8475 |  | 1.5 | 18.7 | 10.6 | 3 | 0
| 0.50694 | 278 | 40.095 | 47.463 | 42.498 | 65.054 |  | 1.5208 | 31.7828 | 28.9208 | 11.0988 | 13.0858 | 28.508 | 28.8757 |  | 1.5208 | 18.1 | 10.6 | 3.0417 | 0
| 0.51389 | 278.25 | 40.084 | 47.452 | 42.487 | 65.027 |  | 1.5417 | 31.7755 | 28.9066 | 11.0864 | 13.0625 | 28.4846 | 28.8614 |  | 1.5417 | 18.9 | 10.6 | 3.0833 | 0
| 0.52083 | 277.688 | 40.072 | 47.441 | 42.476 | 65 |  | 1.5625 | 31.7925 | 28.9324 | 11.104 | 13.0915 | 28.5038 | 28.8963 |  | 1.5625 | 19.3 | 10.6 | 3.125 | 0
| 0.52778 | 277.002 | 40.059 | 47.423 | 42.468 | 64.964 |  | 1.5833 | 31.6909 | 28.8084 | 10.9305 | 12.9357 | 28.3124 | 28.7318 |  | 1.5833 | 19.9 | 10.6 | 3.1667 | 0
| 0.53472 | 277.025 | 40.053 | 47.408 | 42.455 | 64.928 |  | 1.6042 | [7 empty] | 1.6042 | 20 | 10.6 | 3.2083 | 0
| 0.54167 | 277.121 | 40.039 | 47.398 | 42.445 | 64.895 |  | 1.625 | [7 empty] | 1.625 | 20.1 | 10.6 | 3.25 | 0
| 0.54861 | 277.879 | 40.035 | 47.387 | 42.438 | 64.879 |  | 1.6458 | [7 empty] | 1.6458 | 20.9 | 10.6 | 3.2917 | 0
| 0.55556 | 278.867 | 40.03 | 47.382 | 42.434 | 64.866 |  | 1.6667 | [7 empty] | 1.6667 | 20.6 | 10.6 | 3.3333 | 0
| 0.5625 | 278.338 | 40.035 | 47.379 | 42.434 | 64.862 |  | 1.6875 | [7 empty] | 1.6875 | 20.7 | 10.6 | 3.375 | 0
| 0.56944 | 277.724 | 40.03 | 47.37 | 42.429 | 64.858 |  | 1.7083 | [7 empty] | 1.7083 | 20.8 | 10.6 | 3.4167 | 0
| 0.57639 | 278.329 | 40.03 | 47.374 | 42.424 | 64.849 |  | 1.7292 | [7 empty] | 1.7292 | 21.3 | 10.6 | 3.4583 | 0
| 0.58333 | 278.428 | 40.034 | 47.366 | 42.418 | 64.84 |  | 1.75 | [7 empty] | 1.75 | 21.1 | 10.6 | 3.5 | 0
| 0.59028 | 279.236 | 40.03 | 47.368 | 42.419 | 64.837 |  | 1.7708 | [7 empty] | 1.7708 | 20.9 | 10.6 | 3.5417 | 0
| 0.59722 | 279.551 | 40.033 | 47.371 | 42.423 | 64.843 |  | 1.7917 | [7 empty] | 1.7917 | 20.8 | 10.6 | 3.5833 | 0
| 0.60417 | 279.345 | 40.041 | 47.374 | 42.423 | 64.854 |  | 1.8125 | [7 empty] | 1.8125 | 20.7 | 10.6 | 3.625 | 0
| 0.61111 | 277.304 | 40.036 | 47.369 | 42.416 | 64.845 |  | 1.8333 | [7 empty] | 1.8333 | 19.3 | 10.6 | 3.6667 | 0
| 0.61806 | 276.667 | 40.024 | 47.35 | 42.403 | 64.817 |  | 1.8542 | [7 empty] | 1.8542 | 16.8 | 10.6 | 3.7083 | 0
| 0.625 | 276.48 | 40.01 | 47.337 | 42.394 | 64.782 |  | 1.875 | [7 empty] | 1.875 | 14.3 | 10.6 | 3.75 | 0
| 0.63194 | 276.925 | 39.999 | 47.325 | 42.383 | 64.758 |  | 1.8958 | [7 empty] | 1.8958 | 12.9 | 10.6 | 3.7917 | 0
| 0.63889 | 276.433 | 39.993 | 47.31 | 42.373 | 64.728 |  | 1.9167 | [7 empty] | 1.9167 | 11.9 | 10.6 | 3.8333 | 0
| 0.64583 | 277.242 | 39.985 | 47.3 | 42.36 | 64.707 |  | 1.9375 | [7 empty] | 1.9375 | 11 | 10.6 | 3.875 | 0
| 0.65278 | 276.698 | 39.979 | 47.297 | 42.363 | 64.692 |  | 1.9583 | 31.6733 | 28.8147 | 11.0516 | 13.0488 | 28.4625 | 28.8192 |  | 1.9583 | 10.2 | 10.6 | 3.9167 | 0
| 0.65972 | 277.056 | 39.972 | 47.286 | 42.351 | 64.675 |  | 1.9792 | 31.5764 | 28.7679 | 11.0061 | 12.9766 | 28.4158 | 28.777 |  | 1.9792 | 9.5 | 10.6 | 3.9583 | 0
| 0.66667 | 276.681 | 39.972 | 47.283 | 42.348 | 64.663 |  | 2 | 31.5122 | 28.7694 | 10.9901 | 12.9738 | 28.3992 | 28.7717 |  | 2 | 8.9 | 10.6 | 4 | 0
| 0.67361 | 276.895 | 39.962 | 47.269 | 42.338 | 64.646 |  | 2.0208 | 31.4937 | 28.7781 | 11.0117 | 12.9824 | 28.4123 | 28.7803 |  | 2.0208 | 8.6 | 10.6 | 4.0417 | 0
| 0.68056 | 276.546 | 39.956 | 47.261 | 42.328 | 64.629 |  | 2.0417 | 31.4778 | 28.7894 | 11.0206 | 12.9913 | 28.419 | 28.7894 |  | 2.0417 | 8.6 | 10.6 | 4.0833 | 0
| 0.6875 | 276.555 | 39.95 | 47.255 | 42.327 | 64.615 |  | 2.0625 | 31.4256 | 28.7464 | 10.9812 | 12.9496 | 28.3762 | 28.7464 |  | 2.0625 | 8.3 | 10.6 | 4.125 | 0
| 0.69444 | 277.368 | 39.947 | 47.246 | 42.326 | 64.611 |  | 2.0833 | 31.2943 | 28.6651 | 10.9038 | 12.8807 | 28.3152 | 28.6855 |  | 2.0833 | 7.4 | 10.6 | 4.1667 | 0
| 0.70139 | 277.972 | 39.948 | 47.249 | 42.327 | 64.612 |  | 2.1042 | 31.4016 | 28.7314 | 10.9397 | 12.9147 | 28.3544 | 28.7292 |  | 2.1042 | 7.6 | 10.6 | 4.2083 | 0
| 0.70833 | 277.412 | 39.95 | 47.246 | 42.325 | 64.617 |  | 2.125 | 31.422 | 28.745 | 10.9619 | 12.9346 | 28.3792 | 28.7563 |  | 2.125 | 7.6 | 10.6 | 4.25 | 0
| 0.71528 | 276.557 | 39.951 | 47.25 | 42.319 | 64.611 |  | 2.1458 | 31.4151 | 28.745 | 10.9575 | 12.9214 | 28.3769 | 28.754 |  | 2.1458 | 7.2 | 10.6 | 4.2917 | 0
| 0.72222 | 276.182 | 39.946 | 47.237 | 42.314 | 64.598 |  | 2.1667 | 31.4084 | 28.7495 | 10.9508 | 12.9258 | 28.3702 | 28.745 |  | 2.1667 | 7.3 | 10.6 | 4.3333 | 0
| 0.72917 | 276.108 | 39.946 | 47.237 | 42.31 | 64.59 |  | 2.1875 | 31.3948 | 28.7382 | 10.9331 | 12.9036 | 28.3498 | 28.7382 |  | 2.1875 | 7.4 | 10.6 | 4.375 | 0
| 0.73611 | 276.095 | 39.938 | 47.228 | 42.303 | 64.572 |  | 2.2083 | 31.3835 | 28.7247 | 10.9221 | 12.888 | 28.3408 | 28.7292 |  | 2.2083 | 7.6 | 10.6 | 4.4167 | 0
| 0.74306 | 276.006 | 39.929 | 47.219 | 42.296 | 64.558 |  | 2.2292 | 31.442 | 28.7762 | 10.9705 | 12.9477 | 28.3879 | 28.7876 |  | 2.2292 | 7.8 | 11.1 | 4.4583 | 0
| 0.75 | 276.34 | 39.926 | 47.214 | 42.294 | 64.546 |  | 2.25 | 31.4533 | 28.7876 | 10.9882 | 12.9566 | 28.4081 | 28.7988 |  | 2.25 | 7.9 | 11.1 | 4.5 | 0
| 0.75694 | 276.087 | 39.922 | 47.208 | 42.287 | 64.542 |  | 2.2708 | 31.4714 | 28.8102 | 11.0015 | 12.9655 | 28.424 | 28.8191 |  | 2.2708 | 7.7 | 11.1 | 4.5417 | 0
| 0.76389 | 276.4 | 39.916 | 47.2 | 42.291 | 64.528 |  | 2.2917 | 31.451 | 28.7943 | 10.9949 | 12.9455 | 28.4081 | 28.8124 |  | 2.2917 | 7.5 | 11.1 | 4.5833 | 0
| 0.77083 | 276.254 | 39.914 | 47.195 | 42.279 | 64.511 |  | 2.3125 | 31.4744 | 28.8086 | 10.9933 | 12.9549 | 28.4067 | 28.8153 |  | 2.3125 | 8 | 11.1 | 4.625 | 0
| 0.77778 | 276.033 | 39.905 | 47.185 | 42.279 | 64.497 |  | 2.3333 | 31.5016 | 28.8333 | 10.9845 | 12.9591 | 28.4269 | 28.84 |  | 2.3333 | 10.1 | 11.1 | 4.6667 | 0
| 0.78472 | 276.184 | 39.901 | 47.182 | 42.275 | 64.489 |  | 2.3542 | 31.6503 | 28.9385 | 11.0295 | 12.9974 | 28.4711 | 28.8866 |  | 2.3542 | 11.6 | 11.1 | 4.7083 | 0
| 0.79167 | 276.041 | 39.898 | 47.184 | 42.269 | 64.485 |  | 2.375 | 31.6923 | 28.9645 | 11.0527 | 13.0204 | 28.4859 | 28.9058 |  | 2.375 | 12.2 | 11.1 | 4.75 | 0
| 0.79861 | 276.676 | 39.894 | 47.174 | 42.264 | 64.472 |  | 2.3958 | 31.5695 | 28.9073 | 11.0628 | 13.0238 | 28.4627 | 28.9278 |  | 2.3958 | 13.8 | 11.1 | 4.7917 | 0
| 0.80556 | 276.869 | 39.894 | 47.169 | 42.263 | 64.468 |  | 2.4167 | 31.5528 | 28.8817 | 11.0422 | 13.0231 | 28.4506 | 28.9111 |  | 2.4167 | 14.4 | 11.1 | 4.8333 | 0
| 0.8125 | 276.515 | 39.891 | 47.169 | 42.266 | 64.46 |  | 2.4375 | 31.5371 | 28.8753 | 11.0273 | 13.0018 | 28.4396 | 28.9024 |  | 2.4375 | 12.1 | 11.1 | 4.875 | 0
| 0.81944 | 276.527 | 39.884 | 47.158 | 42.264 | 64.449 |  | 2.4583 | 31.5221 | 28.8604 | 11.0174 | 12.9919 | 28.4247 | 28.8898 |  | 2.4583 | 11.2 | 11.1 | 4.9167 | 0
| 0.82639 | 276.98 | 39.884 | 47.16 | 42.261 | 64.449 |  | 2.4792 | 31.5493 | 28.8921 | 11.055 | 13.0119 | 28.4563 | 28.9237 |  | 2.4792 | 10.8 | 11.1 | 4.9583 | 0
| 0.83333 | 277.56 | 39.888 | 47.165 | 42.26 | 64.448 |  | 2.5 | 31.5448 | 28.8943 | 11.0528 | 13.0119 | 28.4563 | 28.9169 |  | 2.5 | 10.9 | 11.1 | 5 | 0
| 0.84028 | 277.656 | 39.886 | 47.164 | 42.26 | 64.449 |  | 2.5208 | 31.5108 | 28.8491 | 10.9997 | 12.9608 | 28.4653 | 28.8695 |  | 2.5208 | 10.8 | 11.1 | 5.0417 | 0
| 0.84722 | 276.881 | 39.885 | 47.165 | 42.265 | 64.453 |  | 2.5417 | 31.641 | 28.884 | 11.0272 | 12.9949 | 28.4913 | 28.9067 |  | 2.5417 | 11.1 | 11.1 | 5.0833 | 0
| 0.85417 | 277.201 | 39.885 | 47.163 | 42.266 | 64.451 |  | 2.5625 | 31.7091 | 28.9564 | 11.0489 | 13.0077 | 28.5071 | 28.9202 |  | 2.5625 | 11.9 | 11.1 | 5.125 | 0
| 0.86111 | 277.587 | 39.892 | 47.167 | 42.264 | 64.454 |  | 2.5833 | 31.721 | 28.9682 | 11.0561 | 13.0213 | 28.5122 | 28.9433 |  | 2.5833 | 12.1 | 11.1 | 5.1667 | 0
| 0.86806 | 277.167 | 39.889 | 47.167 | 42.267 | 64.449 |  | 2.6042 | 31.7505 | 28.9929 | 11.0733 | 13.0361 | 28.5414 | 28.9612 |  | 2.6042 | 13.5 | 11.1 | 5.2083 | 0
| 0.875 | 277.203 | 39.889 | 47.168 | 42.271 | 64.456 |  | 2.625 | 31.7459 | 28.9929 | 11.0689 | 13.0295 | 28.5369 | 28.9612 |  | 2.625 | 14.2 | 11.1 | 5.25 | 0
| 0.88194 | 278.351 | 39.89 | 47.173 | 42.276 | 64.458 |  | 2.6458 | 31.789 | 29.0358 | 11.0954 | 13.0717 | 28.5616 | 29.0018 |  | 2.6458 | 14.1 | 11.1 | 5.2917 | 0
| 0.88889 | 277.931 | 39.895 | 47.175 | 42.276 | 64.471 |  | 2.6667 | 31.7593 | 29.0016 | 11.0754 | 13.0405 | 28.5345 | 28.977 |  | 2.6667 | 13.6 | 11.1 | 5.3333 | 0
| 0.89583 | 278.126 | 39.896 | 47.181 | 42.279 | 64.472 |  | 2.6875 | 31.7623 | 29.0114 | 11.0782 | 13.0477 | 28.5375 | 28.9844 |  | 2.6875 | 13.6 | 11.1 | 5.375 | 0
| 0.90278 | 278.716 | 39.897 | 47.184 | 42.289 | 64.482 |  | 2.7083 | 31.6967 | 28.9595 | 11.0274 | 12.9966 | 28.4878 | 28.9234 |  | 2.7083 | 14.2 | 11.1 | 5.4167 | 0
| 0.90972 | 278.281 | 39.907 | 47.192 | 42.295 | 64.495 |  | 2.7292 | 31.7137 | 28.9764 | 11.046 | 13.0131 | 28.4957 | 28.9516 |  | 2.7292 | 14.1 | 11.1 | 5.4583 | 0
| 0.91667 | 279.242 | 39.912 | 47.199 | 42.3 | 64.509 |  | 2.75 | 31.7226 | 28.9854 | 11.0392 | 13.0175 | 28.5001 | 28.9538 |  | 2.75 | 14.1 | 11.1 | 5.5 | 0
| 0.92361 | 278.384 | 39.915 | 47.209 | 42.308 | 64.521 |  | 2.7708 | 31.5518 | 28.9775 | 11.0384 | 13.0123 | 28.4969 | 28.9484 |  | 2.7708 | 13.7 | 11.1 | 5.5417 | 0
| 0.93056 | 278.718 | 39.923 | 47.215 | 42.307 | 64.536 |  | 2.7917 | 31.5301 | 28.9177 | 11.0263 | 12.9981 | 28.4438 | 28.9404 |  | 2.7917 | 13.7 | 11.1 | 5.5833 | 0
| 0.9375 | 279.707 | 39.931 | 47.223 | 42.313 | 64.544 |  | 2.8125 | 31.5313 | 28.8987 | 11.0409 | 12.9996 | 28.4495 | 28.937 |  | 2.8125 | 12.6 | 11.1 | 5.625 | 0
| 0.94444 | 280.118 | 39.936 | 47.234 | 42.323 | 64.565 |  | 2.8333 | 31.5443 | 28.9163 | 11.0365 | 13.022 | 28.4467 | 28.9524 |  | 2.8333 | 12.1 | 11.1 | 5.6667 | 0
| 0.95139 | 279.977 | 39.948 | 47.251 | 42.339 | 64.582 |  | 2.8542 | 31.5393 | 28.9023 | 11.0406 | 13.0152 | 28.4555 | 28.9567 |  | 2.8542 | 10.8 | 11.1 | 5.7083 | 0
| 0.95833 | 280.645 | 39.957 | 47.259 | 42.349 | 64.615 |  | 2.875 | 31.5189 | 28.8844 | 11.0124 | 12.9981 | 28.4263 | 28.9298 |  | 2.875 | 9.7 | 11.1 | 5.75 | 0
| 0.96528 | 280.921 | 39.972 | 47.276 | 42.357 | 64.639 |  | 2.8958 | 31.5063 | 28.881 | 11.0135 | 12.9749 | 28.4294 | 28.9194 |  | 2.8958 | 9.1 | 11.1 | 5.7917 | 0
| 0.97222 | 281.55 | 39.983 | 47.293 | 42.371 | 64.666 |  | 2.9167 | 31.4901 | 28.8649 | 11.0022 | 12.9614 | 28.4201 | 28.9147 |  | 2.9167 | 8.7 | 11.1 | 5.8333 | 0
| 0.97917 | 281.997 | 39.998 | 47.314 | 42.39 | 64.706 |  | 2.9375 | 31.4635 | 28.8362 | 10.9787 | 12.9381 | 28.3892 | 28.8928 |  | 2.9375 | 8.4 | 11.1 | 5.875 | 0
| 0.98611 | 282.729 | 40.017 | 47.337 | 42.403 | 64.753 |  | 2.9583 | 31.4851 | 28.8601 | 10.9778 | 12.9507 | 28.4107 | 28.912 |  | 2.9583 | 7.6 | 11.1 | 5.9167 | 0
| 0.99306 | 283.266 | 40.039 | 47.363 | 42.427 | 64.797 |  | 2.9792 | 31.4425 | 28.8154 | 10.9521 | 12.9094 | 28.3684 | 28.8698 |  | 2.9792 | 6.6 | 11.1 | 5.9583 | 0
| 1 | 283.084 | 40.054 | 47.387 | 42.444 | 64.842 |  | 3 | 31.4086 | 28.7794 | 10.9212 | 12.8674 | 28.3391 | 28.8361 |  | 3 | 5.6 | 11.1 | 6 | 0
| 1.0069 | 284.292 | 40.081 | 47.415 | 42.465 | 64.89 |  | 3.0208 | 31.3822 | 28.7577 | 10.8956 | 12.8485 | 28.3218 | 28.8232 |  | 3.0208 | 4.8 | 11.1 | 6.0417 | 0
| 1.0139 | 281.235 | 40.092 | 47.435 | 42.477 | 64.916 |  | 3.0417 | 31.3616 | 28.7394 | 10.889 | 12.8197 | 28.3036 | 28.8027 |  | 3.0417 | 4.4 | 11.1 | 6.0833 | 0
| 1.0208 | 281.645 | 40.094 | 47.439 | 42.485 | 64.929 |  | 3.0625 | 31.3241 | 28.7111 | 10.8476 | 12.7961 | 28.2797 | 28.7653 |  | 3.0625 | 3.7 | 11.1 | 6.125 | 0
| 1.0278 | 281.436 | 40.096 | 47.45 | 42.492 | 64.938 |  | 3.0833 | 31.31 | 28.7015 | 10.8449 | 12.8001 | 28.2746 | 28.767 |  | 3.0833 | 3.3 | 11.1 | 6.1667 | 0
| 1.0347 | 282.113 | 40.11 | 47.462 | 42.507 | 64.952 |  | 3.1042 | 31.3122 | 28.697 | 10.845 | 12.7869 | 28.2702 | 28.7626 |  | 3.1042 | 2.8 | 11.1 | 6.2083 | 0
| 1.0417 | 282.115 | 40.111 | 47.473 | 42.505 | 64.966 |  | 3.125 | [7 empty] | 3.125 | 2.4 | 11.1 | 6.25 | 0
| 1.0486 | 282.338 | 40.123 | 47.49 | 42.526 | 64.979 |  | 3.1458 | [7 empty] | 3.1458 | 2.1 | 11.1 | 6.2917 | 0
| 1.0556 | 282.664 | 40.132 | 47.508 | 42.535 | 65.007 |  | 3.1667 | [7 empty] | 3.1667 | 1.7 | 11.1 | 6.3333 | 0
| 1.0625 | 283.007 | 40.147 | 47.526 | 42.549 | 65.036 |  | 3.1875 | [7 empty] | 3.1875 | 1.7 | 11.1 | 6.375 | 0
| 1.0694 | 282.513 | 40.154 | 47.539 | 42.563 | 65.05 |  | 3.2083 | [7 empty] | 3.2083 | 1.4 | 11.1 | 6.4167 | 0
| 1.0764 | 283.104 | 40.168 | 47.553 | 42.577 | 65.072 |  | 3.2292 | [7 empty] | 3.2292 | 1.6 | 11.1 | 6.4583 | 0
| 1.0833 | 282.706 | 40.174 | 47.568 | 42.586 | 65.091 |  | 3.25 | [7 empty] | 3.25 | 1.1 | 11.1 | 6.5 | 0
| 1.0903 | 282.253 | 40.19 | 47.586 | 42.597 | 65.109 |  | 3.2708 | [7 empty] | 3.2708 | 1.8 | 11.1 | 6.5417 | 0
| 1.0972 | 282.669 | 40.194 | 47.597 | 42.611 | 65.122 |  | 3.2917 | [7 empty] | 3.2917 | 1.4 | 11.1 | 6.5833 | 0
| 1.1042 | 283.084 | 40.2 | 47.617 | 42.623 | 65.142 |  | 3.3125 | [7 empty] | 3.3125 | 2.3 | 11.1 | 6.625 | 0
| 1.1111 | 282.38 | 40.212 | 47.629 | 42.632 | 65.163 |  | 3.3333 | [7 empty] | 3.3333 | 4.8 | 11.1 | 6.6667 | 0
| 1.1181 | 283.326 | 40.224 | 47.644 | 42.645 | 65.18 |  | 3.3542 | [7 empty] | 3.3542 | 7.7 | 11.1 | 6.7083 | 0
| 1.125 | 282.569 | 40.235 | 47.662 | 42.658 | 65.202 |  | 3.375 | [7 empty] | 3.375 | 9.4 | 11.1 | 6.75 | 0
| 1.1319 | 282.891 | 40.246 | 47.676 | 42.675 | 65.222 |  | 3.3958 | [7 empty] | 3.3958 | 10.7 | 11.1 | 6.7917 | 0
| 1.1389 | 283.202 | 40.256 | 47.689 | 42.685 | 65.237 |  | 3.4167 | [7 empty] | 3.4167 | 12.1 | 11.1 | 6.8333 | 0
| 1.1458 | 282.851 | 40.266 | 47.703 | 42.692 | 65.254 |  | 3.4375 | [7 empty] | 3.4375 | 12.5 | 11.1 | 6.875 | 0
| 1.1528 | 282.271 | 40.271 | 47.714 | 42.705 | 65.264 |  | 3.4583 | [7 empty] | 3.4583 | 12.7 | 11.1 | 6.9167 | 0
| 1.1597 | 282.565 | 40.275 | 47.726 | 42.711 | 65.265 |  | 3.4792 | [7 empty] | 3.4792 | 12.3 | 11.1 | 6.9583 | 0
| 1.1667 | 281.632 | 40.278 | 47.731 | 42.719 | 65.268 |  | 3.5 | [7 empty] | 3.5 | 13.7 | 11.1 | 7 | 0
| 1.1736 | 281.774 | 40.278 | 47.737 | 42.723 | 65.266 |  | 3.5208 | [7 empty] | 3.5208 | 14.2 | 11.1 | 7.0417 | 0
| 1.1806 | 281.739 | 40.275 | 47.742 | 42.728 | 65.257 |  | 3.5417 | [7 empty] | 3.5417 | 13.8 | 11.1 | 7.0833 | 0
| 1.1875 | 281.837 | 40.278 | 47.747 | 42.728 | 65.259 |  | 3.5625 | [7 empty] | 3.5625 | 15.6 | 11.1 | 7.125 | 0
| 1.1944 | 281.369 | 40.286 | 47.752 | 42.736 | 65.257 |  | 3.5833 | [7 empty] | 3.5833 | 15.1 | 11.1 | 7.1667 | 0
| 1.2014 | 280.988 | 40.286 | 47.755 | 42.735 | 65.253 |  | 3.6042 | [7 empty] | 3.6042 | 15.5 | 11.1 | 7.2083 | 0
| 1.2083 | 280.463 | 40.287 | 47.76 | 42.739 | 65.242 |  | 3.625 | [7 empty] | 3.625 | 15.5 | 11.1 | 7.25 | 0
| 1.2153 | 279.651 | 40.28 | 47.761 | 42.743 | 65.235 |  | 3.6458 | 31.3876 | 28.7335 | 10.6634 | 12.9233 | 28.0637 | 28.9773 |  | 3.6458 | 16 | 11.1 | 7.2917 | 0
| 1.2222 | 279.508 | 40.277 | 47.758 | 42.741 | 65.215 |  | 3.6667 | 31.1355 | 28.44 | 10.452 | 12.7006 | 27.7038 | 28.767 |  | 3.6667 | 16.6 | 11.1 | 7.3333 | 0
| 1.2292 | 278.853 | 40.269 | 47.747 | 42.74 | 65.187 |  | 3.6875 | 31.3374 | 28.5617 | 10.667 | 12.8647 | 27.8325 | 28.9204 |  | 3.6875 | 16.2 | 11.1 | 7.375 | 0
| 1.2361 | 282.43 | 40.257 | 47.742 | 42.733 | 65.159 |  | 3.7083 | 31.4122 | 28.5573 | 10.7622 | 12.898 | 27.9365 | 28.9521 |  | 3.7083 | 16.5 | 11.1 | 7.4167 | 0
| 1.2431 | 283.016 | 40.271 | 47.752 | 42.746 | 65.164 |  | 3.7292 | 31.45 | 28.5268 | 10.8143 | 12.9168 | 28.0239 | 28.9827 |  | 3.7292 | 16.1 | 11.1 | 7.4583 | 0
| 1.25 | 283.301 | 40.29 | 47.776 | 42.765 | 65.212 |  | 3.75 | 31.1345 | 28.1302 | 10.4531 | 12.5797 | 27.7233 | 28.6307 |  | 3.75 | 16 | 11.1 | 7.5 | 0
| 1.2569 | 280.965 | 40.304 | 47.795 | 42.776 | 65.233 |  | 3.7708 | 31.0126 | 27.9769 | 10.3167 | 12.3766 | 27.5792 | 28.4643 |  | 3.7708 | 16.3 | 11.1 | 7.5417 | 0
| 1.2639 | 282.981 | 40.31 | 47.805 | 42.788 | 65.246 |  | 3.7917 | 30.6067 | 27.6649 | 10.1682 | 12.1281 | 27.5587 | 28.394 |  | 3.7917 | 16.1 | 11.1 | 7.5833 | 0
| 1.2708 | 282.454 | 40.326 | 47.821 | 42.796 | 65.267 |  | 3.8125 | 30.969 | 27.8501 | 10.3633 | 12.3452 | 27.7596 | 28.4586 |  | 3.8125 | 15.5 | 11.1 | 7.625 | 0
| 1.2778 | 282.528 | 40.336 | 47.835 | 42.811 | 65.283 |  | 3.8333 | 30.9731 | 27.8402 | 10.4278 | 12.3673 | 27.8988 | 28.5233 |  | 3.8333 | 14.8 | 11.1 | 7.6667 | 0
| 1.2847 | 282.451 | 40.343 | 47.844 | 42.821 | 65.296 |  | 3.8542 | 31.2056 | 27.9984 | 10.667 | 12.6395 | 28.2216 | 28.7587 |  | 3.8542 | 13.3 | 11.1 | 7.7083 | 0
| 1.2917 | 281.562 | 40.35 | 47.856 | 42.826 | 65.306 |  | 3.875 | 31.1056 | 28.025 | 10.6294 | 12.6244 | 28.1085 | 28.4876 |  | 3.875 | 11.3 | 11.1 | 7.75 | 0
| 1.2986 | 281.168 | 40.348 | 47.86 | 42.825 | 65.305 |  | 3.8958 | 31.1875 | 27.922 | 10.6788 | 12.5789 | 28.1633 | 28.5199 |  | 3.8958 | 9.7 | 11.1 | 7.7917 | 0
| 1.3056 | 279.593 | 40.345 | 47.858 | 42.83 | 65.289 |  | 3.9167 | 31.3532 | 28.0624 | 10.8259 | 12.6757 | 28.2789 | 28.6943 |  | 3.9167 | 8.4 | 11.1 | 7.8333 | 0
| 1.3125 | 279.203 | 40.336 | 47.855 | 42.821 | 65.257 |  | 3.9375 | 31.4007 | 28.0782 | 10.7972 | 12.6468 | 28.473 | 28.7304 |  | 3.9375 | 8.2 | 11.1 | 7.875 | 0
| 1.3194 | 280.254 | 40.324 | 47.846 | 42.82 | 65.235 |  | 3.9583 | 31.285 | 27.8997 | 10.6355 | 12.4914 | 28.2922 | 28.3893 |  | 3.9583 | 7.8 | 11.1 | 7.9167 | 0
| 1.3264 | 281.962 | 40.322 | 47.841 | 42.818 | 65.217 |  | 3.9792 | 31.4721 | 28.1426 | 10.92 | 12.7173 | 28.6505 | 28.7928 |  | 3.9792 | 7.5 | 11.1 | 7.9583 | 0
| 1.3333 | 281.247 | 40.324 | 47.845 | 42.824 | 65.218 |  | 4 | 31.5151 | 28.1246 | 10.8963 | 12.7224 | 28.6212 | 28.7635 |  | 4 | 7.3 | 11.1 | 8 | 0
| 1.3403 | 280.294 | 40.332 | 47.855 | 42.83 | 65.229 |  | 4.0208 | 31.3341 | 28.0006 | 10.8499 | 12.6403 | 28.6846 | 28.7998 |  | 4.0208 | 7.2 | 11.1 | 8.0417 | 0
| 1.3472 | 280.463 | 40.337 | 47.855 | 42.833 | 65.227 |  | 4.0417 | 31.2977 | 27.89 | 10.8365 | 12.658 | 28.6507 | 28.7569 |  | 4.0417 | 6.6 | 11.1 | 8.0833 | 0
| 1.3542 | 283.32 | 40.343 | 47.871 | 42.839 | 65.236 |  | 4.0625 | 31.387 | 27.9204 | 10.8156 | 12.444 | 28.6335 | 28.6133 |  | 4.0625 | 6.1 | 11.1 | 8.125 | 0
| 1.3611 | 283.016 | 40.361 | 47.889 | 42.859 | 65.27 |  | 4.0833 | 31.2492 | 27.7402 | 10.6678 | 12.4444 | 28.5256 | 28.5142 |  | 4.0833 | 5.4 | 11.1 | 8.1667 | 0
| 1.3681 | 282.225 | 40.375 | 47.903 | 42.876 | 65.293 |  | 4.1042 | 31.2402 | 27.6862 | 10.7032 | 12.4668 | 28.6206 | 28.6206 |  | 4.1042 | 4.7 | 11.1 | 8.2083 | 0
| 1.375 | 282.45 | 40.387 | 47.911 | 42.881 | 65.318 |  | 4.125 | 31.2833 | 27.7245 | 10.6701 | 12.4623 | 28.616 | 28.5551 |  | 4.125 | 4.6 | 11.1 | 8.25 | 0
| 1.3819 | 283.09 | 40.394 | 47.925 | 42.888 | 65.332 |  | 4.1458 | 31.3682 | 27.7528 | 10.698 | 12.4816 | 28.6126 | 28.5697 |  | 4.1458 | 4.6 | 11.1 | 8.2917 | 0
| 1.3889 | 283.056 | 40.406 | 47.936 | 42.904 | 65.35 |  | 4.1667 | 31.3138 | 27.728 | 10.6759 | 12.4527 | 28.5901 | 28.4997 |  | 4.1667 | 4.4 | 11.1 | 8.3333 | 0
| 1.3958 | 282.085 | 40.42 | 47.957 | 42.913 | 65.365 |  | 4.1875 | 31.0235 | 27.4794 | 10.5405 | 12.2614 | 28.463 | 28.384 |  | 4.1875 | 4.2 | 11.7 | 8.375 | 0
| 1.4028 | 280.997 | 40.421 | 47.962 | 42.916 | 65.378 |  | 4.2083 | 30.9103 | 27.351 | 10.8745 | 12.1483 | 28.2486 | 28.5422 |  | 4.2083 | 3.6 | 11.7 | 8.4167 | 0
| 1.4097 | 280.14 | 40.422 | 47.963 | 42.919 | 65.369 |  | 4.2292 | 30.6729 | 27.0087 | 9.9597 | 11.7868 | 27.9913 | 27.9056 |  | 4.2292 | 3.1 | 11.7 | 8.4583 | 0
| 1.4167 | 279.972 | 40.418 | 47.958 | 42.918 | 65.359 |  | 4.25 | 30.7813 | 27.0672 | 10.0965 | 11.9243 | 28.3117 | 28.0861 |  | 4.25 | 3.5 | 11.7 | 8.5 | 0
| 1.4236 | 280.559 | 40.416 | 47.962 | 42.919 | 65.346 |  | 4.2708 | 30.4406 | 26.737 | 9.7197 | 11.5657 | 27.8543 | 27.7483 |  | 4.2708 | 4.3 | 11.7 | 8.5417 | 0
| 1.4306 | 280.302 | 40.417 | 47.964 | 42.922 | 65.333 |  | 4.2917 | 30.6756 | 26.9619 | 9.9688 | 11.7669 | 28.0119 | 27.9216 |  | 4.2917 | 5.4 | 11.7 | 8.5833 | 0
| 1.4375 | 279.193 | 40.414 | 47.959 | 42.918 | 65.318 |  | 4.3125 | 30.7026 | 26.9619 | 9.9775 | 11.7667 | 28.1155 | 28.0049 |  | 4.3125 | 6.6 | 11.7 | 8.625 | 0
| 1.4444 | 277.956 | 40.404 | 47.946 | 42.911 | 65.29 |  | 4.3333 | 30.7341 | 27.009 | 10.0191 | 11.7992 | 28.1333 | 27.9393 |  | 4.3333 | 7.9 | 11.7 | 8.6667 | 0
| 1.4514 | 279.639 | 40.392 | 47.938 | 42.903 | 65.253 |  | 4.3542 | 30.9964 | 27.3151 | 10.2772 | 12.0822 | 28.3474 | 28.2459 |  | 4.3542 | 9.6 | 11.7 | 8.7083 | 0
| 1.4583 | 279.667 | 40.39 | 47.938 | 42.905 | 65.244 |  | 4.375 | 30.6482 | 26.9288 | 9.8922 | 11.7264 | 28.0041 | 27.9049 |  | 4.375 | 11.1 | 11.7 | 8.75 | 0
| 1.4653 | 278.686 | 40.396 | 47.936 | 42.903 | 65.243 |  | 4.3958 | 30.7479 | 27.0617 | 10.1594 | 11.8611 | 28.2635 | 28.1079 |  | 4.3958 | 13 | 11.7 | 8.7917 | 0
| 1.4722 | 279.07 | 40.392 | 47.936 | 42.898 | 65.225 |  | 4.4167 | 30.3593 | 26.622 | 9.6153 | 11.4277 | 27.7727 | 27.6646 |  | 4.4167 | 14.1 | 11.7 | 8.8333 | 0
| 1.4792 | 278.323 | 40.39 | 47.926 | 42.897 | 65.218 |  | 4.4375 | 30.479 | 26.7457 | 9.7449 | 11.5309 | 27.876 | 27.7116 |  | 4.4375 | 15.1 | 11.7 | 8.875 | 0
| 1.4861 | 278.099 | 40.385 | 47.92 | 42.891 | 65.194 |  | 4.4583 | [7 empty] | 4.4583 | 16 | 11.7 | 8.9167 | 0
| 1.4931 | 277.83 | 40.375 | 47.907 | 42.885 | 65.166 |  | 4.4792 | 30.7825 | 27.1832 | 10.0741 | 11.8473 | 28.2709 | 28.0004 |  | 4.4792 | 17.6 | 11.7 | 8.9583 | 0
| 1.5 | 279.27 | 40.366 | 47.9 | 42.881 | 65.139 |  | 4.5 | 30.8044 | 27.0019 | 10.0332 | 11.8442 | 28.3492 | 28.1869 |  | 4.5 | 17.9 | 11.7 | 9 | 0
| 1.5069 | 276.862 | 40.365 | 47.895 | 42.873 | 65.131 |  | 4.5208 | 30.9184 | 27.1018 | 10.0888 | 11.8824 | 28.3658 | 28.111 |  | 4.5208 | 18.9 | 11.7 | 9.0417 | 0
| 1.5139 | 274.868 | 40.357 | 47.879 | 42.866 | 65.096 |  | 4.5417 | 30.8798 | 27.1016 | 10.1016 | 11.8954 | 28.2308 | 28.1203 |  | 4.5417 | 19.4 | 11.7 | 9.0833 | 0
| 1.5208 | 274.114 | 40.331 | 47.855 | 42.851 | 65.034 |  | 4.5625 | 30.9677 | 27.2161 | 10.3707 | 12.0431 | 28.9747 | 28.6206 |  | 4.5625 | 19.9 | 11.7 | 9.125 | 0
| 1.5278 | 274.296 | 40.305 | 47.826 | 42.825 | 64.97 |  | 4.5833 | 31.6041 | 27.8247 | 10.8982 | 12.6174 | 28.9738 | 28.7821 |  | 4.5833 | 20.6 | 11.7 | 9.1667 | 0
| 1.5347 | 274.055 | 40.284 | 47.798 | 42.802 | 64.907 |  | 4.6042 | 30.7738 | 26.9666 | 10.0118 | 11.7821 | 28.1362 | 28.0209 |  | 4.6042 | 20.7 | 11.7 | 9.2083 | 0
| 1.5417 | 274.427 | 40.268 | 47.775 | 42.785 | 64.855 |  | 4.625 | 30.7286 | 26.8991 | 9.9539 | 11.7422 | 28.1273 | 27.9872 |  | 4.625 | 21.3 | 11.7 | 9.25 | 0
| 1.5486 | 274.045 | 40.251 | 47.755 | 42.774 | 64.816 |  | 4.6458 | [7 empty] | 4.6458 | 21.8 | 11.7 | 9.2917 | 0
| 1.5556 | 273.641 | 40.238 | 47.739 | 42.763 | 64.781 |  | 4.6667 | [7 empty] | 4.6667 | 21.9 | 11.7 | 9.3333 | 0
| 1.5625 | 273.991 | 40.228 | 47.721 | 42.748 | 64.749 |  | 4.6875 | [7 empty] | 4.6875 | 22 | 11.7 | 9.375 | 0
| 1.5694 | 273.453 | 40.219 | 47.708 | 42.735 | 64.707 |  | 4.7083 | [7 empty] | 4.7083 | 22.3 | 11.7 | 9.4167 | 0
| 1.5764 | 273.341 | 40.208 | 47.688 | 42.723 | 64.673 |  | 4.7292 | [7 empty] | 4.7292 | 22.3 | 11.7 | 9.4583 | 0
| 1.5833 | 274.241 | 40.196 | 47.672 | 42.704 | 64.64 |  | 4.75 | [7 empty] | 4.75 | 22.1 | 11.7 | 9.5 | 0
| 1.5903 | 274.104 | 40.189 | 47.659 | 42.696 | 64.61 |  | 4.7708 | [7 empty] | 4.7708 | 21.8 | 11.7 | 9.5417 | 0
| 1.5972 | 274.909 | 40.182 | 47.646 | 42.684 | 64.588 |  | 4.7917 | [7 empty] | 4.7917 | 21.3 | 11.7 | 9.5833 | 0
| 1.6042 | 274.147 | 40.172 | 47.635 | 42.676 | 64.569 |  | 4.8125 | [7 empty] | 4.8125 | 20.3 | 11.7 | 9.625 | 0
| 1.6111 | 274.918 | 40.164 | 47.621 | 42.669 | 64.548 |  | 4.8333 | [7 empty] | 4.8333 | 19.3 | 11.7 | 9.6667 | 0
| 1.6181 | 275.593 | 40.166 | 47.616 | 42.658 | 64.535 |  | 4.8542 | [7 empty] | 4.8542 | 17.7 | 11.7 | 9.7083 | 0
| 1.625 | 275.551 | 40.162 | 47.612 | 42.659 | 64.531 |  | 4.875 | [7 empty] | 4.875 | 15.6 | 11.7 | 9.75 | 0
| 1.6319 | 275.376 | 40.166 | 47.611 | 42.656 | 64.53 |  | 4.8958 | [7 empty] | 4.8958 | 14.1 | 11.7 | 9.7917 | 0
| 1.6389 | 275.951 | 40.165 | 47.607 | 42.654 | 64.526 |  | 4.9167 | [7 empty] | 4.9167 | 12.8 | 11.7 | 9.8333 | 0
| 1.6458 | 275.908 | 40.163 | 47.606 | 42.655 | 64.527 |  | 4.9375 | [7 empty] | 4.9375 | 12 | 11.7 | 9.875 | 0
| 1.6528 | 275.062 | 40.163 | 47.603 | 42.656 | 64.523 |  | 4.9583 | [7 empty] | 4.9583 | 11.3 | 11.7 | 9.9167 | 0
| 1.6597 | 276.105 | 40.166 | 47.603 | 42.653 | 64.526 |  | 4.9792 | [7 empty] | 4.9792 | 10.3 | 11.7 | 9.9583 | 0
| 1.6667 | 275.486 | 40.173 | 47.605 | 42.657 | 64.535 |  | 5 | [7 empty] | 5 | 9.6 | 11.7 | 10 | 0
| 1.6736 | 276.312 | 40.171 | 47.608 | 42.654 | 64.532 |  | 5.0208 | [7 empty] | 5.0208 | 9.4 | 11.7 | 10.0417 | 0
| 1.6806 | 275.835 | 40.174 | 47.611 | 42.655 | 64.544 |  | 5.0417 | 31.2016 | 27.2716 | 10.5569 | 12.1485 | 28.6584 | 28.3447 |  | 5.0417 | 9.1 | 11.7 | 10.0833 | 0
| 1.6875 | 272.714 | 40.171 | 47.604 | 42.657 | 64.541 |  | 5.0625 | 31.308 | 27.4855 | 10.5944 | 12.2771 | 28.8234 | 28.4869 |  | 5.0625 | 8.8 | 11.7 | 10.125 | 0
| 1.6944 | 279.152 | 40.178 | 47.611 | 42.659 | 64.54 |  | 5.0833 | 31.4442 | 27.5153 | 10.7588 | 12.3711 | 28.9549 | 28.6048 |  | 5.0833 | 8.6 | 11.7 | 10.1667 | 0
| 1.7014 | 279.532 | 40.201 | 47.639 | 42.675 | 64.599 |  | 5.1042 | 31.483 | 27.4885 | 11.8635 | 12.4135 | 28.9597 | 28.6886 |  | 5.1042 | 8.3 | 11.7 | 10.2083 | 0
| 1.7083 | 279.318 | 40.228 | 47.66 | 42.697 | 64.656 |  | 5.125 | 31.6801 | 27.7093 |  | 12.6044 | 29.1858 | 28.8264 |  | 5.125 | 7.8 | 11.7 | 10.25 | 0
| 1.7153 | 279.307 | 40.248 | 47.683 | 42.715 | 64.707 |  | 5.1458 | 31.4332 | 27.4569 |  | 12.358 | 28.8987 | 28.5667 |  | 5.1458 | 7.9 | 11.7 | 10.2917 | 0
| 1.7222 | 277.349 | 40.269 | 47.704 | 42.721 | 64.748 |  | 5.1667 | 31.2249 | 27.2858 |  | 12.2759 | 28.7676 | 28.4944 |  | 5.1667 | 8.2 | 11.7 | 10.3333 | 0
| 1.7292 | 280.048 | 40.28 | 47.719 | 42.736 | 64.78 |  | 5.1875 | 31.0869 | 27.1056 |  | 12.0098 | 28.5711 | 28.2618 |  | 5.1875 | 8.4 | 11.7 | 10.375 | 0
| 1.7361 | 280.097 | 40.3 | 47.739 | 42.759 | 64.828 |  | 5.2083 | 30.9286 | 26.9706 |  | 11.9411 | 28.4424 | 28.131 |  | 5.2083 | 8.5 | 11.7 | 10.4167 | 0
| 1.7431 | 280.924 | 40.322 | 47.763 | 42.778 | 64.877 |  | 5.2292 | 31.5011 | 27.475 | 10.7169 | 12.4423 | 28.9688 | 28.6276 |  | 5.2292 | 8.4 | 11.7 | 10.4583 | 0
| 1.75 | 281.139 | 40.339 | 47.788 | 42.789 | 64.921 |  | 5.25 | 31.3879 | 27.3984 | 10.6661 | 12.3269 | 28.8309 | 28.526 |  | 5.25 | 8.1 | 11.7 | 10.5 | 0
| 1.7569 | 283.225 | 40.362 | 47.82 | 42.815 | 64.981 |  | 5.2708 | 31.5282 | 27.4839 | 10.7192 | 12.4089 | 28.9211 | 28.6071 |  | 5.2708 | 8.2 | 11.7 | 10.5417 | 0
| 1.7639 | 279.87 | 40.398 | 47.858 | 42.845 | 65.062 |  | 5.2917 | 31.4843 | 27.4516 | 10.5861 | 12.3839 | 28.9881 | 28.6515 |  | 5.2917 | 8.9 | 11.7 | 10.5833 | 0
| 1.7708 | 280.473 | 40.405 | 47.874 | 42.858 | 65.099 |  | 5.3125 | 31.4193 | 27.3937 | 10.5352 | 12.3237 | 28.9252 | 28.5841 |  | 5.3125 | 10.8 | 11.7 | 10.625 | 0
| 1.7778 | 280.934 | 40.414 | 47.885 | 42.864 | 65.112 |  | 5.3333 | [7 empty] | 5.3333 | 12.7 | 11.7 | 10.6667 | 0
| 1.7847 | 280.448 | 40.418 | 47.893 | 42.875 | 65.129 |  | 5.3542 | [7 empty] | 5.3542 | 13.9 | 11.7 | 10.7083 | 0
| 1.7917 | 279.986 | 40.429 | 47.903 | 42.884 | 65.145 |  | 5.375 | [7 empty] | 5.375 | 14.6 | 11.7 | 10.75 | 0
| 1.7986 | 281.58 | 40.432 | 47.914 | 42.89 | 65.161 |  | 5.3958 | 31.4434 | 27.4283 | 10.5699 | 12.3119 | 28.9666 | 28.6415 |  | 5.3958 | 15.9 | 11.7 | 10.7917 | 0
| 1.8056 | 281.113 | 40.441 | 47.928 | 42.899 | 65.183 |  | 5.4167 | 31.5275 | 27.5931 | 10.6823 | 12.4556 | 28.9689 | 28.6778 |  | 5.4167 | 17.2 | 11.7 | 10.8333 | 0
| 1.8125 | 280.461 | 40.448 | 47.939 | 42.911 | 65.202 |  | 5.4375 | 31.6123 | 27.5895 | 10.6142 | 12.4408 | 29.0535 | 28.7555 |  | 5.4375 | 17.9 | 11.7 | 10.875 | 0
| 1.8194 | 281.24 | 40.462 | 47.955 | 42.92 | 65.222 |  | 5.4583 | 31.5413 | 27.5521 | 10.5885 | 12.433 | 28.9713 | 28.7027 |  | 5.4583 | 19.2 | 11.7 | 10.9167 | 0
| 1.8264 | 281.656 | 40.476 | 47.969 | 42.936 | 65.243 |  | 5.4792 | 31.6205 | 27.6329 | 10.6496 | 12.4921 | 29.093 | 28.7747 |  | 5.4792 | 20.2 | 11.7 | 10.9583 | 0
| 1.8333 | 282.001 | 40.483 | 47.977 | 42.947 | 65.266 |  | 5.5 | 31.6584 | 27.6638 | 10.6884 | 12.5511 | 29.115 | 28.8261 |  | 5.5 | 21.2 | 11.7 | 11 | 0
| 1.8403 | 282.697 | 40.498 | 47.995 | 42.965 | 65.291 |  | 5.5208 | 31.6986 | 27.6855 | 10.7006 | 12.5435 | 29.1325 | 28.8435 |  | 5.5208 | 22 | 11.7 | 11.0417 | 0
| 1.8472 | 283.021 | 40.506 | 48.012 | 42.978 | 65.32 |  | 5.5417 | 31.6716 | 27.665 | 10.6821 | 12.5541 | 29.1256 | 28.839 |  | 5.5417 | 22.7 | 11.7 | 11.0833 | 0
| 1.8542 | 283.454 | 40.517 | 48.034 | 42.995 | 65.356 |  | 5.5625 | 31.7784 | 27.7621 | 10.7747 | 12.6403 | 29.2231 | 28.9251 |  | 5.5625 | 22.9 | 11.7 | 11.125 | 0
| 1.8611 | 283.604 | 40.533 | 48.05 | 43.017 | 65.385 |  | 5.5833 | 31.717 | 27.6976 | 10.6692 | 12.577 | 29.1589 | 28.87 |  | 5.5833 | 23.8 | 11.7 | 11.1667 | 0
| 1.8681 | 283.869 | 40.545 | 48.068 | 43.034 | 65.415 |  | 5.6042 | 31.8091 | 27.8003 | 10.7958 | 12.6752 | 29.2462 | 28.9663 |  | 5.6042 | 24.3 | 11.7 | 11.2083 | 0
| 1.875 | 283.979 | 40.563 | 48.084 | 43.046 | 65.446 |  | 5.625 | 31.6002 | 27.561 | 10.5477 | 12.4204 | 29.0318 | 28.7543 |  | 5.625 | 25.1 | 11.7 | 11.25 | 0
| 1.8819 | 281.701 | 40.574 | 48.105 | 43.066 | 65.473 |  | 5.6458 | 31.6534 | 27.6252 | 10.5927 | 12.4899 | 29.0869 | 28.8208 |  | 5.6458 | 24.7 | 11.7 | 11.2917 | 0
| 1.8889 | 285.787 | 40.581 | 48.123 | 43.083 | 65.489 |  | 5.6667 | 31.7218 | 27.6886 | 11.4213 | 12.5629 | 29.1914 | 28.9003 |  | 5.6667 | 25 | 11.7 | 11.3333 | 0
| 1.8958 | 286.511 | 40.603 | 48.146 | 43.109 | 65.541 |  | 5.6875 | 31.7672 | 27.7044 | 10.7452 | 12.6072 | 29.241 | 28.9544 |  | 5.6875 | 25.1 | 11.7 | 11.375 | 0.6
| 1.9028 | 286.715 | 40.627 | 48.176 | 43.13 | 65.592 |  | 5.7083 | 31.6107 | 27.5465 | 10.5481 | 12.4256 | 29.0854 | 28.7921 |  | 5.7083 | 25.2 | 11.7 | 11.4167 | 0.5
| 1.9097 | 286.994 | 40.652 | 48.209 | 43.157 | 65.645 |  | 5.7292 | [7 empty] | 5.7292 | 26.6 | 11.7 | 11.4583 | 0
| 1.9167 | 281.395 | 40.652 | 48.215 | 43.169 | 65.661 |  | 5.75 | [7 empty] | 5.75 | 26.3 | 11.7 | 11.5 | 0
| 1.9236 | 281.827 | 40.644 | 48.208 | 43.166 | 65.636 |  | 5.7708 | [7 empty] | 5.7708 | 25.9 | 11.7 | 11.5417 | 0
| 1.9306 | 278.606 | 40.636 | 48.208 | 43.163 | 65.612 |  | 5.7917 | [7 empty] | 5.7917 | 25.7 | 11.7 | 11.5833 | 0
| 1.9375 | 279.531 | 40.622 | 48.193 | 43.156 | 65.576 |  | 5.8125 | [7 empty] | 5.8125 | 24.4 | 11.7 | 11.625 | 0
| 1.9444 | 280.942 | 40.605 | 48.184 | 43.146 | 65.534 |  | 5.8333 | [7 empty] | 5.8333 | 23.2 | 11.7 | 11.6667 | 0
| 1.9514 | 281.033 | 40.6 | 48.184 | 43.148 | 65.51 |  | 5.8542 | [7 empty] | 5.8542 | 21 | 11.7 | 11.7083 | 0
| 1.9583 | 281.603 | 40.598 | 48.182 | 43.15 | 65.505 |  | 5.875 | [7 empty] | 5.875 | 18.8 | 11.7 | 11.75 | 0
| 1.9653 | 282.26 | 40.6 | 48.187 | 43.155 | 65.505 |  | 5.8958 | 30.772 | 26.6424 | 9.6033 | 11.5443 | 28.2554 | 27.9759 |  | 5.8958 | 17.2 | 11.7 | 11.7917 | 0
| 1.9722 | 282.574 | 40.608 | 48.199 | 43.163 | 65.512 |  | 5.9167 | 30.754 | 26.6267 | 9.6149 | 11.5579 | 28.3116 | 28.0073 |  | 5.9167 | 16 | 11.7 | 11.8333 | 0
| 1.9792 | 279.531 | 40.606 | 48.201 | 43.163 | 65.505 |  | 5.9375 | 30.8985 | 26.7675 | 9.7487 | 11.7005 | 28.4545 | 28.1026 |  | 5.9375 | 14.9 | 11.7 | 11.875 | 0
| 1.9861 | 280.002 | 40.596 | 48.186 | 43.154 | 65.473 |  | 5.9583 | 30.9433 | 26.8351 | 9.7958 | 11.7363 | 28.4881 | 28.1633 |  | 5.9583 | 14.6 | 11.7 | 11.9167 | 0
| 1.9931 | 279.725 | 40.584 | 48.179 | 43.155 | 65.443 |  | 5.9792 | 31.053 | 26.9358 | 9.8991 | 11.8529 | 28.5751 | 28.2479 |  | 5.9792 | 14.1 | 11.7 | 11.9583 | 0
| 2 | 279.769 | 40.585 | 48.18 | 43.154 | 65.428 |  | 6 | 30.9323 | 26.8178 | 9.7702 | 11.7327 | 28.4728 | 28.1501 |  | 6 | 13.6 | 11.7 | 12 | 0
| 2.0069 | 280.36 | 40.583 | 48.183 | 43.153 | 65.423 |  | 6.0208 | 31.0612 | 26.9916 | 9.9251 | 11.8789 | 28.642 | 28.308 |  | 6.0208 | 13.3 | 11.7 | 12.0417 | 0
| 2.0139 | 280.076 | 40.589 | 48.187 | 43.156 | 65.416 |  | 6.0417 | 31.0987 | 27.0043 | 9.9312 | 11.9025 | 28.6547 | 28.3296 |  | 6.0417 | 13.6 | 11.7 | 12.0833 | 0
| 2.0208 | 281.474 | 40.589 | 48.187 | 43.159 | 65.413 |  | 6.0625 | 31.2796 | 27.1647 | 10.1039 | 12.0576 | 28.8262 | 28.4853 |  | 6.0625 | 13.6 | 11.7 | 12.125 | 0
| 2.0278 | 281.101 | 40.59 | 48.191 | 43.174 | 65.413 |  | 6.0833 | 31.257 | 27.1466 | 10.0972 | 12.062 | 28.8172 | 28.4899 |  | 6.0833 | 12.7 | 11.7 | 12.1667 | 0
| 2.0347 | 280.561 | 40.596 | 48.199 | 43.172 | 65.422 |  | 6.1042 | 31.3387 | 27.1876 | 10.1535 | 12.1205 | 28.8582 | 28.5196 |  | 6.1042 | 13.5 | 11.7 | 12.2083 | 0
| 2.0417 | 280.551 | 40.604 | 48.204 | 43.178 | 65.424 |  | 6.125 | 31.3318 | 27.2077 | 10.1335 | 12.1203 | 28.8513 | 28.5149 |  | 6.125 | 13 | 11.7 | 12.25 | 0
| 2.0486 | 281.716 | 40.607 | 48.216 | 43.182 | 65.428 |  | 6.1458 | 31.2697 | 27.0379 | 9.9026 | 11.9335 | 28.6517 | 28.356 |  | 6.1458 | 12.5 | 11.7 | 12.2917 | 0
| 2.0556 | 281.222 | 40.616 | 48.223 | 43.187 | 65.434 |  | 6.1667 | 31.7303 | 27.5207 | 10.4083 | 12.4892 | 28.951 | 28.5286 |  | 6.1667 | 11.3 | 12.2 | 12.3333 | 0
| 2.0625 | 281.642 | 40.623 | 48.234 | 43.193 | 65.446 |  | 6.1875 | 31.2855 | 27.1527 | 10.0762 | 12.1225 | 28.8304 | 28.4915 |  | 6.1875 | 10.1 | 12.2 | 12.375 | 0
| 2.0694 | 279.695 | 40.629 | 48.246 | 43.206 | 65.461 |  | 6.2083 | 31.2437 | 27.0503 | 10.0023 | 11.9952 | 28.7095 | 28.4092 |  | 6.2083 | 8.8 | 12.2 | 12.4167 | 0
| 2.0764 | 280.22 | 40.627 | 48.244 | 43.209 | 65.44 |  | 6.2292 | 31.2702 | 27.1262 | 10.0242 | 12.037 | 28.7678 | 28.4516 |  | 6.2292 | 8.2 | 12.2 | 12.4583 | 0
| 2.0833 | 280.621 | 40.621 | 48.246 | 43.208 | 65.425 |  | 6.25 | 31.259 | 27.1351 | 9.9732 | 12.0614 | 28.7451 | 28.4493 |  | 6.25 | 8.1 | 12.2 | 12.5 | 0
| 2.0903 | 279.785 | 40.619 | 48.247 | 43.209 | 65.417 |  | 6.2708 | 31.1504 | 26.9911 | 9.8514 | 11.9372 | 28.6435 | 28.3591 |  | 6.2708 | 8.5 | 12.2 | 12.5417 | 0.1
| 2.0972 | 279.65 | 40.62 | 48.249 | 43.211 | 65.415 |  | 6.2917 | 31.3188 | 27.1588 | 10.0535 | 12.0976 | 28.8544 | 28.5405 |  | 6.2917 | 9.2 | 12.2 | 12.5833 | 0.2
| 2.1042 | 280.647 | 40.62 | 48.255 | 43.217 | 65.407 |  | 6.3125 | 31.3822 | 27.1499 | 10.0533 | 12.0554 | 28.9312 | 28.6217 |  | 6.3125 | 12.6 | 12.2 | 12.625 | 0.3
| 2.1111 | 279.98 | 40.626 | 48.264 | 43.22 | 65.413 |  | 6.3333 | 31.2371 | 27.0928 | 9.9253 | 12.0097 | 28.7296 | 28.488 |  | 6.3333 | 14.4 | 12.2 | 12.6667 | 0
| 2.1181 | 280.539 | 40.626 | 48.271 | 43.227 | 65.409 |  | 6.3542 | 30.6637 | 26.5463 | 9.3118 | 11.4358 | 28.1814 | 27.9627 |  | 6.3542 | 16.3 | 12.2 | 12.7083 | 4.8
| 2.125 | 280.594 | 40.636 | 48.276 | 43.234 | 65.411 |  | 6.375 | 30.8062 | 26.6473 | 9.4389 | 11.5082 | 28.3282 | 28.0622 |  | 6.375 | 18.1 | 12.2 | 12.75 | 3.5
| 2.1319 | 280.973 | 40.642 | 48.288 | 43.237 | 65.417 |  | 6.3958 | 31.1373 | 27.024 | 9.7568 | 11.8532 | 28.6983 | 28.333 |  | 6.3958 | 19.9 | 12.2 | 12.7917 | 0
| 2.1389 | 280.806 | 40.64 | 48.298 | 43.249 | 65.424 |  | 6.4167 | 31.5909 | 27.1612 | 10.2937 | 12.1493 | 28.5424 | 28.1705 |  | 6.4167 | 21.3 | 12.2 | 12.8333 | 0.3
| 2.1458 | 281.212 | 40.65 | 48.306 | 43.252 | 65.429 |  | 6.4375 | 30.8021 | 26.6659 | 9.3963 | 11.5259 | 28.3112 | 28.0724 |  | 6.4375 | 22 | 12.2 | 12.875 | 0.6
| 2.1528 | 281.246 | 40.651 | 48.312 | 43.261 | 65.437 |  | 6.4583 | 30.7969 | 26.6448 | 9.4195 | 11.5381 | 28.3241 | 28.1055 |  | 6.4583 | 23.2 | 12.2 | 12.9167 | 0
| 2.1597 | 280.64 | 40.663 | 48.326 | 43.273 | 65.444 |  | 6.4792 | 30.9555 | 26.8476 | 9.5825 | 11.7103 | 28.5045 | 28.2656 |  | 6.4792 | 23.3 | 12.2 | 12.9583 | 0
| 2.1667 | 281.138 | 40.668 | 48.333 | 43.277 | 65.453 |  | 6.5 | 30.8742 | 26.7375 | 9.4718 | 11.6108 | 28.415 | 28.1758 |  | 6.5 | 23.9 | 12.2 | 13 | 0
| 2.1736 | 281.067 | 40.679 | 48.351 | 43.294 | 65.466 |  | 6.5208 | 31.2329 | 27.1393 | 9.8766 | 12.0272 | 28.7762 | 28.4944 |  | 6.5208 | 24.8 | 12.2 | 13.0417 | 0
| 2.1806 | 281.552 | 40.682 | 48.361 | 43.3 | 65.474 |  | 6.5417 | 31.3739 | 27.2367 | 9.9848 | 12.0892 | 28.8288 | 28.583 |  | 6.5417 | 25.8 | 12.2 | 13.0833 | 0
| 2.1875 | 281.303 | 40.687 | 48.373 | 43.312 | 65.481 |  | 6.5625 | 31.3254 | 27.1568 | 9.9063 | 12.044 | 28.8373 | 28.605 |  | 6.5625 | 26.1 | 12.2 | 13.125 | 0
| 2.1944 | 280.858 | 40.693 | 48.378 | 43.322 | 65.483 |  | 6.5833 | 31.5006 | 27.3672 | 10.0942 | 12.2147 | 29.0186 | 28.7637 |  | 6.5833 | 26.7 | 12.2 | 13.1667 | 0
| 2.2014 | 280.922 | 40.698 | 48.392 | 43.326 | 65.491 |  | 6.6042 | 31.6146 | 27.4601 | 10.178 | 12.3188 | 29.0193 | 28.7892 |  | 6.6042 | 26.9 | 12.2 | 13.2083 | 0
| 2.2083 | 280.864 | 40.7 | 48.394 | 43.332 | 65.494 |  | 6.625 | 31.5973 | 27.4453 | 10.1633 | 12.2886 | 29.1106 | 28.8192 |  | 6.625 | 27.4 | 12.2 | 13.25 | 0
| 2.2153 | 278.836 | 40.7 | 48.401 | 43.336 | 65.483 |  | 6.6458 | 31.7121 | 27.5481 | 10.2396 | 12.4027 | 29.2047 | 29.0038 |  | 6.6458 | 28.1 | 12.2 | 13.2917 | 0
| 2.2222 | 279.093 | 40.692 | 48.395 | 43.33 | 65.461 |  | 6.6667 | 31.5873 | 27.4375 | 10.1312 | 12.2699 | 29.1324 | 28.8478 |  | 6.6667 | 28.6 | 12.2 | 13.3333 | 0
| 2.2292 | 278.332 | 40.681 | 48.392 | 43.328 | 65.436 |  | 6.6875 | 31.7552 | 27.6114 | 10.3391 | 12.447 | 29.3107 | 29.0151 |  | 6.6875 | 28.6 | 12.2 | 13.375 | 0.1
| 2.2361 | 278.275 | 40.679 | 48.386 | 43.327 | 65.414 |  | 6.7083 | 31.6554 | 27.4737 | 10.1643 | 12.3031 | 29.1821 | 28.8772 |  | 6.7083 | 28.2 | 12.2 | 13.4167 | 0
| 2.2431 | 279.186 | 40.671 | 48.382 | 43.316 | 65.385 |  | 6.7292 | 31.5376 | 27.3655 | 10.0411 | 12.2039 | 29.0986 | 28.7983 |  | 6.7292 | 28.1 | 12.2 | 13.4583 | 0
| 2.25 | 279.707 | 40.67 | 48.385 | 43.32 | 65.372 |  | 6.75 | 31.6749 | 27.4818 | 10.195 | 12.3203 | 29.2688 | 28.9236 |  | 6.75 | 27.2 | 12.2 | 13.5 | 0
| 2.2569 | 277.259 | 40.675 | 48.388 | 43.327 | 65.373 |  | 6.7708 | 31.7096 | 27.5005 | 10.194 | 12.3301 | 29.256 | 28.9107 |  | 6.7708 | 26.8 | 12.2 | 13.5417 | 0
| 2.2639 | 280.553 | 40.672 | 48.39 | 43.326 | 65.355 |  | 6.7917 | 31.6751 | 27.4752 | 10.1404 | 12.3052 | 29.1671 | 28.8084 |  | 6.7917 | 26.4 | 12.2 | 13.5833 | 0
| 2.2708 | 280.272 | 40.679 | 48.398 | 43.336 | 65.37 |  | 6.8125 | 31.5972 | 27.3775 | 10.0584 | 12.1895 | 29.1683 | 28.7328 |  | 6.8125 | 25.9 | 12.2 | 13.625 | 0
| 2.2778 | 279.766 | 40.69 | 48.409 | 43.346 | 65.385 |  | 6.8333 | 31.4355 | 27.2166 | 9.8528 | 12.043 | 29.0905 | 28.6843 |  | 6.8333 | 25 | 12.2 | 13.6667 | 0
| 2.2847 | 279.186 | 40.698 | 48.415 | 43.352 | 65.383 |  | 6.8542 | 30.9418 | 26.6581 | 9.3062 | 11.4666 | 28.5765 | 28.1369 |  | 6.8542 | 22.8 | 12.2 | 13.7083 | 0
| 2.2917 | 278.77 | 40.697 | 48.417 | 43.351 | 65.374 |  | 6.875 | [7 empty] | 6.875 | 20 | 12.2 | 13.75 | 0
| 2.2986 | 277.874 | 40.69 | 48.414 | 43.351 | 65.353 |  | 6.8958 | 31.2904 | 27.1059 | 9.6754 | 11.9398 | 28.8386 | 28.5069 |  | 6.8958 | 18.8 | 12.2 | 13.7917 | 0
| 2.3056 | 280.351 | 40.683 | 48.41 | 43.35 | 65.335 |  | 6.9167 | 31.0127 | 26.7862 | 9.4663 | 11.6748 | 28.6201 | 28.2795 |  | 6.9167 | 17.6 | 12.2 | 13.8333 | 0
| 2.3125 | 281.533 | 40.699 | 48.434 | 43.365 | 65.368 |  | 6.9375 | 31.3381 | 27.1769 | 9.8297 | 12.0319 | 29.0266 | 28.6382 |  | 6.9375 | 16.8 | 12.2 | 13.875 | 0
| 2.3194 | 282.615 | 40.721 | 48.455 | 43.382 | 65.403 |  | 6.9583 | 31.397 | 27.1637 | 10.0252 | 11.997 | 29.1081 | 28.7309 |  | 6.9583 | 16.4 | 12.2 | 13.9167 | 0
| 2.3264 | 281.129 | 40.735 | 48.478 | 43.4 | 65.434 |  | 6.9792 | 31.4599 | 27.3171 | 9.9739 | 12.1229 | 28.9924 | 28.6853 |  | 6.9792 | 16 | 12.2 | 13.9583 | 0
| 2.3333 | 281.375 | 40.748 | 48.487 | 43.413 | 65.462 |  | 7 | 31.3503 | 27.192 | 9.8294 | 12.1333 | 28.9824 | 28.7746 |  | 7 | 15.7 | 12.2 | 14 | 0
| 2.3403 | 281.216 | 40.758 | 48.503 | 43.423 | 65.477 |  | 7.0208 | 31.4499 | 27.3387 | 9.7342 | 12.0823 | 29.0728 | 28.646 |  | 7.0208 | 15.7 | 12.2 | 14.0417 | 0
| 2.3472 | 280.099 | 40.761 | 48.514 | 43.427 | 65.483 |  | 7.0417 | 31.3231 | 27.1671 | 9.6215 | 12.0158 | 28.8943 | 28.567 |  | 7.0417 | 16 | 12.2 | 14.0833 | 0
| 2.3542 | 280.258 | 40.76 | 48.525 | 43.431 | 65.485 |  | 7.0625 | 31.2287 | 27.1746 | 9.5983 | 12.0102 | 29.0148 | 28.6512 |  | 7.0625 | 15.7 | 12.2 | 14.125 | 0
| 2.3611 | 278.397 | 40.762 | 48.526 | 43.429 | 65.471 |  | 7.0833 | 31.3056 | 27.1113 | 9.6049 | 11.9215 | 28.8883 | 28.5948 |  | 7.0833 | 15.3 | 12.2 | 14.1667 | 0
| 2.3681 | 278.846 | 40.758 | 48.52 | 43.434 | 65.457 |  | 7.1042 | 31.2258 | 27.0837 | 9.5801 | 11.9122 | 28.8583 | 28.5806 |  | 7.1042 | 15.3 | 12.2 | 14.2083 | 0
| 2.375 | 278.22 | 40.755 | 48.518 | 43.429 | 65.44 |  | 7.125 | 31.2031 | 27.0544 | 9.5182 | 11.8746 | 28.82 | 28.5377 |  | 7.125 | 15 | 12.8 | 14.25 | 0
| 2.3819 | 279.356 | 40.749 | 48.517 | 43.433 | 65.42 |  | 7.1458 | 31.186 | 27.0035 | 9.4553 | 11.8137 | 28.8005 | 28.5093 |  | 7.1458 | 14.6 | 12.8 | 14.2917 | 0
| 2.3889 | 280.127 | 40.753 | 48.524 | 43.433 | 65.422 |  | 7.1667 | 31.1742 | 27.0122 | 9.4816 | 11.8223 | 28.7956 | 28.509 |  | 7.1667 | 14.1 | 12.8 | 14.3333 | 0
| 2.3958 | 278.069 | 40.757 | 48.529 | 43.44 | 65.424 |  | 7.1875 | 31.1991 | 27.0371 | 9.4794 | 11.8556 | 28.8453 | 28.554 |  | 7.1875 | 13.9 | 12.8 | 14.375 | 0
| 2.4028 | 277.622 | 40.753 | 48.523 | 43.435 | 65.405 |  | 7.2083 | 31.4077 | 27.2024 | 9.6044 | 11.9607 | 28.9635 | 28.5209 |  | 7.2083 | 13.7 | 12.8 | 14.4167 | 0
| 2.4097 | 278.326 | 40.75 | 48.524 | 43.433 | 65.385 |  | 7.2292 | 31.2461 | 27.1248 | 9.5876 | 11.966 | 28.9082 | 28.5965 |  | 7.2292 | 13.6 | 12.8 | 14.4583 | 0
| 2.4167 | 278.468 | 40.752 | 48.526 | 43.435 | 65.382 |  | 7.25 | 31.3209 | 27.0933 | 9.6473 | 11.9106 | 28.9241 | 28.6914 |  | 7.25 | 13.2 | 12.8 | 14.5 | 0
| 2.4236 | 277.005 | 40.746 | 48.525 | 43.434 | 65.362 |  | 7.2708 | 31.2874 | 27.1142 | 9.6573 | 11.9626 | 28.8681 | 28.5994 |  | 7.2708 | 12.7 | 12.8 | 14.5417 | 0
| 2.4306 | 276.84 | 40.742 | 48.517 | 43.433 | 65.35 |  | 7.2917 | 31.2687 | 27.0461 | 9.6192 | 11.8492 | 28.8202 | 28.5786 |  | 7.2917 | 13 | 12.8 | 14.5833 | 0
| 2.4375 | 277.38 | 40.736 | 48.514 | 43.427 | 65.322 |  | 7.3125 | 31.2666 | 27.0797 | 9.7823 | 11.935 | 28.9264 | 28.6554 |  | 7.3125 | 14.5 | 12.8 | 14.625 | 0.1
| 2.4444 | 277.725 | 40.732 | 48.511 | 43.427 | 65.306 |  | 7.3333 | 31.1153 | 26.9622 | 9.9417 | 11.665 | 28.6487 | 28.3576 |  | 7.3333 | 15.7 | 12.8 | 14.6667 | 0
| 2.4514 | 277.659 | 40.732 | 48.509 | 43.431 | 65.299 |  | 7.3542 | 31.2948 | 27.143 | 10.1273 | 11.9529 | 28.778 | 28.5771 |  | 7.3542 | 16.9 | 12.8 | 14.7083 | 0
| 2.4583 | 278.194 | 40.732 | 48.512 | 43.433 | 65.29 |  | 7.375 | 31.3195 | 27.1894 | 9.933 | 11.9671 | 28.9061 | 28.7233 |  | 7.375 | 18 | 12.8 | 14.75 | 0
| 2.4653 | 279.368 | 40.739 | 48.519 | 43.439 | 65.291 |  | 7.3958 | 31.2803 | 27.1567 | 9.8365 | 11.9504 | 28.9188 | 28.7246 |  | 7.3958 | 19.8 | 12.8 | 14.7917 | 0
| 2.4722 | 278.773 | 40.746 | 48.522 | 43.446 | 65.297 |  | 7.4167 | 31.3275 | 27.1876 | 10.3003 | 11.9275 | 28.9025 | 28.6768 |  | 7.4167 | 21.1 | 12.8 | 14.8333 | 0
| 2.4792 | 278.027 | 40.743 | 48.526 | 43.452 | 65.303 |  | 7.4375 | 30.9875 | 26.8255 | 9.1092 | 11.6053 | 28.5607 | 28.3645 |  | 7.4375 | 21.9 | 12.8 | 14.875 | 0
| 2.4861 | 281.128 | 40.754 | 48.539 | 43.462 | 65.321 |  | 7.4583 | 30.6532 | 26.5336 | 9.2075 | 11.3367 | 28.3051 | 28.1249 |  | 7.4583 | 22.6 | 12.8 | 14.9167 | 0
| 2.4931 | 282.119 | 40.78 | 48.566 | 43.48 | 65.367 |  | 7.4792 | 30.7888 | 26.6144 | 9.2795 | 11.4089 | 28.3748 | 28.2012 |  | 7.4792 | 23.7 | 12.8 | 14.9583 | 0
| 2.5 | 281.98 | 40.8 | 48.588 | 43.497 | 65.408 |  | 7.5 | 30.8157 | 26.6297 | 9.4555 | 11.4437 | 28.4241 | 28.2348 |  | 7.5 | 24.5 | 12.8 | 15 | 0
| 2.5069 | 284.045 | 40.825 | 48.616 | 43.519 | 65.454 |  | 7.5208 | 30.8796 | 26.6956 | 9.4051 | 11.4908 | 28.4474 | 28.2874 |  | 7.5208 | 24.8 | 12.8 | 15.0417 | 0
| 2.5139 | 284.208 | 40.853 | 48.653 | 43.543 | 65.525 |  | 7.5417 | 30.6621 | 26.4703 | 9.2478 | 11.253 | 28.2421 | 28.1109 |  | 7.5417 | 25.6 | 12.8 | 15.0833 | 0
| 2.5208 | 283.235 | 40.88 | 48.681 | 43.573 | 65.586 |  | 7.5625 | 30.8796 | 26.6956 | 8.978 | 11.4764 | 28.4185 | 28.312 |  | 7.5625 | 26.3 | 12.8 | 15.125 | 0
| 2.5278 | 283.262 | 40.905 | 48.701 | 43.586 | 65.633 |  | 7.5833 | 31.1114 | 26.917 | 9.3179 | 11.7337 | 28.7192 | 28.5546 |  | 7.5833 | 26.4 | 12.8 | 15.1667 | 0
| 2.5347 | 283.429 | 40.924 | 48.729 | 43.614 | 65.672 |  | 7.6042 | 31.3325 | 27.148 | 9.5192 | 11.918 | 28.937 | 28.725 |  | 7.6042 | 27.3 | 12.8 | 15.2083 | 0
| 2.5417 | 283.598 | 40.939 | 48.755 | 43.622 | 65.707 |  | 7.625 | 31.8736 | 27.6546 | 9.8118 | 12.4236 | 29.3853 | 29.1934 |  | 7.625 | 27.5 | 12.8 | 15.25 | 0
| 2.5486 | 279.877 | 40.951 | 48.768 | 43.64 | 65.734 |  | 7.6458 | 31.7019 | 27.5268 | 9.702 | 12.2759 | 29.2801 | 29.0815 |  | 7.6458 | 27.8 | 12.8 | 15.2917 | 1.1
| 2.5556 | 279.64 | 40.943 | 48.764 | 43.636 | 65.725 |  | 7.6667 | 31.4886 | 27.3057 | 9.4413 | 12.0593 | 29.0747 | 28.8875 |  | 7.6667 | 27.6 | 12.8 | 15.3333 | 0.4
| 2.5625 | 277.951 | 40.938 | 48.764 | 43.633 | 65.7 |  | 7.6875 | 31.4455 | 27.2583 | 9.3839 | 12.026 | 29.0477 | 28.8559 |  | 7.6875 | 27.8 | 12.8 | 15.375 | 0
| 2.5694 | 277.568 | 40.921 | 48.748 | 43.632 | 65.663 |  | 7.7083 | 31.5249 | 27.3485 | 9.4479 | 12.0966 | 29.1086 | 28.9348 |  | 7.7083 | 27.5 | 12.8 | 15.4167 | 0
| 2.5764 | 281.028 | 40.907 | 48.735 | 43.615 | 65.618 |  | 7.7292 | 31.6543 | 27.4816 | 9.6026 | 12.2317 | 29.3364 | 29.077 |  | 7.7292 | 27.6 | 12.8 | 15.4583 | 0
| 2.5833 | 280.767 | 40.912 | 48.736 | 43.62 | 65.619 |  | 7.75 | 31.6786 | 27.4878 | 9.5602 | 12.2224 | 29.2682 | 29.0719 |  | 7.75 | 27.2 | 12.8 | 15.5 | 0
| 2.5903 | 281.603 | 40.928 | 48.751 | 43.636 | 65.639 |  | 7.7708 | 31.2597 | 27.0577 | 9.1217 | 11.818 | 28.8647 | 28.6865 |  | 7.7708 | 26.6 | 12.8 | 15.5417 | 0
| 2.5972 | 282.658 | 40.939 | 48.764 | 43.65 | 65.669 |  | 7.7917 | 31.2195 | 27.0199 | 9.0607 | 11.7837 | 28.8267 | 28.6508 |  | 7.7917 | 25.8 | 12.8 | 15.5833 | 0
| 2.6042 | 278.329 | 40.943 | 48.769 | 43.649 | 65.677 |  | 7.8125 | [7 empty] | 7.8125 | 25 | 12.8 | 15.625 | 0
| 2.6111 | 277.641 | 40.938 | 48.756 | 43.642 | 65.642 |  | 7.8333 | [7 empty] | 7.8333 | 23.9 | 12.8 | 15.6667 | 0
| 2.6181 | 277.672 | 40.919 | 48.746 | 43.632 | 65.6 |  | 7.8542 | [7 empty] | 7.8542 | 22.2 | 12.8 | 15.7083 | 0
| 2.625 | 276.514 | 40.911 | 48.738 | 43.626 | 65.578 |  | 7.875 | [7 empty] | 7.875 | 20.3 | 12.8 | 15.75 | 0
| 2.6319 | 277.357 | 40.895 | 48.718 | 43.614 | 65.524 |  | 7.8958 | 30.9705 | 26.7483 | 8.731 | 11.5426 | 28.6049 | 28.4312 |  | 7.8958 | 19 | 12.8 | 15.7917 | 0
| 2.6389 | 276.917 | 40.891 | 48.708 | 43.607 | 65.504 |  | 7.9167 | 30.973 | 26.8098 | 8.7319 | 11.5831 | 28.6166 | 28.4587 |  | 7.9167 | 18.3 | 12.8 | 15.8333 | 0
| 2.6458 | 276.932 | 40.881 | 48.7 | 43.602 | 65.474 |  | 7.9375 | 30.9918 | 26.8334 | 8.7133 | 11.5886 | 28.5859 | 28.4731 |  | 7.9375 | 18.1 | 12.8 | 15.875 | 0
| 2.6528 | 277.357 | 40.878 | 48.686 | 43.597 | 65.456 |  | 7.9583 | 31.0618 | 26.8945 | 8.7912 | 11.6666 | 28.6852 | 28.5409 |  | 7.9583 | 17.7 | 12.8 | 15.9167 | 0
| 2.6597 | 278.036 | 40.874 | 48.683 | 43.597 | 65.44 |  | 7.9792 | 31.091 | 26.9307 | 8.8021 | 11.6909 | 28.7348 | 28.5791 |  | 7.9792 | 17.3 | 12.8 | 15.9583 | 0
| 2.6667 | 276.883 | 40.875 | 48.679 | 43.595 | 65.431 |  | 8 | 31.2154 | 27.0752 | 8.9236 | 11.8149 | 28.859 | 28.6987 |  | 8 | 17 | 12.8 | 16 | 0
| 2.6736 | 276.452 | 40.867 | 48.667 | 43.587 | 65.403 |  | 8.0208 | 31.1616 | 27.0037 | 8.8384 | 11.7427 | 28.7942 | 28.6361 |  | 8.0208 | 16.7 | 12.8 | 16.0417 | 0
| 2.6806 | 276.614 | 40.86 | 48.657 | 43.582 | 65.381 |  | 8.0417 | 31.2204 | 27.042 | 8.8804 | 11.8092 | 28.8439 | 28.6791 |  | 8.0417 | 16.3 | 12.8 | 16.0833 | 0
| 2.6875 | 277.315 | 40.851 | 48.654 | 43.58 | 65.362 |  | 8.0625 | 31.187 | 27.0382 | 8.8306 | 11.768 | 28.8377 | 28.6615 |  | 8.0625 | 15.8 | 12.8 | 16.125 | 0
| 2.6944 | 277.57 | 40.857 | 48.646 | 43.576 | 65.359 |  | 8.0833 | 31.1885 | 27.0174 | 8.7993 | 11.7542 | 28.8235 | 28.6632 |  | 8.0833 | 15.4 | 12.8 | 16.1667 | 0
| 2.7014 | 277.24 | 40.855 | 48.646 | 43.574 | 65.351 |  | 8.1042 | 31.2298 | 27.088 | 8.851 | 11.8127 | 28.8805 | 28.7292 |  | 8.1042 | 14.8 | 13.3 | 16.2083 | 0
| 2.7083 | 277.223 | 40.855 | 48.648 | 43.576 | 65.347 |  | 8.125 | 31.2791 | 27.1195 | 8.8773 | 11.8634 | 28.9502 | 28.756 |  | 8.125 | 14.3 | 13.3 | 16.25 | 0
| 2.7153 | 276.936 | 40.853 | 48.638 | 43.574 | 65.343 |  | 8.1458 | 31.2487 | 27.0712 | 8.8038 | 11.8029 | 28.9018 | 28.7212 |  | 8.1458 | 13.8 | 13.3 | 16.2917 | 0
| 2.7222 | 276.459 | 40.853 | 48.637 | 43.574 | 65.333 |  | 8.1667 | 31.2643 | 27.1272 | 8.8058 | 11.8514 | 28.9197 | 28.7594 |  | 8.1667 | 13.3 | 13.3 | 16.3333 | 0
| 2.7292 | 276.557 | 40.847 | 48.631 | 43.567 | 65.312 |  | 8.1875 | 31.296 | 27.152 | 8.8145 | 11.8714 | 28.9536 | 28.7887 |  | 8.1875 | 13.1 | 13.3 | 16.375 | 0
| 2.7361 | 276.241 | 40.84 | 48.625 | 43.564 | 65.299 |  | 8.2083 | 31.2762 | 27.13 | 8.7538 | 11.8368 | 28.8887 | 28.7329 |  | 8.2083 | 13 | 13.3 | 16.4167 | 0
| 2.7431 | 276.958 | 40.845 | 48.618 | 43.562 | 65.295 |  | 8.2292 | 31.2825 | 27.1431 | 8.7822 | 11.8676 | 28.9652 | 28.8093 |  | 8.2292 | 11.9 | 13.3 | 16.4583 | 0
| 2.75 | 277.4 | 40.847 | 48.622 | 43.558 | 65.295 |  | 8.25 | 31.2599 | 27.1408 | 8.727 | 11.8565 | 28.938 | 28.807 |  | 8.25 | 11.3 | 13.3 | 16.5 | 0
| 2.7569 | 277.772 | 40.851 | 48.623 | 43.561 | 65.301 |  | 8.2708 | 31.246 | 27.1046 | 8.6457 | 11.8081 | 28.8588 | 28.7458 |  | 8.2708 | 11.1 | 13.3 | 16.5417 | 0
| 2.7639 | 277.361 | 40.851 | 48.624 | 43.563 | 65.301 |  | 8.2917 | 31.1696 | 27.0465 | 8.5859 | 11.7724 | 28.832 | 28.7304 |  | 8.2917 | 11.9 | 13.3 | 16.5833 | 0
| 2.7708 | 277.638 | 40.853 | 48.623 | 43.563 | 65.301 |  | 8.3125 | 31.1898 | 27.0555 | 8.5835 | 11.7768 | 28.8477 | 28.7325 |  | 8.3125 | 13.4 | 13.3 | 16.625 | 0
| 2.7778 | 277.01 | 40.853 | 48.621 | 43.563 | 65.301 |  | 8.3333 | 31.3026 | 27.1721 | 8.6509 | 11.8555 | 28.9237 | 28.8198 |  | 8.3333 | 14.7 | 13.3 | 16.6667 | 0
| 2.7847 | 277.921 | 40.862 | 48.627 | 43.57 | 65.304 |  | 8.3542 | 31.398 | 27.2645 | 8.7322 | 11.9572 | 29.0436 | 28.9285 |  | 8.3542 | 16.3 | 13.3 | 16.7083 | 0
| 2.7917 | 278.389 | 40.864 | 48.626 | 43.568 | 65.306 |  | 8.375 | 31.4386 | 27.3199 | 8.7641 | 12.0026 | 29.0839 | 28.9733 |  | 8.375 | 17.7 | 13.3 | 16.75 | 0
| 2.7986 | 278.75 | 40.865 | 48.625 | 43.57 | 65.313 |  | 8.3958 | 31.4098 | 27.2817 | 8.6975 | 11.9603 | 29.0368 | 28.942 |  | 8.3958 | 19.3 | 13.3 | 16.7917 | 0
| 2.8056 | 278.012 | 40.868 | 48.632 | 43.574 | 65.317 |  | 8.4167 | 31.4913 | 27.3604 | 8.7544 | 12.0485 | 29.125 | 29.0211 |  | 8.4167 | 20.6 | 13.3 | 16.8333 | 0
| 2.8125 | 278.097 | 40.868 | 48.634 | 43.579 | 65.32 |  | 8.4375 | 30.5873 | 26.4704 | 7.8095 | 11.1842 | 28.2664 | 28.2618 |  | 8.4375 | 21.3 | 13.3 | 16.875 | 0
| 2.8194 | 278.284 | 40.876 | 48.635 | 43.582 | 65.323 |  | 8.4583 | 31.2494 | 27.1139 | 8.5176 | 11.8021 | 28.8605 | 28.8064 |  | 8.4583 | 22.4 | 13.3 | 16.9167 | 0
| 2.8264 | 279.691 | 40.88 | 48.64 | 43.591 | 65.34 |  | 8.4792 | 31.363 | 27.2426 | 8.557 | 11.9126 | 28.9625 | 28.9128 |  | 8.4792 | 23.4 | 13.3 | 16.9583 | 0
| 2.8333 | 279.67 | 40.893 | 48.65 | 43.597 | 65.365 |  | 8.5 | 31.6007 | 27.4637 | 8.7661 | 12.1204 | 29.2177 | 29.1296 |  | 8.5 | 24.2 | 13.3 | 17 | 0
| 2.8403 | 280.009 | 40.905 | 48.665 | 43.608 | 65.387 |  | 8.5208 | 31.734 | 27.6032 | 8.8779 | 12.266 | 29.3439 | 29.2671 |  | 8.5208 | 24.9 | 13.3 | 17.0417 | 0
| 2.8472 | 279.902 | 40.91 | 48.675 | 43.618 | 65.41 |  | 8.5417 | 31.8425 | 27.7156 | 8.9764 | 12.3826 | 29.4927 | 29.3752 |  | 8.5417 | 25.5 | 13.3 | 17.0833 | 0
| 2.8542 | 279.851 | 40.917 | 48.682 | 43.625 | 65.423 |  | 8.5625 | 31.8799 | 27.7638 | 8.9854 | 12.4316 | 29.5027 | 29.4259 |  | 8.5625 | 25.8 | 13.3 | 17.125 | 0
| 2.8611 | 280.152 | 40.925 | 48.688 | 43.628 | 65.43 |  | 8.5833 | 31.8487 | 27.7315 | 8.914 | 12.3844 | 29.4549 | 29.3917 |  | 8.5833 | 26.2 | 13.3 | 17.1667 | 0
| 2.8681 | 279.047 | 40.929 | 48.697 | 43.638 | 65.442 |  | 8.6042 | 31.9148 | 27.7904 | 8.9622 | 12.4374 | 29.523 | 29.4553 |  | 8.6042 | 26.9 | 13.3 | 17.2083 | 0
| 2.875 | 279.282 | 40.934 | 48.702 | 43.642 | 65.453 |  | 8.625 | 31.9152 | 27.7841 | 8.9384 | 12.4268 | 29.5146 | 29.4492 |  | 8.625 | 26.8 | 13.3 | 17.25 | 0
| 2.8819 | 276.322 | 40.935 | 48.703 | 43.642 | 65.457 |  | 8.6458 | 31.9012 | 27.7882 | 8.8804 | 12.4417 | 29.5031 | 29.4624 |  | 8.6458 | 28.1 | 13.3 | 17.2917 | 0
| 2.8889 | 280.367 | 40.929 | 48.705 | 43.648 | 65.453 |  | 8.6667 | 31.8732 | 27.7582 | 8.8247 | 12.399 | 29.4617 | 29.4368 |  | 8.6667 | 28 | 13.3 | 17.3333 | 0
| 2.8958 | 280.886 | 40.941 | 48.718 | 43.66 | 65.476 |  | 8.6875 | 31.8776 | 27.7535 | 8.8226 | 12.4056 | 29.4882 | 29.4408 |  | 8.6875 | 27.9 | 13.3 | 17.375 | 0
| 2.9028 | 281.478 | 40.952 | 48.734 | 43.668 | 65.499 |  | 8.7083 | 31.8844 | 27.767 | 8.8027 | 12.4168 | 29.4995 | 29.4611 |  | 8.7083 | 26.3 | 13.3 | 17.4167 | 0
| 2.9097 | 281.308 | 40.966 | 48.749 | 43.688 | 65.533 |  | 8.7292 | 31.8835 | 27.7706 | 8.7598 | 12.4178 | 29.4762 | 29.4558 |  | 8.7292 | 26.8 | 13.3 | 17.4583 | 0
| 2.9167 | 282.232 | 40.977 | 48.765 | 43.699 | 65.566 |  | 8.75 | 31.9062 | 27.782 | 8.7487 | 12.4334 | 29.501 | 29.4784 |  | 8.75 | 27.2 | 13.3 | 17.5 | 0
| 2.9236 | 282.931 | 40.998 | 48.782 | 43.716 | 65.608 |  | 8.7708 | 31.8656 | 27.7402 | 8.6755 | 12.3841 | 29.4772 | 29.4455 |  | 8.7708 | 26.7 | 13.3 | 17.5417 | 0
| 2.9306 | 279.807 | 41.018 | 48.808 | 43.738 | 65.655 |  | 8.7917 | 31.869 | 27.7487 | 8.6642 | 12.3993 | 29.4738 | 29.4558 |  | 8.7917 | 25.3 | 13.3 | 17.5833 | 0
| 2.9375 | 278.745 | 41.019 | 48.805 | 43.735 | 65.649 |  | 8.8125 | 31.9204 | 27.7915 | 8.668 | 12.4298 | 29.5005 | 29.4914 |  | 8.8125 | 24.4 | 13.3 | 17.625 | 0
| 2.9444 | 279.064 | 41.01 | 48.802 | 43.733 | 65.634 |  | 8.8333 | 31.9415 | 27.8426 | 8.7185 | 12.518 | 29.2215 | 29.5626 |  | 8.8333 | 23.4 | 13.3 | 17.6667 | 0
| 2.9514 | 279.979 | 41.003 | 48.8 | 43.73 | 65.626 |  | 8.8542 | 31.9403 | 27.7967 | 8.6448 | 12.4529 | 29.4779 | 29.4689 |  | 8.8542 | 22.1 | 13.3 | 17.7083 | 0
| 2.9583 | 280.18 | 41.01 | 48.806 | 43.737 | 65.628 |  | 8.875 | 31.7415 | 27.6371 | 8.4214 | 12.2904 | 29.3498 | 29.3678 |  | 8.875 | 20.7 | 13.3 | 17.75 | 0
| 2.9653 | 281.328 | 41.019 | 48.809 | 43.743 | 65.64 |  | 8.8958 | 31.7546 | 27.6486 | 8.3996 | 12.2994 | 29.3246 | 29.3472 |  | 8.8958 | 19.5 | 13.3 | 17.7917 | 0
| 2.9722 | 281.125 | 41.03 | 48.825 | 43.757 | 65.665 |  | 8.9167 | 31.3946 | 27.2824 | 7.9983 | 11.9469 | 29.0127 | 29.0398 |  | 8.9167 | 18.9 | 13.3 | 17.8333 | 0
| 2.9792 | 281.647 | 41.04 | 48.841 | 43.766 | 65.69 |  | 8.9375 | 31.5149 | 27.3825 | 8.0895 | 12.0519 | 29.09 | 29.124 |  | 8.9375 | 18.3 | 13.3 | 17.875 | 0.2
| 2.9861 | 282.476 | 41.058 | 48.853 | 43.785 | 65.716 |  | 8.9583 | 31.496 | 27.3953 | 8.0558 | 12.0579 | 29.1141 | 29.1456 |  | 8.9583 | 17.8 | 13.3 | 17.9167 | 0
| 2.9931 | 281.946 | 41.073 | 48.872 | 43.791 | 65.75 |  | 8.9792 | 31.5864 | 27.5061 | 8.1352 | 12.1533 | 29.2112 | 29.2541 |  | 8.9792 | 17.7 | 13.3 | 17.9583 | 0
| 3 | 282.92 | 41.084 | 48.883 | 43.807 | 65.778 |  | 9 | 31.6657 | 27.5759 | 8.1704 | 12.2197 | 29.2677 | 29.2948 |  | 9 | 17.8 | 13.3 | 18 | 0.1
| 3.0069 | 284.633 | 41.101 | 48.9 | 43.82 | 65.806 |  | 9.0208 | 31.8106 | 27.7268 | 8.2939 | 12.3483 | 29.4011 | 29.4372 |  | 9.0208 | 17.9 | 13.3 | 18.0417 | 0
| 3.0139 | 280.709 | 41.111 | 48.913 | 43.832 | 65.822 |  | 9.0417 | 31.3217 | 27.2373 | 7.8112 | 11.894 | 28.9244 | 28.9876 |  | 9.0417 | 17.8 | 13.3 | 18.0833 | 0
| 3.0208 | 280.875 | 41.108 | 48.91 | 43.831 | 65.817 |  | 9.0625 | 31.376 | 27.2824 | 7.7738 | 11.9251 | 28.983 | 29.035 |  | 9.0625 | 17.8 | 13.3 | 18.125 | 0.3
| 3.0278 | 280.805 | 41.105 | 48.913 | 43.834 | 65.815 |  | 9.0833 | 31.4304 | 27.3412 | 7.7958 | 11.9694 | 29.0373 | 29.0892 |  | 9.0833 | 17.8 | 13.3 | 18.1667 | 0.4
| 3.0347 | 280.08 | 41.107 | 48.916 | 43.833 | 65.811 |  | 9.1042 | 31.5774 | 27.5128 | 7.95 | 12.1289 | 29.1954 | 29.2338 |  | 9.1042 | 17.8 | 13.3 | 18.2083 | 0.2
| 3.0417 | 281.324 | 41.115 | 48.922 | 43.842 | 65.811 |  | 9.125 | 31.6657 | 27.6051 | 8.0007 | 12.2219 | 29.27 | 29.3219 |  | 9.125 | 17.7 | 13.9 | 18.25 | 0
| 3.0486 | 280.929 | 41.119 | 48.924 | 43.853 | 65.82 |  | 9.1458 | 31.976 | 27.8033 | 8.1352 | 12.4215 | 29.4305 | 29.5819 |  | 9.1458 | 17.3 | 13.9 | 18.2917 | 0
| 3.0556 | 281.163 | 41.123 | 48.934 | 43.853 | 65.833 |  | 9.1667 | 31.339 | 27.2254 | 7.5714 | 11.8897 | 28.9395 | 29.0028 |  | 9.1667 | 16.9 | 13.9 | 18.3333 | 0
| 3.0625 | 281.632 | 41.134 | 48.941 | 43.861 | 65.843 |  | 9.1875 | 31.3051 | 27.2435 | 7.8907 | 11.8786 | 28.9305 | 29.0005 |  | 9.1875 | 16.3 | 13.9 | 18.375 | 0
| 3.0694 | 281.765 | 41.142 | 48.955 | 43.868 | 65.862 |  | 9.2083 | 31.4424 | 27.3876 | 7.639 | 11.9999 | 29.054 | 29.1353 |  | 9.2083 | 16.3 | 13.9 | 18.4167 | 0
| 3.0764 | 281.443 | 41.145 | 48.96 | 43.878 | 65.873 |  | 9.2292 | 31.3948 | 27.3197 | 7.5048 | 11.9423 | 29.0156 | 29.0857 |  | 9.2292 | 16.1 | 13.9 | 18.4583 | 0
| 3.0833 | 282.132 | 41.157 | 48.964 | 43.883 | 65.888 |  | 9.25 | 31.2568 | 27.2 | 7.3705 | 11.8271 | 28.8936 | 28.984 |  | 9.25 | 15.8 | 13.9 | 18.5 | 0
| 3.0903 | 281.954 | 41.163 | 48.972 | 43.892 | 65.898 |  | 9.2708 | 31.318 | 27.2542 | 7.4211 | 11.8603 | 28.9117 | 29.0134 |  | 9.2708 | 16 | 13.9 | 18.5417 | 0
| 3.0972 | 281.987 | 41.178 | 48.988 | 43.902 | 65.921 |  | 9.2917 | 31.4242 | 27.3536 | 7.4497 | 11.9511 | 29.0066 | 29.1218 |  | 9.2917 | 16.2 | 13.9 | 18.5833 | 0
| 3.1042 | 282.31 | 41.182 | 48.995 | 43.914 | 65.938 |  | 9.3125 | 31.5084 | 27.4578 | 7.4809 | 12.06 | 29.1516 | 29.2216 |  | 9.3125 | 16.6 | 13.9 | 18.625 | 0
| 3.1111 | 281.801 | 41.198 | 49.008 | 43.923 | 65.96 |  | 9.3333 | 31.3538 | 27.2783 | 7.2799 | 11.8883 | 28.9384 | 29.0717 |  | 9.3333 | 17.1 | 13.9 | 18.6667 | 0
| 3.1181 | 281.597 | 41.205 | 49.015 | 43.929 | 65.975 |  | 9.3542 | 31.3709 | 27.3108 | 7.2805 | 11.918 | 28.9981 | 29.0952 |  | 9.3542 | 18.4 | 13.9 | 18.7083 | 0
| 3.125 | 282.125 | 41.212 | 49.024 | 43.943 | 65.991 |  | 9.375 | 31.4498 | 27.3913 | 7.2991 | 11.9902 | 29.036 | 29.1715 |  | 9.375 | 19.5 | 13.9 | 18.75 | 0
| 3.1319 | 281.737 | 41.221 | 49.035 | 43.947 | 66.01 |  | 9.3958 | 31.6852 | 27.6304 | 7.5168 | 12.2268 | 29.2866 | 29.3906 |  | 9.3958 | 20 | 13.9 | 18.7917 | 0
| 3.1389 | 282.918 | 41.228 | 49.048 | 43.958 | 66.021 |  | 9.4167 | 31.5526 | 27.5044 | 7.3244 | 12.0984 | 29.1542 | 29.2829 |  | 9.4167 | 20.9 | 13.9 | 18.8333 | 0
| 3.1458 | 282.551 | 41.239 | 49.058 | 43.967 | 66.038 |  | 9.4375 | 31.655 | 27.6106 | 7.3819 | 12.1984 | 29.2291 | 29.3804 |  | 9.4375 | 23 | 13.9 | 18.875 | 0
| 3.1528 | 282.479 | 41.246 | 49.065 | 43.978 | 66.056 |  | 9.4583 | 31.3616 | 27.3126 | 7.0282 | 11.8969 | 28.9809 | 29.1411 |  | 9.4583 | 22.9 | 13.9 | 18.9167 | 0
| 3.1597 | 282.906 | 41.255 | 49.075 | 43.984 | 66.072 |  | 9.4792 | 31.4183 | 27.3646 | 7.0634 | 11.9434 | 29.0011 | 29.1591 |  | 9.4792 | 23.3 | 13.9 | 18.9583 | 0
| 3.1667 | 281.81 | 41.26 | 49.086 | 43.996 | 66.083 |  | 9.5 | 31.5461 | 27.4983 | 7.1515 | 12.072 | 29.1396 | 29.2909 |  | 9.5 | 22.6 | 13.9 | 19 | 0
| 3.1736 | 281.29 | 41.265 | 49.089 | 44.003 | 66.083 |  | 9.5208 | 31.6603 | 27.606 | 7.2432 | 12.1841 | 29.2702 | 29.4035 |  | 9.5208 | 23.3 | 13.9 | 19.0417 | 0
| 3.1806 | 282.175 | 41.264 | 49.093 | 44.004 | 66.083 |  | 9.5417 | 32.0055 | 27.9639 | 7.5462 | 12.5261 | 29.5875 | 29.7186 |  | 9.5417 | 23.8 | 13.9 | 19.0833 | 0
| 3.1875 | 282.134 | 41.269 | 49.095 | 44.011 | 66.086 |  | 9.5625 | 32.0462 | 28.0159 | 7.5307 | 12.566 | 29.635 | 29.7774 |  | 9.5625 | 24.3 | 13.9 | 19.125 | 0
| 3.1944 | 282.172 | 41.273 | 49.1 | 44.015 | 66.089 |  | 9.5833 | 31.5517 | 27.4958 | 6.9529 | 12.0673 | 29.1303 | 29.2997 |  | 9.5833 | 23.8 | 13.9 | 19.1667 | 0
| 3.2014 | 281.741 | 41.276 | 49.104 | 44.018 | 66.091 |  | 9.6042 | 31.3037 | 27.2286 | 6.6355 | 11.8166 | 28.8538 | 29.0728 |  | 9.6042 | 21.6 | 13.9 | 19.2083 | 0
| 3.2083 | 281.423 | 41.274 | 49.106 | 44.024 | 66.096 |  | 9.625 | 31.4117 | 27.3461 | 6.7506 | 11.934 | 29.0068 | 29.183 |  | 9.625 | 18.8 | 13.9 | 19.25 | 0
| 3.2153 | 281.149 | 41.281 | 49.107 | 44.025 | 66.099 |  | 9.6458 | 31.5365 | 27.5005 | 6.7606 | 12.0988 | 29.1339 | 29.3101 |  | 9.6458 | 17.7 | 13.9 | 19.2917 | 0
| 3.2222 | 280.522 | 41.282 | 49.112 | 44.028 | 66.094 |  | 9.6667 | 31.7413 | 27.7096 | 7.0379 | 12.2775 | 29.3362 | 29.5239 |  | 9.6667 | 17.5 | 13.9 | 19.3333 | 0
| 3.2292 | 280.803 | 41.278 | 49.111 | 44.025 | 66.085 |  | 9.6875 | 31.5871 | 27.5425 | 6.8157 | 12.1293 | 29.1777 | 29.3676 |  | 9.6875 | 17.2 | 13.9 | 19.375 | 0
| 3.2361 | 279.664 | 41.278 | 49.1 | 44.026 | 66.072 |  | 9.7083 | 31.4965 | 27.4521 | 6.6591 | 12.0495 | 29.0693 | 29.2862 |  | 9.7083 | 16.8 | 13.9 | 19.4167 | 0
| 3.2431 | 281.561 | 41.279 | 49.101 | 44.025 | 66.063 |  | 9.7292 | 31.6714 | 27.6447 | 6.8293 | 12.2339 | 29.2507 | 29.4812 |  | 9.7292 | 17.2 | 13.9 | 19.4583 | 0
| 3.25 | 281.128 | 41.277 | 49.107 | 44.03 | 66.067 |  | 9.75 | 31.6865 | 27.6796 | 6.7882 | 12.2616 | 29.243 | 29.5051 |  | 9.75 | 17.4 | 13.9 | 19.5 | 0
| 3.2569 | 278.941 | 41.28 | 49.103 | 44.035 | 66.063 |  | 9.7708 | 31.6208 | 27.6185 | 6.6074 | 12.2062 | 29.1843 | 29.4487 |  | 9.7708 | 18.5 | 13.9 | 19.5417 | 0
| 3.2639 | 280.016 | 41.27 | 49.093 | 44.021 | 66.042 |  | 9.7917 | 31.8562 | 27.9164 | 6.872 | 12.4256 | 29.3831 | 29.6702 |  | 9.7917 | 18.7 | 13.9 | 19.5833 | 0
| 3.2708 | 278.896 | 41.265 | 49.081 | 44.018 | 66.024 |  | 9.8125 | 31.8452 | 27.8537 | 6.8422 | 12.4109 | 29.3722 | 29.6706 |  | 9.8125 | 18.2 | 13.9 | 19.625 | 0
| 3.2778 | 277.828 | 41.261 | 49.072 | 44.012 | 65.997 |  | 9.8333 | 31.6504 | 27.6576 | 6.6039 | 12.2246 | 29.1755 | 29.4964 |  | 9.8333 | 17.3 | 13.9 | 19.6667 | 0
| 3.2847 | 282.031 | 41.26 | 49.078 | 44.021 | 65.99 |  | 9.8542 | 31.6517 | 27.6746 | 6.5724 | 12.2372 | 29.1723 | 29.4977 |  | 9.8542 | 17 | 13.9 | 19.7083 | 0
| 3.2917 | 280.721 | 41.271 | 49.084 | 44.024 | 66.006 |  | 9.875 | 31.7719 | 27.7829 | 6.6585 | 12.3459 | 29.272 | 29.6065 |  | 9.875 | 16.3 | 13.9 | 19.75 | 0
| 3.2986 | 280.853 | 41.267 | 49.085 | 44.025 | 66.009 |  | 9.8958 | 31.8272 | 27.8514 | 6.682 | 12.3937 | 29.3226 | 29.6731 |  | 9.8958 | 15.8 | 13.9 | 19.7917 | 0
| 3.3056 | 280.026 | 41.269 | 49.08 | 44.027 | 66.003 |  | 9.9167 | 31.8172 | 27.8258 | 6.6308 | 12.3754 | 29.3039 | 29.643 |  | 9.9167 | 15.3 | 13.9 | 19.8333 | 0
| 3.3125 | 278.942 | 41.265 | 49.075 | 44.024 | 65.993 |  | 9.9375 | 31.2111 | 27.2244 | 5.9928 | 11.8112 | 28.7329 | 29.1191 |  | 9.9375 | 14.9 | 13.9 | 19.875 | 0
| 3.3194 | 282.642 | 41.27 | 49.076 | 44.026 | 65.989 |  | 9.9583 | 31.323 | 27.3432 | 6.0801 | 11.9276 | 28.8581 | 29.2218 |  | 9.9583 | 14.4 | 13.9 | 19.9167 | 0
| 3.3264 | 283.456 | 41.283 | 49.089 | 44.035 | 66.02 |  | 9.9792 | 31.3732 | 27.4 | 6.0988 | 11.9684 | 28.8858 | 29.2744 |  | 9.9792 | 14.1 | 13.9 | 19.9583 | 0
| 3.3333 | 282.756 | 41.302 | 49.11 | 44.056 | 66.061 |  | 10 | 31.49 | 27.5205 | 6.1394 | 12.0603 | 28.9526 | 29.3482 |  | 10 | 13.7 | 13.9 | 20 | 0
| 3.3403 | 282.344 | 41.316 | 49.12 | 44.063 | 66.09 |  | 10.0208 | 31.6014 | 27.6831 | 6.2837 | 12.2164 | 29.1249 | 29.5093 |  | 10.0208 | 13.4 | 13.9 | 20.0417 | 0
| 3.3472 | 281.391 | 41.319 | 49.127 | 44.066 | 66.104 |  | 10.0417 | 31.6905 | 27.7291 | 6.3314 | 12.2863 | 29.1643 | 29.5804 |  | 10.0417 | 13.1 | 13.9 | 20.0833 | 0
| 3.3542 | 281.178 | 41.329 | 49.13 | 44.068 | 66.105 |  | 10.0625 | 31.7177 | 27.7471 | 6.2542 | 12.3018 | 29.1236 | 29.5419 |  | 10.0625 | 12.4 | 13.9 | 20.125 | 0
| 3.3611 | 280.729 | 41.33 | 49.133 | 44.069 | 66.11 |  | 10.0833 | 31.7316 | 27.7834 | 6.2853 | 12.311 | 29.1669 | 29.6169 |  | 10.0833 | 12.9 | 13.9 | 20.1667 | 0
| 3.3681 | 280.08 | 41.332 | 49.13 | 44.069 | 66.104 |  | 10.1042 | 31.761 | 27.8173 | 6.2721 | 12.3399 | 29.1714 | 29.6554 |  | 10.1042 | 12.7 | 13.9 | 20.2083 | 0
| 3.375 | 280.384 | 41.323 | 49.127 | 44.067 | 66.096 |  | 10.125 | 31.7684 | 27.7796 | 6.2026 | 12.3053 | 29.1064 | 29.6198 |  | 10.125 | 12.6 | 13.9 | 20.25 | 0
| 3.3819 | 281.317 | 41.324 | 49.125 | 44.071 | 66.099 |  | 10.1458 | 31.7276 | 27.7976 | 6.2026 | 12.323 | 29.1088 | 29.6243 |  | 10.1458 | 12.2 | 13.9 | 20.2917 | 0
| 3.3889 | 281.067 | 41.327 | 49.126 | 44.074 | 66.099 |  | 10.1667 | 31.6235 | 27.6826 | 6.0726 | 12.2476 | 28.9551 | 29.5361 |  | 10.1667 | 12.3 | 13.9 | 20.3333 | 0
| 3.3958 | 279.797 | 41.326 | 49.127 | 44.07 | 66.099 |  | 10.1875 | 31.107 | 27.1509 | 5.4405 | 11.7088 | 28.4556 | 29.0541 |  | 10.1875 | 12.1 | 13.9 | 20.375 | 0
| 3.4028 | 279.01 | 41.319 | 49.117 | 44.069 | 66.09 |  | 10.2083 | 31.2247 | 27.2679 | 5.5043 | 11.8151 | 28.5437 | 29.1378 |  | 10.2083 | 12.1 | 13.9 | 20.4167 | 0
| 3.4097 | 279.041 | 41.313 | 49.108 | 44.06 | 66.064 |  | 10.2292 | 31.668 | 27.7203 | 5.9423 | 12.2516 | 28.9816 | 29.574 |  | 10.2292 | 11.8 | 14.4 | 20.4583 | 0
| 3.4167 | 281.212 | 41.312 | 49.108 | 44.064 | 66.058 |  | 10.25 | 31.2063 | 27.2564 | 5.4338 | 11.8061 | 28.5796 | 29.1873 |  | 10.25 | 11.6 | 14.4 | 20.5 | 0
| 3.4236 | 280.779 | 41.323 | 49.116 | 44.071 | 66.078 |  | 10.2708 | 31.3375 | 27.3824 | 5.5328 | 11.9457 | 28.7151 | 29.3093 |  | 10.2708 | 11.4 | 14.4 | 20.5417 | 0
| 3.4306 | 280.653 | 41.33 | 49.116 | 44.069 | 66.083 |  | 10.2917 | 31.5644 | 27.6263 | 5.7422 | 12.1588 | 28.9052 | 29.4951 |  | 10.2917 | 12.3 | 14.4 | 20.5833 | 0
| 3.4375 | 279.963 | 41.331 | 49.117 | 44.077 | 66.092 |  | 10.3125 | 31.7217 | 27.7736 | 5.8522 | 12.2964 | 29.0619 | 29.6451 |  | 10.3125 | 14.1 | 14.4 | 20.625 | 0
| 3.4444 | 279.664 | 41.335 | 49.117 | 44.07 | 66.091 |  | 10.3333 | 31.7441 | 27.7937 | 5.8159 | 12.3045 | 29.2061 | 29.6628 |  | 10.3333 | 15.4 | 14.4 | 20.6667 | 0
| 3.4514 | 279.257 | 41.332 | 49.111 | 44.073 | 66.082 |  | 10.3542 | 31.7995 | 27.8579 | 5.8056 | 12.3407 | 29.2115 | 29.7089 |  | 10.3542 | 16.1 | 14.4 | 20.7083 | 0
| 3.4583 | 279.142 | 41.326 | 49.107 | 44.074 | 66.07 |  | 10.375 | 31.6023 | 27.6482 | 5.6485 | 12.1959 | 29.0869 | 29.5773 |  | 10.375 | 16.9 | 14.4 | 20.75 | 0
| 3.4653 | 278.933 | 41.324 | 49.099 | 44.062 | 66.06 |  | 10.3958 | 31.386 | 27.4429 | 5.3558 | 11.9812 | 28.8821 | 29.3768 |  | 10.3958 | 18 | 14.4 | 20.7917 | 0
| 3.4722 | 278.495 | 41.32 | 49.089 | 44.06 | 66.042 |  | 10.4167 | [7 empty] | 10.4167 | 19.1 | 14.4 | 20.8333 | 0
| 3.4792 | 279.545 | 41.313 | 49.079 | 44.051 | 66.023 |  | 10.4375 | 31.7193 | 27.7546 | 5.5533 | 12.269 | 29.1241 | 29.6144 |  | 10.4375 | 20.6 | 14.4 | 20.875 | 0
| 3.4861 | 279.624 | 41.312 | 49.079 | 44.045 | 66.013 |  | 10.4583 | 31.4092 | 27.7813 | 5.4711 | 12.1974 | 29.0177 | 29.6073 |  | 10.4583 | 21.2 | 14.4 | 20.9167 | 0
| 3.4931 | 279.959 | 41.312 | 49.069 | 44.051 | 66.007 |  | 10.4792 | 31.6495 | 27.7362 | 5.4773 | 12.2171 | 29.1355 | 29.6393 |  | 10.4792 | 22.1 | 14.4 | 20.9583 | 0
| 3.5 | 278.77 | 41.312 | 49.068 | 44.041 | 65.995 |  | 10.5 | 31.4616 | 27.5115 | 5.2123 | 11.9303 | 28.9043 | 29.4349 |  | 10.5 | 23.1 | 14.4 | 21 | 0
| 3.5069 | 279.335 | 41.305 | 49.06 | 44.037 | 65.983 |  | 10.5208 | 31.6338 | 27.711 | 5.3778 | 12.2278 | 29.0723 | 29.6031 |  | 10.5208 | 22.6 | 14.4 | 21.0417 | 0
| 3.5139 | 278.656 | 41.312 | 49.052 | 44.04 | 65.982 |  | 10.5417 | 31.5478 | 27.613 | 5.2491 | 12.1314 | 29.0511 | 29.5592 |  | 10.5417 | 22.8 | 14.4 | 21.0833 | 0
| 3.5208 | 278.983 | 41.308 | 49.05 | 44.031 | 65.971 |  | 10.5625 | 31.7414 | 27.7908 | 5.3866 | 12.3144 | 29.211 | 29.7306 |  | 10.5625 | 22.8 | 14.4 | 21.125 | 0
| 3.5278 | 278.639 | 41.3 | 49.044 | 44.029 | 65.959 |  | 10.5833 | 31.7612 | 27.8365 | 5.4043 | 12.348 | 29.2097 | 29.7722 |  | 10.5833 | 23.7 | 14.4 | 21.1667 | 0
| 3.5347 | 278.127 | 41.295 | 49.027 | 44.024 | 65.948 |  | 10.6042 | 31.8419 | 27.9078 | 5.4318 | 12.4047 | 29.2927 | 29.8462 |  | 10.6042 | 25.5 | 14.4 | 21.2083 | 0
| 3.5417 | 278.237 | 41.291 | 49.023 | 44.021 | 65.932 |  | 10.625 | 31.7496 | 27.8046 | 5.2839 | 12.3161 | 29.1872 | 29.727 |  | 10.625 | 25.7 | 14.4 | 21.25 | 0
| 3.5486 | 278.164 | 41.286 | 49.014 | 44.013 | 65.924 |  | 10.6458 | 31.7678 | 27.8385 | 5.2861 | 12.3515 | 29.2369 | 29.7722 |  | 10.6458 | 26.3 | 14.4 | 21.2917 | 0
| 3.5556 | 278.931 | 41.291 | 49.011 | 44.011 | 65.911 |  | 10.6667 | 31.7315 | 27.8136 | 5.2442 | 12.325 | 29.1917 | 29.7609 |  | 10.6667 | 25.7 | 14.4 | 21.3333 | 0
| 3.5625 | 278.213 | 41.287 | 49.007 | 44.003 | 65.912 |  | 10.6875 | 31.7641 | 27.846 | 5.2337 | 12.3479 | 29.2086 | 29.7913 |  | 10.6875 | 25.7 | 14.4 | 21.375 | 0
| 3.5694 | 278.311 | 41.284 | 48.998 | 44.004 | 65.907 |  | 10.7083 | 31.7822 | 27.8641 | 5.2183 | 12.3612 | 29.2311 | 29.8117 |  | 10.7083 | 26.4 | 14.4 | 21.4167 | 0
| 3.5764 | 275.581 | 41.285 | 48.991 | 43.995 | 65.895 |  | 10.7292 | 31.8218 | 27.89 | 5.2132 | 12.4 | 29.2477 | 29.8193 |  | 10.7292 | 26.4 | 14.4 | 21.4583 | 0
| 3.5833 | 275.224 | 41.261 | 48.962 | 43.98 | 65.847 |  | 10.75 | 31.7402 | 27.8155 | 5.1016 | 12.3248 | 29.1931 | 29.7624 |  | 10.75 | 25.3 | 14.4 | 21.5 | 0
| 3.5903 | 276.463 | 41.245 | 48.945 | 43.958 | 65.803 |  | 10.7708 | 31.7354 | 27.8093 | 5.068 | 12.3301 | 29.2049 | 29.7652 |  | 10.7708 | 24.1 | 14.4 | 21.5417 | 0
| 3.5972 | 275.351 | 41.231 | 48.924 | 43.944 | 65.768 |  | 10.7917 | 31.7728 | 27.8407 | 5.0635 | 12.3498 | 29.229 | 29.7827 |  | 10.7917 | 23.9 | 14.4 | 21.5833 | 0
| 3.6042 | 276.269 | 41.219 | 48.906 | 43.928 | 65.734 |  | 10.8125 | 31.746 | 27.8256 | 5.0227 | 12.335 | 29.2159 | 29.7696 |  | 10.8125 | 22.4 | 14.4 | 21.625 | 0
| 3.6111 | 275.589 | 41.21 | 48.889 | 43.918 | 65.706 |  | 10.8333 | 31.7584 | 27.8296 | 5.0028 | 12.337 | 29.2285 | 29.7778 |  | 10.8333 | 21.7 | 14.4 | 21.6667 | 0
| 3.6181 | 275.538 | 41.199 | 48.872 | 43.907 | 65.688 |  | 10.8542 | 31.7682 | 27.8376 | 4.9799 | 12.3449 | 29.2453 | 29.7855 |  | 10.8542 | 20.4 | 14.4 | 21.7083 | 0
| 3.625 | 3.569 | 41.148 | 48.808 | 43.864 | 65.602 |  | 10.875 | 31.7389 | 27.8107 | 4.9322 | 12.3387 | 29.1979 | 29.7336 |  | 10.875 | 19.7 | 14.4 | 21.75 | 0
| 3.6319 | 0.575 | 40.325 | 47.942 | 43.22 | 63.808 |  | 10.8958 | 31.7172 | 27.7915 | 4.8722 | 12.3025 | 29.1923 | 29.7394 |  | 10.8958 | 19.3 | 14.4 | 21.7917 | 0
| 3.6389 | 0.594 | 39.508 | 47.096 | 42.562 | 61.903 |  | 10.9167 | 31.7572 | 27.8336 | 4.8366 | 12.2953 | 29.2482 | 29.7613 |  | 10.9167 | 18.9 | 14.4 | 21.8333 | 0.1
| 3.6458 | 0.698 | 38.822 | 46.35 | 41.994 | 60.261 |  | 10.9375 | 31.7778 | 27.8383 | 4.8395 | 12.3181 | 29.262 | 29.7661 |  | 10.9375 | 18.6 | 14.4 | 21.875 | 0
| 3.6528 | 0.693 | 38.251 | 45.68 | 41.494 | 58.844 |  | 10.9583 | 31.7902 | 27.8462 | 4.8432 | 12.3328 | 29.2654 | 29.7742 |  | 10.9583 | 18.2 | 14.4 | 21.9167 | 0.9
| 3.6597 | 0.714 | 37.773 | 45.065 | 41.038 | 57.606 |  | 10.9792 | 31.7773 | 27.8377 | 4.7733 | 12.3222 | 29.3 | 29.7884 |  | 10.9792 | 17.8 | 14.4 | 21.9583 | 0.5
| 3.6667 | 0.543 | 37.357 | 44.494 | 40.623 | 56.508 |  | 11 | 31.2161 | 27.2761 | 4.1566 | 11.8059 | 28.7714 | 29.3022 |  | 11 | 17.5 | 14.4 | 22 | 0.1
| 3.6736 | 0.674 | 36.984 | 43.963 | 40.231 | 55.533 |  | 11.0208 | 31.2726 | 27.3552 | 4.1962 | 11.8525 | 28.8053 | 29.3293 |  | 11.0208 | 17.4 | 14.4 | 22.0417 | 0
| 3.6806 | 87.19 | 36.646 | 43.47 | 39.869 | 54.641 |  | 11.0417 | 31.2817 | 27.3755 | 4.1896 | 11.8812 | 28.8279 | 29.3655 |  | 11.0417 | 17.8 | 14.4 | 22.0833 | 0
| 3.6875 | 276.481 | 36.864 | 43.569 | 39.92 | 54.911 |  | 11.0625 | 31.3337 | 27.4252 | 4.1983 | 11.9321 | 28.8595 | 29.4062 |  | 11.0625 | 17.9 | 14.4 | 22.125 | 0
| 3.6944 | 318.69 | 37.509 | 44.099 | 40.314 | 56.242 |  | 11.0833 | 31.4739 | 27.5765 | 4.3365 | 12.0695 | 29.0153 | 29.5555 |  | 11.0833 | 17.5 | 14.4 | 22.1667 | 0
| 3.7014 | 279.367 | 37.689 | 44.174 | 40.393 | 56.695 |  | 11.1042 | 31.6996 | 27.8056 | 4.554 | 12.2801 | 29.2225 | 29.7584 |  | 11.1042 | 16.8 | 14.4 | 22.2083 | 0.3
| 3.7292 | 284.474 | 38.779 | 45.337 | 41.153 | 59.435 |  | 11.125 | 31.7365 | 27.8377 | 4.5545 | 12.305 | 29.2481 | 29.7976 |  | 11.125 | 16.3 | 14.4 | 22.25 | 0.3
| 3.7361 | 285.195 | 39.031 | 45.665 | 41.381 | 60.106 |  | 11.1458 | 31.2997 | 27.3984 | 4.056 | 11.8973 | 28.8144 | 29.3792 |  | 11.1458 | 15.7 | 14.4 | 22.2917 | 0
| 3.7431 | 283.93 | 39.224 | 45.94 | 41.561 | 60.658 |  | 11.1667 | 31.3173 | 27.4365 | 4.0524 | 11.9129 | 28.8252 | 29.4058 |  | 11.1667 | 15.6 | 14.4 | 22.3333 | 0
| 3.75 | 284.152 | 39.381 | 46.171 | 41.716 | 61.121 |  | 11.1875 | 31.7088 | 27.8194 | 4.4517 | 12.2852 | 29.1821 | 29.7768 |  | 11.1875 | 15.4 | 14.4 | 22.375 | 0
| 3.7569 | 284.46 | 39.515 | 46.358 | 41.854 | 61.518 |  | 11.2083 | 31.367 | 27.495 | 4.0854 | 11.9772 | 28.9223 | 29.5009 |  | 11.2083 | 15.2 | 14.4 | 22.4167 | 0
| 3.7639 | 284.263 | 39.634 | 46.515 | 41.979 | 61.878 |  | 11.2292 | 31.6441 | 27.782 | 4.3536 | 12.2417 | 29.138 | 29.7122 |  | 11.2292 | 14.9 | 14.4 | 22.4583 | 0
| 3.7847 | 267.318 | 39.867 | 46.802 | 42.202 | 62.613 |  | 11.25 | 31.712 | 27.8428 | 4.4041 | 12.2904 | 29.2261 | 29.796 |  | 11.25 | 15.1 | 14.4 | 22.5 | 0
| 3.7917 | 276.76 | 39.839 | 46.786 | 42.189 | 62.59 |  | 11.2708 | 31.2549 | 27.3699 | 3.8877 | 11.8605 | 28.781 | 29.3821 |  | 11.2708 | 15.2 | 14.4 | 22.5417 | 0.8
| 3.7986 | 275.835 | 39.865 | 46.826 | 42.22 | 62.687 |  | 11.2917 | 31.6282 | 27.7594 | 4.2768 | 12.2151 | 29.1289 | 29.7122 |  | 11.2917 | 15.4 | 14.4 | 22.5833 | 0.3
| 3.8056 | 275.264 | 39.891 | 46.879 | 42.247 | 62.768 |  | 11.3125 | 31.6748 | 27.7921 | 4.3083 | 12.2535 | 29.1774 | 29.772 |  | 11.3125 | 15.9 | 14.4 | 22.625 | 0
| 3.8125 | 275.354 | 39.916 | 46.949 | 42.29 | 62.865 |  | 11.3333 | 31.3599 | 27.4967 | 3.943 | 11.9742 | 28.879 | 29.489 |  | 11.3333 | 16.7 | 14.4 | 22.6667 | 0
| 3.8194 | 275.775 | 39.949 | 47.031 | 42.334 | 62.961 |  | 11.3542 | 31.645 | 27.7446 | 4.2271 | 12.2268 | 29.0099 | 29.7626 |  | 11.3542 | 17.3 | 14.4 | 22.7083 | 0
| 3.8264 | 276.623 | 39.981 | 47.127 | 42.388 | 63.066 |  | 11.375 | 31.6333 | 27.7262 | 4.1939 | 12.2155 | 28.9667 | 29.7171 |  | 11.375 | 17.2 | 14.4 | 22.75 | 0
| 3.8333 | 276.755 | 40.014 | 47.227 | 42.453 | 63.183 |  | 11.3958 | 31.6507 | 27.7593 | 4.1977 | 12.237 | 28.9908 | 29.7548 |  | 11.3958 | 15.7 | 14.4 | 22.7917 | 0
| 3.8403 | 276.994 | 40.055 | 47.334 | 42.523 | 63.312 |  | 11.4167 | 31.6077 | 27.7075 | 4.1363 | 12.186 | 28.8598 | 29.6914 |  | 11.4167 | 15.1 | 14.4 | 22.8333 | 0
| 3.8472 | 278.455 | 40.098 | 47.441 | 42.593 | 63.443 |  | 11.4375 | 31.6722 | 27.7693 | 4.1897 | 12.2267 | 28.9376 | 29.749 |  | 11.4375 | 15.7 | 14.4 | 22.875 | 0
| 3.8542 | 278.039 | 40.145 | 47.546 | 42.665 | 63.579 |  | 11.4583 | 31.4006 | 27.5059 | 3.8836 | 11.9896 | 28.6961 | 29.5455 |  | 11.4583 | 15.8 | 14.4 | 22.9167 | 0
| 3.8611 | 277.55 | 40.198 | 47.655 | 42.736 | 63.708 |  | 11.4792 | 31.611 | 27.7108 | 4.086 | 12.1868 | 28.9556 | 29.7061 |  | 11.4792 | 15.9 | 14.4 | 22.9583 | 0
| 3.8681 | 277.786 | 40.242 | 47.755 | 42.814 | 63.843 |  | 11.5 | 31.6981 | 27.8087 | 4.1657 | 12.2607 | 29.1193 | 29.8246 |  | 11.5 | 15.8 | 14.4 | 23 | 0
| 3.875 | 277.857 | 40.293 | 47.858 | 42.882 | 63.974 |  | 11.5208 | 31.6618 | 27.8379 | 4.1325 | 12.2474 | 29.1598 | 29.8086 |  | 11.5208 | 16.4 | 14.4 | 23.0417 | 0
| 3.8819 | 277.764 | 40.335 | 47.95 | 42.955 | 64.098 |  | 11.5417 | 31.4526 | 27.6042 | 3.8375 | 12.046 | 28.9416 | 29.5834 |  | 11.5417 | 16.8 | 14.4 | 23.0833 | 0
| 3.8889 | 279.642 | 40.384 | 48.039 | 43.026 | 64.215 |  | 11.5625 | 31.5819 | 27.7332 | 3.9717 | 12.1725 | 29.0821 | 29.7125 |  | 11.5625 | 17.4 | 14.4 | 23.125 | 0
| 3.8958 | 279.116 | 40.436 | 48.144 | 43.101 | 64.359 |  | 11.5833 | 31.6543 | 27.8057 | 4.0312 | 12.2258 | 29.1679 | 29.7668 |  | 11.5833 | 17.9 | 14.4 | 23.1667 | 0
| 3.9028 | 281.044 | 40.494 | 48.238 | 43.166 | 64.497 |  | 11.6042 | 31.6128 | 27.7728 | 3.9946 | 12.2047 | 29.1196 | 29.7546 |  | 11.6042 | 18.1 | 14.4 | 23.2083 | 0.1
| 3.9097 | 281.814 | 40.556 | 48.341 | 43.242 | 64.655 |  | 11.625 | 31.511 | 27.6666 | 3.8604 | 12.1094 | 29.0225 | 29.6551 |  | 11.625 | 18.8 | 14.4 | 23.25 | 0
| 3.9167 | 280.418 | 40.615 | 48.439 | 43.319 | 64.796 |  | 11.6458 | 31.5376 | 27.6996 | 3.8591 | 12.1416 | 29.0647 | 29.6929 |  | 11.6458 | 18.9 | 14.4 | 23.2917 | 0
| 3.9236 | 281.193 | 40.671 | 48.523 | 43.389 | 64.926 |  | 11.6667 | 31.4222 | 27.5866 | 3.7316 | 12.0242 | 28.9112 | 29.5866 |  | 11.6667 | 19.4 | 14.4 | 23.3333 | 0.4
| 3.9306 | 278.367 | 40.725 | 48.618 | 43.463 | 65.072 |  | 11.6875 | 31.4946 | 27.6566 | 3.78 | 12.0752 | 28.9676 | 29.6341 |  | 11.6875 | 19.6 | 14.4 | 23.375 | 0.7
| 3.9375 | 278.617 | 40.77 | 48.697 | 43.519 | 65.171 |  | 11.7083 | 31.5127 | 27.686 | 3.8085 | 12.1106 | 29.0082 | 29.6906 |  | 11.7083 | 19.4 | 14.4 | 23.4167 | 1
| 3.9444 | 279.245 | 40.811 | 48.761 | 43.579 | 65.267 |  | 11.7292 | 31.6552 | 27.8285 | 3.9449 | 12.248 | 29.1596 | 29.8173 |  | 11.7292 | 19.6 | 15 | 23.4583 | 1.2
| 3.9514 | 280.57 | 40.848 | 48.831 | 43.631 | 65.366 |  | 11.75 | 31.6643 | 27.8262 | 3.9405 | 12.2369 | 29.1008 | 29.7969 |  | 11.75 | 19.8 | 15 | 23.5 | 0.7
| 3.9583 | 280.646 | 40.897 | 48.909 | 43.692 | 65.472 |  | 11.7708 | 31.5194 | 27.6883 | 3.7866 | 12.1239 | 29.0308 | 29.7132 |  | 11.7708 | 19.8 | 15 | 23.5417 | 1.3
| 3.9653 | 281.354 | 40.941 | 48.984 | 43.755 | 65.582 |  | 11.7917 | 31.2424 | 27.3938 | 3.3202 | 11.8375 | 28.7838 | 29.4546 |  | 11.7917 | 19.6 | 15 | 23.5833 | 0.3
| 3.9722 | 282.021 | 40.993 | 49.057 | 43.816 | 65.697 |  | 11.8125 | 31.2737 | 27.4455 | 3.3641 | 11.8903 | 28.806 | 29.5016 |  | 11.8125 | 19.1 | 15 | 23.625 | 0
| 3.9792 | 281.562 | 41.045 | 49.13 | 43.87 | 65.807 |  | 11.8333 | 31.1896 | 27.3414 | 3.2189 | 11.7948 | 28.7154 | 29.3974 |  | 11.8333 | 18.7 | 15 | 23.6667 | 0.2
| 3.9861 | 281.658 | 41.09 | 49.204 | 43.928 | 65.917 |  | 11.8542 | 31.1422 | 27.3171 | 3.1562 | 11.7556 | 28.684 | 29.3773 |  | 11.8542 | 18.2 | 15 | 23.7083 | 0
| 3.9931 | 278.943 | 41.139 | 49.271 | 43.98 | 66.02 |  | 11.875 | 31.5531 | 27.7386 | 3.6083 | 12.1646 | 29.0603 | 29.7541 |  | 11.875 | 16.8 | 15 | 23.75 | 0
| 4 | 280.203 | 41.166 | 49.326 | 44.025 | 66.084 |  | 11.8958 | 30.8995 | 27.075 | 2.8572 | 11.5247 | 28.4575 | 29.1619 |  | 11.8958 | 16.1 | 15 | 23.7917 | 0
| 4.0069 | 280.248 | 41.196 | 49.38 | 44.068 | 66.152 |  | 11.9167 | 30.9522 | 27.0873 | 2.874 | 11.559 | 28.4539 | 29.1764 |  | 11.9167 | 15.6 | 15 | 23.8333 | 0
| 4.0139 | 279.83 | 41.233 | 49.44 | 44.116 | 66.228 |  | 11.9375 | 31.178 | 27.3516 | 3.1557 | 11.7897 | 28.7314 | 29.4159 |  | 11.9375 | 15.2 | 15 | 23.875 | 0
| 4.0208 | 279.87 | 41.268 | 49.488 | 44.159 | 66.303 |  | 11.9583 | 31.5311 | 27.7145 | 3.5588 | 12.1204 | 29.0456 | 29.7216 |  | 11.9583 | 14.3 | 15 | 23.9167 | 0
| 4.0278 | 279.422 | 41.302 | 49.541 | 44.2 | 66.371 |  | 11.9792 | 31.2238 | 27.3728 | 3.2384 | 11.8727 | 28.8225 | 29.5141 |  | 11.9792 | 13.7 | 15 | 23.9583 | 0
| 4.0347 | 279.459 | 41.331 | 49.59 | 44.25 | 66.437 |  | 12 | 30.8888 | 26.9778 | 2.7779 | 11.4876 | 28.4069 | 29.143 |  | 12 | 12.9 | 15 | 24 | 0
| 4.0417 | 279.559 | 41.365 | 49.639 | 44.284 | 66.503 |  | 12.0208 | 30.9203 | 27.0343 | 2.8262 | 11.5318 | 28.4046 | 29.1815 |  | 12.0208 | 12.2 | 15 | 24.0417 | 0
| 4.0486 | 280.423 | 41.396 | 49.686 | 44.323 | 66.563 |  | 12.0417 | 31.3548 | 27.5009 | 3.3566 | 12.0242 | 28.888 | 29.659 |  | 12.0417 | 11.8 | 15 | 24.0833 | 0
| 4.0556 | 280.768 | 41.43 | 49.734 | 44.365 | 66.627 |  | 12.0625 | 31.4569 | 27.6137 | 3.4072 | 12.0819 | 28.8678 | 29.7225 |  | 12.0625 | 11.3 | 15 | 24.125 | 0
| 4.0625 | 280.868 | 41.461 | 49.784 | 44.409 | 66.697 |  | 12.0833 | 30.8709 | 26.9944 | 2.6736 | 11.495 | 28.3125 | 29.1661 |  | 12.0833 | 10.9 | 15 | 24.1667 | 0
| 4.0694 | 280.615 | 41.496 | 49.832 | 44.446 | 66.763 |  | 12.1042 | 31.5485 | 27.6013 | 3.3758 | 12.0656 | 28.8714 | 29.7215 |  | 12.1042 | 10.6 | 15 | 24.2083 | 0
| 4.0764 | 280.723 | 41.534 | 49.879 | 44.485 | 66.834 |  | 12.125 | 31.2905 | 27.4346 | 3.0485 | 11.9216 | 28.6929 | 29.5632 |  | 12.125 | 10.3 | 15 | 24.25 | 0
| 4.0833 | 281.321 | 41.564 | 49.929 | 44.53 | 66.903 |  | 12.1458 | 31.2073 | 27.334 | 2.8521 | 11.7852 | 28.5604 | 29.3965 |  | 12.1458 | 10.4 | 15 | 24.2917 | 0
| 4.0903 | 281.106 | 41.607 | 49.981 | 44.57 | 66.978 |  | 12.1667 | 31.3816 | 27.5591 | 3.0585 | 12.0024 | 28.7884 | 29.6679 |  | 12.1667 | 10.2 | 15 | 24.3333 | 0
| 4.0972 | 281.679 | 41.646 | 50.033 | 44.613 | 67.053 |  | 12.1875 | 31.497 | 27.6447 | 2.9772 | 12.0866 | 28.9059 | 29.7223 |  | 12.1875 | 10.4 | 15 | 24.375 | 0
| 4.1042 | 281.154 | 41.679 | 50.085 | 44.657 | 67.127 |  | 12.2083 | 31.1553 | 27.3136 | 2.5426 | 11.803 | 28.6281 | 29.4733 |  | 12.2083 | 10.1 | 15 | 24.4167 | 0
| 4.1111 | 281.797 | 41.709 | 50.131 | 44.699 | 67.195 |  | 12.2292 | 31.4835 | 27.6132 | 2.8367 | 12.0734 | 28.8766 | 29.7019 |  | 12.2292 | 9.9 | 15 | 24.4583 | 0
| 4.1181 | 281.075 | 41.744 | 50.175 | 44.743 | 67.259 |  | 12.25 | 31.0083 | 27.1449 | 2.3232 | 11.6302 | 28.4182 | 29.2879 |  | 12.25 | 10.1 | 15 | 24.5 | 0
| 4.125 | 281.492 | 41.772 | 50.221 | 44.781 | 67.322 |  | 12.2708 | 31.1304 | 27.2821 | 2.6194 | 11.7808 | 28.5649 | 29.4214 |  | 12.2708 | 10.6 | 15 | 24.5417 | 0
| 4.1319 | 282.078 | 41.805 | 50.27 | 44.815 | 67.387 |  | 12.2917 | 31.4359 | 27.5793 | 3.2069 | 11.9773 | 28.7633 | 29.5907 |  | 12.2917 | 11.2 | 15 | 24.5833 | 0
| 4.1389 | 282.117 | 41.844 | 50.315 | 44.859 | 67.457 |  | 12.3125 | 31.0506 | 27.1914 | 2.8474 | 11.6661 | 28.5209 | 29.3521 |  | 12.3125 | 12 | 15 | 24.625 | 0
| 4.1458 | 282.059 | 41.875 | 50.363 | 44.898 | 67.516 |  | 12.3333 | 31.3982 | 27.6163 | 3.2392 | 12.0195 | 29.0057 | 29.6928 |  | 12.3333 | 13.6 | 15 | 24.6667 | 0
| 4.1528 | 281.384 | 41.903 | 50.401 | 44.928 | 67.57 |  | 12.3542 | 31.4829 | 27.6869 | 3.3685 | 12.0861 | 29.0493 | 29.7524 |  | 12.3542 | 14.7 | 15 | 24.7083 | 0
| 4.1597 | 281.492 | 41.932 | 50.441 | 44.961 | 67.62 |  | 12.375 | 31.1395 | 27.3306 | 2.949 | 11.7429 | 28.7129 | 29.4267 |  | 12.375 | 15.5 | 15 | 24.75 | 0
| 4.1667 | 282.083 | 41.957 | 50.48 | 44.999 | 67.677 |  | 12.3958 | 31.337 | 27.5434 | 3.1768 | 11.9556 | 28.8784 | 29.6037 |  | 12.3958 | 16.4 | 15 | 24.7917 | 0
| 4.1736 | 281.701 | 41.984 | 50.521 | 45.035 | 67.727 |  | 12.4167 | 31.5137 | 27.6946 | 3.2728 | 12.0837 | 29.0365 | 29.7553 |  | 12.4167 | 17.1 | 15 | 24.8333 | 0
| 4.1806 | 281.87 | 42.011 | 50.563 | 45.073 | 67.78 |  | 12.4375 | 31.4553 | 27.6745 | 3.2378 | 12.053 | 29.0166 | 29.7443 |  | 12.4375 | 17.6 | 15 | 24.875 | 0
| 4.1875 | 281.456 | 42.038 | 50.598 | 45.107 | 67.83 |  | 12.4583 | 31.3261 | 27.5519 | 3.138 | 11.9681 | 28.9192 | 29.6511 |  | 12.4583 | 18 | 15 | 24.9167 | 0
| 4.1944 | 281.77 | 42.067 | 50.639 | 45.138 | 67.878 |  | 12.4792 | 31.3845 | 27.6053 | 3.2004 | 12.0026 | 28.9569 | 29.6911 |  | 12.4792 | 18.7 | 15 | 24.9583 | 0
| 4.2014 | 282.077 | 42.09 | 50.674 | 45.178 | 67.925 |  | 12.5 | 31.5202 | 27.72 | 3.3641 | 12.115 | 29.0675 | 29.7905 |  | 12.5 | 20.6 | 15 | 25 | 0
| 4.2083 | 282.167 | 42.116 | 50.708 | 45.199 | 67.975 |  | 12.5208 | 31.4758 | 27.7062 | 3.35 | 12.11 | 29.047 | 29.779 |  | 12.5208 | 21.7 | 15 | 25.0417 | 0
| 4.2153 | 281.868 | 42.144 | 50.743 | 45.231 | 68.019 |  | 12.5417 | 31.4554 | 27.6633 | 3.3369 | 12.0968 | 28.8823 | 29.8084 |  | 12.5417 | 22.3 | 15 | 25.0833 | 0
| 4.2222 | 282.206 | 42.166 | 50.777 | 45.261 | 68.062 |  | 12.5625 | 31.4642 | 27.6653 | 3.295 | 12.0876 | 28.8819 | 29.7855 |  | 12.5625 | 22.4 | 15 | 25.125 | 0
| 4.2292 | 281.472 | 42.192 | 50.812 | 45.295 | 68.108 |  | 12.5833 | 31.4392 | 27.6947 | 3.2884 | 12.0655 | 28.979 | 29.7697 |  | 12.5833 | 21 | 15 | 25.1667 | 0
| 4.2361 | 282.078 | 42.211 | 50.847 | 45.325 | 68.151 |  | 12.6042 | 31.4387 | 27.6368 | 3.2589 | 12.0796 | 28.9117 | 29.8178 |  | 12.6042 | 20.9 | 15 | 25.2083 | 0
| 4.2431 | 280.825 | 42.238 | 50.878 | 45.351 | 68.192 |  | 12.625 | 31.4143 | 27.6043 | 3.193 | 12.0478 | 28.8403 | 29.7396 |  | 12.625 | 19.1 | 15 | 25.25 | 0
| 4.25 | 281.83 | 42.264 | 50.908 | 45.377 | 68.23 |  | 12.6458 | 31.4081 | 27.6191 | 3.2525 | 12.0717 | 28.8254 | 29.7203 |  | 12.6458 | 14.9 | 15 | 25.2917 | 0
| 4.2569 | 282.126 | 42.287 | 50.945 | 45.404 | 68.276 |  | 12.6667 | 31.311 | 27.5157 | 3.0953 | 11.9681 | 28.7647 | 29.6574 |  | 12.6667 | 14.2 | 15 | 25.3333 | 0
| 4.2639 | 282.397 | 42.308 | 50.981 | 45.437 | 68.322 |  | 12.6875 | 31.2674 | 27.4791 | 3.0489 | 11.9345 | 28.7191 | 29.6297 |  | 12.6875 | 14.3 | 15 | 25.375 | 0
| 4.2708 | 281.798 | 42.335 | 51.011 | 45.468 | 68.365 |  | 12.7083 | 31.4154 | 27.6196 | 3.1667 | 12.031 | 28.842 | 29.7642 |  | 12.7083 | 14.3 | 15 | 25.4167 | 0
| 4.2778 | 281.778 | 42.356 | 51.042 | 45.495 | 68.403 |  | 12.7292 | 31.3995 | 27.6196 | 3.1448 | 12.0553 | 28.8329 | 29.7596 |  | 12.7292 | 13.8 | 15 | 25.4583 | 0
| 4.2847 | 281.585 | 42.38 | 51.071 | 45.523 | 68.442 |  | 12.75 | 31.3995 | 27.6331 | 3.1557 | 12.0642 | 28.8306 | 29.7438 |  | 12.75 | 13.4 | 15 | 25.5 | 0
| 4.2917 | 281.243 | 42.395 | 51.098 | 45.546 | 68.47 |  | 12.7708 | 31.3758 | 27.6118 | 3.0782 | 12.0368 | 28.7505 | 29.7315 |  | 12.7708 | 13.4 | 15 | 25.5417 | 0
| 4.2986 | 280.868 | 42.413 | 51.123 | 45.573 | 68.491 |  | 12.7917 | 31.3056 | 27.5509 | 3.0057 | 11.9925 | 28.7596 | 29.6953 |  | 12.7917 | 13.7 | 15 | 25.5833 | 0
| 4.3056 | 280.766 | 42.426 | 51.147 | 45.587 | 68.525 |  | 12.8125 | 31.3124 | 27.5689 | 2.9882 | 11.9858 | 28.7573 | 29.6999 |  | 12.8125 | 13.8 | 15 | 25.625 | 0
| 4.3125 | 279.973 | 42.442 | 51.168 | 45.615 | 68.543 |  | 12.8333 | 31.3147 | 27.5555 | 2.9157 | 11.9748 | 28.7393 | 29.6704 |  | 12.8333 | 13.8 | 15 | 25.6667 | 0
| 4.3194 | 279.995 | 42.46 | 51.19 | 45.632 | 68.56 |  | 12.8542 | 31.3282 | 27.5915 | 2.9574 | 12.008 | 28.746 | 29.6953 |  | 12.8542 | 13.5 | 15 | 25.7083 | 0
| 4.3264 | 280.022 | 42.467 | 51.208 | 45.644 | 68.574 |  | 12.875 | 31.3441 | 27.6118 | 2.9618 | 12.0301 | 28.7821 | 29.745 |  | 12.875 | 13.3 | 15 | 25.75 | 0
| 4.3333 | 279.279 | 42.48 | 51.227 | 45.661 | 68.595 |  | 12.8958 | 31.317 | 27.5938 | 2.9188 | 12.0043 | 28.7575 | 29.7204 |  | 12.8958 | 13.1 | 15 | 25.7917 | 0
| 4.3403 | 278.814 | 42.495 | 51.242 | 45.683 | 68.612 |  | 12.9167 | 31.3057 | 27.5916 | 2.9123 | 12.0043 | 28.7327 | 29.7204 |  | 12.9167 | 13 | 15 | 25.8333 | 0
| 4.3472 | 279.269 | 42.503 | 51.254 | 45.692 | 68.62 |  | 12.9375 | 31.3373 | 27.6141 | 2.9583 | 12.0374 | 28.6988 | 29.7453 |  | 12.9375 | 12.8 | 15 | 25.875 | 0
| 4.3542 | 278.41 | 42.513 | 51.266 | 45.707 | 68.627 |  | 12.9583 | 31.2951 | 27.5856 | 2.885 | 11.9875 | 28.6251 | 29.6918 |  | 12.9583 | 12.5 | 15 | 25.9167 | 0
| 4.3611 | 277.976 | 42.519 | 51.28 | 45.722 | 68.628 |  | 12.9792 | 31.2553 | 27.5572 | 2.8373 | 11.9706 | 28.696 | 29.6838 |  | 12.9792 | 12.3 | 15 | 25.9583 | 0
| 4.3681 | 277.476 | 42.522 | 51.287 | 45.729 | 68.625 |  | 13 | 31.241 | 27.5475 | 2.8236 | 11.9633 | 28.6817 | 29.6808 |  | 13 | 11.9 | 15 | 26 | 0
| 4.375 | 277.448 | 42.526 | 51.29 | 45.737 | 68.624 |  | 13.0208 | 31.2438 | 27.5526 | 2.8074 | 11.9665 | 28.6734 | 29.6725 |  | 13.0208 | 11.4 | 15 | 26.0417 | 0
| 4.3819 | 276.738 | 42.527 | 51.296 | 45.744 | 68.61 |  | 13.0417 | 31.2192 | 27.5348 | 2.6231 | 11.9468 | 28.6623 | 29.6637 |  | 13.0417 | 10.8 | 15 | 26.0833 | 0
| 4.3889 | 279.784 | 42.532 | 51.296 | 45.747 | 68.605 |  | 13.0625 | 31.1942 | 27.5145 | 2.5034 | 11.9362 | 28.6511 | 29.657 |  | 13.0625 | 10.3 | 15 | 26.125 | 0
| 4.3958 | 280.671 | 42.552 | 51.319 | 45.766 | 68.632 |  | 13.0833 | 31.2258 | 27.5483 | 2.3498 | 11.9628 | 28.6692 | 29.6796 |  | 13.0833 | 10 | 15 | 26.1667 | 4.4
| 4.4028 | 280.136 | 42.581 | 51.346 | 45.791 | 68.683 |  | 13.1042 | 31.1979 | 27.5205 | 2.1716 | 11.9312 | 28.63 | 29.654 |  | 13.1042 | 9.6 | 15 | 26.2083 | 0.9
| 4.4097 | 278.598 | 42.607 | 51.371 | 45.815 | 68.724 |  | 13.125 | 31.182 | 27.5024 | 2.0336 | 11.9245 | 28.6232 | 29.6495 |  | 13.125 | 9.4 | 15 | 26.25 | 0
| 4.4167 | 277.995 | 42.624 | 51.394 | 45.832 | 68.749 |  | 13.1458 | 31.2114 | 27.5361 | 1.9481 | 11.9511 | 28.6526 | 29.6835 |  | 13.1458 | 8.5 | 15 | 26.2917 | 0
| 4.4236 | 277.041 | 42.632 | 51.403 | 45.845 | 68.757 |  | 13.1667 | 31.1644 | 27.5029 | 1.9054 | 11.9143 | 28.6103 | 29.6456 |  | 13.1667 | 8.6 | 15 | 26.3333 | 0
| 4.4306 | 276.22 | 42.634 | 51.402 | 45.848 | 68.756 |  | 13.1875 | 31.1644 | 27.5006 | 1.8769 | 11.9188 | 28.617 | 29.6478 |  | 13.1875 | 8.6 | 15 | 26.375 | 0.1
| 4.4375 | 275.396 | 42.637 | 51.41 | 45.857 | 68.749 |  | 13.2083 | 31.1553 | 27.4938 | 1.8659 | 11.9143 | 28.6057 | 29.641 |  | 13.2083 | 8.5 | 15 | 26.4167 | 2.2
| 4.4444 | 275.717 | 42.634 | 51.412 | 45.857 | 68.736 |  | 13.2292 | 31.1372 | 27.4736 | 1.833 | 11.9054 | 28.5741 | 29.6252 |  | 13.2292 | 8 | 15 | 26.4583 | 0
| 4.4514 | 276.399 | 42.643 | 51.417 | 45.863 | 68.733 |  | 13.25 | 31.1499 | 27.4974 | 1.8492 | 11.9131 | 28.5957 | 29.6378 |  | 13.25 | 8.8 | 15 | 26.5 | 0
| 4.4583 | 276.444 | 42.653 | 51.425 | 45.871 | 68.743 |  | 13.2708 | 31.1319 | 27.475 | 1.8229 | 11.8954 | 28.5889 | 29.6287 |  | 13.2708 | 9.1 | 15 | 26.5417 | 0
| 4.4653 | 276.44 | 42.656 | 51.436 | 45.883 | 68.749 |  | 13.2917 | 31.1427 | 27.4992 | 1.8293 | 11.9017 | 28.575 | 29.6508 |  | 13.2917 | 9.2 | 15 | 26.5833 | 0
| 4.4722 | 275.267 | 42.663 | 51.437 | 45.891 | 68.744 |  | 13.3125 | 31.1502 | 27.5045 | 1.8363 | 11.9155 | 28.6139 | 29.6605 |  | 13.3125 | 9.3 | 15 | 26.625 | 0
| 4.4792 | 275.605 | 42.669 | 51.445 | 45.891 | 68.744 |  | 13.3333 | 30.774 | 27.1366 | 1.3685 | 11.5687 | 28.2519 | 29.3224 |  | 13.3333 | 9.5 | 15 | 26.6667 | 0
| 4.4861 | 274.89 | 42.669 | 51.446 | 45.896 | 68.737 |  | 13.3542 | 30.8733 | 27.2379 | 1.4802 | 11.6684 | 28.006 | 29.4107 |  | 13.3542 | 9.6 | 15 | 26.7083 | 0
| 4.4931 | 274.747 | 42.67 | 51.442 | 45.895 | 68.727 |  | 13.375 | 31.1153 | 27.4832 | 1.7648 | 11.9143 | 28.5949 | 29.6504 |  | 13.375 | 9.2 | 15 | 26.75 | 0
| 4.5 | 274.647 | 42.67 | 51.44 | 45.894 | 68.713 |  | 13.3958 | 31.1365 | 27.5246 | 1.8091 | 11.9237 | 28.7604 | 29.6873 |  | 13.3958 | 9.1 | 15 | 26.7917 | 0
| 4.5069 | 274.411 | 42.664 | 51.435 | 45.902 | 68.696 |  | 13.4167 | 30.8783 | 27.2765 | 1.5058 | 11.6946 | 28.5386 | 29.4672 |  | 13.4167 | 10.7 | 15 | 26.8333 | 0
| 4.5139 | 274.084 | 42.67 | 51.437 | 45.909 | 68.69 |  | 13.4375 | 30.9459 | 27.3866 | 1.5649 | 11.7499 | 28.5882 | 29.4941 |  | 13.4375 | 10.7 | 15 | 26.875 | 0
| 4.5208 | 274.592 | 42.672 | 51.439 | 45.902 | 68.687 |  | 13.4583 | 30.9473 | 27.3835 | 1.5942 | 11.7642 | 28.6075 | 29.5294 |  | 13.4583 | 11.1 | 15 | 26.9167 | 0
| 4.5278 | 273.684 | 42.677 | 51.438 | 45.907 | 68.68 |  | 13.4792 | 31.1033 | 27.5455 | 1.7759 | 11.897 | 28.7046 | 29.6764 |  | 13.4792 | 11.6 | 15 | 26.9583 | 0
| 4.5347 | 273.247 | 42.678 | 51.439 | 45.909 | 68.671 |  | 13.5 | 30.8497 | 27.2635 | 1.4123 | 11.6398 | 28.5279 | 29.4224 |  | 13.5 | 11.7 | 15 | 27 | 0
| 4.5417 | 273.774 | 42.677 | 51.433 | 45.906 | 68.658 |  | 13.5208 | 30.8564 | 27.3155 | 1.4845 | 11.6974 | 28.5167 | 29.4609 |  | 13.5208 | 12.3 | 15 | 27.0417 | 0
| 4.5486 | 273.397 | 42.68 | 51.436 | 45.909 | 68.653 |  | 13.5417 | 31.1343 | 27.5538 | 1.7453 | 11.9175 | 28.7508 | 29.7113 |  | 13.5417 | 11.9 | 15 | 27.0833 | 0
| 4.5556 | 274.049 | 42.683 | 51.433 | 45.908 | 68.651 |  | 13.5625 | 31.0619 | 27.5402 | 1.7037 | 11.8843 | 28.7034 | 29.6728 |  | 13.5625 | 13 | 15 | 27.125 | 0
| 4.5625 | 274.147 | 42.688 | 51.442 | 45.915 | 68.651 |  | 13.5833 | 31.1082 | 27.5548 | 1.7482 | 11.9161 | 28.7586 | 29.7055 |  | 13.5833 | 12.9 | 15 | 27.1667 | 0
| 4.5694 | 274.086 | 42.691 | 51.44 | 45.915 | 68.649 |  | 13.6042 | 31.0562 | 27.521 | 1.6737 | 11.8607 | 28.6774 | 29.6579 |  | 13.6042 | 13.6 | 15 | 27.2083 | 0
| 4.5764 | 273.922 | 42.696 | 51.443 | 45.918 | 68.658 |  | 13.625 | 31.0763 | 27.5542 | 1.7034 | 11.8954 | 28.6995 | 29.6936 |  | 13.625 | 13.7 | 15 | 27.25 | 0
| 4.5833 | 274.044 | 42.704 | 51.45 | 45.923 | 68.664 |  | 13.6458 | 31.0536 | 27.5248 | 1.6771 | 11.8799 | 28.6973 | 29.6733 |  | 13.6458 | 13.8 | 15 | 27.2917 | 0
| 4.5903 | 274.151 | 42.711 | 51.453 | 45.926 | 68.672 |  | 13.6667 | 31.0672 | 27.5519 | 1.6859 | 11.8887 | 28.7153 | 29.6913 |  | 13.6667 | 13.2 | 15 | 27.3333 | 0
| 4.5972 | 274.599 | 42.721 | 51.462 | 45.936 | 68.682 |  | 13.6875 | 31.0455 | 27.5193 | 1.6785 | 11.8788 | 28.6938 | 29.6767 |  | 13.6875 | 12.9 | 15 | 27.375 | 0
| 4.6042 | 280.754 | 42.737 | 51.476 | 45.948 | 68.708 |  | 13.7083 | 31.0794 | 27.5621 | 1.6828 | 11.901 | 28.7073 | 29.6903 |  | 13.7083 | 12.4 | 15 | 27.4167 | 0
| 4.6111 | 280.358 | 42.784 | 51.523 | 45.986 | 68.8 |  | 13.7292 | 31.0026 | 27.4993 | 1.6269 | 11.8463 | 28.649 | 29.65 |  | 13.7292 | 12.8 | 15 | 27.4583 | 0
| 4.6181 | 279.986 | 42.825 | 51.567 | 46.018 | 68.89 |  | 13.75 | 31.0106 | 27.4937 | 1.6021 | 11.8499 | 28.6569 | 29.6354 |  | 13.75 | 12.4 | 15 | 27.5 | 0
| 4.625 | 279.765 | 42.862 | 51.603 | 46.05 | 68.971 |  | 13.7708 | 31.0024 | 27.508 | 1.6004 | 11.8417 | 28.6713 | 29.6409 |  | 13.7708 | 12.3 | 15 | 27.5417 | 0
| 4.6319 | 279.621 | 42.893 | 51.638 | 46.077 | 69.042 |  | 13.7917 | 31.0409 | 27.5372 | 1.642 | 11.8772 | 28.6961 | 29.6837 |  | 13.7917 | 11.9 | 15 | 27.5833 | 0
| 4.6389 | 280.652 | 42.918 | 51.667 | 46.103 | 69.1 |  | 13.8125 | 30.9976 | 27.5168 | 1.623 | 11.8488 | 28.6554 | 29.6567 |  | 13.8125 | 12.1 | 15 | 27.625 | 0
| 4.6458 | 280.604 | 42.945 | 51.702 | 46.125 | 69.158 |  | 13.8333 | 30.9923 | 27.489 | 1.5743 | 11.8415 | 28.6705 | 29.6356 |  | 13.8333 | 11.7 | 15 | 27.6667 | 0
| 4.6528 | 280.09 | 42.974 | 51.728 | 46.154 | 69.224 |  | 13.8542 | 30.9851 | 27.4908 | 1.5412 | 11.8368 | 28.6701 | 29.633 |  | 13.8542 | 11.2 | 15 | 27.7083 | 0
| 4.6597 | 280.302 | 42.997 | 51.759 | 46.181 | 69.277 |  | 13.875 | 30.9682 | 27.4674 | 1.5077 | 11.8316 | 28.6624 | 29.6412 |  | 13.875 | 10.9 | 15 | 27.75 | 5.3
| 4.6667 | 280.679 | 43.023 | 51.788 | 46.2 | 69.332 |  | 13.8958 | 30.9607 | 27.4666 | 1.5183 | 11.82 | 28.6573 | 29.627 |  | 13.8958 | 10.7 | 15 | 27.7917 | 5.1
| 4.6736 | 280.584 | 43.043 | 51.819 | 46.224 | 69.381 |  | 13.9167 | 30.9457 | 27.4628 | 1.4822 | 11.8123 | 28.6265 | 29.6029 |  | 13.9167 | 10.2 | 15 | 27.8333 | 0.9
| 4.6806 | 281.076 | 43.065 | 51.845 | 46.252 | 69.432 |  | 13.9375 | 30.9374 | 27.4435 | 1.4596 | 11.8047 | 28.6275 | 29.6063 |  | 13.9375 | 9.8 | 15 | 27.875 | 0.1
| 4.6875 | 280.182 | 43.089 | 51.873 | 46.277 | 69.476 |  | 13.9583 | 30.9138 | 27.4401 | 1.4471 | 11.7834 | 28.5925 | 29.5939 |  | 13.9583 | 9.1 | 15 | 27.9167 | 0
| 4.6944 | 279.853 | 43.105 | 51.893 | 46.298 | 69.517 |  | 13.9792 | 30.9318 | 27.4492 | 1.4602 | 11.8166 | 28.6445 | 29.6188 |  | 13.9792 | 8.4 | 15 | 27.9583 | 0
| 4.7014 | 280.834 | 43.131 | 51.92 | 46.316 | 69.56 |  | 14 | 30.9079 | 27.4343 | 1.4068 | 11.7823 | 28.6295 | 29.5903 |  | 14 | 8.3 | 15 | 28 | 0
| 4.7083 | 281.103 | 43.145 | 51.945 | 46.342 | 69.596 |  | 14.0208 | 30.8798 | 27.4132 | 1.3648 | 11.7663 | 28.6017 | 29.5602 |  | 14.0208 | 8.1 | 15 | 28.0417 | 0
| 4.7153 | 279.948 | 43.167 | 51.971 | 46.36 | 69.637 |  | 14.0417 | 30.8726 | 27.4105 | 1.3536 | 11.7593 | 28.6149 | 29.5554 |  | 14.0417 | 7.7 | 15 | 28.0833 | 0
| 4.7222 | 280.347 | 43.185 | 51.993 | 46.386 | 69.679 |  | 14.0625 | 30.8161 | 27.3544 | 1.1641 | 11.6204 | 28.4909 | 29.4788 |  | 14.0625 | 7.1 | 15 | 28.125 | 0
| 4.7292 | 280.304 | 43.201 | 52.016 | 46.402 | 69.714 |  | 14.0833 | 30.6138 | 27.1866 | 1.0728 | 11.5592 | 28.3724 | 29.3623 |  | 14.0833 | 5.6 | 15 | 28.1667 | 0
| 4.7361 | 280.487 | 43.218 | 52.042 | 46.427 | 69.754 |  | 14.1042 | 30.8241 | 27.4028 | 1.2894 | 11.7231 | 28.6005 | 29.5433 |  | 14.1042 | 6 | 15 | 28.2083 | 0
| 4.7431 | 280.705 | 43.241 | 52.062 | 46.446 | 69.787 |  | 14.125 | 30.4767 | 27.0681 | 0.84471 | 11.4165 | 28.2402 | 29.2026 |  | 14.125 | 5.9 | 15 | 28.25 | 8.8
| 4.75 | 280.406 | 43.254 | 52.085 | 46.461 | 69.82 |  | 14.1458 | 30.8113 | 27.3451 | 1.1444 | 11.647 | 28.4299 | 29.4562 |  | 14.1458 | 5.1 | 15 | 28.2917 | 0
| 4.7569 | 280.282 | 43.266 | 52.108 | 46.478 | 69.848 |  | 14.1667 | 30.7277 | 27.2707 | 1.1313 | 11.6071 | 28.4457 | 29.4041 |  | 14.1667 | 4.2 | 15 | 28.3333 | 0
| 4.7639 | 280.65 | 43.286 | 52.13 | 46.496 | 69.88 |  | 14.1875 | 30.5378 | 27.1401 | 0.91685 | 11.6027 | 28.4005 | 29.3633 |  | 14.1875 | 4.9 | 15 | 28.375 | 0
| 4.7708 | 280.806 | 43.297 | 52.146 | 46.513 | 69.91 |  | 14.2083 | 30.5289 | 26.9715 | 0.78147 | 11.3724 | 28.1456 | 29.0695 |  | 14.2083 | 4.9 | 15 | 28.4167 | 0
| 4.7778 | 279.784 | 43.311 | 52.169 | 46.535 | 69.934 |  | 14.2292 | 29.9949 | 26.5725 | 0.34394 | 11.0288 | 28.0388 | 28.9694 |  | 14.2292 | 3.7 | 15 | 28.4583 | 0
| 4.7847 | 279.967 | 43.325 | 52.184 | 46.548 | 69.957 |  | 14.25 | 30.6071 | 27.0787 | 0.88821 | 11.4872 | 28.3774 | 29.4331 |  | 14.25 | 2.7 | 15 | 28.5 | 0
| 4.7917 | 280.273 | 43.339 | 52.196 | 46.559 | 69.979 |  | 14.2708 | 30.58 | 27.2048 | 0.89037 | 11.5492 | 28.2036 | 29.3177 |  | 14.2708 | 2.7 | 15 | 28.5417 | 0
| 4.7986 | 280.767 | 43.349 | 52.21 | 46.573 | 70 |  | 14.2917 | 30.428 | 26.9678 | 0.49664 | 11.2542 | 28.0744 | 28.989 |  | 14.2917 | 4.4 | 15 | 28.5833 | 0
| 4.8056 | 279.992 | 43.364 | 52.227 | 46.592 | 70.027 |  | 14.3125 | [7 empty] | 14.3125 | 5.9 | 15 | 28.625 | 0
| 4.8125 | 280.584 | 43.375 | 52.24 | 46.609 | 70.05 |  | 14.3333 | [7 empty] | 14.3333 | 6.7 | 15 | 28.6667 | 0
| 4.8194 | 280.488 | 43.387 | 52.26 | 46.624 | 70.07 |  | 14.3542 | [7 empty] | 14.3542 | 7.2 | 15 | 28.7083 | 0
| 4.8264 | 280.85 | 43.398 | 52.274 | 46.634 | 70.097 |  | 14.375 | 30.3693 | 26.9272 | 0.51657 | 11.3167 | 28.1864 | 29.3269 |  | 14.375 | 7.8 | 15 | 28.75 | 0
| 4.8333 | 281.236 | 43.416 | 52.299 | 46.654 | 70.123 |  | 14.3958 | 30.3319 | 26.9102 | 0.54351 | 11.2777 | 28.1287 | 29.1494 |  | 14.3958 | 8.2 | 15 | 28.7917 | 0
| 4.8403 | 281.71 | 43.432 | 52.32 | 46.674 | 70.154 |  | 14.4167 | 30.227 | 26.784 | 0.36925 | 11.141 | 27.9804 | 28.9961 |  | 14.4167 | 8.6 | 15 | 28.8333 | 0
| 4.8472 | 282.214 | 43.453 | 52.347 | 46.698 | 70.191 |  | 14.4375 | 30.169 | 26.6608 | 0.24518 | 11.2083 | 28.038 | 29.1282 |  | 14.4375 | 9.2 | 15 | 28.875 | 1.2
| 4.8542 | 282.697 | 43.474 | 52.376 | 46.713 | 70.236 |  | 14.4583 | 30.7107 | 27.3166 | 1.0725 | 11.6677 | 28.5404 | 29.5165 |  | 14.4583 | 10.6 | 15 | 28.9167 | 2.1
| 4.8611 | 283.21 | 43.495 | 52.402 | 46.737 | 70.28 |  | 14.4792 | 30.7242 | 27.3504 | 1.0463 | 11.7253 | 28.5427 | 29.5074 |  | 14.4792 | 11.4 | 15 | 28.9583 | 2.1
| 4.8681 | 284.117 | 43.514 | 52.428 | 46.757 | 70.321 |  | 14.5 | 30.7852 | 27.3864 | 1.0791 | 11.7342 | 28.5494 | 29.5956 |  | 14.5 | 10.9 | 15 | 29 | 10.7
| 4.875 | 283.042 | 43.533 | 52.453 | 46.787 | 70.361 |  | 14.5208 | 30.7727 | 27.3356 | 1.0929 | 11.6264 | 28.4895 | 29.531 |  | 14.5208 | 10.6 | 15 | 29.0417 | 8.2
| 4.8819 | 282.39 | 43.548 | 52.474 | 46.807 | 70.386 |  | 14.5417 | 30.7681 | 27.3874 | 1.0579 | 11.7327 | 28.5346 | 29.5671 |  | 14.5417 | 11.9 | 15 | 29.0833 | 1
| 4.8889 | 284.586 | 43.554 | 52.492 | 46.819 | 70.407 |  | 14.5625 | 30.6235 | 27.2703 | 1.036 | 11.6884 | 28.5188 | 29.531 |  | 14.5625 | 11.3 | 15 | 29.125 | 0.3
| 4.8958 | 284.601 | 43.58 | 52.531 | 46.844 | 70.451 |  | 14.5833 | 30.7885 | 27.4189 | 1.1016 | 11.7637 | 28.5595 | 29.592 |  | 14.5833 | 11.8 | 15 | 29.1667 | 0.6
| 4.9028 | 285.198 | 43.599 | 52.552 | 46.87 | 70.495 |  | 14.6042 | 30.7658 | 27.4054 | 1.06 | 11.7438 | 28.5572 | 29.5898 |  | 14.6042 | 10.5 | 15 | 29.2083 | 0
| 4.9097 | 285.131 | 43.624 | 52.58 | 46.903 | 70.544 |  | 14.625 | 30.7343 | 27.3693 | 1.0164 | 11.7128 | 28.5098 | 29.5558 |  | 14.625 | 10.8 | 15 | 29.25 | 0
| 4.9167 | 285.412 | 43.648 | 52.607 | 46.931 | 70.596 |  | 14.6458 | 30.7764 | 27.4091 | 1.0545 | 11.7538 | 28.5564 | 29.6024 |  | 14.6458 | 11.6 | 15 | 29.2917 | 0
| 4.9236 | 285.739 | 43.674 | 52.638 | 46.954 | 70.642 |  | 14.6667 | 30.772 | 27.4091 | 1.0589 | 11.756 | 28.5564 | 29.5979 |  | 14.6667 | 12.6 | 15 | 29.3333 | 0.1
| 4.9306 | 285.795 | 43.696 | 52.672 | 46.981 | 70.691 |  | 14.6875 | 30.785 | 27.4153 | 1.0402 | 11.755 | 28.567 | 29.6152 |  | 14.6875 | 11.9 | 15 | 29.375 | 1.3
| 4.9375 | 286.928 | 43.717 | 52.712 | 47.002 | 70.742 |  | 14.7083 | 30.7895 | 27.4401 | 1.0971 | 11.7749 | 28.5738 | 29.6424 |  | 14.7083 | 13.3 | 15 | 29.4167 | 1.1
| 4.9444 | 280.455 | 43.745 | 52.748 | 47.038 | 70.797 |  | 14.7292 | 30.6637 | 27.2346 | 0.96157 | 11.6952 | 28.5151 | 29.5474 |  | 14.7292 | 12.1 | 15 | 29.4583 | 0
| 4.9514 | 281 | 43.737 | 52.744 | 47.035 | 70.78 |  | 14.75 | 30.7168 | 27.3902 | 0.99635 | 11.7193 | 28.5192 | 29.5788 |  | 14.75 | 12.7 | 15 | 29.5 | 0
| 4.9583 | 278.603 | 43.715 | 52.739 | 47.031 | 70.747 |  | 14.7708 | 30.7157 | 27.2721 | 0.95192 | 11.7384 | 28.5453 | 29.5733 |  | 14.7708 | 12.2 | 15 | 29.5417 | 0
| 4.9653 | 278.598 | 43.702 | 52.727 | 47.027 | 70.694 |  | 14.7917 | 30.7003 | 27.3626 | 0.94207 | 11.715 | 28.5257 | 29.5672 |  | 14.7917 | 11.7 | 15 | 29.5833 | 0
| 4.9722 | 279.833 | 43.686 | 52.717 | 47.014 | 70.652 |  | 14.8125 | 30.698 | 27.367 | 0.87632 | 11.7083 | 28.5142 | 29.5558 |  | 14.8125 | 11.3 | 15 | 29.625 | 0
| 4.9792 | 279.888 | 43.679 | 52.718 | 47.021 | 70.629 |  | 14.8333 | 30.6884 | 27.3552 | 0.90657 | 11.7013 | 28.4913 | 29.5509 |  | 14.8333 | 10.8 | 15 | 29.6667 | 0
| 4.9861 | 280.526 | 43.679 | 52.721 | 47.021 | 70.619 |  | 14.8542 | 30.5932 | 27.2918 | 0.82546 | 11.6434 | 28.466 | 29.5053 |  | 14.8542 | 10.3 | 15 | 29.7083 | 0
| 4.9931 | 279.551 | 43.679 | 52.726 | 47.032 | 70.614 |  | 14.875 | 30.7129 | 27.3886 | 0.9369 | 11.7364 | 28.5428 | 29.5936 |  | 14.875 | 9.9 | 15 | 29.75 | 0
| 5 | 281.165 | 43.685 | 52.731 | 47.037 | 70.605 |  | 14.8958 | 30.6514 | 27.3296 | 0.83391 | 11.6808 | 28.4973 | 29.5119 |  | 14.8958 | 9.3 | 15 | 29.7917 | 0
| 5.0069 | 278.56 | 43.681 | 52.727 | 47.032 | 70.594 |  | 14.9167 | 30.665 | 27.3544 | 0.87325 | 11.7052 | 28.5312 | 29.5798 |  | 14.9167 | 9.2 | 15 | 29.8333 | 0
| 5.0139 | 278.784 | 43.672 | 52.724 | 47.028 | 70.569 |  | 14.9375 | 30.6133 | 27.3052 | 0.7854 | 11.6555 | 28.4797 | 29.5057 |  | 14.9375 | 9.2 | 15 | 29.875 | 0
| 5.0208 | 279.25 | 43.672 | 52.726 | 47.035 | 70.555 |  | 14.9583 | 30.6472 | 27.3459 | 0.84444 | 11.6777 | 28.4933 | 29.5464 |  | 14.9583 | 8.5 | 15 | 29.9167 | 0
| 5.0278 | 279.478 | 43.68 | 52.731 | 47.032 | 70.553 |  | 14.9792 | 30.6206 | 27.3126 | 0.77266 | 11.6626 | 28.4871 | 29.5063 |  | 14.9792 | 8.2 | 15 | 29.9583 | 0
| 5.0347 | 279.425 | 43.686 | 52.74 | 47.039 | 70.548 |  | 15 | 30.4444 | 27.1415 | 0.56069 | 11.4854 | 28.284 | 29.3389 |  | 15 | 8.1 | 15 | 30 | 0
| 5.0417 | 280.252 | 43.688 | 52.748 | 47.048 | 70.561 |  | 15.0208 | 30.6161 | 27.2991 | 0.75953 | 11.647 | 28.4691 | 29.4995 |  | 15.0208 | 8.4 | 14.4 | 30.0417 | 0
| 5.0486 | 280.919 | 43.7 | 52.759 | 47.062 | 70.566 |  | 15.0417 | 30.6116 | 27.3081 | 0.74198 | 11.6493 | 28.4081 | 29.4271 |  | 15.0417 | 8.5 | 14.4 | 30.0833 | 0
| 5.0556 | 277.933 | 43.711 | 52.777 | 47.069 | 70.586 |  | 15.0625 | 30.6048 | 27.3126 | 2.1516 | 11.6493 | 28.4758 | 29.4973 |  | 15.0625 | 8.4 | 14.4 | 30.125 | 0
| 5.0625 | 278.105 | 43.707 | 52.794 | 47.074 | 70.579 |  | 15.0833 | 30.6025 | 27.3058 | 0.82286 | 11.6537 | 28.4668 | 29.4882 |  | 15.0833 | 8.2 | 14.4 | 30.1667 | 0
| 5.0694 | 281.793 | 43.708 | 52.783 | 47.073 | 70.56 |  | 15.1042 | 30.6139 | 27.3328 | 0.81635 | 11.6692 | 28.4894 | 29.5085 |  | 15.1042 | 7.8 | 14.4 | 30.2083 | 0
| 5.0764 | 281.281 | 43.721 | 52.8 | 47.084 | 70.581 |  | 15.125 | 30.5889 | 27.3283 | 0.98676 | 11.6692 | 28.4826 | 29.5199 |  | 15.125 | 7.6 | 14.4 | 30.25 | 0
| 5.0833 | 281.149 | 43.74 | 52.821 | 47.099 | 70.613 |  | 15.1458 | 30.2931 | 27.0357 | 0.73325 | 11.4036 | 28.2276 | 29.2598 |  | 15.1458 | 7.4 | 14.4 | 30.2917 | 0
| 5.0903 | 281.445 | 43.756 | 52.839 | 47.112 | 70.639 |  | 15.1667 | 30.4917 | 27.2022 | 1.0043 | 11.523 | 28.4262 | 29.4204 |  | 15.1667 | 7.2 | 14.4 | 30.3333 | 0
| 5.0972 | 281.063 | 43.774 | 52.864 | 47.133 | 70.674 |  | 15.1875 | 30.5935 | 27.3148 | 1.1093 | 11.6538 | 28.5119 | 29.5017 |  | 15.1875 | 7 | 14.4 | 30.375 | 0
| 5.1042 | 281.487 | 43.79 | 52.894 | 47.149 | 70.702 |  | 15.2083 | 30.5708 | 27.3035 | 1.0546 | 11.6515 | 28.46 | 29.4927 |  | 15.2083 | 7 | 14.4 | 30.4167 | 0
| 5.1111 | 281.609 | 43.803 | 52.903 | 47.168 | 70.731 |  | 15.2292 | 30.5685 | 27.3035 | 1.0196 | 11.6471 | 28.4691 | 29.4859 |  | 15.2292 | 7 | 14.4 | 30.4583 | 0
| 5.1181 | 281.865 | 43.816 | 52.925 | 47.183 | 70.754 |  | 15.25 | 30.5528 | 27.2472 | 0.9562 | 11.6294 | 28.293 | 29.4747 |  | 15.25 | 7.1 | 14.4 | 30.5 | 0
| 5.125 | 281.886 | 43.833 | 52.941 | 47.195 | 70.78 |  | 15.2708 | 30.5528 | 27.2472 | 0.93435 | 11.636 | 28.3066 | 29.4815 |  | 15.2708 | 7.1 | 14.4 | 30.5417 | 0
| 5.1319 | 282.151 | 43.844 | 52.963 | 47.215 | 70.807 |  | 15.2917 | 30.5475 | 27.2285 | 0.83332 | 11.6155 | 28.2923 | 29.4672 |  | 15.2917 | 7.2 | 14.4 | 30.5833 | 0
| 5.1389 | 281.507 | 43.861 | 52.985 | 47.234 | 70.832 |  | 15.3125 | 30.5361 | 27.2353 | 0.79398 | 11.6178 | 28.281 | 29.4762 |  | 15.3125 | 7.1 | 14.4 | 30.625 | 0
| 5.1458 | 281.709 | 43.871 | 53.01 | 47.25 | 70.851 |  | 15.3333 | 30.4481 | 27.1362 | 0.72397 | 11.5447 | 28.2337 | 29.4174 |  | 15.3333 | 7.2 | 14.4 | 30.6667 | 0
| 5.1528 | 281.814 | 43.885 | 53.024 | 47.261 | 70.873 |  | 15.3542 | 30.5092 | 27.2196 | 0.75029 | 11.6067 | 28.2585 | 29.449 |  | 15.3542 | 7.3 | 14.4 | 30.7083 | 0
| 5.1597 | 281.611 | 43.894 | 53.046 | 47.281 | 70.891 |  | 15.375 | 30.4798 | 27.1904 | 0.68695 | 11.5824 | 28.2382 | 29.4286 |  | 15.375 | 7.6 | 14.4 | 30.75 | 0
| 5.1667 | 281.453 | 43.911 | 53.066 | 47.296 | 70.913 |  | 15.3958 | 30.5014 | 27.2231 | 0.67897 | 11.6009 | 28.3882 | 29.4569 |  | 15.3958 | 7.9 | 14.4 | 30.7917 | 0
| 5.1736 | 281.554 | 43.92 | 53.085 | 47.31 | 70.936 |  | 15.4167 | 30.5186 | 27.2941 | 0.67558 | 11.6196 | 28.4233 | 29.4806 |  | 15.4167 | 8.8 | 14.4 | 30.8333 | 0
| 5.1806 | 281.205 | 43.931 | 53.102 | 47.325 | 70.947 |  | 15.4375 | 30.5008 | 27.2764 | 0.64309 | 11.6176 | 28.4417 | 29.4808 |  | 15.4375 | 9.6 | 14.4 | 30.875 | 0
| 5.1875 | 281.131 | 43.941 | 53.117 | 47.337 | 70.962 |  | 15.4583 | 30.5105 | 27.2816 | 0.68054 | 11.6158 | 28.4353 | 29.4903 |  | 15.4583 | 9.4 | 14.4 | 30.9167 | 0
| 5.1944 | 280.356 | 43.946 | 53.13 | 47.348 | 70.969 |  | 15.4792 | 30.4811 | 27.2569 | 0.61941 | 11.5892 | 28.3925 | 29.4473 |  | 15.4792 | 9.8 | 14.4 | 30.9583 | 0
| 5.2014 | 280.47 | 43.95 | 53.148 | 47.36 | 70.974 |  | 15.5 | 30.4965 | 27.2827 | 0.54074 | 11.5852 | 28.3891 | 29.4483 |  | 15.5 | 10.3 | 14.4 | 31 | 0
| 5.2083 | 280.59 | 43.959 | 53.152 | 47.37 | 70.984 |  | 15.5208 | 30.3594 | 27.1416 | 0.41295 | 11.4916 | 28.2731 | 29.3569 |  | 15.5208 | 10.8 | 14.4 | 31.0417 | 0
| 5.2153 | 279.589 | 43.964 | 53.169 | 47.379 | 70.986 |  | 15.5417 | 30.4993 | 27.2876 | 0.55541 | 11.6186 | 28.4033 | 29.4874 |  | 15.5417 | 11.2 | 14.4 | 31.0833 | 0
| 5.2222 | 279.156 | 43.967 | 53.173 | 47.384 | 70.976 |  | 15.5625 | 30.5029 | 27.2845 | 0.50896 | 11.6112 | 28.2851 | 29.4684 |  | 15.5625 | 12.7 | 14.4 | 31.125 | 0
| 5.2292 | 279.96 | 43.964 | 53.178 | 47.389 | 70.967 |  | 15.5833 | 30.5097 | 27.307 | 0.49583 | 11.6488 | 28.4453 | 29.5204 |  | 15.5833 | 11.4 | 14.4 | 31.1667 | 0
| 5.2361 | 280.575 | 43.966 | 53.184 | 47.393 | 70.964 |  | 15.6042 | 30.5029 | 27.3115 | 0.49804 | 11.6378 | 28.4069 | 29.5091 |  | 15.6042 | 11.4 | 14.4 | 31.2083 | 0
| 5.2431 | 280.338 | 43.978 | 53.198 | 47.403 | 70.975 |  | 15.625 | 30.4916 | 27.2596 | 0.45202 | 11.6156 | 28.3438 | 29.378 |  | 15.625 | 12 | 14.4 | 31.25 | 0
| 5.25 | 279.969 | 43.988 | 53.212 | 47.416 | 70.984 |  | 15.6458 | 30.4631 | 27.2606 | 0.44897 | 11.597 | 28.3718 | 29.4489 |  | 15.6458 | 12.6 | 14.4 | 31.2917 | 0
| 5.2569 | 278.229 | 43.996 | 53.219 | 47.432 | 70.99 |  | 15.6667 | 30.2862 | 27.0618 | 0.25832 | 11.4132 | 28.2049 | 29.2839 |  | 15.6667 | 12.2 | 14.4 | 31.3333 | 0
| 5.2639 | 276.937 | 43.993 | 53.219 | 47.426 | 70.978 |  | 15.6875 | 30.4606 | 27.267 | 0.44361 | 11.5987 | 28.3944 | 29.467 |  | 15.6875 | 12.5 | 14.4 | 31.375 | 0
| 5.2708 | 276.689 | 43.975 | 53.214 | 47.419 | 70.941 |  | 15.7083 | 30.2759 | 27.0919 | 0.19449 | 11.4469 | 28.2579 | 29.3143 |  | 15.7083 | 13.2 | 14.4 | 31.4167 | 0.1
| 5.2778 | 279.735 | 43.982 | 53.218 | 47.425 | 70.931 |  | 15.7292 | 30.2147 | 27.0355 | 0.15288 | 11.385 | 28.1745 | 29.2646 |  | 15.7292 | 13.7 | 14.4 | 31.4583 | 0.3
| 5.2847 | 279.005 | 43.991 | 53.228 | 47.435 | 70.945 |  | 15.75 | 30.4254 | 27.2567 | 0.4924 | 11.604 | 28.3909 | 29.4636 |  | 15.75 | 14.3 | 14.4 | 31.5 | 0.4
| 5.2917 | 280.681 | 44.002 | 53.319 | 47.445 | 70.956 |  | 15.7708 | 30.4221 | 27.2603 | 0.48743 | 11.5831 | 28.374 | 29.4648 |  | 15.7708 | 12.8 | 14.4 | 31.5417 | 0
| 5.2986 | 279.902 | 44.014 | 53.335 | 47.456 | 70.978 |  | 15.7917 | 30.4331 | 27.2894 | 0.53334 | 11.6028 | 28.3668 | 29.4848 |  | 15.7917 | 12.8 | 14.4 | 31.5833 | 0.3
| 5.3056 | 279.902 | 44.024 | 53.345 | 47.472 | 70.995 |  | 15.8125 | 30.1852 | 27.0288 | 0.21943 | 11.3716 | 28.1132 | 29.2215 |  | 15.8125 | 12.7 | 14.4 | 31.625 | 0.4
| 5.3125 | 280.497 | 44.037 | 53.351 | 47.483 | 71.012 |  | 15.8333 | 30.1853 | 27.0268 | 0.81341 | 11.3766 | 28.1358 | 29.2374 |  | 15.8333 | 12 | 14.4 | 31.6667 | 1.4
| 5.3194 | 279.597 | 44.052 | 53.323 | 47.496 | 71.031 |  | 15.8542 | 30.1873 | 27.0446 | 1.2678 | 11.394 | 28.1646 | 29.2709 |  | 15.8542 | 11.6 | 14.4 | 31.7083 | 0
| 5.3264 | 281.793 | 44.058 | 53.313 | 47.505 | 71.042 |  | 15.875 | 30.194 | 27.0534 | 1.274 | 11.3959 | 28.144 | 29.2684 |  | 15.875 | 10.9 | 14.4 | 31.75 | 0.6
| 5.3333 | 281.975 | 44.076 | 53.318 | 47.524 | 71.071 |  | 15.8958 | 30.2665 | 27.1437 | 1.4564 | 11.4871 | 28.2408 | 29.3408 |  | 15.8958 | 10.2 | 14.4 | 31.7917 | 0.1
| 5.3403 | 280.793 | 44.094 | 53.339 | 47.543 | 71.105 |  | 15.9167 | 30.3246 | 27.2111 | 1.5723 | 11.5401 | 28.2725 | 29.3905 |  | 15.9167 | 9.3 | 14.4 | 31.8333 | 0
| 5.3472 | 280.067 | 44.105 | 53.351 | 47.556 | 71.123 |  | 15.9375 | 30.3308 | 27.2084 | 1.5728 | 11.5448 | 28.315 | 29.4016 |  | 15.9375 | 8.2 | 14.4 | 31.875 | 0
| 5.3542 | 279.805 | 44.112 | 53.363 | 47.565 | 71.135 |  | 15.9583 | 30.2853 | 27.127 | 1.4478 | 11.5091 | 28.2403 | 29.3133 |  | 15.9583 | 7.3 | 14.4 | 31.9167 | 0
| 5.3611 | 279.317 | 44.118 | 53.371 | 47.572 | 71.137 |  | 15.9792 | 30.2837 | 27.166 | 1.5017 | 11.4859 | 28.2728 | 29.3664 |  | 15.9792 | 6.1 | 14.4 | 31.9583 | 0.1
| 5.3681 | 278.893 | 44.123 | 53.38 | 47.581 | 71.141 |  | 16 | 30.1348 | 27.0175 | 1.3265 | 11.3531 | 28.1285 | 29.2331 |  | 16 | 5.4 | 14.4 | 32 | 0.1
| 5.375 | 279.568 | 44.125 | 53.386 | 47.584 | 71.138 |  | 16.0208 | 30.1506 | 27.0288 | 1.3528 | 11.3665 | 28.2007 | 29.2535 |  | 16.0208 | 5.2 | 14.4 | 32.0417 | 0
| 5.3819 | 278.928 | 44.129 | 53.391 | 47.589 | 71.136 |  | 16.0417 | 30.18 | 27.0694 | 1.4426 | 11.455 | 28.2098 | 29.2851 |  | 16.0417 | 5.7 | 14.4 | 32.0833 | 0
| 5.3889 | 278.773 | 44.135 | 53.403 | 47.603 | 71.139 |  | 16.0625 | 30.0784 | 26.9591 | 1.2718 | 11.3043 | 28.0855 | 29.1627 |  | 16.0625 | 6.1 | 14.4 | 32.125 | 0
| 5.3958 | 278.497 | 44.138 | 53.407 | 47.604 | 71.135 |  | 16.0833 | 30.0174 | 26.9006 | 1.1886 | 11.249 | 28.0156 | 29.1108 |  | 16.0833 | 6.4 | 14.4 | 32.1667 | 0
| 5.4028 | 277.175 | 44.136 | 53.411 | 47.608 | 71.122 |  | 16.1042 | 30.1348 | 27.0153 | 1.3987 | 11.3685 | 28.1058 | 29.1718 |  | 16.1042 | 6.3 | 14.4 | 32.2083 | 0
| 5.4097 | 276.004 | 44.133 | 53.406 | 47.602 | 71.095 |  | 16.125 | 30.1348 | 26.9951 | 1.3899 | 11.3752 | 28.1238 | 29.2284 |  | 16.125 | 6.2 | 14.4 | 32.25 | 0.4
| 5.4167 | 275.073 | 44.12 | 53.395 | 47.601 | 71.064 |  | 16.1458 | 30.0806 | 26.9546 | 1.3243 | 11.3021 | 28.0471 | 29.1538 |  | 16.1458 | 6.1 | 14.4 | 32.2917 | 0.1
| 5.4236 | 275.308 | 44.113 | 53.388 | 47.591 | 71.034 |  | 16.1667 | 30.1416 | 27.0176 | 1.4096 | 11.3818 | 28.1397 | 29.2351 |  | 16.1667 | 6.1 | 14.4 | 32.3333 | 0
| 5.4306 | 274.149 | 44.103 | 53.375 | 47.58 | 70.998 |  | 16.1875 | 30.1483 | 27.0424 | 1.4184 | 11.3995 | 28.1419 | 29.2418 |  | 16.1875 | 6.1 | 14.4 | 32.375 | 0
| 5.4375 | 277.021 | 44.094 | 53.367 | 47.574 | 70.961 |  | 16.2083 | 30.2071 | 27.0986 | 1.5038 | 11.4527 | 28.1893 | 29.303 |  | 16.2083 | 6.1 | 14.4 | 32.4167 | 0
| 5.4444 | 277.864 | 44.101 | 53.375 | 47.577 | 70.966 |  | 16.2292 | 30.2409 | 27.1414 | 1.5147 | 11.4792 | 28.2141 | 29.3482 |  | 16.2292 | 6 | 14.4 | 32.4583 | 0
| 5.4514 | 276.883 | 44.115 | 53.386 | 47.596 | 70.983 |  | 16.25 | 30.2749 | 27.1708 | 1.3638 | 11.517 | 28.2864 | 29.3889 |  | 16.25 | 6.2 | 14.4 | 32.5 | 0
| 5.4583 | 276.78 | 44.128 | 53.391 | 47.599 | 70.996 |  | 16.2708 | 30.2499 | 27.1481 | 1.2455 | 11.5013 | 28.2704 | 29.3593 |  | 16.2708 | 6.7 | 14.4 | 32.5417 | 0
| 5.4653 | 276.334 | 44.132 | 53.393 | 47.599 | 70.996 |  | 16.2917 | 29.9192 | 26.8409 | 0.8352 | 11.1923 | 27.9647 | 29.0664 |  | 16.2917 | 7.4 | 14.4 | 32.5833 | 0
| 5.4722 | 276.681 | 44.139 | 53.4 | 47.601 | 70.997 |  | 16.3125 | 29.9558 | 26.8819 | 0.90973 | 11.2236 | 27.9898 | 29.1073 |  | 16.3125 | 7.9 | 14.4 | 32.625 | 0
| 5.4792 | 275.593 | 44.14 | 53.406 | 47.604 | 71 |  | 16.3333 | 29.9452 | 26.8644 | 0.91049 | 11.2132 | 27.993 | 29.09 |  | 16.3333 | 8.4 | 14.4 | 32.6667 | 0
| 5.4861 | 275.516 | 44.14 | 53.403 | 47.608 | 70.99 |  | 16.3542 | 30.2679 | 27.2083 | 1.3727 | 11.5241 | 28.2581 | 29.4372 |  | 16.3542 | 9.1 | 14.4 | 32.7083 | 0
| 5.4931 | 275.221 | 44.139 | 53.398 | 47.604 | 70.969 |  | 16.375 | 30.291 | 27.1999 | 1.3993 | 11.5201 | 28.2812 | 29.3856 |  | 16.375 | 9.9 | 14.4 | 32.75 | 0
| 5.5 | 274.999 | 44.139 | 53.414 | 47.599 | 70.961 |  | 16.3958 | 30.082 | 27.0345 | 1.2168 | 11.3645 | 28.1209 | 29.2474 |  | 16.3958 | 10.6 | 14.4 | 32.7917 | 0
| 5.5069 | 275.42 | 44.138 | 53.411 | 47.599 | 70.948 |  | 16.4167 | 30.2958 | 27.2407 | 1.3027 | 11.5488 | 28.1103 | 29.2164 |  | 16.4167 | 11.3 | 14.4 | 32.8333 | 0
| 5.5139 | 274.936 | 44.139 | 53.396 | 47.599 | 70.938 |  | 16.4375 | 30.0279 | 26.9871 | 1.199 | 11.3223 | 28.0761 | 29.191 |  | 16.4375 | 12.4 | 14.4 | 32.875 | 0
| 5.5208 | 274.989 | 44.146 | 53.399 | 47.603 | 70.935 |  | 16.4583 | 30.0132 | 26.9611 | 1.2327 | 11.3057 | 28.055 | 29.1946 |  | 16.4583 | 13.4 | 14.4 | 32.9167 | 0
| 5.5278 | 274.933 | 44.142 | 53.397 | 47.604 | 70.925 |  | 16.4792 | 30.0421 | 27.0191 | 1.306 | 11.3491 | 28.1063 | 29.246 |  | 16.4792 | 13.9 | 14.4 | 32.9583 | 0
| 5.5347 | 273.892 | 44.137 | 53.395 | 47.6 | 70.916 |  | 16.5 | 30.3328 | 27.2931 | 1.567 | 11.5867 | 28.3012 | 29.4616 |  | 16.5 | 14.4 | 14.4 | 33 | 0
| 5.5417 | 274.814 | 44.135 | 53.39 | 47.595 | 70.898 |  | 16.5208 | 30.1358 | 27.1171 | 1.4073 | 11.454 | 28.1952 | 29.317 |  | 16.5208 | 14.7 | 14.4 | 33.0417 | 0
| 5.5486 | 274.84 | 44.135 | 53.391 | 47.592 | 70.888 |  | 16.5417 | 30.2626 | 27.2164 | 1.556 | 11.5358 | 28.2966 | 29.4119 |  | 16.5417 | 15.3 | 14.4 | 33.0833 | 0
| 5.5556 | 274.96 | 44.141 | 53.39 | 47.596 | 70.881 |  | 16.5625 | 30.2671 | 27.248 | 1.567 | 11.5557 | 28.2876 | 29.439 |  | 16.5625 | 15 | 14.4 | 33.125 | 0
| 5.5625 | 274.854 | 44.146 | 53.389 | 47.592 | 70.883 |  | 16.5833 | 30.2729 | 27.2514 | 1.5941 | 11.5766 | 28.3273 | 29.4652 |  | 16.5833 | 14.7 | 14.4 | 33.1667 | 0
| 5.5694 | 274.242 | 44.148 | 53.396 | 47.599 | 70.885 |  | 16.6042 | 30.2706 | 27.2402 | 1.5438 | 11.5479 | 28.2913 | 29.429 |  | 16.6042 | 15.8 | 14.4 | 33.2083 | 0
| 5.5764 | 273.281 | 44.145 | 53.387 | 47.597 | 70.871 |  | 16.625 | 30.2495 | 27.2348 | 1.5273 | 11.5358 | 28.2794 | 29.4328 |  | 16.625 | 15.7 | 14.4 | 33.25 | 0
| 5.5833 | 273.85 | 44.14 | 53.38 | 47.595 | 70.858 |  | 16.6458 | [7 empty] | 16.6458 | 16.9 | 14.4 | 33.2917 | 0
| 5.5903 | 274.008 | 44.144 | 53.383 | 47.584 | 70.844 |  | 16.6667 | 29.9191 | 26.9324 | 1.0594 | 11.2904 | 28.0135 | 29.1482 |  | 16.6667 | 16.6 | 14.4 | 33.3333 | 0
| 5.5972 | 274.167 | 44.144 | 53.386 | 47.582 | 70.842 |  | 16.6875 | 29.9656 | 26.9494 | 1.1151 | 11.2915 | 28.0668 | 29.188 |  | 16.6875 | 17.1 | 14.4 | 33.375 | 0
| 5.6042 | 274.474 | 44.151 | 53.387 | 47.589 | 70.843 |  | 16.7083 | 30.2096 | 27.2083 | 1.466 | 11.5185 | 28.2872 | 29.436 |  | 16.7083 | 16.5 | 14.4 | 33.4167 | 0
| 5.6111 | 274.912 | 44.151 | 53.388 | 47.586 | 70.85 |  | 16.7292 | 30.0262 | 27.0346 | 1.1269 | 11.3593 | 28.1227 | 29.2688 |  | 16.7292 | 17.3 | 14.4 | 33.4583 | 0
| 5.6181 | 275.296 | 44.162 | 53.396 | 47.594 | 70.853 |  | 16.75 | 30.1666 | 27.127 | 1.3698 | 11.492 | 28.2962 | 29.4044 |  | 16.75 | 16.9 | 14.4 | 33.5 | 0
| 5.625 | 275.07 | 44.168 | 53.4 | 47.592 | 70.862 |  | 16.7708 | 30.1841 | 27.1806 | 1.4275 | 11.5019 | 28.2684 | 29.3947 |  | 16.7708 | 16.8 | 14.4 | 33.5417 | 0
| 5.6319 | 278.756 | 44.169 | 53.407 | 47.602 | 70.867 |  | 16.7917 | 30.1826 | 27.1794 | 1.3944 | 11.4878 | 28.2284 | 29.3773 |  | 16.7917 | 16.3 | 14.4 | 33.5833 | 0
| 5.6389 | 278.76 | 44.201 | 53.44 | 47.624 | 70.927 |  | 16.8125 | 30.1668 | 27.184 | 1.3904 | 11.4946 | 28.2506 | 29.3997 |  | 16.8125 | 14.1 | 14.4 | 33.625 | 0.6
| 5.6458 | 278.262 | 44.233 | 53.469 | 47.645 | 70.99 |  | 16.8333 | 29.8001 | 26.8027 | 0.95738 | 11.1361 | 27.8988 | 29.0517 |  | 16.8333 | 13.1 | 14.4 | 33.6667 | 0
| 5.6528 | 279.24 | 44.261 | 53.49 | 47.673 | 71.05 |  | 16.8542 | 29.8845 | 26.9005 | 1.1027 | 11.2432 | 27.9963 | 29.1405 |  | 16.8542 | 12.4 | 13.9 | 33.7083 | 0
| 5.6597 | 279.599 | 44.286 | 53.525 | 47.698 | 71.103 |  | 16.875 | 30.0382 | 27.0696 | 1.3787 | 11.4026 | 28.1875 | 29.3345 |  | 16.875 | 11.9 | 13.9 | 33.75 | 0
| 5.6667 | 279.678 | 44.307 | 53.551 | 47.718 | 71.155 |  | 16.8958 | 30.1785 | 27.2164 | 1.5494 | 11.5199 | 28.2552 | 29.4114 |  | 16.8958 | 11.6 | 13.9 | 33.7917 | 0
| 5.6736 | 280.392 | 44.335 | 53.576 | 47.739 | 71.212 |  | 16.9167 | 30.1303 | 27.1683 | 1.5554 | 11.4838 | 28.2227 | 29.3767 |  | 16.9167 | 11.5 | 13.9 | 33.8333 | 0
| 5.6806 | 279.183 | 44.363 | 53.607 | 47.763 | 71.271 |  | 16.9375 | 30.1234 | 27.1524 | 1.6429 | 11.4528 | 28.1957 | 29.3653 |  | 16.9375 | 12.5 | 13.9 | 33.875 | 0
| 5.6875 | 279.743 | 44.38 | 53.63 | 47.778 | 71.311 |  | 16.9583 | 30.1076 | 27.1479 | 1.713 | 11.4572 | 28.1935 | 29.3405 |  | 16.9583 | 12.7 | 13.9 | 33.9167 | 0
| 5.6944 | 278.683 | 44.394 | 53.651 | 47.793 | 71.343 |  | 16.9792 | 30.1144 | 27.1411 | 1.7984 | 11.4638 | 28.2137 | 29.345 |  | 16.9792 | 12.9 | 13.9 | 33.9583 | 0
| 5.7014 | 278.698 | 44.411 | 53.671 | 47.813 | 71.379 |  | 17 | 30.1122 | 27.1479 | 1.9714 | 11.4439 | 28.198 | 29.3315 |  | 17 | 12.8 | 13.9 | 34 | 0
| 5.7083 | 278.531 | 44.419 | 53.688 | 47.826 | 71.406 |  | 17.0208 | 30.1076 | 27.1524 | 1.897 | 11.455 | 28.1957 | 29.3247 |  | 17.0208 | 12.8 | 13.9 | 34.0417 | 0
| 5.7153 | 279.682 | 44.437 | 53.707 | 47.85 | 71.442 |  | 17.0417 | 30.1189 | 27.1637 | 1.9342 | 11.4528 | 28.2047 | 29.3495 |  | 17.0417 | 12.6 | 13.9 | 34.0833 | 0
| 5.7222 | 279.859 | 44.455 | 53.727 | 47.862 | 71.472 |  | 17.0625 | 30.1144 | 27.1705 | 1.9845 | 11.4683 | 28.2025 | 29.354 |  | 17.0625 | 12.4 | 13.9 | 34.125 | 0
| 5.7292 | 278.782 | 44.471 | 53.743 | 47.878 | 71.503 |  | 17.0833 | 30.094 | 27.1501 | 2.0437 | 11.4484 | 28.207 | 29.3473 |  | 17.0833 | 12.4 | 13.9 | 34.1667 | 0
| 5.7361 | 278.198 | 44.477 | 53.765 | 47.891 | 71.529 |  | 17.1042 | 30.0963 | 27.1796 | 1.8838 | 11.4638 | 28.2092 | 29.3382 |  | 17.1042 | 12.3 | 13.9 | 34.2083 | 0
| 5.7431 | 277.643 | 44.495 | 53.775 | 47.907 | 71.552 |  | 17.125 | 29.9845 | 27.041 | 1.73 | 11.3394 | 28.1069 | 29.2335 |  | 17.125 | 11.7 | 13.9 | 34.25 | 0
| 5.75 | 278.522 | 44.506 | 53.791 | 47.917 | 71.572 |  | 17.1458 | 30.1136 | 27.1743 | 1.8943 | 11.4721 | 28.2196 | 29.3487 |  | 17.1458 | 11.2 | 13.9 | 34.2917 | 0
| 5.7569 | 278.652 | 44.52 | 53.809 | 47.933 | 71.601 |  | 17.1667 | 29.8057 | 26.8695 | 1.498 | 11.18 | 27.9401 | 29.0798 |  | 17.1667 | 10.7 | 13.9 | 34.3333 | 0
| 5.7639 | 279.376 | 44.526 | 53.823 | 47.945 | 71.619 |  | 17.1875 | 30.0793 | 27.1334 | 1.8393 | 11.432 | 28.1764 | 29.3123 |  | 17.1875 | 10.5 | 13.9 | 34.375 | 0
| 5.7708 | 275.278 | 44.54 | 53.838 | 47.955 | 71.641 |  | 17.2083 | 30.0929 | 27.1649 | 1.8458 | 11.4541 | 28.2193 | 29.3665 |  | 17.2083 | 10.3 | 13.9 | 34.4167 | 0
| 5.7778 | 275.213 | 44.533 | 53.835 | 47.957 | 71.63 |  | 17.2292 | 30.0884 | 27.1694 | 1.8349 | 11.4475 | 28.2125 | 29.353 |  | 17.2292 | 10 | 13.9 | 34.4583 | 2.3
| 5.7847 | 275.724 | 44.527 | 53.827 | 47.955 | 71.605 |  | 17.25 | 30.0884 | 27.1739 | 1.8021 | 11.4541 | 28.1945 | 29.3484 |  | 17.25 | 9.8 | 13.9 | 34.5 | 6.5
| 5.7917 | 276.266 | 44.523 | 53.826 | 47.958 | 71.592 |  | 17.2708 | 30.0567 | 27.1469 | 1.8021 | 11.4298 | 28.1697 | 29.3258 |  | 17.2708 | 10.1 | 13.9 | 34.5417 | 0.3
| 5.7986 | 276.956 | 44.527 | 53.828 | 47.966 | 71.588 |  | 17.2917 | 29.9571 | 27.043 | 1.6969 | 11.3456 | 28.1042 | 29.2512 |  | 17.2917 | 10.6 | 13.9 | 34.5833 | 0.1
| 5.8056 | 276.209 | 44.529 | 53.837 | 47.97 | 71.595 |  | 17.3125 | 30.0357 | 27.1328 | 1.7996 | 11.4206 | 28.1624 | 29.3206 |  | 17.3125 | 11.3 | 13.9 | 34.625 | 0
| 5.8125 | 276.984 | 44.539 | 53.845 | 47.981 | 71.606 |  | 17.3333 | 30.0479 | 27.1403 | 1.8157 | 11.4303 | 28.1862 | 29.324 |  | 17.3333 | 12.3 | 13.9 | 34.6667 | 0
| 5.8194 | 277.107 | 44.546 | 53.859 | 47.988 | 71.618 |  | 17.3542 | 30.0449 | 27.1462 | 1.8255 | 11.4361 | 28.1766 | 29.3347 |  | 17.3542 | 13.8 | 13.9 | 34.7083 | 0
| 5.8264 | 277.897 | 44.558 | 53.875 | 48.003 | 71.64 |  | 17.375 | 30.0537 | 27.155 | 1.8137 | 11.4311 | 28.1651 | 29.3344 |  | 17.375 | 14.7 | 13.9 | 34.75 | 0
| 5.8333 | 278.426 | 44.574 | 53.893 | 48.014 | 71.665 |  | 17.3958 | 30.0348 | 27.1427 | 1.8038 | 11.4235 | 28.1555 | 29.3179 |  | 17.3958 | 15.1 | 13.9 | 34.7917 | 0
| 5.8403 | 279.149 | 44.59 | 53.91 | 48.031 | 71.691 |  | 17.4167 | 30.051 | 27.1611 | 1.7822 | 11.4395 | 28.1897 | 29.3476 |  | 17.4167 | 15.8 | 13.9 | 34.8333 | 0
| 5.8472 | 279.903 | 44.607 | 53.932 | 48.054 | 71.723 |  | 17.4375 | 30.0281 | 27.1561 | 1.7791 | 11.4344 | 28.1513 | 29.336 |  | 17.4375 | 16.2 | 13.9 | 34.875 | 0
| 5.8542 | 280.593 | 44.619 | 53.957 | 48.071 | 71.762 |  | 17.4792 | 30.017 | 27.1405 | 1.7086 | 11.4232 | 28.1427 | 29.3296 |  | 17.4583 | 16.6 | 13.9 | 34.9167 | 0
| 5.8611 | 280.447 | 44.642 | 53.976 | 48.09 | 71.792 |  | 17.5 | 30.0182 | 27.1484 | 1.7073 | 11.4332 | 28.1509 | 29.3399 |  | 17.4792 | 17.3 | 13.9 | 34.9583 | 0
| 5.8681 | 281.01 | 44.657 | 53.999 | 48.108 | 71.827 |  | 17.5208 | 30.0294 | 27.1392 | 1.6702 | 11.4155 | 28.099 | 29.333 |  | 17.5 | 17.8 | 13.9 | 35 | 0
| 5.875 | 280.81 | 44.676 | 54.025 | 48.128 | 71.858 |  | 17.5417 | 30.0105 | 27.1654 | 1.693 | 11.4278 | 28.1479 | 29.3458 |  | 17.5208 | 19.4 | 13.9
| 5.8819 | 280.491 | 44.688 | 54.043 | 48.146 | 71.893 |  | 17.5625 | 30.0263 | 27.1742 | 1.6966 | 11.445 | 28.1749 | 29.3549 |  | 17.5417 | 19.8 | 13.9
| 5.8889 | 282.097 | 44.696 | 54.058 | 48.157 | 71.907 |  | 17.5833 | 29.9969 | 27.1584 | 1.6616 | 11.4295 | 28.1479 | 29.3413 |  | 17.5625 | 19.5 | 13.9
| 5.8958 | 280.867 | 44.711 | 54.083 | 48.178 | 71.936 |  | 17.6042 | 30.0014 | 27.1584 | 1.6726 | 11.4317 | 28.1524 | 29.3571 |  | 17.5833 | 20.3 | 13.9
| 5.9028 | 283.833 | 44.728 | 54.105 | 48.204 | 71.966 |  | 17.625 | 30.0169 | 27.1761 | 1.6782 | 11.4356 | 28.136 | 29.3545 |  | 17.6042 | 19.7 | 13.9
| 5.9097 | 284.275 | 44.754 | 54.144 | 48.235 | 72.025 |  | 17.6458 | 29.9948 | 27.1585 | 1.659 | 11.4249 | 28.1297 | 29.3439 |  | 17.625 | 19.2 | 13.9
| 5.9167 | 284.793 | 44.788 | 54.179 | 48.263 | 72.092 |  | 17.6667 | 30.0458 | 27.2002 | 1.7049 | 11.4738 | 28.1895 | 29.379 |  | 17.6458 | 20.3 | 13.9
| 5.9236 | 285.581 | 44.824 | 54.222 | 48.296 | 72.156 |  | 17.6875 | 30.0865 | 27.252 | 1.7443 | 11.5205 | 28.2482 | 29.4378 |  | 17.6667 | 20.4 | 13.9
| 5.9306 | 283.82 | 44.845 | 54.259 | 48.327 | 72.222 |  | 17.7083 | 30.0489 | 27.2303 | 1.7149 | 11.4796 | 28.1701 | 29.4046 |  | 17.6875 | 21.4 | 13.9
| 5.9375 | 284.454 | 44.87 | 54.286 | 48.353 | 72.252 |  | 17.7292 | 30.0589 | 27.2314 | 1.7162 | 11.4916 | 28.2075 | 29.4145 |  | 17.7083 | 20.5 | 13.9
| 5.9444 | 285.189 | 44.886 | 54.315 | 48.372 | 72.293 |  | 17.75 | 30.034 | 27.2112 | 1.6942 | 11.4699 | 28.1827 | 29.392 |  | 17.7292 | 20.7 | 13.9
| 5.9514 | 285.895 | 44.91 | 54.35 | 48.403 | 72.346 |  | 17.7708 | 30.0428 | 27.2176 | 1.705 | 11.4892 | 28.1981 | 29.412 |  | 17.75 | 20.3 | 13.9
| 5.9583 | 285.665 | 44.938 | 54.383 | 48.435 | 72.399 |  | 17.7917 | 30.0227 | 27.1978 | 1.6621 | 11.4698 | 28.1667 | 29.392 |  | 17.7708 | 20.7 | 13.9
| 5.9653 | 286.264 | 44.962 | 54.421 | 48.464 | 72.458 |  | 17.8125 | 30.0146 | 27.1898 | 1.6412 | 11.4663 | 28.1718 | 29.3791 |  | 17.7917 | 19.8 | 13.9
| 5.9722 | 276.617 | 44.998 | 54.46 | 48.491 | 72.521 |  | 17.8333 | 29.9875 | 27.1246 | 1.6252 | 11.4471 | 27.962 | 29.3656 |  | 17.8125 | 19 | 13.9
| 5.9792 | 277.507 | 44.972 | 54.445 | 48.478 | 72.47 |  | 17.8542 | 29.9717 | 27.1091 | 1.6038 | 11.4407 | 27.982 | 29.3542 |  | 17.8333 | 18.2 | 13.9
| 5.9861 | 277.95 | 44.943 | 54.424 | 48.465 | 72.4 |  | 17.875 | 29.9671 | 27.1069 | 1.6065 | 11.4343 | 27.9816 | 29.3473 |  | 17.8542 | 17 | 13.9
| 5.9931 | 278.133 | 44.92 | 54.414 | 48.459 | 72.35 |  | 17.8958 | 29.9633 | 27.0965 | 1.5946 | 11.4286 | 27.9824 | 29.3436 |  | 17.875 | 14.9 | 13.9
| 6 | 278.686 | 44.908 | 54.4 | 48.447 | 72.306 |  | 17.9167 | 29.9447 | 27.087 | 1.5723 | 11.4126 | 27.9838 | 29.3316 |  | 17.8958 | 13.8 | 13.9
| 6.0069 | 279.104 | 44.906 | 54.402 | 48.447 | 72.279 |  | 17.9375 | 29.9673 | 27.105 | 1.6029 | 11.4281 | 28.0042 | 29.3475 |  | 17.9167 | 13.3 | 13.9
| 6.0139 | 277.617 | 44.899 | 54.396 | 48.441 | 72.249 |  | 17.9583 | 29.9418 | 27.0863 | 1.5827 | 11.4054 | 27.9899 | 29.3331 |  | 17.9375 | 12.9 | 13.9
| 6.0208 | 278.402 | 44.891 | 54.39 | 48.44 | 72.224 |  | 17.9792 | 29.9456 | 27.088 | 1.5692 | 11.4093 | 27.9983 | 29.3258 |  | 17.9583 | 12.8 | 13.9
| 6.0278 | 278.359 | 44.882 | 54.381 | 48.439 | 72.194 |  | 18 | 29.9615 | 27.1038 | 1.5845 | 11.4204 | 27.9983 | 29.3439 |  | 17.9792 | 12.8 | 13.9
| 6.0347 | 277.795 | 44.88 | 54.384 | 48.431 | 72.177 |  | 18.0208 | 29.9524 | 27.106 | 1.5801 | 11.4204 | 27.9916 | 29.3393 |  | 18 | 12.6 | 13.9
| 6.0417 | 278.848 | 44.879 | 54.387 | 48.434 | 72.162 |  | 18.0417 | 29.9479 | 27.097 | 1.5736 | 11.416 | 27.996 | 29.3439 |  | 18.0208 | 12.2 | 13.9
| 6.0486 | 278.816 | 44.885 | 54.391 | 48.445 | 72.162 |  | 18.0625 | 29.9388 | 27.097 | 1.5604 | 11.4116 | 27.9893 | 29.3348 |  | 18.0417 | 12.3 | 13.9
| 6.0556 | 279.181 | 44.894 | 54.397 | 48.447 | 72.167 |  | 18.0833 | 29.8975 | 27.0627 | 1.5324 | 11.3739 | 27.9617 | 29.3071 |  | 18.0625 | 12.2 | 13.9
| 6.0625 | 278.927 | 44.901 | 54.408 | 48.457 | 72.172 |  | 18.1042 | 29.9337 | 27.0988 | 1.5543 | 11.3983 | 27.9931 | 29.3319 |  | 18.0833 | 11.8 | 13.9
| 6.0694 | 279.032 | 44.913 | 54.419 | 48.465 | 72.185 |  | 18.125 | 29.9039 | 27.0713 | 1.5277 | 11.3802 | 27.977 | 29.3066 |  | 18.1042 | 12.1 | 13.9
| 6.0764 | 279.746 | 44.923 | 54.427 | 48.469 | 72.194 |  | 18.1458 | 29.9152 | 27.0827 | 1.5387 | 11.3891 | 27.9928 | 29.318 |  | 18.125 | 11.8 | 13.9
| 6.0833 | 279.638 | 44.93 | 54.442 | 48.485 | 72.204 |  | 18.1667 | 29.9001 | 27.0722 | 1.5215 | 11.3785 | 27.9753 | 29.3074 |  | 18.1458 | 11.7 | 13.9
| 6.0903 | 279.876 | 44.937 | 54.456 | 48.492 | 72.213 |  | 18.1875 | 29.9115 | 27.079 | 1.5303 | 11.3807 | 27.9911 | 29.3164 |  | 18.1667 | 11.4 | 13.9
| 6.0972 | 278.799 | 44.946 | 54.467 | 48.507 | 72.228 |  | 18.2083 | 29.9454 | 27.115 | 1.5763 | 11.4051 | 28.2256 | 29.339 |  | 18.1875 | 11.4 | 13.9
| 6.1042 | 278.04 | 44.951 | 54.47 | 48.508 | 72.227 |  | 18.2292 | 29.8849 | 27.0616 | 1.5007 | 11.3661 | 27.9781 | 29.3011 |  | 18.2083 | 11.2 | 13.9
| 6.1111 | 277.936 | 44.946 | 54.476 | 48.505 | 72.212 |  | 18.25 | 29.74 | 26.9057 | 1.2928 | 11.2068 | 27.8136 | 29.152 |  | 18.2292 | 11.1 | 13.9
| 6.1181 | 278.232 | 44.946 | 54.478 | 48.508 | 72.197 |  | 18.2708 | 29.6359 | 26.8176 | 1.2054 | 11.1272 | 27.7348 | 29.0773 |  | 18.25 | 10.8 | 13.9
| 6.125 | 278.002 | 44.948 | 54.487 | 48.514 | 72.197 |  | 18.2917 | 29.6178 | 26.8109 | 1.1923 | 11.1272 | 27.7392 | 29.0706 |  | 18.2708 | 10.7 | 13.9
| 6.1319 | 277.702 | 44.949 | 54.495 | 48.522 | 72.188 |  | 18.3125 | 29.6586 | 26.8334 | 1.2316 | 11.1448 | 27.7572 | 29.0932 |  | 18.2917 | 11.1 | 13.9
| 6.1389 | 278.1 | 44.951 | 54.498 | 48.525 | 72.184 |  | 18.3333 | 29.743 | 26.9311 | 1.3351 | 11.232 | 27.8619 | 29.1867 |  | 18.3125 | 11.3 | 13.9
| 6.1458 | 277.841 | 44.958 | 54.502 | 48.527 | 72.177 |  | 18.3542 | 29.8551 | 27.0948 | 1.4759 | 11.3501 | 27.9691 | 29.2941 |  | 18.3333 | 11.5 | 13.9
| 6.1528 | 278.109 | 44.959 | 54.508 | 48.536 | 72.173 |  | 18.375 | 29.8936 | 27.1423 | 1.5111 | 11.3636 | 28.1383 | 29.3236 |  | 18.3542 | 12.1 | 13.9
| 6.1597 | 277.954 | 44.966 | 54.514 | 48.54 | 72.176 |  | 18.3958 | 29.8822 | 27.1399 | 1.498 | 11.3614 | 28.1226 | 29.3145 |  | 18.375 | 12.6 | 13.9
| 6.1667 | 277.791 | 44.965 | 54.526 | 48.548 | 72.179 |  | 18.4167 | 29.9 | 27.1756 | 1.5321 | 11.3917 | 28.138 | 29.3458 |  | 18.3958 | 13.2 | 13.9
| 6.1736 | 277.815 | 44.974 | 54.536 | 48.559 | 72.182 |  | 18.4375 | 29.9055 | 27.1743 | 1.535 | 11.3904 | 28.1572 | 29.3491 |  | 18.4167 | 14.3 | 13.9
| 6.1806 | 278.189 | 44.98 | 54.538 | 48.562 | 72.174 |  | 18.4583 | 29.8793 | 27.1593 | 1.5029 | 11.3713 | 28.1493 | 29.3411 |  | 18.4375 | 15.1 | 13.9
| 6.1875 | 278.17 | 44.978 | 54.548 | 48.571 | 72.173 |  | 18.4792 | 29.8712 | 27.1467 | 1.4817 | 11.3656 | 28.1346 | 29.3308 |  | 18.4583 | 15.3 | 13.9
| 6.1944 | 278.055 | 44.986 | 54.555 | 48.576 | 72.175 |  | 18.5 | 29.8758 | 27.1625 | 1.5189 | 11.3744 | 28.1436 | 29.3511 |  | 18.4792 | 15.4 | 13.9
| 6.2014 | 277.834 | 44.989 | 54.568 | 48.586 | 72.178 |  | 18.5208 | 29.639 | 26.9216 | 1.2263 | 11.1582 | 27.91 | 29.1281 |  | 18.5 | 15.9 | 13.9
| 6.2083 | 278.254 | 44.994 | 54.577 | 48.587 | 72.176 |  | 18.5417 | 29.6527 | 26.9444 | 1.2484 | 11.1696 | 27.9238 | 29.1487 |  | 18.5208 | 15.6 | 13.9
| 6.2153 | 277.918 | 45.001 | 54.588 | 48.602 | 72.185 |  | 18.5625 | 29.6987 | 26.9811 | 1.2774 | 11.2122 | 27.9787 | 29.1947 |  | 18.5417 | 16.3 | 13.9
| 6.2222 | 278.173 | 45.011 | 54.597 | 48.604 | 72.182 |  | 18.5833 | 29.6987 | 26.9947 | 1.3015 | 11.2233 | 27.9697 | 29.2014 |  | 18.5625 | 16.6 | 13.9
| 6.2292 | 278.511 | 45.017 | 54.605 | 48.613 | 72.192 |  | 18.6042 | 29.7168 | 27.0127 | 1.3255 | 11.2366 | 27.9877 | 29.2195 |  | 18.5833 | 16.8 | 13.9
| 6.2361 | 280.671 | 45.027 | 54.619 | 48.621 | 72.203 |  | 18.625 | 29.7768 | 27.0702 | 1.3956 | 11.2947 | 28.0568 | 29.2773 |  | 18.6042 | 16.8 | 13.9
| 6.2431 | 280.217 | 45.039 | 54.641 | 48.647 | 72.231 |  | 18.6458 | 29.8199 | 27.1038 | 1.4322 | 11.3299 | 28.0885 | 29.318 |  | 18.625 | 16.9 | 13.9
| 6.25 | 281.51 | 45.063 | 54.662 | 48.667 | 72.265 |  | 18.6667 | 29.8436 | 27.1433 | 1.4791 | 11.36 | 28.1215 | 29.3487 |  | 18.6458 | 17.8 | 13.9
| 6.2569 | 279.614 | 45.078 | 54.689 | 48.685 | 72.303 |  | 18.6875 | 29.8392 | 27.141 | 1.4791 | 11.3577 | 28.1147 | 29.3532 |  | 18.6667 | 19.2 | 13.9
| 6.2639 | 279.352 | 45.094 | 54.703 | 48.697 | 72.322 |  | 18.7083 | 29.7917 | 27.105 | 1.4529 | 11.3133 | 28.0558 | 29.3126 |  | 18.6875 | 19.8 | 13.9
| 6.2708 | 277.846 | 45.095 | 54.714 | 48.706 | 72.328 |  | 18.7292 | 29.8592 | 27.1698 | 1.4906 | 11.3784 | 28.139 | 29.3688 |  | 18.7083 | 18.9 | 13.9
| 6.2778 | 277.982 | 45.096 | 54.721 | 48.71 | 72.317 |  | 18.75 | 29.8796 | 27.188 | 1.5146 | 11.4007 | 28.166 | 29.3981 |  | 18.7292 | 19.2 | 13.9
| 6.2847 | 277.544 | 45.098 | 54.727 | 48.71 | 72.312 |  | 18.7708 | 29.8414 | 27.159 | 1.4826 | 11.3682 | 28.1191 | 29.3667 |  | 18.75 | 19.3 | 13.9
| 6.2917 | 277.348 | 45.095 | 54.733 | 48.718 | 72.301 |  | 18.7917 | 29.8443 | 27.1687 | 1.4916 | 11.3727 | 28.1264 | 29.3674 |  | 18.7708 | 18.4 | 13.9
| 6.2986 | 280.427 | 45.096 | 54.74 | 48.721 | 72.295 |  | 18.8125 | 29.851 | 27.1755 | 1.4942 | 11.3751 | 28.1351 | 29.3716 |  | 18.7917 | 17.9 | 13.9
| 6.3056 | 280.148 | 45.111 | 54.763 | 48.735 | 72.322 |  | 18.8333 | 29.8323 | 27.1638 | 1.4683 | 11.3728 | 28.1343 | 29.3598 |  | 18.8125 | 17.8 | 13.9
| 6.3125 | 280.085 | 45.131 | 54.78 | 48.754 | 72.35 |  | 18.8542 | 29.8121 | 27.1439 | 1.4391 | 11.3537 | 28.1116 | 29.3485 |  | 18.8333 | 16.5 | 13.9
| 6.3194 | 279.806 | 45.144 | 54.796 | 48.767 | 72.368 |  | 18.875 | 29.801 | 27.1332 | 1.4245 | 11.3386 | 28.1003 | 29.3306 |  | 18.8542 | 15.3 | 13.9
| 6.3264 | 279.01 | 45.159 | 54.812 | 48.779 | 72.385 |  | 18.8958 | 29.7869 | 27.1146 | 1.4041 | 11.329 | 28.0971 | 29.3186 |  | 18.875 | 13.8 | 13.9
| 6.3333 | 278.131 | 45.161 | 54.82 | 48.788 | 72.388 |  | 18.9167 | 29.7619 | 27.099 | 1.3741 | 11.3072 | 28.0677 | 29.3004 |  | 18.8958 | 12.6 | 13.9
| 6.3403 | 276.713 | 45.16 | 54.827 | 48.79 | 72.377 |  | 18.9375 | 29.7244 | 27.0752 | 1.3316 | 11.2817 | 28.0618 | 29.2721 |  | 18.9167 | 11.8 | 13.9
| 6.3472 | 279.478 | 45.165 | 54.834 | 48.799 | 72.38 |  | 18.9583 | 29.7234 | 27.0741 | 1.3242 | 11.2697 | 28.0584 | 29.2641 |  | 18.9375 | 11.1 | 14.4
| 6.3542 | 281.941 | 45.18 | 54.855 | 48.818 | 72.401 |  | 18.9792 | 29.7222 | 27.066 | 1.306 | 11.2578 | 28.0414 | 29.2585 |  | 18.9583 | 10.5 | 14.4
| 6.3611 | 280.593 | 45.206 | 54.882 | 48.835 | 72.447 |  | 19 | 29.7096 | 27.0624 | 1.3073 | 11.2634 | 28.0423 | 29.2617 |  | 18.9792 | 10.1 | 14.4
| 6.3681 | 280.676 | 45.231 | 54.908 | 48.853 | 72.488 |  | 19.0208 | 29.7118 | 27.0397 | 1.3071 | 11.2631 | 28.0375 | 29.2615 |  | 19 | 9.9 | 14.4
| 6.375 | 280.737 | 45.249 | 54.931 | 48.878 | 72.517 |  | 19.0417 | 29.7022 | 27.0165 | 1.2871 | 11.2494 | 28.0279 | 29.2542 |  | 19.0208 | 9.3 | 14.4
| 6.3819 | 280.096 | 45.263 | 54.951 | 48.89 | 72.55 |  | 19.0625 | 29.7202 | 27.021 | 1.3001 | 11.2649 | 28.0415 | 29.2655 |  | 19.0417 | 8.8 | 14.4
| 6.3889 | 279.438 | 45.28 | 54.966 | 48.907 | 72.569 |  | 19.0833 | 29.7128 | 27.0045 | 1.302 | 11.2578 | 28.0273 | 29.2626 |  | 19.0625 | 8.8 | 14.4
| 6.3958 | 278.905 | 45.282 | 54.983 | 48.921 | 72.576 |  | 19.1042 | 29.6993 | 26.9933 | 1.2867 | 11.2422 | 28.0273 | 29.2581 |  | 19.0833 | 8.7 | 14.4
| 6.4028 | 280.386 | 45.288 | 54.994 | 48.92 | 72.584 |  | 19.125 | 29.6676 | 26.9528 | 1.2451 | 11.2135 | 28.0071 | 29.2265 |  | 19.1042 | 8.8 | 14.4
| 6.4097 | 279.738 | 45.31 | 55.015 | 48.935 | 72.61 |  | 19.1458 | 29.7197 | 27.0158 | 1.302 | 11.2644 | 28.0566 | 29.2717 |  | 19.125 | 9.1 | 14.4
| 6.4167 | 278.844 | 45.322 | 55.033 | 48.951 | 72.633 |  | 19.1667 | 29.7151 | 27.0113 | 1.3085 | 11.26 | 28.0589 | 29.2739 |  | 19.1458 | 9.1 | 14.4
| 6.4236 | 277.714 | 45.329 | 55.041 | 48.962 | 72.638 |  | 19.1875 | 29.6993 | 26.9978 | 1.2867 | 11.2422 | 28.0499 | 29.2604 |  | 19.1667 | 9 | 14.4
| 6.4306 | 277.653 | 45.329 | 55.047 | 48.972 | 72.628 |  | 19.2083 | 29.6789 | 26.9753 | 1.2648 | 11.2268 | 28.0409 | 29.2401 |  | 19.1875 | 8.8 | 14.4
| 6.4375 | 277.074 | 45.328 | 55.051 | 48.971 | 72.617 |  | 19.2292 | 29.6902 | 27.0002 | 1.2867 | 11.2335 | 28.0363 | 29.2603 |  | 19.2083 | 9.4 | 14.4
| 6.4444 | 275.709 | 45.328 | 55.051 | 48.972 | 72.604 |  | 19.25 | 29.7022 | 27.0101 | 1.2983 | 11.2519 | 28.0756 | 29.2747 |  | 19.2292 | 9.5 | 14.4
| 6.4514 | 276.069 | 45.325 | 55.051 | 48.971 | 72.592 |  | 19.2708 | 29.6569 | 26.9853 | 1.261 | 11.2099 | 28.0282 | 29.2453 |  | 19.25 | 9.9 | 14.4
| 6.4583 | 275.916 | 45.324 | 55.055 | 48.971 | 72.577 |  | 19.2917 | 29.7112 | 27.0777 | 1.3202 | 11.2542 | 28.0756 | 29.2905 |  | 19.2708 | 10.2 | 14.4
| 6.4653 | 275.308 | 45.328 | 55.048 | 48.974 | 72.565 |  | 19.3125 | 29.7257 | 27.09 | 1.3208 | 11.2637 | 28.1037 | 29.3096 |  | 19.2917 | 10.3 | 14.4
| 6.4722 | 275.307 | 45.329 | 55.046 | 48.967 | 72.548 |  | 19.3333 | 29.7242 | 27.0931 | 1.3345 | 11.2711 | 28.1113 | 29.317 |  | 19.3125 | 10.8 | 14.4
| 6.4792 | 275.752 | 45.324 | 55.046 | 48.972 | 72.533 |  | 19.3542 | 29.731 | 27.1042 | 1.3405 | 11.2841 | 28.1183 | 29.3239 |  | 19.3333 | 11.8 | 14.4
| 6.4861 | 275.313 | 45.319 | 55.043 | 48.969 | 72.508 |  | 19.375 | 29.7313 | 27.1067 | 1.3584 | 11.2823 | 28.1233 | 29.3334 |  | 19.3542 | 12.5 | 14.4
| 6.4931 | 274.869 | 45.317 | 55.042 | 48.966 | 72.485 |  | 19.3958 | 29.7306 | 27.1171 | 1.3572 | 11.2902 | 28.1226 | 29.3349 |  | 19.375 | 13.6 | 14.4
| 6.5 | 275.045 | 45.318 | 55.032 | 48.963 | 72.475 |  | 19.4167 | 29.7252 | 27.1026 | 1.3605 | 11.287 | 28.1151 | 29.3407 |  | 19.3958 | 14.3 | 14.4
| 6.5069 | 275.305 | 45.317 | 55.035 | 48.961 | 72.461 |  | 19.4375 | 29.7364 | 27.1227 | 1.3708 | 11.2999 | 28.1288 | 29.3522 |  | 19.4167 | 15.7 | 14.4
| 6.5139 | 275.355 | 45.318 | 55.032 | 48.962 | 72.449 |  | 19.4583 | 29.7412 | 27.1343 | 1.3885 | 11.3179 | 28.1381 | 29.3637 |  | 19.4375 | 16.3 | 14.4
| 6.5208 | 275.853 | 45.326 | 55.037 | 48.96 | 72.448 |  | 19.4792 | 29.7485 | 27.148 | 1.4035 | 11.3245 | 28.1071 | 29.3822 |  | 19.4583 | 16.7 | 14.4
| 6.5278 | 275.829 | 45.328 | 55.037 | 48.98 | 72.45 |  | 19.5 | 29.742 | 27.1415 | 1.3928 | 11.316 | 28.1098 | 29.378 |  | 19.4792 | 17.6 | 14.4
| 6.5347 | 277.322 | 45.333 | 55.038 | 48.969 | 72.447 |  | 19.5208 | 29.6968 | 27.1009 | 1.36 | 11.2784 | 28.0895 | 29.3395 |  | 19.5 | 18.8 | 14.4
| 6.5417 | 278.177 | 45.35 | 55.056 | 48.981 | 72.471 |  | 19.5417 | 29.7306 | 27.1413 | 1.4008 | 11.3089 | 28.1121 | 29.3825 |  | 19.5208 | 18.6 | 14.4
| 6.5486 | 277.805 | 45.37 | 55.073 | 48.996 | 72.503 |  | 19.5625 | 29.7277 | 27.1362 | 1.3962 | 11.3131 | 28.1274 | 29.3775 |  | 19.5417 | 18.6 | 14.4
| 6.5556 | 278.624 | 45.39 | 55.09 | 49.017 | 72.543 |  | 19.5833 | 29.7181 | 27.1152 | 1.3667 | 11.2967 | 28.1246 | 29.37 |  | 19.5625 | 19.3 | 14.4
| 6.5625 | 277.573 | 45.411 | 55.108 | 49.027 | 72.573 |  | 19.6042 | 29.7221 | 27.1259 | 1.3919 | 11.3006 | 28.1243 | 29.3832 |  | 19.5833 | 20.1 | 14.4
| 6.5694 | 278.296 | 45.428 | 55.13 | 49.04 | 72.604 |  | 19.625 | 29.6973 | 27.1123 | 1.3679 | 11.2785 | 28.1085 | 29.3652 |  | 19.6042 | 20.3 | 14.4
| 6.5764 | 277.483 | 45.439 | 55.143 | 49.056 | 72.633 |  | 19.6458 | 29.686 | 27.0966 | 1.3569 | 11.2652 | 28.095 | 29.3493 |  | 19.625 | 21.2 | 14.4
| 6.5833 | 277.457 | 45.45 | 55.158 | 49.068 | 72.657 |  | 19.6667 | 29.7109 | 27.1259 | 1.3876 | 11.2962 | 28.1243 | 29.3764 |  | 19.6458 | 20.4 | 14.4
| 6.5903 | 278.007 | 45.464 | 55.176 | 49.075 | 72.671 |  | 19.6875 | 29.7012 | 27.1186 | 1.3762 | 11.291 | 28.1146 | 29.3624 |  | 19.6667 | 20.8 | 14.4
| 6.5972 | 277.513 | 45.475 | 55.191 | 49.084 | 72.692 |  | 19.7083 | 29.6953 | 27.1218 | 1.3686 | 11.292 | 28.1356 | 29.3698 |  | 19.6875 | 20.3 | 14.4
| 6.6042 | 277.834 | 45.486 | 55.201 | 49.098 | 72.713 |  | 19.7292 | 29.6956 | 27.1244 | 1.373 | 11.2964 | 28.1064 | 29.3723 |  | 19.7083 | 19.2 | 14.4
| 6.6111 | 278.011 | 45.503 | 55.219 | 49.114 | 72.74 |  | 19.75 | 29.6982 | 27.1248 | 1.3623 | 11.2945 | 28.118 | 29.3705 |  | 19.7292 | 18.9 | 14.4
| 6.6181 | 277.647 | 45.518 | 55.234 | 49.121 | 72.766 |  | 19.7708 | 29.7095 | 27.1406 | 1.3732 | 11.3077 | 28.1225 | 29.3909 |  | 19.75 | 18.7 | 14.4
| 6.625 | 278.462 | 45.528 | 55.254 | 49.139 | 72.79 |  | 19.7917 | 29.6679 | 27.1083 | 1.334 | 11.2832 | 28.1012 | 29.356 |  | 19.7708 | 18.3 | 14.4
| 6.6319 | 278.677 | 45.543 | 55.273 | 49.154 | 72.821 |  | 19.8125 | 29.6837 | 27.1218 | 1.3558 | 11.2876 | 28.1035 | 29.3719 |  | 19.7917 | 18.1 | 14.4
| 6.6389 | 275.647 | 45.561 | 55.294 | 49.175 | 72.847 |  | 19.8333 | 29.6611 | 27.1038 | 1.3187 | 11.2654 | 28.0809 | 29.3537 |  | 19.8125 | 17.9 | 14.4
| 6.6458 | 275.772 | 45.564 | 55.296 | 49.174 | 72.845 |  | 19.8542 | 29.6701 | 27.1218 | 1.3427 | 11.2853 | 28.0944 | 29.3696 |  | 19.8333 | 17.9 | 14.4
| 6.6528 | 275.692 | 45.555 | 55.288 | 49.181 | 72.83 |  | 19.875 | 29.6573 | 27.1046 | 1.3285 | 11.2774 | 28.095 | 29.3589 |  | 19.8542 | 17.7 | 14.4
| 6.6597 | 274.896 | 45.553 | 55.29 | 49.18 | 72.813 |  | 19.8958 | 29.6618 | 27.1203 | 1.335 | 11.2795 | 28.0928 | 29.3657 |  | 19.875 | 17.1 | 14.4
| 6.6667 | 276.208 | 45.551 | 55.289 | 49.177 | 72.8 |  | 19.9167 | 29.6307 | 27.0984 | 1.3134 | 11.2645 | 28.0639 | 29.3526 |  | 19.8958 | 16.3 | 14.4
| 6.6736 | 274.324 | 45.555 | 55.296 | 49.184 | 72.8 |  | 19.9375 | 29.6624 | 27.13 | 1.3243 | 11.291 | 28.0932 | 29.373 |  | 19.9167 | 16.1 | 14.4
| 6.6806 | 275.164 | 45.554 | 55.294 | 49.183 | 72.792 |  | 19.9583 | 29.6308 | 27.0985 | 1.3011 | 11.2583 | 28.0549 | 29.3459 |  | 19.9375 | 16 | 14.4
| 6.6875 | 274.617 | 45.556 | 55.3 | 49.197 | 72.791 |  | 19.9792 | 29.6389 | 27.1135 | 1.3092 | 11.2685 | 28.0742 | 29.3518 |  | 19.9583 | 15.7 | 14.4
| 6.6944 | 279.819 | 45.573 | 55.311 | 49.202 | 72.811 |  | 20 | 29.6366 | 27.1135 | 1.3048 | 11.2664 | 28.0674 | 29.363 |  | 19.9792 | 15.6 | 14.4
| 6.7014 | 282.893 | 45.628 | 55.365 | 49.247 | 72.908 |  | 20.0208 | 29.6337 | 27.1129 | 1.313 | 11.2746 | 28.0802 | 29.3556 |  | 20 | 14.8 | 14.4
| 6.7083 | 283.038 | 45.683 | 55.418 | 49.292 | 73.027 |  | 20.0417 | 29.6269 | 27.1129 | 1.3065 | 11.2724 | 28.087 | 29.3578 |  | 20.0208 | 14.4 | 14.4
| 6.7153 | 282.794 | 45.734 | 55.467 | 49.331 | 73.138 |  | 20.0625 | 29.6037 | 27.0942 | 1.2907 | 11.2498 | 28.057 | 29.3368 |  | 20.0417 | 14.3 | 14.4
| 6.7222 | 282.7 | 45.777 | 55.52 | 49.377 | 73.228 |  | 20.0833 | 29.6001 | 27.0976 | 1.2789 | 11.2465 | 28.0467 | 29.3333 |  | 20.0625 | 14.2 | 14.4
| 6.7292 | 282.499 | 45.815 | 55.567 | 49.416 | 73.316 |  | 20.1042 | 29.5994 | 27.0969 | 1.2849 | 11.2503 | 28.0526 | 29.3394 |  | 20.0833 | 13.8 | 14.4
| 6.7361 | 283.307 | 45.846 | 55.606 | 49.447 | 73.396 |  | 20.125 | 29.6016 | 27.1059 | 1.2893 | 11.2547 | 28.0593 | 29.3529 |  | 20.1042 | 13.2 | 14.4
| 6.7431 | 283.448 | 45.876 | 55.64 | 49.484 | 73.471 |  | 20.1458 | 29.5755 | 27.0799 | 1.2622 | 11.2293 | 28.049 | 29.3223 |  | 20.125 | 12.7 | 14.4
| 6.75 | 282.714 | 45.912 | 55.683 | 49.51 | 73.537 |  | 20.1667 | 29.566 | 27.0683 | 1.2422 | 11.2178 | 28.0395 | 29.3196 |  | 20.1458 | 12.6 | 14.4
| 6.7569 | 284.272 | 45.941 | 55.721 | 49.545 | 73.598 |  | 20.1875 | 29.5519 | 27.0655 | 1.2309 | 11.2107 | 28.0389 | 29.3122 |  | 20.1667 | 12.4 | 14.4
| 6.7639 | 283.289 | 45.963 | 55.754 | 49.573 | 73.658 |  | 20.2083 | 29.5555 | 27.0624 | 1.2258 | 11.2144 | 28.0402 | 29.3068 |  | 20.1875 | 12 | 14.4
| 6.7708 | 283.905 | 45.992 | 55.789 | 49.6 | 73.713 |  | 20.2292 | 29.5849 | 27.0987 | 1.2653 | 11.2365 | 28.065 | 29.343 |  | 20.2083 | 11.4 | 14.4
| 6.7778 | 283.419 | 46.016 | 55.823 | 49.633 | 73.764 |  | 20.25 | 29.5871 | 27.0987 | 1.2653 | 11.2365 | 28.0446 | 29.3452 |  | 20.2292 | 10.9 | 14.4
| 6.7847 | 284.524 | 46.047 | 55.858 | 49.658 | 73.82 |  | 20.2708 | 29.5397 | 27.0624 | 1.2215 | 11.1923 | 28.0199 | 29.3023 |  | 20.25 | 10.7 | 14.4
| 6.7917 | 284.75 | 46.073 | 55.89 | 49.683 | 73.873 |  | 20.2917 | 29.5448 | 27.0652 | 1.2351 | 11.2017 | 28.0206 | 29.3187 |  | 20.2708 | 11.1 | 14.4
| 6.7986 | 284.899 | 46.1 | 55.928 | 49.718 | 73.932 |  | 20.3125 | 29.5711 | 27.0822 | 1.2515 | 11.2229 | 28.0424 | 29.3405 |  | 20.2917 | 11.7 | 14.4
| 6.8056 | 285.007 | 46.131 | 55.965 | 49.751 | 73.991 |  | 20.3333 | 29.5626 | 27.0782 | 1.2607 | 11.219 | 28.0386 | 29.332 |  | 20.3125 | 12.6 | 14.4
| 6.8125 | 284.679 | 46.157 | 55.995 | 49.779 | 74.043 |  | 20.3542 | 29.577 | 27.0924 | 1.2767 | 11.2266 | 28.0577 | 29.3554 |  | 20.3333 | 14.5 | 14.4
| 6.8194 | 285.706 | 46.181 | 56.035 | 49.803 | 74.098 |  | 20.375 | 29.5911 | 27.1176 | 1.329 | 11.2576 | 28.081 | 29.3786 |  | 20.3542 | 15.6 | 14.4
| 6.8264 | 285.742 | 46.208 | 56.07 | 49.839 | 74.155 |  | 20.3958 | 29.5664 | 27.095 | 1.2935 | 11.233 | 28.0632 | 29.3652 |  | 20.375 | 16.7 | 14.4
| 6.8333 | 286.32 | 46.236 | 56.109 | 49.872 | 74.215 |  | 20.4167 | 29.5869 | 27.1176 | 1.3177 | 11.251 | 28.0725 | 29.3813 |  | 20.3958 | 17.8 | 14.4
| 6.8403 | 280.52 | 46.265 | 56.144 | 49.903 | 74.277 |  | 20.4375 | 29.5889 | 27.1172 | 1.3168 | 11.2525 | 28.0836 | 29.3855 |  | 20.4167 | 18.6 | 14.4
| 6.8472 | 280.835 | 46.256 | 56.141 | 49.899 | 74.251 |  | 20.4583 | 29.5931 | 27.1281 | 1.3182 | 11.263 | 28.1036 | 29.3942 |  | 20.4375 | 19 | 14.4
| 6.8542 | 281.85 | 46.245 | 56.145 | 49.907 | 74.226 |  | 20.5 | 29.5714 | 27.1061 | 1.2959 | 11.2322 | 28.0751 | 29.3726 |  | 20.4583 | 19.9 | 14.4
| 6.8611 | 282.541 | 46.24 | 56.157 | 49.907 | 74.206 |  | 20.5208 | 29.5149 | 27.0611 | 1.2455 | 11.1922 | 28.0096 | 29.3342 |  | 20.4792 | 20.4 | 14.4
| 6.8681 | 283.213 | 46.25 | 56.167 | 49.919 | 74.213 |  | 20.5417 | 29.5647 | 27.0903 | 1.2862 | 11.227 | 28.0885 | 29.3749 |  | 20.5 | 21 | 14.4
| 6.875 | 283.183 | 46.253 | 56.186 | 49.934 | 74.218 |  | 20.5625 | 29.5376 | 27.0745 | 1.2533 | 11.2137 | 28.0479 | 29.3523 |  | 20.5208 | 22.3 | 14.4
| 6.8819 | 283.163 | 46.263 | 56.197 | 49.951 | 74.225 |  | 20.5833 | 29.5689 | 27.1169 | 1.2938 | 11.2439 | 28.0902 | 29.3972 |  | 20.5417 | 22.3 | 14.4
| 6.8889 | 281.378 | 46.27 | 56.212 | 49.964 | 74.236 |  | 20.6042 | 29.5794 | 27.1206 | 1.3121 | 11.2604 | 28.1301 | 29.4078 |  | 20.5625 | 22.6 | 14.4
| 6.8958 | 281.157 | 46.265 | 56.207 | 49.958 | 74.214 |  | 20.625 | 29.5926 | 27.1359 | 1.3307 | 11.2662 | 28.1341 | 29.4233 |  | 20.5833 | 22.6 | 14.4
| 6.9028 | 280.657 | 46.255 | 56.208 | 49.963 | 74.188 |  | 20.6458 | 29.6498 | 27.2064 | 1.4077 | 11.3353 | 28.1844 | 29.4827 |  | 20.6042 | 23 | 14.4
| 6.9097 | 281.752 | 46.253 | 56.207 | 49.969 | 74.166 |  | 20.6667 | 29.6495 | 27.206 | 1.4088 | 11.3366 | 28.202 | 29.4936 |  | 20.625 | 23.1 | 14.4
| 6.9167 | 281.897 | 46.25 | 56.212 | 49.979 | 74.157 |  | 20.6875 | 29.6302 | 27.1843 | 1.3873 | 11.3195 | 28.1757 | 29.4766 |  | 20.6458 | 23.8 | 14.4
| 6.9236 | 282.057 | 46.26 | 56.22 | 49.981 | 74.156 |  | 20.7083 | 29.5736 | 27.1301 | 1.326 | 11.2508 | 28.1214 | 29.4179 |  | 20.6667 | 23.9 | 14.4
| 6.9306 | 282.847 | 46.269 | 56.236 | 50 | 74.172 |  | 20.7292 | 29.6302 | 27.182 | 1.3742 | 11.304 | 28.1734 | 29.4721 |  | 20.6875 | 24.6 | 14.4
| 6.9375 | 283.539 | 46.288 | 56.254 | 50.015 | 74.192 |  | 20.75 | 29.5927 | 27.1492 | 1.3384 | 11.2721 | 28.1405 | 29.4391 |  | 20.7083 | 24.6 | 14.4
| 6.9444 | 283.287 | 46.299 | 56.269 | 50.029 | 74.213 |  | 20.7708 | 29.5898 | 27.1419 | 1.3184 | 11.265 | 28.131 | 29.434 |  | 20.7292 | 24.8 | 14.4
| 6.9514 | 283.311 | 46.318 | 56.294 | 50.043 | 74.24 |  | 20.7917 | 29.5939 | 27.1552 | 1.3424 | 11.2694 | 28.1286 | 29.4404 |  | 20.75 | 24.2 | 14.4
| 6.9583 | 284.618 | 46.333 | 56.313 | 50.07 | 74.267 |  | 20.8125 | 29.6003 | 27.164 | 1.3455 | 11.2787 | 28.1557 | 29.4445 |  | 20.7708 | 24.4 | 14.4
| 6.9653 | 285.405 | 46.359 | 56.338 | 50.09 | 74.304 |  | 20.8333 | 29.6011 | 27.1674 | 1.3546 | 11.2807 | 28.1432 | 29.4497 |  | 20.7917 | 24.1 | 14.4
| 6.9722 | 285.993 | 46.378 | 56.367 | 50.109 | 74.355 |  | 20.8542 | 29.6042 | 27.155 | 1.3236 | 11.271 | 28.1484 | 29.4347 |  | 20.8125 | 23.3 | 14.4
| 6.9792 | 279.138 | 46.405 | 56.398 | 50.135 | 74.4 |  | 20.875 | 29.612 | 27.1675 | 1.3291 | 11.272 | 28.1716 | 29.4425 |  | 20.8333 | 22.8 | 14.4
| 6.9861 | 275.66 | 46.38 | 56.38 | 50.123 | 74.35 |  | 20.8958 | 29.5932 | 27.149 | 1.2988 | 11.2652 | 28.1843 | 29.4192 |  | 20.8542 | 20.8 | 14.4
| 6.9931 | 276.167 | 46.339 | 56.35 | 50.098 | 74.26 |  | 20.9167 | 29.6437 | 27.195 | 1.35 | 11.308 | 28.2277 | 29.4718 |  | 20.875 | 18.9 | 14.4
| 7 | 277.472 | 46.313 | 56.33 | 50.077 | 74.189 |  | 20.9375 | 29.6187 | 27.1792 | 1.3309 | 11.2928 | 28.223 | 29.4469 |  | 20.8958 | 17.4 | 14.4
| 7.0069 | 275.018 | 46.292 | 56.312 | 50.072 | 74.127 |  | 20.9583 | 29.6183 | 27.1789 | 1.3219 | 11.2903 | 28.2113 | 29.4465 |  | 20.9167 | 16.6 | 14.4
| 7.0139 | 275.097 | 46.271 | 56.286 | 50.04 | 74.053 |  | 20.9792 | 29.6342 | 27.2038 | 1.3329 | 11.3102 | 28.2226 | 29.4759 |  | 20.9375 | 15.8 | 14.4
| 7.0208 | 275.508 | 46.244 | 56.262 | 50.024 | 73.983 |  | 21 | 29.6168 | 27.1865 | 1.3164 | 11.2912 | 28.2188 | 29.4584 |  | 20.9583 | 15.3 | 14.4
| 7.0278 | 276.375 | 46.226 | 56.244 | 50.016 | 73.919 |  | 21.0208 | 29.6077 | 27.2 | 1.3187 | 11.2957 | 28.2006 | 29.4562 |  | 20.9792 | 15.2 | 14.4
| 7.0347 | 275.737 | 46.215 | 56.231 | 50 | 73.874 |  | 21.0417 | 29.6145 | 27.2023 | 1.3055 | 11.2978 | 28.2029 | 29.4653 |  | 21 | 15.2 | 14.4
| 7.0417 | 276.09 | 46.207 | 56.21 | 49.99 | 73.831 |  | 21.0625 | 29.5609 | 27.1466 | 1.2606 | 11.2455 | 28.1493 | 29.416 |  | 21.0208 | 14.8 | 14.4
| 7.0486 | 276.507 | 46.205 | 56.205 | 49.979 | 73.802 |  | 21.0833 | 29.5493 | 27.1351 | 1.2386 | 11.2277 | 28.14 | 29.4045 |  | 21.0417 | 14.6 | 14.4
| 7.0556 | 277.094 | 46.2 | 56.202 | 49.976 | 73.778 |  | 21.1042 | 29.5318 | 27.1245 | 1.2223 | 11.211 | 28.1226 | 29.3894 |  | 21.0625 | 14.3 | 14.4
| 7.0625 | 276.686 | 46.202 | 56.197 | 49.977 | 73.764 |  | 21.125 | 29.559 | 27.1563 | 1.2441 | 11.2441 | 28.1565 | 29.4233 |  | 21.0833 | 13.9 | 14.4
| 7.0694 | 277.496 | 46.203 | 56.195 | 49.977 | 73.753 |  | 21.1458 | 29.515 | 27.1192 | 1.2084 | 11.2057 | 28.1058 | 29.3839 |  | 21.1042 | 13.3 | 14.4
| 7.0764 | 277.054 | 46.202 | 56.199 | 49.981 | 73.74 |  | 21.1667 | 29.5053 | 27.1094 | 1.1883 | 11.194 | 28.0983 | 29.3833 |  | 21.125 | 12.8 | 14.4
| 7.0833 | 277.499 | 46.21 | 56.201 | 49.974 | 73.738 |  | 21.1875 | 29.4952 | 27.1015 | 1.1766 | 11.1776 | 28.0836 | 29.3686 |  | 21.1458 | 12.1 | 14.4
| 7.0903 | 278.089 | 46.211 | 56.202 | 49.979 | 73.733 |  | 21.2083 | 29.4823 | 27.0999 | 1.1625 | 11.1699 | 28.064 | 29.3648 |  | 21.1667 | 11.8 | 14.4
| 7.0972 | 278.491 | 46.22 | 56.212 | 49.991 | 73.739 |  | 21.2292 | 29.4914 | 27.1045 | 1.1625 | 11.181 | 28.0934 | 29.3738 |  | 21.1875 | 11.5 | 14.4
| 7.1042 | 278.165 | 46.227 | 56.223 | 49.994 | 73.754 |  | 21.25 | 29.4642 | 27.0842 | 1.1385 | 11.1544 | 28.064 | 29.3467 |  | 21.2083 | 11.2 | 14.4
| 7.1111 | 279.117 | 46.237 | 56.234 | 50 | 73.761 |  | 21.2708 | 29.4714 | 27.0937 | 1.1564 | 11.1681 | 28.0826 | 29.3652 |  | 21.2292 | 10.8 | 14.4
| 7.1181 | 278.486 | 46.246 | 56.244 | 50.007 | 73.767 |  | 21.2917 | 29.4261 | 27.0487 | 1.1061 | 11.1238 | 28.0263 | 29.3246 |  | 21.25 | 10.7 | 14.4
| 7.125 | 279.676 | 46.257 | 56.258 | 50.013 | 73.779 |  | 21.3125 | 29.4921 | 27.121 | 1.18 | 11.1945 | 28.1056 | 29.3971 |  | 21.2708 | 11.2 | 14.4
| 7.1319 | 278.902 | 46.265 | 56.274 | 50.024 | 73.793 |  | 21.3333 | 29.5077 | 27.134 | 1.2012 | 11.2052 | 28.1168 | 29.4172 |  | 21.2917 | 12.5 | 14.4
| 7.1389 | 279.126 | 46.275 | 56.286 | 50.033 | 73.808 |  | 21.3542 | 29.5165 | 27.1449 | 1.2289 | 11.2158 | 28.1236 | 29.4305 |  | 21.3125 | 12.7 | 14.4
| 7.1458 | 279.536 | 46.285 | 56.303 | 50.05 | 73.822 |  | 21.375 | 29.5407 | 27.1687 | 1.2536 | 11.2367 | 28.1367 | 29.4548 |  | 21.3333 | 15.1 | 14.4
| 7.1528 | 279.065 | 46.29 | 56.314 | 50.059 | 73.829 |  | 21.3958 | 29.546 | 27.1872 | 1.2732 | 11.2504 | 28.158 | 29.4714 |  | 21.3542 | 17.4 | 14.4
| 7.1597 | 278.995 | 46.302 | 56.329 | 50.067 | 73.841 |  | 21.4167 | 29.5898 | 27.2353 | 1.3299 | 11.2929 | 28.1906 | 29.5152 |  | 21.375 | 19.5 | 14.4
| 7.1667 | 279.275 | 46.308 | 56.339 | 50.077 | 73.857 |  | 21.4375 | 29.5821 | 27.2364 | 1.3328 | 11.2961 | 28.1763 | 29.5211 |  | 21.3958 | 21.4 | 14.4
| 7.1736 | 279.766 | 46.318 | 56.352 | 50.09 | 73.864 |  | 21.4583 | 29.5947 | 27.249 | 1.3467 | 11.308 | 28.1934 | 29.5361 |  | 21.4167 | 23.1 | 14.4
| 7.1806 | 279.219 | 46.323 | 56.369 | 50.099 | 73.876 |  | 21.4792 | 29.6156 | 27.2673 | 1.3746 | 11.3233 | 28.2139 | 29.5569 |  | 21.4375 | 23.8 | 14.4
| 7.1875 | 279.684 | 46.334 | 56.385 | 50.115 | 73.892 |  | 21.5 | 29.593 | 27.2356 | 1.3384 | 11.2891 | 28.2069 | 29.532 |  | 21.4583 | 24.6 | 14.4
| 7.1944 | 279.816 | 46.342 | 56.401 | 50.126 | 73.905 |  | 21.5208 | 29.5614 | 27.1996 | 1.3142 | 11.2626 | 28.1842 | 29.5049 |  | 21.4792 | 24.8 | 14.4
| 7.2014 | 279.856 | 46.355 | 56.417 | 50.143 | 73.918 |  | 21.5417 | 29.5839 | 27.2083 | 1.3219 | 11.2663 | 28.193 | 29.5206 |  | 21.5 | 26.3 | 14.4
| 7.2083 | 279.516 | 46.366 | 56.442 | 50.152 | 73.933 |  | 21.5625 | 29.5598 | 27.1931 | 1.3004 | 11.2467 | 28.1913 | 29.5079 |  | 21.5208 | 26.6 | 14.4
| 7.2153 | 279.634 | 46.378 | 56.454 | 50.159 | 73.949 |  | 21.5833 | 29.5539 | 27.1782 | 1.2811 | 11.234 | 28.1763 | 29.4931 |  | 21.5417 | 26.4 | 14.4
| 7.2222 | 280.159 | 46.379 | 56.479 | 50.177 | 73.959 |  | 21.6042 | 29.5155 | 27.1466 | 1.2526 | 11.203 | 28.1469 | 29.4682 |  | 21.5625 | 26.7 | 14.4
| 7.2292 | 279.614 | 46.395 | 56.494 | 50.186 | 73.976 |  | 21.625 | 29.5449 | 27.1782 | 1.2811 | 11.2319 | 28.1831 | 29.4931 |  | 21.5833 | 27.4 | 14.4
| 7.2361 | 277.866 | 46.404 | 56.516 | 50.202 | 73.996 |  | 21.6458 | 29.5649 | 27.187 | 1.2875 | 11.2383 | 28.2032 | 29.5062 |  | 21.6042 | 28.4 | 14.4
| 7.2431 | 278.179 | 46.412 | 56.526 | 50.212 | 73.996 |  | 21.6667 | 29.5719 | 27.1919 | 1.2778 | 11.2416 | 28.2332 | 29.5087 |  | 21.625 | 28.4 | 14.4
| 7.25 | 279.268 | 46.409 | 56.541 | 50.22 | 73.992 |  | 21.6875 | 29.5784 | 27.1941 | 1.2854 | 11.2466 | 28.247 | 29.522 |  | 21.6458 | 28.3 | 14.4
| 7.2569 | 276.556 | 46.411 | 56.54 | 50.221 | 73.982 |  | 21.7083 | 29.5621 | 27.1803 | 1.2685 | 11.2314 | 28.2328 | 29.5033 |  | 21.6667 | 27.4 | 14.4
| 7.2639 | 276.322 | 46.399 | 56.536 | 50.22 | 73.947 |  | 21.7292 | 29.5878 | 27.2015 | 1.302 | 11.252 | 28.2561 | 29.5245 |  | 21.6875 | 25.4 | 15
| 7.2708 | 276.627 | 46.386 | 56.527 | 50.214 | 73.916 |  | 21.75 | 29.5777 | 27.1465 | 1.2738 | 11.2388 | 28.0906 | 29.51 |  | 21.7083 | 24.2 | 15
| 7.2778 | 276.158 | 46.382 | 56.522 | 50.213 | 73.89 |  | 21.7708 | 29.5592 | 27.1306 | 1.2675 | 11.234 | 28.0831 | 29.5051 |  | 21.7292 | 23.7 | 15
| 7.2847 | 276.413 | 46.379 | 56.524 | 50.213 | 73.859 |  | 21.7917 | 29.5513 | 27.132 | 1.2522 | 11.218 | 28.2216 | 29.4948 |  | 21.75 | 23.1 | 15
| 7.2917 | 279.319 | 46.378 | 56.528 | 50.212 | 73.847 |  | 21.8125 | 29.5526 | 27.1242 | 1.2492 | 11.217 | 28.2362 | 29.4984 |  | 21.7708 | 22.3 | 15
| 7.2986 | 279.588 | 46.399 | 56.545 | 50.235 | 73.877 |  | 21.8333 | 29.5561 | 27.1211 | 1.242 | 11.2162 | 28.1991 | 29.4996 |  | 21.7917 | 18.6 | 15
| 7.3056 | 278.936 | 46.42 | 56.566 | 50.247 | 73.898 |  | 21.8542 | 29.5877 | 27.2001 | 1.2704 | 11.2471 | 28.2961 | 29.5312 |  | 21.8125 | 18.4 | 15
| 7.3125 | 279.081 | 46.432 | 56.582 | 50.252 | 73.92 |  | 21.875 | 29.5444 | 27.1231 | 1.225 | 11.2032 | 28.0951 | 29.4835 |  | 21.8333 | 18.4 | 15
| 7.3194 | 278.464 | 46.44 | 56.593 | 50.264 | 73.929 |  | 21.8958 | 29.5826 | 27.1478 | 1.2575 | 11.2382 | 28.1194 | 29.5193 |  | 21.8542 | 17.6 | 15
| 7.3264 | 278.562 | 46.444 | 56.602 | 50.277 | 73.935 |  | 21.9167 | 29.5916 | 27.1862 | 1.2662 | 11.2559 | 28.1962 | 29.5397 |  | 21.875 | 17.7 | 15
| 7.3333 | 277.929 | 46.454 | 56.615 | 50.288 | 73.943 |  | 21.9375 | 29.5497 | 27.1174 | 1.2152 | 11.2128 | 28.1113 | 29.4978 |  | 21.8958 | 17.8 | 15
| 7.3403 | 277.496 | 46.453 | 56.622 | 50.287 | 73.937 |  | 21.9583 | 29.5248 | 27.1039 | 1.1851 | 11.1932 | 28.0683 | 29.4751 |  | 21.9167 | 16.7 | 15
| 7.3472 | 276.31 | 46.459 | 56.625 | 50.293 | 73.931 |  | 21.9792 | 29.5125 | 27.0985 | 1.1735 | 11.1857 | 28.0606 | 29.4741 |  | 21.9375 | 16.5 | 15
| 7.3542 | 275.893 | 46.453 | 56.622 | 50.291 | 73.914 |  | 22 | 29.5149 | 27.1053 | 1.1713 | 11.199 | 28.0808 | 29.4944 |  | 21.9583 | 15.7 | 15
| 7.3611 | 275.111 | 46.449 | 56.62 | 50.288 | 73.892 |  | 22.0208 | 29.4903 | 27.092 | 1.1451 | 11.1793 | 28.0428 | 29.4698 |  | 21.9792 | 13.8 | 15
| 7.3681 | 278.909 | 46.448 | 56.624 | 50.286 | 73.872 |  | 22.0417 | 29.4789 | 27.0897 | 1.1365 | 11.1793 | 28.0338 | 29.4744 |  | 22 | 13.4 | 15
| 7.375 | 280.423 | 46.464 | 56.647 | 50.308 | 73.903 |  | 22.0625 | 29.4812 | 27.0943 | 1.1342 | 11.1771 | 28.036 | 29.4766 |  | 22.0208 | 13.3 | 15
| 7.3819 | 279.786 | 46.492 | 56.674 | 50.332 | 73.955 |  | 22.0833 | 29.4676 | 27.083 | 1.1211 | 11.166 | 28.0044 | 29.4698 |  | 22.0417 | 13.4 | 15
| 7.3889 | 279.113 | 46.516 | 56.699 | 50.353 | 73.996 |  | 22.1042 | 29.4563 | 27.0853 | 1.1146 | 11.1638 | 27.9819 | 29.4676 |  | 22.0625 | 13.4 | 15
| 7.3958 | 278.579 | 46.528 | 56.715 | 50.363 | 74.018 |  | 22.125 | 29.4428 | 27.0694 | 1.108 | 11.155 | 27.9887 | 29.4586 |  | 22.0833 | 13.3 | 15
| 7.4028 | 278.363 | 46.536 | 56.728 | 50.373 | 74.033 |  | 22.1458 | 29.4247 | 27.0582 | 1.0949 | 11.1395 | 27.9661 | 29.4518 |  | 22.1042 | 13.3 | 15
| 7.4097 | 277.558 | 46.539 | 56.737 | 50.376 | 74.035 |  | 22.1667 | 29.4315 | 27.0672 | 1.0927 | 11.1461 | 27.9481 | 29.4518 |  | 22.125 | 13.4 | 15
| 7.4167 | 276.244 | 46.545 | 56.742 | 50.388 | 74.038 |  | 22.1875 | 29.4518 | 27.092 | 1.1058 | 11.166 | 27.9639 | 29.4879 |  | 22.1458 | 13.4 | 15
| 7.4236 | 275.256 | 46.54 | 56.745 | 50.385 | 74.017 |  | 22.2083 | 29.4224 | 27.0718 | 1.0913 | 11.1377 | 27.9233 | 29.4654 |  | 22.1667 | 13.4 | 15
| 7.4306 | 276.465 | 46.539 | 56.746 | 50.386 | 74.006 |  | 22.2292 | 29.4427 | 27.0944 | 1.0957 | 11.1643 | 27.9706 | 29.4812 |  | 22.1875 | 13.3 | 15
| 7.4375 | 276.436 | 46.547 | 56.749 | 50.393 | 73.995 |  | 22.25 | 29.4427 | 27.0877 | 1.0913 | 11.1598 | 27.9638 | 29.4879 |  | 22.2083 | 12.9 | 15
| 7.4444 | 275.781 | 46.548 | 56.75 | 50.387 | 73.984 |  | 22.2708 | 29.4053 | 27.0571 | 1.0555 | 11.1257 | 27.9152 | 29.4528 |  | 22.2292 | 12.6 | 15
| 7.4514 | 276.277 | 46.549 | 56.756 | 50.393 | 73.98 |  | 22.2917 | 29.394 | 27.048 | 1.0489 | 11.1146 | 27.9288 | 29.4528 |  | 22.25 | 12.3 | 15
| 7.4583 | 276.437 | 46.556 | 56.765 | 50.4 | 73.98 |  | 22.3125 | 29.3646 | 27.0232 | 1.0183 | 11.0859 | 27.8882 | 29.4256 |  | 22.2708 | 12.2 | 15
| 7.4653 | 273.759 | 46.557 | 56.762 | 50.403 | 73.974 |  | 22.3333 | 29.4211 | 27.0727 | 1.0658 | 11.1298 | 27.9357 | 29.4754 |  | 22.2917 | 12.2 | 15
| 7.4722 | 273.062 | 46.544 | 56.753 | 50.395 | 73.941 |  | 22.3542 | 29.3556 | 27.0118 | 1.009 | 11.0745 | 28.0416 | 29.4167 |  | 22.3125 | 12.3 | 15
| 7.4792 | 277.395 | 46.55 | 56.751 | 50.399 | 73.921 |  | 22.375 | 29.4189 | 27.1246 | 1.0725 | 11.1321 | 28.0981 | 29.4822 |  | 22.3333 | 12.6 | 15
| 7.4861 | 277.536 | 46.564 | 56.771 | 50.411 | 73.953 |  | 22.3958 | 29.3783 | 27.0817 | 1.0288 | 11.0901 | 28.0733 | 29.446 |  | 22.3542 | 13.1 | 15
| 7.4931 | 277.221 | 46.585 | 56.792 | 50.422 | 73.98 |  | 22.4167 | 29.4135 | 27.1145 | 1.0408 | 11.1135 | 28.0838 | 29.4677 |  | 22.375 | 13.3 | 15
| 7.5 | 276.896 | 46.597 | 56.799 | 50.434 | 74.003 |  | 22.4375 | 29.3683 | 27.0716 | 1.0233 | 11.0715 | 28.0544 | 29.4429 |  | 22.3958 | 13.9 | 15
| 7.5069 | 277.659 | 46.612 | 56.809 | 50.447 | 74.012 |  | 22.4583 | 29.4174 | 27.1251 | 1.0616 | 11.1347 | 28.1013 | 29.4919 |  | 22.4167 | 14.2 | 15
| 7.5139 | 277.018 | 46.624 | 56.822 | 50.453 | 74.031 |  | 22.4792 | 29.3586 | 27.0867 | 1.0353 | 11.0949 | 28.0631 | 29.4626 |  | 22.4375 | 14.8 | 15
| 7.5208 | 276.51 | 46.637 | 56.834 | 50.464 | 74.036 |  | 22.5 | 29.4106 | 27.0731 | 1.079 | 11.1347 | 27.9615 | 29.5078 |  | 22.4583 | 15.2 | 15
| 7.5278 | 276.631 | 46.638 | 56.841 | 50.472 | 74.046 |  | 22.5208 | 29.3924 | 27.0618 | 1.0789 | 11.128 | 27.9345 | 29.501 |  | 22.4792 | 14.8 | 15
| 7.5347 | 275.899 | 46.64 | 56.855 | 50.481 | 74.053 |  | 22.5417 | 29.3969 | 27.0529 | 1.0491 | 11.1129 | 27.9524 | 29.501 |  | 22.5 | 15.7 | 15
| 7.5417 | 276.796 | 46.649 | 56.862 | 50.493 | 74.055 |  | 22.5625 | 29.3879 | 27.0372 | 1.0402 | 11.1062 | 27.932 | 29.4875 |  | 22.5208 | 14.6 | 15
| 7.5486 | 276.985 | 46.66 | 56.873 | 50.499 | 74.064 |  | 22.5833 | 29.3676 | 27.0305 | 1.0249 | 11.1017 | 27.932 | 29.4806 |  | 22.5417 | 14.3 | 15
| 7.5556 | 277.075 | 46.667 | 56.886 | 50.502 | 74.088 |  | 22.6042 | 29.3558 | 27.0209 | 1.013 | 11.0923 | 28.0489 | 29.4802 |  | 22.5625 | 13.5 | 15
| 7.5625 | 276.322 | 46.679 | 56.895 | 50.516 | 74.097 |  | 22.625 | 29.3514 | 26.9916 | 0.98463 | 11.0678 | 28.0714 | 29.4622 |  | 22.5833 | 13.3 | 15
| 7.5694 | 277.16 | 46.687 | 56.899 | 50.524 | 74.109 |  | 22.6458 | 29.3611 | 27.0239 | 1.01 | 11.0868 | 28.0813 | 29.4788 |  | 22.6042 | 13.7 | 15
| 7.5764 | 275.119 | 46.692 | 56.909 | 50.528 | 74.113 |  | 22.6667 | 29.3476 | 27.042 | 0.97721 | 11.0735 | 28.0633 | 29.4766 |  | 22.625 | 14.3 | 15
| 7.5833 | 275.238 | 46.697 | 56.911 | 50.53 | 74.108 |  | 22.6875 | 29.3804 | 27.1017 | 1.0305 | 11.1121 | 28.0961 | 29.5138 |  | 22.6458 | 14 | 15
| 7.5903 | 275.694 | 46.699 | 56.912 | 50.528 | 74.1 |  | 22.7083 | 29.3804 | 27.086 | 1.0174 | 11.101 | 28.1006 | 29.507 |  | 22.6667 | 13.7 | 15
| 7.5972 | 275.017 | 46.71 | 56.916 | 50.534 | 74.097 |  | 22.7292 | 29.3646 | 27.0882 | 1.0218 | 11.101 | 28.0759 | 29.507 |  | 22.6875 | 14 | 15
| 7.6042 | 275.27 | 46.706 | 56.919 | 50.535 | 74.093 |  | 22.75 | 29.3601 | 27.0701 | 0.99987 | 11.0921 | 28.0893 | 29.498 |  | 22.7083 | 14.8 | 15
| 7.6111 | 275.294 | 46.707 | 56.921 | 50.537 | 74.087 |  | 22.7708 | 29.394 | 27.0995 | 1.0349 | 11.1121 | 28.0961 | 29.5274 |  | 22.7292 | 15.1 | 15
| 7.6181 | 276.147 | 46.715 | 56.93 | 50.541 | 74.091 |  | 22.7917 | 29.379 | 27.098 | 1.0135 | 11.1082 | 28.0945 | 29.5192 |  | 22.75 | 15.1 | 15
| 7.625 | 275.816 | 46.721 | 56.933 | 50.545 | 74.095 |  | 22.8125 | 29.3531 | 27.079 | 0.9887 | 11.0896 | 28.071 | 29.5023 |  | 22.7708 | 15.2 | 15
| 7.6319 | 275.742 | 46.729 | 56.936 | 50.56 | 74.101 |  | 22.8333 | 29.3463 | 27.0723 | 0.98645 | 11.0762 | 28.0505 | 29.4933 |  | 22.7917 | 14.8 | 15
| 7.6389 | 275.409 | 46.735 | 56.948 | 50.564 | 74.109 |  | 22.8542 | 29.3181 | 27.051 | 0.95724 | 11.0621 | 28.0472 | 29.4832 |  | 22.8125 | 14.6 | 15
| 7.6458 | 275.219 | 46.744 | 56.954 | 50.572 | 74.116 |  | 22.875 | 29.3384 | 27.0668 | 0.97264 | 11.0776 | 28.0607 | 29.5035 |  | 22.8333 | 13.7 | 15
| 7.6528 | 275.708 | 46.754 | 56.96 | 50.581 | 74.121 |  | 22.8958 | 29.3408 | 27.0713 | 0.97264 | 11.0887 | 28.0652 | 29.5125 |  | 22.8542 | 13.2 | 15
| 7.6597 | 275.238 | 46.764 | 56.962 | 50.587 | 74.13 |  | 22.9167 | 29.343 | 27.0849 | 0.98792 | 11.0931 | 28.0405 | 29.5239 |  | 22.875 | 12.9 | 15
| 7.6667 | 276.056 | 46.771 | 56.975 | 50.591 | 74.142 |  | 22.9375 | 29.3058 | 27.0388 | 0.9305 | 11.0548 | 28.035 | 29.4822 |  | 22.8958 | 12.9 | 15
| 7.6736 | 275.25 | 46.78 | 56.982 | 50.603 | 74.149 |  | 22.9583 | 29.3058 | 27.0366 | 0.92172 | 11.0592 | 28.0553 | 29.4845 |  | 22.9167 | 12.9 | 15
| 7.6806 | 274.594 | 46.784 | 56.987 | 50.608 | 74.153 |  | 22.9792 | 29.2968 | 27.0456 | 0.9305 | 11.0569 | 28.044 | 29.4913 |  | 22.9375 | 12.8 | 15
| 7.6875 | 273.304 | 46.784 | 56.989 | 50.614 | 74.149 |  | 23 | 29.2683 | 27.0217 | 0.90113 | 11.036 | 28.0134 | 29.4696 |  | 22.9583 | 12.7 | 15
| 7.6944 | 274.141 | 46.785 | 56.99 | 50.61 | 74.136 |  | 23.0208 | 29.2683 | 27.0173 | 0.89677 | 11.0316 | 27.9998 | 29.4696 |  | 22.9792 | 12.7 | 15
| 7.7014 | 273.248 | 46.781 | 56.983 | 50.614 | 74.128 |  | 23.0417 | 29.2637 | 27.0173 | 0.89026 | 11.0293 | 27.9952 | 29.4696 |  | 23 | 12.6 | 15
| 7.7083 | 273.748 | 46.785 | 56.987 | 50.616 | 74.121 |  | 23.0625 | 29.266 | 27.0173 | 0.88579 | 11.0272 | 27.9975 | 29.4741 |  | 23.0208 | 12.4 | 15
| 7.7153 | 273.982 | 46.791 | 56.991 | 50.618 | 74.124 |  | 23.0833 | 29.2706 | 27.0262 | 0.90113 | 11.0404 | 27.9998 | 29.4877 |  | 23.0417 | 12.3 | 15
| 7.7222 | 274.094 | 46.795 | 56.996 | 50.619 | 74.128 |  | 23.1042 | 29.2397 | 27.0022 | 0.86218 | 11.0055 | 27.9711 | 29.4567 |  | 23.0625 | 12.2 | 15
| 7.7292 | 273.626 | 46.8 | 57 | 50.628 | 74.125 |  | 23.125 | 29.2351 | 26.9931 | 0.85997 | 11.0033 | 27.9666 | 29.4567 |  | 23.0833 | 12.1 | 15
| 7.7361 | 280.556 | 46.825 | 57.02 | 50.65 | 74.166 |  | 23.1458 | 29.2374 | 26.9999 | 0.85997 | 11.0055 | 27.9734 | 29.459 |  | 23.1042 | 12.1 | 15
| 7.7431 | 280.943 | 46.874 | 57.076 | 50.685 | 74.27 |  | 23.1667 | 29.2329 | 26.9954 | 0.85555 | 11.0099 | 27.9802 | 29.459 |  | 23.125 | 12.1 | 15
| 7.75 | 280.65 | 46.921 | 57.118 | 50.724 | 74.365 |  | 23.1875 | 29.2225 | 26.9513 | 0.84608 | 11.0089 | 27.8188 | 29.4555 |  | 23.1458 | 12 | 15
| 7.7569 | 280.735 | 46.963 | 57.167 | 50.764 | 74.454 |  | 23.2083 | 29.2266 | 26.9419 | 0.84576 | 11.0108 | 27.8162 | 29.4619 |  | 23.1667 | 11.9 | 15
| 7.7639 | 281.191 | 46.994 | 57.206 | 50.794 | 74.536 |  | 23.2292 | 29.2002 | 26.9269 | 0.82497 | 10.9984 | 27.7806 | 29.4489 |  | 23.1875 | 11.9 | 15
| 7.7708 | 280.646 | 47.027 | 57.238 | 50.825 | 74.608 |  | 23.25 | 29.1956 | 26.9223 | 0.82061 | 10.994 | 27.8144 | 29.4421 |  | 23.2083 | 11.8 | 15
| 7.7778 | 280.745 | 47.055 | 57.274 | 50.855 | 74.67 |  | 23.2708 | 29.1685 | 26.9359 | 0.79871 | 10.9675 | 27.9046 | 29.4172 |  | 23.2292 | 11.4 | 15
| 7.7847 | 281.28 | 47.083 | 57.304 | 50.882 | 74.727 |  | 23.2917 | 29.207 | 26.9921 | 0.84396 | 11.0091 | 27.8393 | 29.4648 |  | 23.25 | 11.3 | 15
| 7.7917 | 280.037 | 47.1 | 57.334 | 50.902 | 74.776 |  | 23.3125 | 29.2182 | 26.9447 | 0.84616 | 11.0268 | 27.7965 | 29.4693 |  | 23.2708 | 11.3 | 15
| 7.7986 | 280.85 | 47.122 | 57.355 | 50.925 | 74.821 |  | 23.3333 | 29.1802 | 26.9204 | 0.82083 | 10.9965 | 27.7788 | 29.4537 |  | 23.2917 | 11.5 | 15
| 7.8056 | 281.472 | 47.143 | 57.386 | 50.952 | 74.863 |  | 23.3542 | 29.1892 | 26.9249 | 0.82524 | 11.0097 | 27.7855 | 29.4605 |  | 23.3125 | 11.7 | 15
| 7.8125 | 281.47 | 47.164 | 57.415 | 50.97 | 74.91 |  | 23.375 | 29.187 | 26.9249 | 0.83175 | 11.0097 | 27.7833 | 29.4673 |  | 23.3333 | 11.8 | 15
| 7.8194 | 281.037 | 47.186 | 57.448 | 50.997 | 74.962 |  | 23.3958 | 29.1937 | 26.9362 | 0.83611 | 11.012 | 27.79 | 29.4741 |  | 23.3542 | 11.4 | 15
| 7.8264 | 43.323 | 47.205 | 57.475 | 51.017 | 74.998 |  | 23.4167 | 29.1688 | 26.9159 | 0.81432 | 10.9943 | 27.7743 | 29.456 |  | 23.375 | 11.3 | 15
| 7.8333 | 278.753 | 46.747 | 56.993 | 50.664 | 74.025 |  | 23.4375 | 29.1666 | 26.9181 | 0.80769 | 11.0032 | 27.7923 | 29.4605 |  | 23.3958 | 11.2 | 15
| 7.8403 | 278.361 | 46.732 | 57.004 | 50.646 | 73.924 |  | 23.4583 | 29.1621 | 26.9069 | 0.80555 | 10.9965 | 27.7878 | 29.456 |  | 23.4167 | 11.2 | 15
| 7.8472 | 278.912 | 46.803 | 57.066 | 50.704 | 74.045 |  | 23.4792 | 29.1463 | 26.8888 | 0.77062 | 10.9766 | 27.7675 | 29.4379 |  | 23.4375 | 11.3 | 15
| 7.8542 | 279.172 | 46.871 | 57.118 | 50.744 | 74.151 |  | 23.5 | 29.1304 | 26.873 | 0.75749 | 10.9567 | 27.7539 | 29.4289 |  | 23.4583 | 11.3 | 15
| 7.8611 | 279.559 | 46.927 | 57.159 | 50.775 | 74.246 |  | 23.5208 | 29.1237 | 26.8798 | 0.75093 | 10.9611 | 27.7743 | 29.4266 |  | 23.4792 | 11.2 | 15
| 7.8681 | 280.755 | 46.966 | 57.197 | 50.811 | 74.333 |  | 23.5417 | 29.1191 | 26.8617 | 0.72908 | 10.9522 | 27.7653 | 29.4153 |  | 23.5 | 11.4 | 15
| 7.875 | 280.366 | 47.001 | 57.23 | 50.841 | 74.4 |  | 23.5625 | 29.1056 | 26.8527 | 0.72478 | 10.939 | 27.7494 | 29.404 |  | 23.5208 | 11.6 | 15
| 7.8819 | 279.764 | 47.027 | 57.264 | 50.864 | 74.463 |  | 23.5833 | 29.1457 | 26.8971 | 0.75637 | 10.9801 | 27.8007 | 29.4486 |  | 23.5417 | 11.4 | 15
| 7.8889 | 281.863 | 47.06 | 57.302 | 50.893 | 74.539 |  | 23.6042 | 29.1299 | 26.8791 | 0.74329 | 10.9647 | 27.7872 | 29.435 |  | 23.5625 | 11.4 | 15
| 7.8958 | 282.576 | 47.087 | 57.339 | 50.925 | 74.609 |  | 23.625 | 29.1389 | 26.8881 | 0.74771 | 10.9735 | 27.7939 | 29.4418 |  | 23.5833 | 11.4 | 15
| 7.9028 | 282.683 | 47.113 | 57.374 | 50.953 | 74.671 |  | 23.6458 | 29.1118 | 26.87 | 0.73016 | 10.9558 | 27.7805 | 29.4328 |  | 23.6042 | 11.7 | 15
| 7.9097 | 282.75 | 47.137 | 57.41 | 50.979 | 74.734 |  | 23.6667 | 29.1163 | 26.8723 | 0.72581 | 10.958 | 27.7895 | 29.4305 |  | 23.625 | 11.9 | 15
| 7.9167 | 282.887 | 47.165 | 57.445 | 51.01 | 74.795 |  | 23.6875 | 29.1118 | 26.8723 | 0.7193 | 10.9602 | 27.7737 | 29.4283 |  | 23.6458 | 11.6 | 15
| 7.9236 | 283.24 | 47.187 | 57.475 | 51.045 | 74.851 |  | 23.7083 | 29.1118 | 26.8677 | 0.7193 | 10.9558 | 27.7715 | 29.4328 |  | 23.6667 | 11.8 | 15
| 7.9306 | 283.419 | 47.214 | 57.512 | 51.068 | 74.903 |  | 23.7292 | 29.1005 | 26.8543 | 0.6996 | 10.9491 | 27.7579 | 29.4192 |  | 23.6875 | 11.8 | 15
| 7.9375 | 284.018 | 47.233 | 57.545 | 51.093 | 74.959 |  | 23.75 | 29.0801 | 26.8429 | 0.68211 | 10.9381 | 27.7827 | 29.4057 |  | 23.7083 | 11.6 | 15
| 7.9444 | 45.521 | 47.233 | 57.557 | 51.1 | 74.983 |  | 23.7708 | 29.0621 | 26.8272 | 0.66468 | 10.9226 | 27.7467 | 29.3943 |  | 23.7292 | 11.6 | 15
| 7.9514 | 280.682 | 46.633 | 56.943 | 50.636 | 73.677 |  | 23.7917 | 29.0711 | 26.8317 | 0.6559 | 10.9226 | 27.7625 | 29.3876 |  | 23.75 | 11.5 | 15
| 7.9583 | 279.509 | 46.649 | 56.979 | 50.64 | 73.622 |  | 23.8125 | 29.0898 | 26.8547 | 0.67167 | 10.9454 | 27.7857 | 29.4221 |  | 23.7708 | 11.6 | 15
| 7.9653 | 279.816 | 46.742 | 57.061 | 50.706 | 73.784 |  | 23.8333 | 29.083 | 26.8525 | 0.67167 | 10.9498 | 27.815 | 29.4198 |  | 23.7917 | 11.5 | 15
| 7.9722 | 281.06 | 46.835 | 57.128 | 50.767 | 73.933 |  | 23.8542 | 29.0762 | 26.866 | 0.67388 | 10.9498 | 27.842 | 29.4244 |  | 23.8125 | 11.4 | 15
| 7.9792 | 281.408 | 46.902 | 57.184 | 50.813 | 74.059 |  | 23.875 | 29.0785 | 26.8683 | 0.67609 | 10.9586 | 27.8307 | 29.4334 |  | 23.8333 | 11.4 | 15
| 7.9861 | 281.116 | 46.958 | 57.234 | 50.85 | 74.171 |  | 23.8958 | 29.0807 | 26.8729 | 0.66952 | 10.963 | 27.8285 | 29.4357 |  | 23.8542 | 11.1 | 15
| 7.9931 | 281.325 | 47.004 | 57.279 | 50.886 | 74.271 |  | 23.9167 | 29.0582 | 26.8637 | 0.6586 | 10.9387 | 27.7993 | 29.4312 |  | 23.875 | 11.2 | 15
| 8 | 281.753 | 47.044 | 57.321 | 50.918 | 74.357 |  | 23.9375 | 29.0446 | 26.857 | 0.64773 | 10.9431 | 27.7812 | 29.4176 |  | 23.8958 | 10.8 | 15
| 8.0069 | 278.558 | 47.07 | 57.354 | 50.94 | 74.418 |  | 23.9583 | 29.0468 | 26.8615 | 0.64988 | 10.9431 | 27.7564 | 29.4198 |  | 23.9167 | 10.7 | 15
| 8.0139 | 278.96 | 47.078 | 57.373 | 50.954 | 74.449 |  | 23.9792 | 29.0468 | 26.8593 | 0.64553 | 10.9409 | 27.7654 | 29.4221 |  | 23.9375 | 10.6 | 15
| 8.0208 | 278.876 | 47.09 | 57.399 | 50.973 | 74.484 |  | 24 | 29.0491 | 26.8637 | 0.6586 | 10.9431 | 27.7496 | 29.4267 |  | 23.9583 | 10.6 | 15
| 8.0278 | 277.487 | 47.104 | 57.418 | 50.985 | 74.512 |  | 24.0208 | 29.0265 | 26.8503 | 0.6346 | 10.9387 | 27.7542 | 29.4153 |  | 23.9792 | 10.6 | 15
| 8.0347 | 277.672 | 47.112 | 57.432 | 50.996 | 74.527 |  | 24.0417 | 29.022 | 26.8525 | 0.63239 | 10.9365 | 27.7316 | 29.4108 |  | 24 | 10.4 | 15
| 8.0417 | 278.317 | 47.117 | 57.45 | 51.008 | 74.538 |  | 24.0625 | 29.0242 | 26.8525 | 0.64111 | 10.9387 | 27.7249 | 29.4131 |  | 24.0208 | 10.4 | 15
| 8.0486 | 278.52 | 47.129 | 57.468 | 51.024 | 74.558 |  | 24.0833 | 29.0152 | 26.8525 | 0.62798 | 10.9321 | 27.7181 | 29.4153 |  | 24.0417 | 10.4 | 15
| 8.0556 | 278.49 | 47.138 | 57.489 | 51.038 | 74.579 |  | 24.1042 | 29.013 | 26.8503 | 0.63025 | 10.9409 | 27.7316 | 29.4198 |  | 24.0625 | 10.4 | 15
| 8.0625 | 278.584 | 47.151 | 57.51 | 51.055 | 74.598 |  | 24.125 | 29.0197 | 26.8615 | 0.63675 | 10.9431 | 27.7316 | 29.4267 |  | 24.0833 | 10.4 | 15
| 8.0694 | 278.279 | 47.165 | 57.53 | 51.069 | 74.624 |  | 24.1458 | 29.0311 | 26.866 | 0.64988 | 10.9519 | 27.7406 | 29.4312 |  | 24.1042 | 10.4 | 15
| 8.0764 | 279.534 | 47.178 | 57.56 | 51.087 | 74.647 |  | 24.1667 | 28.9957 | 26.842 | 0.62046 | 10.922 | 27.712 | 29.407 |  | 24.125 | 10.3 | 15
| 8.0833 | 279.558 | 47.197 | 57.577 | 51.106 | 74.677 |  | 24.1875 | 28.9934 | 26.8466 | 0.61395 | 10.9309 | 27.7143 | 29.4138 |  | 24.1458 | 10.2 | 15
| 8.0903 | 279.577 | 47.208 | 57.599 | 51.12 | 74.704 |  | 24.2083 | 28.9957 | 26.8466 | 0.6096 | 10.9309 | 27.7075 | 29.4092 |  | 24.1667 | 10.1 | 15
| 8.0972 | 279.061 | 47.222 | 57.619 | 51.14 | 74.724 |  | 24.2292 | 28.9798 | 26.8285 | 0.59211 | 10.9198 | 27.7075 | 29.4003 |  | 24.1875 | 10 | 15
| 8.1042 | 279.362 | 47.237 | 57.647 | 51.158 | 74.756 |  | 24.25 | 28.9483 | 26.8082 | 0.57241 | 10.8955 | 27.6783 | 29.3731 |  | 24.2083 | 9.8 | 15
| 8.1111 | 279.196 | 47.256 | 57.668 | 51.174 | 74.777 |  | 24.2708 | 28.954 | 26.8184 | 0.5755 | 10.901 | 27.6818 | 29.3879 |  | 24.2292 | 9.7 | 15
| 8.1181 | 279.289 | 47.269 | 57.693 | 51.19 | 74.807 |  | 24.2917 | 28.9647 | 26.838 | 0.605 | 10.9199 | 27.7443 | 29.4009 |  | 24.25 | 10.1 | 15
| 8.125 | 279.51 | 47.284 | 57.71 | 51.205 | 74.828 |  | 24.3125 | 28.9105 | 26.7906 | 0.54167 | 10.8647 | 27.7759 | 29.3512 |  | 24.2708 | 10.2 | 15
| 8.1319 | 278.782 | 47.295 | 57.738 | 51.222 | 74.852 |  | 24.3333 | 28.9397 | 26.867 | 0.57787 | 10.9084 | 27.8119 | 29.3917 |  | 24.2917 | 10.6 | 15
| 8.1389 | 279.916 | 47.31 | 57.754 | 51.235 | 74.876 |  | 24.3542 | 28.8968 | 26.84 | 0.53841 | 10.862 | 27.7646 | 29.3465 |  | 24.3125 | 11.2 | 15
| 8.1458 | 279.514 | 47.319 | 57.773 | 51.254 | 74.897 |  | 24.375 | 28.9327 | 26.8758 | 0.57986 | 10.9062 | 27.805 | 29.3915 |  | 24.3333 | 11.6 | 15
| 8.1528 | 279.122 | 47.337 | 57.794 | 51.272 | 74.916 |  | 24.3958 | 28.9584 | 26.8967 | 0.61085 | 10.9356 | 27.8194 | 29.4126 |  | 24.3542 | 11.7 | 15
| 8.1597 | 279.609 | 47.35 | 57.81 | 51.289 | 74.934 |  | 24.4167 | 28.9329 | 26.878 | 0.59424 | 10.9105 | 27.8032 | 29.4029 |  | 24.375 | 12.1 | 15
| 8.1667 | 279.281 | 47.363 | 57.821 | 51.299 | 74.951 |  | 24.4375 | 28.8969 | 26.8418 | 0.55479 | 10.8818 | 27.7784 | 29.3645 |  | 24.3958 | 12.5 | 15
| 8.1736 | 279.39 | 47.369 | 57.842 | 51.321 | 74.971 |  | 24.4583 | 28.8878 | 26.8441 | 0.56356 | 10.8818 | 27.7897 | 29.3691 |  | 24.4167 | 12.9 | 15
| 8.1806 | 279.028 | 47.383 | 57.859 | 51.338 | 74.988 |  | 24.4792 | 28.9155 | 26.883 | 0.57918 | 10.9025 | 27.8061 | 29.3944 |  | 24.4375 | 13.7 | 15
| 8.1875 | 216.403 | 47.378 | 57.86 | 51.337 | 74.981 |  | 24.5 | 28.8817 | 26.8311 | 0.55071 | 10.8848 | 27.7745 | 29.3674 |  | 24.4583 | 13.8 | 15
| 8.1944 | 273.796 | 47.192 | 57.67 | 51.191 | 74.541 |  | 24.5208 | 28.8817 | 26.8334 | 0.55949 | 10.8826 | 27.7881 | 29.3696 |  | 24.4792 | 13.8 | 15
| 8.2014 | 272.921 | 47.184 | 57.675 | 51.183 | 74.503 |  | 24.5417 | 28.9064 | 26.8559 | 0.57692 | 10.9088 | 27.8106 | 29.399 |  | 24.5 | 14.1 | 15
| 8.2083 | 280.822 | 47.216 | 57.7 | 51.209 | 74.535 |  | 24.5625 | 28.911 | 26.8672 | 0.5879 | 10.9154 | 27.8218 | 29.408 |  | 24.5208 | 14.5 | 15
| 8.2153 | 279.78 | 47.27 | 57.75 | 51.254 | 74.626 |  | 24.5833 | 28.8849 | 26.8479 | 0.56003 | 10.8984 | 27.7912 | 29.3864 |  | 24.5417 | 14.3 | 15
| 8.2222 | 279.32 | 47.311 | 57.791 | 51.282 | 74.692 |  | 24.6042 | 28.8578 | 26.8231 | 0.54468 | 10.8807 | 27.7754 | 29.3661 |  | 24.5625 | 14.1 | 15
| 8.2292 | 278.992 | 47.335 | 57.82 | 51.299 | 74.742 |  | 24.625 | 28.8533 | 26.8185 | 0.54027 | 10.8807 | 27.7822 | 29.3661 |  | 24.5833 | 14.2 | 15
| 8.2361 | 280.612 | 47.366 | 57.849 | 51.323 | 74.792 |  | 24.6458 | 28.8285 | 26.8028 | 0.5315 | 10.8522 | 27.7349 | 29.3502 |  | 24.6042 | 14.1 | 15
| 8.2431 | 280.424 | 47.393 | 57.881 | 51.351 | 74.846 |  | 24.6667 | 28.8888 | 26.8585 | 0.57628 | 10.9044 | 27.7951 | 29.3993 |  | 24.625 | 14.3 | 15
| 8.25 | 279.691 | 47.42 | 57.914 | 51.379 | 74.898 |  | 24.6875 | 28.882 | 26.8539 | 0.57402 | 10.9066 | 27.8064 | 29.3879 |  | 24.6458 | 14.3 | 15
| 8.2569 | 278.632 | 47.436 | 57.94 | 51.398 | 74.938 |  | 24.7083 | 28.8639 | 26.8359 | 0.55873 | 10.8888 | 27.7771 | 29.3812 |  | 24.6667 | 14.6 | 15
| 8.2639 | 281.085 | 47.456 | 57.965 | 51.415 | 74.974 |  | 24.7292 | 28.8097 | 26.802 | 0.5237 | 10.8422 | 27.714 | 29.3405 |  | 24.6875 | 14.7 | 15
| 8.2708 | 152.067 | 47.312 | 57.82 | 51.305 | 74.744 |  | 24.75 | 28.8814 | 26.8509 | 0.56833 | 10.9098 | 27.8104 | 29.3918 |  | 24.7083 | 14.7 | 15
| 8.2778 | 279.459 | 46.946 | 57.457 | 51.019 | 73.829 |  | 24.7708 | 28.8611 | 26.8486 | 0.56392 | 10.8943 | 27.7833 | 29.3874 |  | 24.7292 | 14.9 | 15
| 8.2847 | 278.079 | 47.018 | 57.535 | 51.065 | 73.942 |  | 24.7917 | 28.8571 | 26.8538 | 0.5564 | 10.8976 | 27.7749 | 29.3834 |  | 24.75 | 15.2 | 15
| 8.2917 | 277.636 | 47.1 | 57.597 | 51.126 | 74.074 |  | 24.8125 | 28.8458 | 26.847 | 0.55867 | 10.8954 | 27.7749 | 29.3857 |  | 24.7708 | 15.7 | 15
| 8.2986 | 277.751 | 47.159 | 57.645 | 51.162 | 74.169 |  | 24.8333 | 28.8638 | 26.8741 | 0.58272 | 10.9175 | 27.7929 | 29.4128 |  | 24.7917 | 15.4 | 15
| 8.3056 | 276.99 | 47.21 | 57.686 | 51.192 | 74.257 |  | 24.8542 | 28.825 | 26.84 | 0.53661 | 10.886 | 27.7586 | 29.3718 |  | 24.8125 | 15.2 | 15
| 8.3125 | 275.566 | 47.241 | 57.715 | 51.215 | 74.317 |  | 24.875 | 28.8066 | 26.8106 | 0.50235 | 10.8638 | 27.7355 | 29.3443 |  | 24.8333 | 15.4 | 15
| 8.3194 | 275.318 | 47.264 | 57.736 | 51.23 | 74.357 |  | 24.8958 | 28.7965 | 26.8165 | 0.49313 | 10.8629 | 27.7117 | 29.3387 |  | 24.8542 | 15.2 | 15
| 8.3264 | 274.378 | 47.272 | 57.748 | 51.238 | 74.378 |  | 24.9167 | 28.781 | 26.7966 | 0.47468 | 10.8459 | 27.6377 | 29.3256 |  | 24.875 | 14 | 15
| 8.3333 | 276.921 | 47.293 | 57.772 | 51.259 | 74.411 |  | 24.9375 | 28.7821 | 26.7934 | 0.46072 | 10.847 | 27.5801 | 29.3221 |  | 24.8958 | 12.6 | 15
| 8.3403 | 277.155 | 47.318 | 57.793 | 51.279 | 74.459 |  | 24.9583 | 28.7628 | 26.7855 | 0.44904 | 10.8328 | 27.5383 | 29.3119 |  | 24.9167 | 11.6 | 15
| 8.3472 | 276.038 | 47.336 | 57.817 | 51.295 | 74.496 |  | 24.9792 | 28.7572 | 26.7756 | 0.42865 | 10.8231 | 27.526 | 29.2996 |  | 24.9375 | 10.9 | 15
| 8.3542 | 278.746 | 47.355 | 57.85 | 51.314 | 74.537 |  | 25 | 28.7504 | 26.7801 | 0.43717 | 10.8207 | 27.5303 | 29.3041 |  | 24.9583 | 10.4 | 15
| 8.3611 | 278.145 | 47.383 | 57.88 | 51.339 | 74.596 |  | 25.0208 | 28.7296 | 26.7549 | 0.41281 | 10.8092 | 27.5095 | 29.2856 |  | 24.9792 | 9.8 | 15
| 8.3681 | 277.505 | 47.408 | 57.906 | 51.359 | 74.647 |  | 25.0417 | 28.7299 | 26.7417 | 0.40859 | 10.8073 | 27.5098 | 29.2859 |  | 25 | 9.2 | 15
| 8.375 | 277.4 | 47.423 | 57.928 | 51.386 | 74.682 |  | 25.0625 | 28.7061 | 26.7044 | 0.38151 | 10.793 | 27.477 | 29.2688 |  | 25.0208 | 8.8 | 15
| 8.3819 | 276.892 | 47.439 | 57.949 | 51.4 | 74.709 |  | 25.0833 | 28.7196 | 26.7202 | 0.40778 | 10.8106 | 27.4994 | 29.2937 |  | 25.0417 | 8.4 | 15
| 8.3889 | 275.645 | 47.451 | 57.964 | 51.411 | 74.728 |  | 25.1042 | 28.6937 | 26.6989 | 0.37198 | 10.7877 | 27.4691 | 29.2723 |  | 25.0625 | 8.1 | 15
| 8.3958 | 275.326 | 47.453 | 57.977 | 51.419 | 74.735 |  | 25.125 | 28.7005 | 26.7124 | 0.3764 | 10.8009 | 27.4781 | 29.2859 |  | 25.0833 | 8.2 | 15
| 8.4028 | 273.32 | 47.449 | 57.977 | 51.422 | 74.722 |  | 25.1458 | 28.6524 | 26.6442 | 0.31476 | 10.7473 | 27.4323 | 29.249 |  | 25.1042 | 7.8 | 15
| 8.4097 | 274.671 | 47.447 | 57.974 | 51.415 | 74.695 |  | 25.1667 | 28.6299 | 26.669 | 0.34318 | 10.7717 | 27.4143 | 29.24 |  | 25.125 | 7.5 | 15
| 8.4167 | 272.845 | 47.443 | 57.976 | 51.42 | 74.684 |  | 25.1875 | 28.6501 | 26.6803 | 0.32988 | 10.7648 | 27.3871 | 29.224 |  | 25.1458 | 7.1 | 15
| 8.4236 | 281.239 | 47.468 | 58.006 | 51.44 | 74.716 |  | 25.2083 | 28.6198 | 26.6613 | 0.31404 | 10.7531 | 27.4177 | 29.239 |  | 25.1667 | 6.9 | 15
| 8.4306 | 280.057 | 47.518 | 58.054 | 51.484 | 74.812 |  | 25.2292 | 28.4662 | 26.5034 | 0.122 | 10.5984 | 27.2668 | 29.1079 |  | 25.1875 | 6.6 | 15
| 8.4375 | 280.01 | 47.558 | 58.102 | 51.515 | 74.897 |  | 25.25 | 28.6401 | 26.6727 | 0.33809 | 10.7619 | 27.4087 | 29.2459 |  | 25.2083 | 6.3 | 15
| 8.4444 | 279.012 | 47.584 | 58.13 | 51.546 | 74.951 |  | 25.2708 | 28.5949 | 26.632 | 0.2901 | 10.7156 | 27.3592 | 29.2097 |  | 25.2292 | 5.9 | 15
| 8.4514 | 278.607 | 47.607 | 58.154 | 51.564 | 74.99 |  | 25.2917 | 28.6639 | 26.7007 | 0.36741 | 10.7851 | 27.4528 | 29.2649 |  | 25.25 | 5.9 | 15
| 8.4583 | 263.905 | 47.244 | 57.786 | 51.284 | 74.289 |  | 25.3125 | 28.6572 | 26.7007 | 0.36782 | 10.7899 | 27.4396 | 29.2765 |  | 25.2708 | 6.1 | 15
| 8.4653 | 282.91 | 47.137 | 57.694 | 51.195 | 73.927 |  | 25.3333 | 28.6376 | 26.7033 | 0.33701 | 10.779 | 27.4584 | 29.2657 |  | 25.2917 | 7 | 15
| 8.4722 | 281.596 | 47.248 | 57.806 | 51.275 | 74.137 |  | 25.3542 | 28.6917 | 26.7819 | 0.42122 | 10.8186 | 27.6298 | 29.313 |  | 25.3125 | 9.1 | 15
| 8.4792 | 280.539 | 47.354 | 57.889 | 51.351 | 74.326 |  | 25.375 | 28.6663 | 26.7696 | 0.41228 | 10.804 | 27.6407 | 29.3033 |  | 25.3333 | 10.5 | 15
| 8.4861 | 278.88 | 47.432 | 57.95 | 51.4 | 74.476 |  | 25.3958 | [7 empty] | 25.3542 | 12.1 | 15
| 8.4931 | 277.736 | 47.483 | 57.998 | 51.436 | 74.589 |  | 25.4167 | [7 empty] | 25.375 | 14 | 15
| 8.5 | 278.438 | 47.521 | 58.031 | 51.469 | 74.662 |  | 25.4375 | [7 empty] | 25.3958 | 15.3 | 15
| 8.5069 | 280.187 | 47.552 | 58.067 | 51.484 | 74.733 |  | 25.4583 | 28.6348 | 26.7643 | 0.393 | 10.7949 | 27.588 | 29.2873 |  | 25.4167 | 16.3 | 15
| 8.5139 | 277.419 | 47.587 | 58.103 | 51.522 | 74.813 |  | 25.4792 | 28.6192 | 26.7778 | 0.41487 | 10.8082 | 27.5948 | 29.3191 |  | 25.4375 | 17.6 | 15
| 8.5208 | 276.702 | 47.598 | 58.122 | 51.535 | 74.845 |  | 25.5 | 28.6896 | 26.8299 | 0.47757 | 10.8587 | 27.6423 | 29.3646 |  | 25.4583 | 18.4 | 15
| 8.5278 | 276.193 | 47.612 | 58.138 | 51.548 | 74.872 |  | 25.5208 | 28.6758 | 26.8113 | 0.46558 | 10.8467 | 27.6305 | 29.3507 |  | 25.4792 | 19.5 | 15
| 8.5347 | 276.25 | 47.62 | 58.154 | 51.561 | 74.891 |  | 25.5417 | 28.6779 | 26.8087 | 0.46228 | 10.837 | 27.6097 | 29.3527 |  | 25.5 | 20.2 | 15
| 8.5417 | 276.201 | 47.633 | 58.172 | 51.578 | 74.915 |  | 25.5625 | 28.7037 | 26.841 | 0.50785 | 10.8658 | 27.633 | 29.3785 |  | 25.5208 | 21.8 | 15
| 8.5486 | 275.338 | 47.64 | 58.187 | 51.589 | 74.932 |  | 25.5833 | 28.6849 | 26.8176 | 0.49331 | 10.8535 | 27.6299 | 29.371 |  | 25.5417 | 22.1 | 15
| 8.5556 | 275.687 | 47.647 | 58.199 | 51.593 | 74.941 |  | 25.6042 | 28.7029 | 26.8379 | 0.52614 | 10.8757 | 27.6525 | 29.3823 |  | 25.5625 | 22.9 | 15
| 8.5625 | 275.932 | 47.653 | 58.21 | 51.6 | 74.951 |  | 25.625 | 28.7571 | 26.8873 | 0.57988 | 10.9192 | 27.7176 | 29.4297 |  | 25.5833 | 22.8 | 15
| 8.5694 | 275.547 | 47.66 | 58.219 | 51.608 | 74.956 |  | 25.6458 | 28.694 | 26.831 | 0.52294 | 10.866 | 27.659 | 29.38 |  | 25.6042 | 23.2 | 15
| 8.5764 | 276.06 | 47.668 | 58.232 | 51.618 | 74.969 |  | 25.6667 | 28.7312 | 26.8589 | 0.55854 | 10.8955 | 27.6915 | 29.4059 |  | 25.625 | 23.5 | 15
| 8.5833 | 276.368 | 47.678 | 58.243 | 51.624 | 74.986 |  | 25.6875 | 28.7425 | 26.8657 | 0.56517 | 10.9066 | 27.7095 | 29.4173 |  | 25.6458 | 24.2 | 15
| 8.5903 | 148.9 | 47.568 | 58.134 | 51.54 | 74.809 |  | 25.7083 | 28.7244 | 26.8499 | 0.55856 | 10.8933 | 27.6892 | 29.4014 |  | 25.6667 | 24 | 15
| 8.5972 | 279.07 | 47.23 | 57.794 | 51.274 | 73.984 |  | 25.7292 | 28.7357 | 26.8702 | 0.56292 | 10.9132 | 27.7073 | 29.4126 |  | 25.6875 | 24.7 | 15
| 8.6042 | 278.85 | 47.318 | 57.873 | 51.333 | 74.122 |  | 25.75 | 28.7492 | 26.8499 | 0.58261 | 10.9266 | 27.7366 | 29.4353 |  | 25.7083 | 24.3 | 15
| 8.6111 | 278.716 | 47.41 | 57.957 | 51.392 | 74.282 |  | 25.7708 | 28.7312 | 26.8341 | 0.55856 | 10.9132 | 27.7163 | 29.4126 |  | 25.7292 | 24.3 | 15
| 8.6181 | 278.936 | 47.49 | 58.015 | 51.448 | 74.43 |  | 25.7917 | 28.6989 | 26.8066 | 0.54287 | 10.8884 | 27.6932 | 29.3939 |  | 25.75 | 24.6 | 15
| 8.625 | 278.418 | 47.543 | 58.063 | 51.483 | 74.541 |  | 25.8125 | 28.7022 | 26.8103 | 0.5193 | 10.8908 | 27.6859 | 29.3839 |  | 25.7708 | 24.3 | 15
| 8.6319 | 278.628 | 47.594 | 58.113 | 51.52 | 74.646 |  | 25.8333 | 28.6915 | 26.7999 | 0.51285 | 10.8861 | 27.7027 | 29.38 |  | 25.7917 | 25.1 | 15
| 8.6389 | 278.559 | 47.634 | 58.151 | 51.558 | 74.732 |  | 25.8542 | 28.6968 | 26.8032 | 0.52095 | 10.8852 | 27.6926 | 29.3786 |  | 25.8125 | 25.4 | 15
| 8.6458 | 278.207 | 47.669 | 58.187 | 51.584 | 74.815 |  | 25.875 | 27.9279 | 26.2671 | 0.034683 | 10.2397 | 27.1759 | 28.796 |  | 25.8333 | 22.9 | 15
| 8.6528 | 278.972 | 47.699 | 58.226 | 51.617 | 74.89 |  | 25.8958 | 28.2402 | 26.3791 | -0.005081 | 10.4563 | 27.2272 | 28.9712 |  | 25.8542 | 20.3 | 15
| 8.6597 | 278.939 | 47.734 | 58.257 | 51.643 | 74.964 |  | 25.9167 | 28.6416 | 26.7625 | 0.45347 | 10.8449 | 27.6567 | 29.3328 |  | 25.875 | 19.6 | 15
| 8.6667 | 146.833 | 47.574 | 58.095 | 51.525 | 74.718 |  | 25.9375 | 28.6413 | 26.7849 | 0.47161 | 10.8585 | 27.6652 | 29.3504 |  | 25.8958 | 18.8 | 15
| 8.6736 | 278.779 | 47.226 | 57.753 | 51.247 | 73.86 |  | 25.9583 | 28.6411 | 26.7939 | 0.46946 | 10.8624 | 27.6538 | 29.3571 |  | 25.9167 | 17.8 | 15
| 8.6806 | 277.83 | 47.313 | 57.844 | 51.315 | 74.015 |  | 25.9792 | 28.6859 | 26.8409 | 0.52193 | 10.9107 | 27.7052 | 29.3976 |  | 25.9375 | 17.2 | 15
| 8.6875 | 278.77 | 47.417 | 57.926 | 51.383 | 74.203 |  | 26 | 28.7039 | 26.8635 | 0.54384 | 10.935 | 27.7209 | 29.4156 |  | 25.9583 | 16.6 | 15
| 8.6944 | 278.314 | 47.503 | 57.996 | 51.448 | 74.363 |  | 26.0208 | 28.6569 | 26.8324 | 0.50774 | 10.8894 | 27.6695 | 29.382 |  | 25.9792 | 16.2 | 15
| 8.7014 | 276.954 | 47.572 | 58.053 | 51.497 | 74.508 |  | 26.0417 | 28.6682 | 26.8369 | 0.5143 | 10.9027 | 27.7033 | 29.3843 |  | 26 | 16.3 | 15
| 8.7083 | 278.215 | 47.623 | 58.096 | 51.534 | 74.609 |  | 26.0625 | 28.6366 | 26.8098 | 0.47712 | 10.8717 | 27.6695 | 29.3617 |  | 26.0208 | 16.3 | 15
| 8.7153 | 277.372 | 47.658 | 58.134 | 51.567 | 74.706 |  | 26.0833 | 28.6344 | 26.8211 | 0.49466 | 10.8784 | 27.6628 | 29.3685 |  | 26.0417 | 16.2 | 15
| 8.7222 | 278.367 | 47.692 | 58.167 | 51.593 | 74.776 |  | 26.1042 | 28.5982 | 26.7851 | 0.45521 | 10.8518 | 27.638 | 29.3301 |  | 26.0625 | 16 | 15
| 8.7292 | 278.525 | 47.723 | 58.201 | 51.622 | 74.854 |  | 26.125 | 28.605 | 26.7557 | 0.46834 | 10.8497 | 27.5142 | 29.3346 |  | 26.0833 | 16.1 | 15
| 8.7361 | 278.758 | 47.754 | 58.24 | 51.656 | 74.934 |  | 26.1458 | 28.6253 | 26.7807 | 0.47586 | 10.8633 | 27.4894 | 29.3482 |  | 26.1042 | 16.3 | 15
| 8.7431 | 43.546 | 47.783 | 58.273 | 51.683 | 75.003 |  | 26.1667 | 28.6194 | 26.7726 | 0.47953 | 10.8579 | 27.4993 | 29.3559 |  | 26.125 | 16.4 | 15
| 8.75 | 278.959 | 47.329 | 57.81 | 51.33 | 74.045 |  | 26.1875 | 28.5752 | 26.7466 | 0.42091 | 10.843 | 27.4551 | 29.3252 |  | 26.1458 | 16.9 | 15
| 8.7569 | 278.84 | 47.367 | 57.863 | 51.362 | 74.069 |  | 26.2083 | 28.6384 | 26.8029 | 0.48233 | 10.8717 | 27.4866 | 29.3727 |  | 26.1667 | 15.1 | 15
| 8.7639 | 277.646 | 47.462 | 57.943 | 51.425 | 74.244 |  | 26.2292 | 28.591 | 26.758 | 0.45469 | 10.8456 | 27.473 | 29.3387 |  | 26.1875 | 14.2 | 15
| 8.7708 | 277.018 | 47.544 | 58.009 | 51.477 | 74.396 |  | 26.25 | 28.5616 | 26.7354 | 0.41959 | 10.8235 | 27.4527 | 29.3161 |  | 26.2083 | 13.9 | 15
| 8.7778 | 277.519 | 47.604 | 58.064 | 51.522 | 74.517 |  | 26.2708 | 28.5459 | 26.7218 | 0.40646 | 10.8102 | 27.446 | 29.2981 |  | 26.2292 | 13.8 | 15
| 8.7847 | 275.055 | 47.654 | 58.111 | 51.562 | 74.622 |  | 26.2917 | 28.5776 | 26.7535 | 0.43276 | 10.8347 | 27.4754 | 29.3298 |  | 26.25 | 13.7 | 15
| 8.7917 | 275.573 | 47.675 | 58.139 | 51.577 | 74.684 |  | 26.3125 | 28.5677 | 26.7502 | 0.42904 | 10.8314 | 27.5488 | 29.3265 |  | 26.2708 | 13.8 | 15
| 8.7986 | 277.916 | 47.702 | 58.166 | 51.606 | 74.738 |  | 26.3333 | 28.5741 | 26.7498 | 0.43106 | 10.8313 | 27.6297 | 29.3262 |  | 26.2917 | 13.8 | 15
| 8.8056 | 276.44 | 47.731 | 58.202 | 51.633 | 74.811 |  | 26.3542 | 28.5514 | 26.7585 | 0.41682 | 10.8395 | 27.607 | 29.3373 |  | 26.3125 | 14.2 | 15
| 8.8125 | 276.848 | 47.753 | 58.232 | 51.663 | 74.871 |  | 26.375 | 28.522 | 26.7427 | 0.37307 | 10.8219 | 27.4334 | 29.3282 |  | 26.3333 | 14.6 | 15
| 8.8194 | 278.329 | 47.776 | 58.261 | 51.689 | 74.924 |  | 26.3958 | 28.5063 | 26.7337 | 0.34454 | 10.802 | 27.4086 | 29.3056 |  | 26.3542 | 14.9 | 15
| 8.8264 | 278.057 | 47.806 | 58.295 | 51.71 | 74.989 |  | 26.4167 | 28.5244 | 26.7539 | 0.37728 | 10.8223 | 27.4265 | 29.3237 |  | 26.375 | 15.3 | 15
| 8.8333 | 264.353 | 47.445 | 57.929 | 51.435 | 74.292 |  | 26.4375 | 28.5263 | 26.7782 | 0.38934 | 10.8303 | 27.5865 | 29.328 |  | 26.3958 | 15.3 | 15
| 8.8403 | 279.77 | 47.352 | 57.857 | 51.362 | 73.982 |  | 26.4583 | 28.5372 | 26.8294 | 0.42089 | 10.8513 | 27.5992 | 29.3476 |  | 26.4167 | 15.6 | 15
| 8.8472 | 280.491 | 47.455 | 57.958 | 51.431 | 74.177 |  | 26.4792 | 28.5396 | 26.8157 | 0.40232 | 10.8483 | 27.5831 | 29.3567 |  | 26.4375 | 16 | 15
| 8.8542 | 280.387 | 47.553 | 58.043 | 51.508 | 74.363 |  | 26.5 | 28.5288 | 26.8204 | 0.40823 | 10.8412 | 27.5697 | 29.3504 |  | 26.4583 | 17.3 | 15
| 8.8611 | 280.092 | 47.636 | 58.108 | 51.566 | 74.517 |  | 26.5208 | 28.5391 | 26.8305 | 0.4329 | 10.862 | 27.5844 | 29.3652 |  | 26.4792 | 18.8 | 15
| 8.8681 | 279.684 | 47.692 | 58.169 | 51.613 | 74.646 |  | 26.5417 | 28.5507 | 26.8465 | 0.45194 | 10.8727 | 27.6094 | 29.3881 |  | 26.5 | 19.7 | 15
| 8.875 | 280.048 | 47.739 | 58.224 | 51.655 | 74.757 |  | 26.5625 | 28.566 | 26.8594 | 0.48126 | 10.8892 | 27.6198 | 29.4079 |  | 26.5208 | 20.6 | 15
| 8.8819 | 278.998 | 47.781 | 58.27 | 51.694 | 74.85 |  | 26.5833 | 28.5502 | 26.8436 | 0.47905 | 10.876 | 27.6018 | 29.3943 |  | 26.5417 | 20.8 | 15
| 8.8889 | 276.22 | 47.811 | 58.31 | 51.718 | 74.926 |  | 26.6042 | 28.5508 | 26.8529 | 0.47411 | 10.8846 | 27.6156 | 29.3995 |  | 26.5625 | 20.7 | 15
| 8.8958 | 280.421 | 47.834 | 58.346 | 51.75 | 74.991 |  | 26.625 | 28.5621 | 26.8552 | 0.47626 | 10.8824 | 27.6134 | 29.4062 |  | 26.5833 | 21.7 | 15
| 8.9028 | 265.777 | 47.376 | 57.878 | 51.396 | 74.093 |  | 26.6458 | 28.5566 | 26.8427 | 0.47906 | 10.8697 | 27.5985 | 29.4005 |  | 26.6042 | 21.9 | 15
| 8.9097 | 279.738 | 47.302 | 57.825 | 51.335 | 73.815 |  | 26.6667 | 28.5566 | 26.8405 | 0.46145 | 10.872 | 27.5963 | 29.3982 |  | 26.625 | 23.3 | 15
| 8.9167 | 280.077 | 47.412 | 57.928 | 51.413 | 74.019 |  | 26.6875 | 28.5378 | 26.824 | 0.45455 | 10.8537 | 27.5775 | 29.3794 |  | 26.6458 | 22.6 | 15
| 8.9236 | 280.109 | 47.519 | 58.022 | 51.499 | 74.213 |  | 26.7083 | 28.5509 | 26.8327 | 0.46096 | 10.8602 | 27.5931 | 29.3904 |  | 26.6667 | 23.3 | 15
| 8.9306 | 280.807 | 47.6 | 58.097 | 51.553 | 74.385 |  | 26.7292 | 28.553 | 26.835 | 0.46317 | 10.8692 | 27.6203 | 29.3949 |  | 26.6875 | 23.6 | 15
| 8.9375 | 278.455 | 47.673 | 58.163 | 51.606 | 74.524 |  | 26.75 | 28.5358 | 26.8359 | 0.44916 | 10.8726 | 27.5963 | 29.398 |  | 26.7083 | 23.6 | 15
| 8.9444 | 277.502 | 47.716 | 58.211 | 51.64 | 74.628 |  | 26.7708 | 28.5413 | 26.8392 | 0.4507 | 10.8739 | 27.593 | 29.399 |  | 26.7292 | 23.2 | 15
| 8.9514 | 278.79 | 47.744 | 58.248 | 51.674 | 74.699 |  | 26.7917 | 28.5448 | 26.8361 | 0.46346 | 10.8779 | 27.5991 | 29.4095 |  | 26.75 | 22.9 | 15
| 8.9583 | 278.568 | 47.772 | 58.287 | 51.709 | 74.774 |  | 26.8125 | 28.5427 | 26.8591 | 0.46906 | 10.8878 | 27.5974 | 29.4142 |  | 26.7708 | 22.5 | 15
| 8.9653 | 278.279 | 47.804 | 58.328 | 51.732 | 74.841 |  | 26.8333 | 28.5117 | 26.8442 | 0.43319 | 10.8734 | 27.5553 | 29.4013 |  | 26.7917 | 22.2 | 15
| 8.9722 | 279.908 | 47.831 | 58.36 | 51.763 | 74.913 |  | 26.8542 | 28.5028 | 26.831 | 0.42767 | 10.8609 | 27.5535 | 29.3925 |  | 26.8125 | 21.8 | 15
| 8.9792 | 279.696 | 47.862 | 58.408 | 51.79 | 74.985 |  | 26.875 | 28.4749 | 26.7986 | 0.38777 | 10.8271 | 27.5278 | 29.36 |  | 26.8333 | 18.9 | 15
| 8.9861 | 267.11 | 47.515 | 58.056 | 51.534 | 74.325 |  | 26.8958 | 28.4915 | 26.8087 | 0.41769 | 10.8529 | 27.5378 | 29.3766 |  | 26.8542 | 18.2 | 15
| 8.9931 | 279.683 | 47.437 | 57.999 | 51.467 | 74.039 |  | 26.9167 | 28.4769 | 26.801 | 0.40617 | 10.8256 | 27.5077 | 29.3621 |  | 26.875 | 17.8 | 15
| 9 | 279.699 | 47.53 | 58.087 | 51.542 | 74.215 |  | 26.9375 | 28.454 | 26.8007 | 0.37318 | 10.8205 | 27.478 | 29.3572 |  | 26.8958 | 17.3 | 15
| 9.0069 | 276.243 | 47.616 | 58.172 | 51.602 | 74.381 |  | 26.9583 | 28.4248 | 26.7739 | 0.34571 | 10.7946 | 27.388 | 29.3349 |  | 26.9167 | 16.8 | 15
| 9.0139 | 275.275 | 47.667 | 58.216 | 51.639 | 74.476 |  | 26.9792 | 28.4216 | 26.7708 | 0.33216 | 10.7894 | 27.3556 | 29.3317 |  | 26.9375 | 16.2 | 15
| 9.0208 | 274.979 | 47.699 | 58.248 | 51.652 | 74.532 |  | 27 | 28.4163 | 26.768 | 0.3296 | 10.78 | 27.3279 | 29.3288 |  | 26.9583 | 15.7 | 15
| 9.0278 | 276.067 | 47.721 | 58.278 | 51.68 | 74.587 |  | 27.0208 | 28.4344 | 26.8063 | 0.37778 | 10.8065 | 27.3256 | 29.3672 |  | 26.9792 | 15.2 | 15
| 9.0347 | 275.786 | 47.748 | 58.312 | 51.702 | 74.643 |  | 27.0417 | 28.4015 | 26.7578 | 0.3179 | 10.7656 | 27.2997 | 29.3139 |  | 27 | 14.7 | 15
| 9.0417 | 272.615 | 47.767 | 58.334 | 51.725 | 74.687 |  | 27.0625 | 28.3744 | 26.7375 | 0.29604 | 10.7501 | 27.2862 | 29.3026 |  | 27.0208 | 14.3 | 15
| 9.0486 | 285.393 | 47.82 | 58.388 | 51.763 | 74.787 |  | 27.0833 | 28.3835 | 26.7398 | 0.28505 | 10.7634 | 27.2772 | 29.3207 |  | 27.0417 | 14.1 | 15
| 9.0556 | 285.118 | 47.899 | 58.483 | 51.837 | 74.963 |  | 27.1042 | 28.365 | 26.7057 | 0.2726 | 10.7415 | 27.243 | 29.3022 |  | 27.0625 | 14 | 15
| 9.0625 | 260.27 | 47.569 | 58.142 | 51.581 | 74.351 |  | 27.125 | 28.3989 | 26.7283 | 0.3296 | 10.7702 | 27.2746 | 29.3317 |  | 27.0833 | 13.8 | 15
| 9.0694 | 278.86 | 47.46 | 58.053 | 51.491 | 73.994 |  | 27.1458 | 28.3876 | 26.7147 | 0.30328 | 10.7613 | 27.2678 | 29.3203 |  | 27.1042 | 13.4 | 15
| 9.0764 | 278.253 | 47.548 | 58.139 | 51.563 | 74.163 |  | 27.1667 | 28.3222 | 26.6606 | 0.24413 | 10.7106 | 27.2115 | 29.2774 |  | 27.125 | 13.2 | 15
| 9.0833 | 278.567 | 47.634 | 58.22 | 51.624 | 74.322 |  | 27.1875 | 28.3509 | 26.6982 | 0.26261 | 10.7363 | 27.2401 | 29.3108 |  | 27.1458 | 13.2 | 15
| 9.0903 | 279.514 | 47.704 | 58.286 | 51.679 | 74.457 |  | 27.2083 | 28.3532 | 26.687 | 0.27138 | 10.7231 | 27.2197 | 29.313 |  | 27.1667 | 13.6 | 15
| 9.0972 | 278.822 | 47.761 | 58.349 | 51.725 | 74.58 |  | 27.2292 | 28.3707 | 26.7202 | 0.30601 | 10.7536 | 27.2574 | 29.3304 |  | 27.1875 | 13.7 | 15
| 9.1042 | 279.166 | 47.812 | 58.402 | 51.762 | 74.68 |  | 27.25 | 28.3324 | 26.6706 | 0.25993 | 10.7093 | 27.228 | 29.283 |  | 27.2083 | 13.9 | 15
| 9.1111 | 278.693 | 47.85 | 58.445 | 51.8 | 74.771 |  | 27.2708 | 28.383 | 26.7547 | 0.31221 | 10.7628 | 27.2649 | 29.3495 |  | 27.2292 | 13.9 | 15
| 9.1181 | 278.249 | 47.882 | 58.489 | 51.829 | 74.845 |  | 27.2917 | 28.3718 | 26.7706 | 0.30991 | 10.7542 | 27.2783 | 29.3404 |  | 27.25 | 14.3 | 15
| 9.125 | 278.853 | 47.91 | 58.526 | 51.86 | 74.912 |  | 27.3125 | 28.3667 | 26.7608 | 0.313 | 10.7597 | 27.4176 | 29.3465 |  | 27.2708 | 14.5 | 15
| 9.1319 | 278.29 | 47.936 | 58.569 | 51.887 | 74.975 |  | 27.3333 | 28.346 | 26.7489 | 0.29736 | 10.7372 | 27.3899 | 29.3348 |  | 27.2917 | 14.7 | 15
| 9.1389 | 151.447 | 47.749 | 58.379 | 51.742 | 74.664 |  | 27.3542 | 28.2321 | 26.6347 | 0.15904 | 10.6308 | 27.2935 | 29.2318 |  | 27.3125 | 14.9 | 15
| 9.1458 | 279.799 | 47.442 | 58.089 | 51.518 | 73.894 |  | 27.375 | 28.3895 | 26.7828 | 0.35041 | 10.7737 | 27.4327 | 29.3713 |  | 27.3333 | 15.7 | 15
| 9.1528 | 279.916 | 47.543 | 58.196 | 51.589 | 74.074 |  | 27.3958 | 28.4012 | 26.81 | 0.3868 | 10.802 | 27.4463 | 29.3874 |  | 27.3542 | 16.3 | 15
| 9.1597 | 279.387 | 47.653 | 58.292 | 51.667 | 74.268 |  | 27.4167 | 28.4079 | 26.812 | 0.38573 | 10.7857 | 27.437 | 29.3919 |  | 27.375 | 17.8 | 15
| 9.1667 | 279.224 | 47.732 | 58.369 | 51.73 | 74.433 |  | 27.4375 | 28.23 | 26.6541 | 0.17263 | 10.6522 | 27.2812 | 29.2542 |  | 27.3958 | 19.6 | 15
| 9.1736 | 278.052 | 47.797 | 58.438 | 51.781 | 74.566 |  | 27.4583 | 28.1872 | 26.6136 | 0.13544 | 10.6057 | 27.2247 | 29.2203 |  | 27.4167 | 21.6 | 15
| 9.1806 | 278.101 | 47.847 | 58.492 | 51.825 | 74.671 |  | 27.4792 | 28.2267 | 26.6353 | 0.17691 | 10.6304 | 27.235 | 29.2535 |  | 27.4375 | 22.4 | 15
| 9.1875 | 278 | 47.886 | 58.537 | 51.858 | 74.762 |  | 27.5 | 28.2389 | 26.67 | 0.19282 | 10.6687 | 27.2743 | 29.2862 |  | 27.4583 | 22.4 | 15
| 9.1944 | 278.38 | 47.921 | 58.582 | 51.89 | 74.84 |  | 27.5208 | 28.2728 | 26.7016 | 0.24309 | 10.6909 | 27.3217 | 29.3109 |  | 27.4792 | 22.7 | 15
| 9.2014 | 278.993 | 47.952 | 58.621 | 51.925 | 74.914 |  | 27.5417 | 28.3092 | 26.7334 | 0.2935 | 10.7419 | 27.3489 | 29.3565 |  | 27.5 | 24 | 15
| 9.2083 | 277.952 | 47.98 | 58.663 | 51.955 | 74.983 |  | 27.5625 | 28.3422 | 26.78 | 0.33822 | 10.7786 | 27.3799 | 29.3943 |  | 27.5208 | 24.1 | 15
| 9.2153 | 265.992 | 47.697 | 58.374 | 51.737 | 74.45 |  | 27.5833 | 28.3368 | 26.7634 | 0.34355 | 10.7686 | 27.352 | 29.3914 |  | 27.5417 | 23.5 | 15
| 9.2222 | 278.265 | 47.626 | 58.327 | 51.688 | 74.204 |  | 27.6042 | 28.3527 | 26.7681 | 0.34274 | 10.7592 | 27.3475 | 29.3849 |  | 27.5625 | 24.3 | 15
| 9.2292 | 277.148 | 47.71 | 58.413 | 51.752 | 74.359 |  | 27.625 | 28.3218 | 26.7439 | 0.31123 | 10.7316 | 27.3236 | 29.3698 |  | 27.5833 | 25.2 | 15
| 9.2361 | 278.736 | 47.786 | 58.485 | 51.809 | 74.494 |  | 27.6458 | 28.3535 | 26.7822 | 0.32953 | 10.7853 | 27.3731 | 29.4078 |  | 27.6042 | 25.8 | 15
| 9.2431 | 279.361 | 47.854 | 58.549 | 51.86 | 74.63 |  | 27.6667 | 28.2412 | 26.67 | 0.1972 | 10.6622 | 27.2428 | 29.2953 |  | 27.625 | 26.5 | 15
| 9.25 | 279.469 | 47.915 | 58.612 | 51.907 | 74.743 |  | 27.6875 | 28.1765 | 26.6054 | 0.10011 | 10.5991 | 27.2301 | 29.2643 |  | 27.6458 | 25.8 | 15
| 9.2569 | 277.018 | 47.955 | 58.66 | 51.951 | 74.842 |  | 27.7083 | 28.215 | 26.6077 | 0.15574 | 10.6508 | 27.158 | 29.28 |  | 27.6667 | 25 | 15
| 9.2639 | 280.121 | 47.981 | 58.692 | 51.971 | 74.894 |  | 27.7292 | 27.9696 | 26.4078 | -0.054451 | 10.4862 | 26.906 | 29.1244 |  | 27.6875 | 23.8 | 15
| 9.2708 | 280.368 | 48.021 | 58.741 | 52.015 | 74.989 |  | 27.75 | 28.1801 | 26.5667 | 0.049946 | 10.6052 | 27.0539 | 29.2453 |  | 27.7083 | 22.8 | 15
| 9.2778 | 268.503 | 47.641 | 58.349 | 51.717 | 74.231 |  | 27.7708 | 28.1856 | 26.6087 | -0.043701 | 10.6273 | 27.0487 | 29.251 |  | 27.7292 | 21.2 | 15
| 9.2847 | 278.549 | 47.589 | 58.313 | 51.672 | 74.018 |  | 27.7917 | 28.1613 | 26.5825 | -0.097164 | 10.5798 | 27.0427 | 29.2199 |  | 27.75 | 20 | 15
| 9.2917 | 277.882 | 47.684 | 58.41 | 51.748 | 74.204 |  | 27.8125 | 28.1543 | 26.6094 | -0.061306 | 10.6091 | 27.0472 | 29.2378 |  | 27.7708 | 19.2 | 15
| 9.2986 | 276.096 | 47.773 | 58.485 | 51.812 | 74.354 |  | 27.8333 | 28.1949 | 26.6591 | 0.002087 | 10.66 | 27.0856 | 29.2876 |  | 27.7917 | 16.3 | 15
| 9.3056 | 274.416 | 47.824 | 58.537 | 51.85 | 74.459 |  | 27.8542 | 28.2309 | 26.6793 | 0.04805 | 10.6889 | 27.1036 | 29.3191 |  | 27.8125 | 16 | 15
| 9.3125 | 276.298 | 47.861 | 58.572 | 51.876 | 74.529 |  | 27.875 | 28.276 | 26.729 | 0.10941 | 10.7443 | 27.185 | 29.3666 |  | 27.8333 | 15.7 | 15
| 9.3194 | 276.16 | 47.9 | 58.62 | 51.91 | 74.615 |  | 27.8958 | 28.1378 | 26.5998 | -0.036812 | 10.6135 | 27.0173 | 29.2371 |  | 27.8542 | 15.8 | 15
| 9.3264 | 274.86 | 47.936 | 58.654 | 51.941 | 74.688 |  | 27.9167 | 28.14 | 26.6134 | -0.052208 | 10.6268 | 27.033 | 29.2438 |  | 27.875 | 15.9 | 15
| 9.3333 | 274.483 | 47.959 | 58.687 | 51.962 | 74.738 |  | 27.9375 | 28.1715 | 26.6291 | -0.01717 | 10.6379 | 27.0466 | 29.2664 |  | 27.8958 | 15.8 | 15
| 9.3403 | 274.442 | 47.976 | 58.716 | 51.984 | 74.782 |  | 27.9583 | 28.2505 | 26.7284 | 0.10537 | 10.7327 | 27.1618 | 29.3614 |  | 27.9167 | 15.4 | 15
| 9.3472 | 273.435 | 47.993 | 58.734 | 51.999 | 74.811 |  | 27.9792 | 28.1722 | 26.6524 | 0.01918 | 10.6564 | 27.0541 | 29.2852 |  | 27.9375 | 15.4 | 15
| 9.3542 | 273.039 | 48.001 | 58.749 | 52.014 | 74.837 |  | 28 | 28.1541 | 26.63 | -0.017986 | 10.6431 | 27.0317 | 29.2672 |  | 27.9583 | 15.5 | 15
| 9.3611 | 273.94 | 48.009 | 58.768 | 52.027 | 74.849 |  | 28.0208 | 28.17 | 26.639 | -0.009212 | 10.6452 | 27.0407 | 29.2739 |  | 27.9792 | 15.3 | 15
| 9.3681 | 273.543 | 48.021 | 58.784 | 52.043 | 74.863 |  | 28.0417 | 28.1652 | 26.6299 | -0.004848 | 10.6341 | 27.0226 | 29.2717 |  | 28 | 15.1 | 15
| 9.375 | 272.851 | 48.026 | 58.802 | 52.049 | 74.877 |  | 28.0625 | 28.1495 | 26.6299 | -0.013622 | 10.6364 | 27.0091 | 29.2739 |  | 28.0208 | 14.7 | 15.6
| 9.3819 | 280.812 | 48.05 | 58.827 | 52.071 | 74.914 |  | 28.0833 | 28.1264 | 26.6136 | -0.038071 | 10.6137 | 26.9769 | 29.2552 |  | 28.0417 | 14.4 | 15.6
| 9.3889 | 44.945 | 48.062 | 58.85 | 52.085 | 74.974 |  | 28.1042 | 28.1196 | 26.6024 | -0.046787 | 10.6093 | 26.9747 | 29.2439 |  | 28.0625 | 14.2 | 15.6
| 9.3958 | 279.667 | 47.564 | 58.329 | 51.69 | 73.858 |  | 28.125 | 28.1309 | 26.6204 | -0.035805 | 10.6116 | 26.9724 | 29.2642 |  | 28.0833 | 14 | 15.6
| 9.4028 | 281.191 | 47.634 | 58.411 | 51.74 | 73.947 |  | 28.1458 | 28.1062 | 26.5979 | -0.062126 | 10.5961 | 26.9544 | 29.2552 |  | 28.1042 | 13.8 | 15.6
| 9.4097 | 282.645 | 47.762 | 58.535 | 51.831 | 74.194 |  | 28.1667 | 28.1489 | 26.6385 | -0.000824 | 10.6336 | 26.9972 | 29.2846 |  | 28.125 | 13.4 | 15.6
| 9.4167 | 281.617 | 47.882 | 58.646 | 51.924 | 74.429 |  | 28.1875 | 28.1062 | 26.6226 | -0.029297 | 10.616 | 26.9634 | 29.2598 |  | 28.1458 | 13.3 | 15.6
| 9.4236 | 281.074 | 47.972 | 58.731 | 51.981 | 74.617 |  | 28.2083 | 28.1542 | 26.6662 | 0.010406 | 10.6518 | 27.0045 | 29.3055 |  | 28.1667 | 13.2 | 15.6
| 9.4306 | 281.565 | 48.046 | 58.814 | 52.044 | 74.781 |  | 28.2292 | 28.1836 | 26.6706 | 0.003841 | 10.663 | 27.0091 | 29.3146 |  | 28.1875 | 13.1 | 15.6
| 9.4375 | 280.608 | 48.11 | 58.88 | 52.101 | 74.928 |  | 28.25 | 28.1407 | 26.6639 | -0.020214 | 10.6342 | 26.9662 | 29.2943 |  | 28.2083 | 13.7 | 15.6
| 9.4444 | 45.298 | 48.028 | 58.801 | 52.039 | 74.843 |  | 28.2708 | 28.1903 | 26.7111 | 0.021313 | 10.6874 | 27.009 | 29.3394 |  | 28.2292 | 13.7 | 15.6
| 9.4514 | 278.971 | 47.485 | 58.24 | 51.613 | 73.586 |  | 28.2917 | 28.1677 | 26.6863 | 0.008183 | 10.659 | 27 | 29.3146 |  | 28.25 | 14 | 15.6
| 9.4583 | 276.786 | 47.564 | 58.334 | 51.67 | 73.709 |  | 28.3125 | 28.2088 | 26.7113 | 0.053467 | 10.694 | 27.0453 | 29.3534 |  | 28.2708 | 14.3 | 15.6
| 9.4653 | 278.36 | 47.685 | 58.443 | 51.761 | 73.934 |  | 28.3333 | 28.1479 | 26.682 | 0.009655 | 10.6586 | 27.0092 | 29.3262 |  | 28.2917 | 14.6 | 15.6
| 9.4722 | 275.329 | 47.788 | 58.532 | 51.826 | 74.128 |  | 28.3542 | 28.1817 | 26.7155 | 0.03801 | 10.6893 | 27.0156 | 29.3577 |  | 28.3125 | 14.8 | 15.6
| 9.4792 | 273.786 | 47.852 | 58.591 | 51.872 | 74.261 |  | 28.375 | 28.2159 | 26.7292 | 0.074429 | 10.7111 | 27.0407 | 29.3829 |  | 28.3333 | 15.3 | 15.6
| 9.4861 | 274.42 | 47.894 | 58.63 | 51.902 | 74.352 |  | 28.3958 | 28.1976 | 26.7222 | 0.072056 | 10.7086 | 27.0154 | 29.3803 |  | 28.3542 | 15.4 | 15.6
| 9.4931 | 273.947 | 47.93 | 58.672 | 51.931 | 74.435 |  | 28.4167 | 28.1735 | 26.6821 | 0.060558 | 10.6707 | 26.9888 | 29.3651 |  | 28.375 | 15.7 | 15.6
| 9.5 | 273.701 | 47.96 | 58.706 | 51.954 | 74.507 |  | 28.4375 | 28.1426 | 26.7007 | 0.019321 | 10.6555 | 26.9894 | 29.3432 |  | 28.3958 | 15.9 | 15.6
| 9.5069 | 275.394 | 47.989 | 58.742 | 51.99 | 74.578 |  | 28.4583 | 28.1518 | 26.7298 | 0.027168 | 10.6482 | 26.996 | 29.3454 |  | 28.4167 | 16.2 | 15.6
| 9.5139 | 273.661 | 48.016 | 58.777 | 52.012 | 74.645 |  | 28.4792 | 28.1037 | 26.686 | -0.015907 | 10.618 | 27.013 | 29.3242 |  | 28.4375 | 16.7 | 15.6
| 9.5208 | 273.858 | 48.027 | 58.798 | 52.032 | 74.686 |  | 28.5 | 28.1171 | 26.7039 | -0.0014 | 10.6395 | 27.1031 | 29.3379 |  | 28.4583 | 16.9 | 15.6
| 9.5278 | 273.916 | 48.045 | 58.825 | 52.054 | 74.735 |  | 28.5208 | 28.1593 | 26.7392 | 0.069389 | 10.6694 | 27.1407 | 29.3733 |  | 28.4792 | 18.2 | 15.6
| 9.5347 | 274.359 | 48.068 | 58.854 | 52.076 | 74.779 |  | 28.5417 | 28.1263 | 26.7154 | 0.024109 | 10.6546 | 27.1122 | 29.3517 |  | 28.5 | 19.8 | 15.6
| 9.5417 | 274.093 | 48.082 | 58.875 | 52.094 | 74.819 |  | 28.5625 | 28.1231 | 26.7168 | 0.038071 | 10.6534 | 27.1046 | 29.3623 |  | 28.5208 | 20.6 | 15.6
| 9.5486 | 273.514 | 48.091 | 58.896 | 52.111 | 74.845 |  | 28.5833 | 28.1435 | 26.7349 | 0.070839 | 10.6667 | 27.1136 | 29.3713 |  | 28.5417 | 20.5 | 15.6
| 9.5556 | 280.182 | 48.118 | 58.93 | 52.133 | 74.892 |  | 28.6042 | 28.2186 | 26.7941 | 0.14475 | 10.7375 | 27.2046 | 29.4423 |  | 28.5625 | 21.1 | 15.6
| 9.5625 | 44.188 | 48.172 | 58.988 | 52.183 | 75.011 |  | 28.625 | 28.092 | 26.7334 | 0.057301 | 10.6622 | 27.1053 | 29.3745 |  | 28.5833 | 22.2 | 15.6
| 9.5694 | 279.932 | 47.751 | 58.544 | 51.851 | 74.106 |  | 28.6458 | 28.1553 | 26.7604 | 0.096638 | 10.6954 | 27.1188 | 29.4129 |  | 28.6042 | 22.2 | 15.6
| 9.5764 | 277.791 | 47.81 | 58.62 | 51.894 | 74.182 |  | 28.6667 | 28.2078 | 26.7742 | 0.12091 | 10.7224 | 27.1778 | 29.4245 |  | 28.625 | 23.4 | 15.6
| 9.5833 | 277.401 | 47.909 | 58.717 | 51.973 | 74.371 |  | 28.6875 | 28.1582 | 26.7495 | 0.069317 | 10.6898 | 27.1465 | 29.4109 |  | 28.6458 | 23.6 | 15.6
| 9.5903 | 278.248 | 47.99 | 58.791 | 52.032 | 74.534 |  | 28.7083 | 28.1831 | 26.7698 | 0.099995 | 10.7119 | 27.1645 | 29.4336 |  | 28.6667 | 23.2 | 15.6
| 9.5972 | 277.542 | 48.058 | 58.858 | 52.078 | 74.665 |  | 28.7292 | 28.1764 | 26.7608 | 0.091278 | 10.7009 | 27.1442 | 29.4155 |  | 28.6875 | 22.7 | 15.6
| 9.6042 | 278.49 | 48.109 | 58.913 | 52.126 | 74.779 |  | 28.75 | 28.1645 | 26.7355 | 0.071251 | 10.6828 | 27.1302 | 29.3968 |  | 28.7083 | 22.4 | 15.6
| 9.6111 | 278.644 | 48.152 | 58.968 | 52.164 | 74.887 |  | 28.7708 | 28.1436 | 26.7371 | 0.055504 | 10.6779 | 27.1204 | 29.2832 |  | 28.7292 | 22.8 | 15.6
| 9.6181 | 279.498 | 48.198 | 59.023 | 52.21 | 74.986 |  | 28.7917 | 28.0957 | 26.6847 | 0.004936 | 10.631 | 27.059 | 29.3526 |  | 28.75 | 22.8 | 15.6
| 9.625 | 264.498 | 47.817 | 58.621 | 51.917 | 74.246 |  | 28.8125 | 28.0899 | 26.6989 | 0.004086 | 10.6344 | 27.0554 | 29.3623 |  | 28.7708 | 22.7 | 15.6
| 9.6319 | 279.129 | 47.78 | 58.597 | 51.886 | 74.057 |  | 28.8333 | 28.05 | 26.621 | -0.077751 | 10.5957 | 26.8601 | 29.3021 |  | 28.7917 | 22.6 | 15.6
| 9.6389 | 279.68 | 47.88 | 58.701 | 51.964 | 74.258 |  | 28.8542 | 28.1002 | 26.6353 | -0.008606 | 10.6302 | 26.8022 | 29.3547 |  | 28.8125 | 22 | 15.6
| 9.6458 | 280.618 | 47.979 | 58.793 | 52.038 | 74.45 |  | 28.875 | 28.0868 | 26.6471 | -0.020412 | 10.6356 | 26.9043 | 29.3574 |  | 28.8333 | 21.3 | 15.6
| 9.6528 | 281.659 | 48.064 | 58.876 | 52.111 | 74.627 |  | 28.8958 | 28.0376 | 26.6116 | -0.11348 | 10.59 | 26.8304 | 29.3216 |  | 28.8542 | 20.4 | 15.6
| 9.6667 | 265.807 | 48.175 | 58.998 | 52.202 | 74.887 |  | 28.9167 | 28.0592 | 26.6175 | -0.078995 | 10.5961 | 26.8499 | 29.3207 |  | 28.875 | 19.2 | 15.6
| 9.6736 | 266.199 | 48.135 | 58.962 | 52.174 | 74.816 |  | 28.9375 | 28.0308 | 26.605 | -0.13654 | 10.5442 | 26.8397 | 29.3082 |  | 28.8958 | 18.1 | 15.6
| 9.6806 | 264.28 | 48.101 | 58.929 | 52.147 | 74.734 |  | 28.9583 | 27.9294 | 26.5035 | -0.27436 | 10.4733 | 26.7449 | 29.2155 |  | 28.9167 | 17.6 | 15.6
| 9.6875 | 262.004 | 48.06 | 58.893 | 52.124 | 74.637 |  | 28.9792 | 27.8157 | 26.4057 | -0.38864 | 10.3574 | 26.6335 | 29.1129 |  | 28.9375 | 17.2 | 15.6
| 9.6944 | 262.582 | 48.016 | 58.849 | 52.088 | 74.536 |  | 29 | 27.7996 | 26.3874 | -0.41953 | 10.3261 | 26.5925 | 29.0944 |  | 28.9583 | 16.8 | 15.6
| 9.7014 | 263.271 | 47.982 | 58.808 | 52.061 | 74.444 |  | 29.0208 | 27.9215 | 26.2008 | -0.72222 | 10.1144 | 26.3856 | 28.8983 |  | 28.9792 | 16.6 | 15.6
| 9.7083 | 263.19 | 47.956 | 58.778 | 52.035 | 74.37 |  | 29.0417 | 30.0218 | 29.0156 | -0.60421 | 10.2074 | 26.4938 | 28.984 |  | 29 | 16.3 | 15.6
| 9.7153 | 263.189 | 47.933 | 58.746 | 52.012 | 74.296 |  | 29.0625 | 30.9089 | 28.077 | -0.71792 | 10.1432 | 26.4172 | 28.9389 |  | 29.0208 | 15.8 | 15.6
| 9.7222 | 263.612 | 47.907 | 58.717 | 51.987 | 74.228 |  | 29.0833 | 31.0671 | 27.7593 | -0.76377 | 10.1055 | 26.3766 | 28.8937 |  | 29.0417 | 15.4 | 15.6
| 9.7292 | 261.853 | 47.894 | 58.688 | 51.966 | 74.17 |  | 29.1042 | 31.2819 | 27.712 | -0.61519 | 10.1874 | 26.4622 | 28.9795 |  | 29.0625 | 15.4 | 15.6
| 9.7361 | 262.02 | 47.873 | 58.662 | 51.946 | 74.105 |  | 29.125 | 31.2796 | 27.5589 | -0.67638 | 10.1167 | 26.3923 | 28.9231 |  | 29.0833 | 15.7 | 15.6
| 9.7431 | 262.629 | 47.855 | 58.635 | 51.923 | 74.044 |  | 29.1458 | 31.6007 | 27.7592 | -0.34204 | 10.3601 | 26.5905 | 29.1058 |  | 29.1042 | 15.8 | 15.6
| 9.75 | 261.845 | 47.839 | 58.609 | 51.899 | 73.995 |  | 29.1667 | 31.7048 | 27.7839 | -0.26104 | 10.391 | 26.6874 | 29.1939 |  | 29.125 | 15.7 | 15.6
| 9.7569 | 262.641 | 47.823 | 58.585 | 51.88 | 73.939 |  | 29.1875 | 31.7433 | 27.7254 | -0.25889 | 10.4199 | 26.6784 | 29.1961 |  | 29.1458 | 15.7 | 15.6
| 9.7639 | 262.631 | 47.814 | 58.568 | 51.863 | 73.902 |  | 29.2083 | 31.6618 | 27.606 | -0.412 | 10.2957 | 26.5589 | 29.081 |  | 29.1667 | 15.8 | 15.6
| 9.7708 | 262.371 | 47.797 | 58.544 | 51.844 | 73.864 |  | 29.2292 | 31.6727 | 27.5718 | -0.44593 | 10.266 | 26.5155 | 29.0736 |  | 29.1875 | 15.7 | 15.6
| 9.7778 | 261.728 | 47.785 | 58.526 | 51.827 | 73.825 |  | 29.25 | 31.641 | 27.5106 | -0.48306 | 10.224 | 26.4478 | 29.0172 |  | 29.2083 | 15.6 | 15.6
| 9.7847 | 262.647 | 47.773 | 58.505 | 51.808 | 73.788 |  | 29.2708 | 31.6727 | 27.5016 | -0.48091 | 10.2284 | 26.4501 | 29.0195 |  | 29.2292 | 15.7 | 15.6
| 9.7917 | 261.754 | 47.765 | 58.487 | 51.792 | 73.751 |  | 29.2917 | 31.7021 | 27.4948 | -0.44814 | 10.2284 | 26.4478 | 29.0421 |  | 29.25 | 15.8 | 15.6
| 9.7986 | 261.74 | 47.752 | 58.472 | 51.784 | 73.716 |  | 29.3125 | 31.7338 | 27.4993 | -0.43936 | 10.2682 | 26.4726 | 29.0421 |  | 29.2708 | 15.8 | 15.6
| 9.8056 | 262.964 | 47.741 | 58.457 | 51.765 | 73.686 |  | 29.3333 | 31.8312 | 27.5875 | -0.30816 | 10.3789 | 26.5515 | 29.1324 |  | 29.2917 | 15.6 | 15.6
| 9.8125 | 263.67 | 47.737 | 58.441 | 51.756 | 73.664 |  | 29.3542 | 31.9048 | 27.6315 | -0.22129 | 10.489 | 26.6249 | 29.172 |  | 29.3125 | 15.5 | 15.6
| 9.8194 | 263.929 | 47.733 | 58.434 | 51.752 | 73.649 |  | 29.375 | 31.9886 | 27.7216 | -0.10102 | 10.6175 | 26.6926 | 29.2511 |  | 29.3333 | 15.4 | 15.6
| 9.8264 | 263.448 | 47.732 | 58.427 | 51.745 | 73.64 |  | 29.3958 | 32.0294 | 27.7374 | -0.03315 | 10.7638 | 26.697 | 29.2736 |  | 29.3542 | 15.3 | 15.6
| 9.8333 | 263.657 | 47.729 | 58.424 | 51.74 | 73.631 |  | 29.4167 | 31.9479 | 27.6946 | -0.112 | 10.9383 | 26.652 | 29.2285 |  | 29.375 | 15.2 | 15.6
| 9.8403 | 263.501 | 47.727 | 58.417 | 51.736 | 73.621 |  | 29.4375 | 32.1605 | 27.8115 | 0.052032 | 11.4003 | 26.76 | 29.3367 |  | 29.3958 | 15.2 | 15.6
| 9.8472 | 263.745 | 47.73 | 58.412 | 51.737 | 73.613 |  | 29.4583 | 32.2512 | 27.8858 | 0.12769 | 11.9599 | 26.8027 | 29.3751 |  | 29.4167 | 15.4 | 15.6
| 9.8542 | 264.217 | 47.721 | 58.406 | 51.728 | 73.601 |  | 29.4792 | 32.2862 | 27.9117 | 0.19377 | 12.6143 | 26.8305 | 29.3895 |  | 29.4375 | 15.7 | 15.6
| 9.8611 | 263.79 | 47.719 | 58.403 | 51.729 | 73.595 |  | 29.5 | 32.3412 | 27.9617 | 0.26538 | 13.2911 | 26.8556 | 29.4217 |  | 29.4583 | 16.2 | 15.6
| 9.8681 | 263.651 | 47.709 | 58.398 | 51.721 | 73.578 |  | 29.5208 | 32.3479 | 27.9595 | 0.2698 | 13.8579 | 26.8579 | 29.4081 |  | 29.4792 | 16.9 | 15.6
| 9.875 | 263.447 | 47.706 | 58.39 | 51.713 | 73.564 |  | 29.5417 | 32.3593 | 27.9865 | 0.28944 | 14.3162 | 26.8894 | 29.4148 |  | 29.5 | 17.3 | 15.6
| 9.8819 | 263.64 | 47.701 | 58.386 | 51.714 | 73.557 |  | 29.5625 | 32.3457 | 28.018 | 0.29821 | 14.6478 | 26.8376 | 29.3809 |  | 29.5208 | 18.5 | 15.6
| 9.8889 | 265.657 | 47.7 | 58.382 | 51.709 | 73.545 |  | 29.5833 | 32.3821 | 28.0475 | 0.37271 | 14.9676 | 26.885 | 29.4173 |  | 29.5417 | 17.4 | 15.6
| 9.8958 | 265.136 | 47.707 | 58.386 | 51.714 | 73.553 |  | 29.6042 | 32.3775 | 28.0339 | 0.38369 | 15.172 | 26.8895 | 29.3991 |  | 29.5625 | 17.7 | 15.6
| 9.9028 | 265.44 | 47.714 | 58.398 | 51.721 | 73.565 |  | 29.625 | 32.4115 | 28.0407 | 0.43842 | 15.361 | 26.9053 | 29.4127 |  | 29.5833 | 18.3 | 15.6
| 9.9097 | 266.573 | 47.725 | 58.405 | 51.728 | 73.591 |  | 29.6458 | 32.3685 | 28.0092 | 0.44063 | 15.4809 | 26.8782 | 29.3901 |  | 29.6042 | 17.7 | 15.6
| 9.9167 | 267.73 | 47.736 | 58.422 | 51.74 | 73.617 |  | 29.6667 | 32.4075 | 28.0434 | 0.51644 | 15.6432 | 26.9325 | 29.4288 |  | 29.625 | 18.1 | 15.6
| 9.9236 | 264.295 | 47.743 | 58.431 | 51.742 | 73.627 |  | 29.6875 | 32.4137 | 28.0429 | 0.6005 | 15.7446 | 27.0016 | 29.4484 |  | 29.6458 | 17.8 | 15.6
| 9.9306 | 264.291 | 47.735 | 58.429 | 51.737 | 73.616 |  | 29.7083 | 32.3685 | 27.9975 | 0.59614 | 15.789 | 26.9452 | 29.401 |  | 29.6667 | 18.6 | 15.6
| 9.9375 | 265.092 | 47.731 | 58.422 | 51.737 | 73.604 |  | 29.7292 | 32.4069 | 28.0337 | 0.68818 | 15.9092 | 27.0016 | 29.4394 |  | 29.6875 | 18.9 | 15.6
| 9.9444 | 264.769 | 47.731 | 58.422 | 51.743 | 73.595 |  | 29.75 | 32.3988 | 28.0211 | 0.7303 | 15.9656 | 26.9506 | 29.3905 |  | 29.7083 | 18.7 | 15.6
| 9.9514 | 265.833 | 47.729 | 58.424 | 51.737 | 73.595 |  | 29.7708 | 32.3728 | 28.0493 | 0.78033 | 16.0115 | 27.0219 | 29.4393 |  | 29.7292 | 18.7 | 15.6
| 9.9583 | 265.226 | 47.731 | 58.43 | 51.762 | 73.603 |  | 29.7917 | 32.3597 | 28.0251 | 0.82763 | 16.0414 | 27.0001 | 29.4287 |  | 29.75 | 18.2 | 16.1
| 9.9653 | 265.98 | 47.743 | 58.438 | 51.744 | 73.61 |  | 29.8125 | 32.3656 | 28.0286 | 0.89732 | 16.0918 | 27.0264 | 29.4458 |  | 29.7708 | 17.9 | 16.1
| 9.9722 | 267.084 | 47.75 | 58.448 | 51.758 | 73.624 |  | 29.8333 | 32.306 | 27.9786 | 0.90685 | 16.092 | 26.9878 | 29.4048 |  | 29.7917 | 17.6 | 16.1
| 9.9792 | 267.251 | 47.76 | 58.458 | 51.765 | 73.642 |  | 29.8542 | 32.2171 | 27.8517 | 0.83772 | 16.0198 | 26.8405 | 29.2505 |  | 29.8125 | 17.5 | 16.1
| 9.9861 | 261.794 | 47.763 | 58.463 | 51.769 | 73.651 |  | 29.875 | [7 empty] | 29.8333 | 17.1 | 16.1
| 9.9931 | 264.971 | 47.743 | 58.441 | 51.751 | 73.601 |  | 29.8958 | [7 empty] | 29.8542 | 16.7 | 16.1
| 10 | 266.527 | 47.738 | 58.441 | 51.75 | 73.587 |  | 29.9167 | [7 empty] | 29.875 | 16.2 | 16.1
| 10.0069 | 266.97 | 47.747 | 58.45 | 51.75 | 73.597 |  | 29.9375 | [7 empty] | 29.8958 | 15.9 | 16.1
| 10.0139 | 266.674 | 47.757 | 58.466 | 51.76 | 73.618 |  | 29.9583 | [7 empty] | 29.9167 | 15.8 | 16.1
| 10.0208 | 266.762 | 47.767 | 58.479 | 51.77 | 73.634 |  | 29.9792 | [7 empty] | 29.9375 | 15.7 | 16.1
| 10.0278 | 267.219 | 47.777 | 58.492 | 51.777 | 73.651 |  | 30 | [7 empty] | 29.9583 | 15.4 | 16.1
| 10.0347 | 267.702 | 47.785 | 58.506 | 51.786 | 73.668 |  | 30.0208 | [7 empty] | 29.9792 | 15.4 | 16.1
| 10.0417 | 267.109 | 47.795 | 58.52 | 51.8 | 73.688 |  | 30.0417 | [7 empty] | 30 | 15 | 16.1
| 10.0486 | 267.852 | 47.807 | 58.537 | 51.809 | 73.714 |  | 30.0625 | [7 empty] | 30.0208 | 14.5 | 16.1
| 10.0556 | 267.266 | 47.819 | 58.552 | 51.813 | 73.73 |  | 30.0833 | [7 empty] | 30.0417 | 14.8 | 16.1
| 10.0625 | 264.308 | 47.826 | 58.564 | 51.825 | 73.748 |  | 30.1042 | [7 empty] | 30.0625 | 14.9 | 16.1
| 10.0694 | 264.93 | 47.816 | 58.56 | 51.822 | 73.73 |  | 30.125 | [7 empty] | 30.0833 | 14.9 | 16.1
| 10.0764 | 264.094 | 47.806 | 58.549 | 51.812 | 73.698 |  | 30.1458 | [7 empty] | 30.1042 | 14.9 | 16.1
| 10.0833 | 264.57 | 47.792 | 58.543 | 51.807 | 73.665 |  | 30.1667 | [7 empty] | 30.125 | 14.7 | 16.1
| 10.0903 | 264.311 | 47.79 | 58.535 | 51.801 | 73.645 |  | 30.1875 | 32.1895 | 27.8378 | 2.5006 | 16.2208 | 26.9557 | 29.4266 |  | 30.1458 | 14.6 | 16.1
| 10.0972 | 264.936 | 47.785 | 58.535 | 51.798 | 73.633 |  | 30.2083 | 32.1895 | 27.8401 | 2.6497 | 16.2298 | 26.9444 | 29.4333 |  | 30.1667 | 14.5 | 16.1
| 10.1042 | 265.274 | 47.786 | 58.544 | 51.801 | 73.626 |  | 30.2292 | 32.1737 | 27.8198 | 2.7879 | 16.2142 | 26.9625 | 29.4221 |  | 30.1875 | 14.2 | 16.1
| 10.1111 | 264.678 | 47.79 | 58.552 | 51.802 | 73.623 |  | 30.25 | 32.1827 | 27.8311 | 2.9723 | 16.2298 | 26.9963 | 29.4447 |  | 30.2083 | 14.3 | 16.1
| 10.1181 | 264.906 | 47.792 | 58.547 | 51.795 | 73.619 |  | 30.2708 | 32.1329 | 27.7905 | 3.1106 | 16.1942 | 26.9693 | 29.404 |  | 30.2292 | 14.2 | 16.1
| 10.125 | 264.547 | 47.789 | 58.548 | 51.799 | 73.614 |  | 30.2917 | 32.1397 | 27.7931 | 3.3369 | 16.192 | 26.9986 | 29.4131 |  | 30.25 | 14.6 | 16.1
| 10.1319 | 265.779 | 47.792 | 58.553 | 51.806 | 73.608 |  | 30.3125 | 32.1311 | 27.789 | 3.5964 | 16.1879 | 26.9921 | 29.4135 |  | 30.2708 | 14.4 | 16.1
| 10.1389 | 265.513 | 47.791 | 58.556 | 51.803 | 73.608 |  | 30.3333 | 32.1364 | 27.783 | 3.7836 | 16.1772 | 27.0198 | 29.4141 |  | 30.2917 | 15.2 | 16.1
| 10.1458 | 265.026 | 47.795 | 58.561 | 51.804 | 73.603 |  | 30.3542 | 32.1566 | 27.7963 | 4.3348 | 16.1877 | 27.0397 | 29.4297 |  | 30.3125 | 15.9 | 16.1
| 10.1528 | 264.527 | 47.796 | 58.565 | 51.809 | 73.601 |  | 30.375 | 32.1542 | 27.7572 | 4.8175 | 16.176 | 27.046 | 29.4272 |  | 30.3333 | 16.3 | 16.1
| 10.1597 | 264.742 | 47.801 | 58.568 | 51.808 | 73.6 |  | 30.3958 | 32.1044 | 27.7098 | 5.349 | 16.1181 | 26.9896 | 29.391 |  | 30.3542 | 17.1 | 16.1
| 10.1667 | 265.254 | 47.802 | 58.569 | 51.803 | 73.595 |  | 30.4167 | 32.1542 | 27.757 | 5.9289 | 16.1511 | 27.0029 | 29.4338 |  | 30.375 | 17.5 | 16.1
| 10.1736 | 264.51 | 47.799 | 58.569 | 51.803 | 73.587 |  | 30.4375 | 32.1135 | 27.6937 | 6.4575 | 16.1021 | 26.9624 | 29.4091 |  | 30.3958 | 18.2 | 16.1
| 10.1806 | 264.024 | 47.8 | 58.57 | 51.808 | 73.572 |  | 30.4583 | 32.1633 | 27.752 | 7.0231 | 16.1416 | 27.0115 | 29.4516 |  | 30.4167 | 18.2 | 16.1
| 10.1875 | 264.368 | 47.798 | 58.569 | 51.798 | 73.564 |  | 30.4792 | 32.1066 | 27.6843 | 7.4093 | 16.0859 | 26.9641 | 29.3975 |  | 30.4375 | 18.4 | 16.1
| 10.1944 | 264.57 | 47.794 | 58.568 | 51.802 | 73.557 |  | 30.5 | 32.1383 | 27.7227 | 7.8953 | 16.1148 | 26.998 | 29.4336 |  | 30.4583 | 18.6 | 16.1
| 10.2014 | 264.567 | 47.791 | 58.566 | 51.802 | 73.544 |  | 30.5208 | 32.1565 | 27.743 | 8.278 | 16.1193 | 27.0206 | 29.4516 |  | 30.4792 | 20.6 | 16.1
| 10.2083 | 263.641 | 47.788 | 58.571 | 51.801 | 73.539 |  | 30.5417 | 32.1043 | 27.6933 | 8.5999 | 16.0592 | 26.9731 | 29.4065 |  | 30.5 | 19.6 | 16.1
| 10.2153 | 263.06 | 47.789 | 58.564 | 51.796 | 73.518 |  | 30.5625 | 32.166 | 27.7316 | 8.9746 | 16.0945 | 27.0205 | 29.4542 |  | 30.5208 | 19 | 16.1
| 10.2222 | 265.801 | 47.791 | 58.569 | 51.798 | 73.52 |  | 30.5833 | 32.1026 | 27.6933 | 9.2572 | 16.0501 | 26.998 | 29.4113 |  | 30.5417 | 19.6 | 16.1
| 10.2292 | 265.192 | 47.798 | 58.578 | 51.804 | 73.535 |  | 30.6042 | 32.0822 | 27.6865 | 9.6018 | 16.0389 | 26.9574 | 29.4316 |  | 30.5625 | 20.7 | 16.1
| 10.2361 | 267.073 | 47.809 | 58.596 | 51.814 | 73.552 |  | 30.625 | 32.1373 | 27.7434 | 9.9933 | 16.0615 | 26.9918 | 29.4685 |  | 30.5833 | 21.5 | 16.1
| 10.2431 | 266.893 | 47.824 | 58.611 | 51.823 | 73.577 |  | 30.6458 | 32.1053 | 27.7025 | 10.2828 | 16.0232 | 26.9441 | 29.4319 |  | 30.6042 | 20.8 | 16.1
| 10.25 | 266.285 | 47.834 | 58.622 | 51.833 | 73.592 |  | 30.6667 | 32.0944 | 27.6943 | 10.5386 | 16.0107 | 26.9472 | 29.4325 |  | 30.625 | 20.5 | 16.1
| 10.2569 | 264.621 | 47.836 | 58.629 | 51.845 | 73.602 |  | 30.6875 | 32.0916 | 27.6984 | 10.7444 | 15.997 | 26.9513 | 29.4389 |  | 30.6458 | 21.9 | 16.1
| 10.2639 | 265.519 | 47.835 | 58.635 | 51.84 | 73.598 |  | 30.7083 | 32.0853 | 27.6899 | 10.8937 | 15.9756 | 26.9472 | 29.4348 |  | 30.6667 | 20.4 | 16.1
| 10.2708 | 265.299 | 47.833 | 58.639 | 51.843 | 73.601 |  | 30.7292 | 32.0982 | 27.6909 | 11.0448 | 15.9719 | 26.9777 | 29.4452 |  | 30.6875 | 19.6 | 16.1
| 10.2778 | 264.989 | 47.837 | 58.647 | 51.848 | 73.602 |  | 30.75 | [7 empty] | 30.7083 | 19.7 | 16.1
| 10.2847 | 265.591 | 47.841 | 58.646 | 51.847 | 73.597 |  | 30.7708 | 32.1517 | 27.7372 | 11.3339 | 15.9885 | 27.0105 | 29.4872 |  | 30.7292 | 20.1 | 16.1
| 10.2917 | 264.329 | 47.846 | 58.648 | 51.849 | 73.596 |  | 30.7917 | 32.1403 | 27.7508 | 11.436 | 15.9818 | 26.9878 | 29.503 |  | 30.75 | 21.6 | 16.1
| 10.2986 | 263.956 | 47.839 | 58.651 | 51.847 | 73.581 |  | 30.8125 | 32.1302 | 27.7454 | 11.5042 | 15.9632 | 26.9803 | 29.4907 |  | 30.7708 | 21.1 | 16.1
| 10.3056 | 266.096 | 47.84 | 58.65 | 51.848 | 73.566 |  | 30.8333 | 32.0494 | 27.6652 | 11.5162 | 15.882 | 26.9114 | 29.4284 |  | 30.7917 | 20.9 | 16.1
| 10.3125 | 265.103 | 47.848 | 58.659 | 51.845 | 73.58 |  | 30.8542 | 31.9714 | 27.6829 | 11.6088 | 15.8661 | 26.9424 | 29.448 |  | 30.8125 | 20.7 | 16.1
| 10.3194 | 265.209 | 47.848 | 58.66 | 51.851 | 73.583 |  | 30.875 | 32.1294 | 27.7033 | 11.7195 | 15.8841 | 26.9694 | 29.4522 |  | 30.8333 | 19.9 | 16.1
| 10.3264 | 264.907 | 47.849 | 58.668 | 51.857 | 73.578 |  | 30.8958 | 32.0879 | 27.6782 | 11.7393 | 15.8594 | 26.9443 | 29.4267 |  | 30.8542 | 19.1 | 16.1
| 10.3333 | 263.768 | 47.846 | 58.667 | 51.854 | 73.57 |  | 30.9167 | 32.0588 | 27.656 | 11.7733 | 15.8269 | 26.8977 | 29.4092 |  | 30.875 | 17.6 | 16.1
| 10.3403 | 263.479 | 47.841 | 58.664 | 51.852 | 73.555 |  | 30.9375 | 32.0247 | 27.6356 | 11.8002 | 15.7938 | 26.8638 | 29.3933 |  | 30.8958 | 16.3 | 16.1
| 10.3472 | 266.004 | 47.846 | 58.663 | 51.844 | 73.542 |  | 30.9583 | 31.999 | 27.6123 | 11.8019 | 15.7599 | 26.7821 | 29.3633 |  | 30.9167 | 15.3 | 16.1
| 10.3542 | 265.247 | 47.853 | 58.674 | 51.852 | 73.556 |  | 30.9792 | 32.0205 | 27.6067 | 11.8431 | 15.7478 | 26.7901 | 29.3646 |  | 30.9375 | 14.6 | 16.1
| 10.3611 | 264.831 | 47.857 | 58.678 | 51.858 | 73.56 |  | 31 | 32.0614 | 27.6652 | 11.9296 | 15.7679 | 26.7924 | 29.4188 |  | 30.9583 | 13.9 | 16.1
| 10.3681 | 264.813 | 47.864 | 58.686 | 51.857 | 73.559 |  | 31.0208 | 32.0239 | 27.6325 | 11.8954 | 15.7157 | 26.7529 | 29.395 |  | 30.9792 | 13.4 | 16.1
| 10.375 | 263.933 | 47.859 | 58.687 | 51.861 | 73.564 |  | 31.0417 | 31.9929 | 27.5995 | 11.9031 | 15.6812 | 26.7246 | 29.3597 |  | 31 | 13 | 16.1
| 10.3819 | 265.264 | 47.86 | 58.69 | 51.857 | 73.555 |  | 31.0625 | 32.0075 | 27.6095 | 11.9375 | 15.6712 | 26.7301 | 29.3696 |  | 31.0208 | 12.8 | 16.1
| 10.3889 | 264.352 | 47.863 | 58.695 | 51.86 | 73.555 |  | 31.0833 | 32.0029 | 27.605 | 11.953 | 15.6667 | 26.7256 | 29.3606 |  | 31.0417 | 12.4 | 16.1
| 10.3958 | 266.234 | 47.857 | 58.696 | 51.862 | 73.54 |  | 31.1042 | 31.9698 | 27.5789 | 11.9521 | 15.6235 | 26.6951 | 29.3367 |  | 31.0625 | 11.9 | 16.1
| 10.4028 | 267.867 | 47.873 | 58.709 | 51.868 | 73.569 |  | 31.125 | 31.9879 | 27.5946 | 11.992 | 15.6346 | 26.7153 | 29.357 |  | 31.0833 | 11.6 | 16.1
| 10.4097 | 266.133 | 47.893 | 58.733 | 51.884 | 73.608 |  | 31.1458 | 31.9697 | 27.5764 | 11.9587 | 15.59 | 26.6815 | 29.3366 |  | 31.1042 | 11.6 | 16.1
| 10.4167 | 266.551 | 47.906 | 58.748 | 51.891 | 73.626 |  | 31.1667 | 31.9878 | 27.5899 | 11.9808 | 15.5921 | 26.6974 | 29.3525 |  | 31.125 | 11.6 | 16.1
| 10.4236 | 266.179 | 47.914 | 58.751 | 51.903 | 73.641 |  | 31.1875 | 31.9633 | 27.5857 | 11.97 | 15.5613 | 26.6864 | 29.3461 |  | 31.1458 | 11.2 | 16.1
| 10.4306 | 264.829 | 47.919 | 58.769 | 51.905 | 73.654 |  | 31.2083 | 31.9723 | 27.597 | 11.9744 | 15.5591 | 26.6796 | 29.3551 |  | 31.1667 | 11.1 | 16.1
| 10.4375 | 263.995 | 47.923 | 58.768 | 51.907 | 73.659 |  | 31.2292 | 31.9633 | 27.5766 | 11.9855 | 15.5324 | 26.6774 | 29.3438 |  | 31.1875 | 10.7 | 16.1
| 10.4444 | 263.408 | 47.914 | 58.768 | 51.906 | 73.642 |  | 31.25 | 31.9704 | 27.5817 | 11.9858 | 15.5082 | 26.6799 | 29.3419 |  | 31.2083 | 10.6 | 16.1
| 10.4514 | 262.588 | 47.905 | 58.764 | 51.896 | 73.62 |  | 31.2708 | 31.9679 | 27.5883 | 12.0056 | 15.5037 | 26.6797 | 29.3575 |  | 31.2292 | 10.4 | 16.1
| 10.4583 | 264.293 | 47.898 | 58.751 | 51.893 | 73.594 |  | 31.2917 | 31.9808 | 27.5899 | 12.0222 | 15.4914 | 26.7034 | 29.3656 |  | 31.25 | 10.7 | 16.1
| 10.4653 | 262.639 | 47.902 | 58.751 | 51.891 | 73.586 |  | 31.3125 | 31.9922 | 27.5944 | 12.0241 | 15.48 | 26.8026 | 29.3725 |  | 31.2708 | 11.9 | 16.1
| 10.4722 | 263.235 | 47.89 | 58.745 | 51.88 | 73.567 |  | 31.3333 | 31.9784 | 27.5875 | 11.9995 | 15.4575 | 26.8361 | 29.3766 |  | 31.2917 | 12.6 | 16.1
| 10.4792 | 261.817 | 47.884 | 58.737 | 51.872 | 73.543 |  | 31.3542 | 31.9999 | 27.5684 | 11.9892 | 15.4539 | 26.758 | 29.3912 |  | 31.3125 | 13.2 | 16.1
| 10.4861 | 262.552 | 47.878 | 58.73 | 51.863 | 73.517 |  | 31.375 | 31.9432 | 27.5121 | 11.9715 | 15.3916 | 26.6859 | 29.3257 |  | 31.3333 | 13.8 | 16.1
| 10.4931 | 261.946 | 47.869 | 58.717 | 51.855 | 73.491 |  | 31.3958 | 31.9609 | 27.5157 | 11.9927 | 15.3996 | 26.6602 | 29.3543 |  | 31.3542 | 14.3 | 16.1
| 10.5 | 262.484 | 47.861 | 58.701 | 51.843 | 73.46 |  | 31.4167 | 31.9473 | 27.4999 | 11.9905 | 15.3663 | 26.6445 | 29.343 |  | 31.375 | 15.1 | 16.1
| 10.5069 | 261.381 | 47.861 | 58.707 | 51.842 | 73.453 |  | 31.4375 | 31.9246 | 27.484 | 11.9285 | 15.3284 | 26.6241 | 29.3204 |  | 31.3958 | 15.3 | 16.1
| 10.5139 | 262.216 | 47.854 | 58.693 | 51.833 | 73.433 |  | 31.4583 | 31.9042 | 27.484 | 11.9329 | 15.304 | 26.5723 | 29.3047 |  | 31.4167 | 15.5 | 16.1
| 10.5208 | 258.374 | 47.847 | 58.688 | 51.822 | 73.409 |  | 31.4792 | 31.9155 | 27.4909 | 11.9351 | 15.3018 | 26.6174 | 29.3204 |  | 31.4375 | 15.9 | 16.1
| 10.5278 | 262.309 | 47.828 | 58.661 | 51.808 | 73.36 |  | 31.5 | 31.9155 | 27.4953 | 11.9417 | 15.2906 | 26.6174 | 29.3295 |  | 31.4583 | 16.4 | 16.1
| 10.5347 | 261.751 | 47.823 | 58.659 | 51.803 | 73.35 |  | 31.5208 | 31.9178 | 27.4863 | 11.9883 | 15.264 | 26.6174 | 29.3227 |  | 31.4792 | 16.5 | 16.1
| 10.5417 | 262.204 | 47.824 | 58.656 | 51.797 | 73.34 |  | 31.5417 | 31.9291 | 27.5043 | 11.9617 | 15.2506 | 26.6219 | 29.3385 |  | 31.5 | 16.6 | 16.1
| 10.5486 | 262.762 | 47.829 | 58.651 | 51.791 | 73.335 |  | 31.5625 | 31.9404 | 27.5089 | 11.9905 | 15.2529 | 26.658 | 29.3476 |  | 31.5208 | 16 | 16.1
| 10.5556 | 261.949 | 47.828 | 58.654 | 51.793 | 73.332 |  | 31.5833 | 31.9609 | 27.5383 | 12.0193 | 15.2551 | 26.6512 | 29.3815 |  | 31.5417 | 16.3 | 16.1
| 10.5625 | 261.468 | 47.827 | 58.645 | 51.783 | 73.319 |  | 31.6042 | 31.9676 | 27.545 | 12.0791 | 15.2529 | 26.685 | 29.3837 |  | 31.5625 | 16.1 | 16.1
| 10.5694 | 261.392 | 47.825 | 58.641 | 51.782 | 73.313 |  | 31.625 | 31.9722 | 27.5518 | 12.0326 | 15.2418 | 26.6738 | 29.3882 |  | 31.5833 | 16 | 16.1
| 10.5764 | 261.568 | 47.821 | 58.639 | 51.776 | 73.298 |  | 31.6458 | 31.9602 | 27.5306 | 12.0428 | 15.2232 | 26.6776 | 29.3877 |  | 31.6042 | 15.8 | 16.1
| 10.5833 | 262.129 | 47.822 | 58.636 | 51.774 | 73.293 |  | 31.6667 | 31.9942 | 27.5578 | 12.0848 | 15.2321 | 26.6978 | 29.4057 |  | 31.625 | 15.7 | 16.1
| 10.5903 | 262.852 | 47.818 | 58.631 | 51.774 | 73.284 |  | 31.6875 | 31.9874 | 27.5646 | 12.0228 | 15.2165 | 26.6956 | 29.4035 |  | 31.6458 | 15.9 | 16.1
| 10.5972 | 263.423 | 47.82 | 58.633 | 51.769 | 73.286 |  | 31.7083 | 31.9852 | 27.5578 | 12.0715 | 15.2031 | 26.6911 | 29.4103 |  | 31.6667 | 15.6 | 16.1
| 10.6042 | 263.121 | 47.822 | 58.64 | 51.769 | 73.292 |  | 31.7292 | 32.0078 | 27.5827 | 12.0494 | 15.2076 | 26.7092 | 29.4306 |  | 31.6875 | 15.7 | 16.1
| 10.6111 | 261.917 | 47.828 | 58.634 | 51.767 | 73.292 |  | 31.75 | 31.9706 | 27.5501 | 12.0176 | 15.1579 | 26.663 | 29.3866 |  | 31.7083 | 15.8 | 16.1
| 10.6181 | 260.803 | 47.821 | 58.636 | 51.759 | 73.288 |  | 31.7708 | 31.9683 | 27.5388 | 11.9888 | 15.1445 | 26.654 | 29.3911 |  | 31.7292 | 15.8 | 16.1
| 10.625 | 260.663 | 47.823 | 58.628 | 51.753 | 73.278 |  | 31.7917 | 31.9367 | 27.5072 | 11.9622 | 15.1067 | 26.627 | 29.355 |  | 31.75 | 15.8 | 16.1
| 10.6319 | 260.997 | 47.813 | 58.624 | 51.749 | 73.263 |  | 31.8125 | 31.9072 | 27.4846 | 11.9511 | 15.0756 | 26.5954 | 29.3347 |  | 31.7708 | 15.8 | 16.1
| 10.6389 | 260.448 | 47.805 | 58.615 | 51.739 | 73.238 |  | 31.8333 | 31.9199 | 27.5107 | 11.9765 | 15.0856 | 26.6057 | 29.3676 |  | 31.7917 | 15.8 | 16.1
| 10.6458 | 260.482 | 47.802 | 58.6 | 51.734 | 73.223 |  | 31.8542 | 31.9584 | 27.5311 | 11.9853 | 15.1034 | 26.6327 | 29.3857 |  | 31.8125 | 15.9 | 16.1
| 10.6528 | 261.416 | 47.797 | 58.601 | 51.731 | 73.209 |  | 31.875 | 31.9607 | 27.5513 | 11.961 | 15.0967 | 26.644 | 29.3924 |  | 31.8333 | 15.9 | 16.1
| 10.6597 | 260.728 | 47.795 | 58.597 | 51.729 | 73.206 |  | 31.8958 | 31.9675 | 27.5491 | 11.9655 | 15.09 | 26.653 | 29.4196 |  | 31.8542 | 15.7 | 16.1
| 10.6667 | 260.966 | 47.799 | 58.595 | 51.727 | 73.202 |  | 31.9167 | 31.9924 | 27.5649 | 11.9898 | 15.0856 | 26.6305 | 29.415 |  | 31.875 | 15.6 | 16.1
| 10.6736 | 260.856 | 47.8 | 58.6 | 51.727 | 73.205 |  | 31.9375 | 31.9788 | 27.5491 | 11.9655 | 15.0789 | 26.6462 | 29.4309 |  | 31.8958 | 15.6 | 16.1
| 10.6806 | 260.864 | 47.797 | 58.596 | 51.72 | 73.201 |  | 31.9583 | 31.9698 | 27.5604 | 11.9632 | 15.0656 | 26.6395 | 29.415 |  | 31.9167 | 15.5 | 16.1
| 10.6875 | 258.465 | 47.794 | 58.596 | 51.724 | 73.192 |  | 31.9792 | 31.9426 | 27.5445 | 11.9167 | 15.0501 | 26.635 | 29.4219 |  | 31.9375 | 15.6 | 16.1
| 10.6944 | 259.288 | 47.782 | 58.581 | 51.72 | 73.164 |  | 32 | 31.9992 | 27.5875 | 11.972 | 15.059 | 26.6395 | 29.449 |  | 31.9583 | 15.6 | 16.1
| 10.7014 | 259.276 | 47.769 | 58.569 | 51.701 | 73.139 |  | 32.0208 | 31.9924 | 27.5739 | 11.9831 | 15.0479 | 26.6169 | 29.4241 |  | 31.9792 | 15.6 | 16.1
| 10.7083 | 259.551 | 47.76 | 58.558 | 51.688 | 73.115 |  | 32.0417 | 31.972 | 27.5627 | 11.9167 | 15.0323 | 26.6035 | 29.4264 |  | 32 | 15.5 | 16.1
| 10.7153 | 263.533 | 47.756 | 58.548 | 51.686 | 73.099 |  | 32.0625 | 31.9652 | 27.5649 | 11.9189 | 15.0257 | 26.6057 | 29.4219 |  | 32.0208 | 15.5 | 16.1
| 10.7222 | 263.283 | 47.766 | 58.562 | 51.693 | 73.127 |  | 32.0833 | 31.9018 | 27.5017 | 11.8437 | 14.9789 | 26.5426 | 29.3698 |  | 32.0417 | 15.4 | 16.1
| 10.7292 | 263.379 | 47.79 | 58.582 | 51.707 | 73.169 |  | 32.1042 | 31.8995 | 27.5017 | 11.8547 | 14.9701 | 26.5358 | 29.3631 |  | 32.0625 | 15.4 | 16.1
| 10.7361 | 264.671 | 47.816 | 58.607 | 51.726 | 73.217 |  | 32.125 | 31.8815 | 27.4881 | 11.8126 | 14.9479 | 26.511 | 29.345 |  | 32.0833 | 15.4 | 16.1
| 10.7431 | 264.259 | 47.838 | 58.636 | 51.744 | 73.266 |  | 32.1458 | 31.8769 | 27.4836 | 11.8104 | 14.9412 | 26.5043 | 29.3427 |  | 32.1042 | 15.4 | 16.1
| 10.75 | 266.032 | 47.862 | 58.661 | 51.764 | 73.321 |  | 32.1667 | 31.8882 | 27.4993 | 11.8104 | 14.9368 | 26.5065 | 29.3563 |  | 32.125 | 15.3 | 16.1
| 10.7569 | 265.802 | 47.88 | 58.69 | 51.778 | 73.376 |  | 32.1875 | 31.8951 | 27.5017 | 11.8104 | 14.939 | 26.5268 | 29.3541 |  | 32.1458 | 15.3 | 16.1
| 10.7639 | 265.868 | 47.902 | 58.718 | 51.802 | 73.42 |  | 32.2083 | 31.9131 | 27.5197 | 11.8149 | 14.9456 | 26.5448 | 29.3767 |  | 32.1667 | 15.3 | 16.1
| 10.7708 | 264.871 | 47.919 | 58.745 | 51.817 | 73.469 |  | 32.2292 | 31.9199 | 27.5197 | 11.8348 | 14.939 | 26.538 | 29.3789 |  | 32.1875 | 15.2 | 16.1
| 10.7778 | 264.727 | 47.927 | 58.758 | 51.819 | 73.493 |  | 32.25 | 31.9109 | 27.5197 | 11.8016 | 14.9345 | 26.529 | 29.3857 |  | 32.2083 | 15.1 | 16.1
| 10.7847 | 265.054 | 47.936 | 58.769 | 51.828 | 73.511 |  | 32.2708 | 31.9357 | 27.5445 | 11.8038 | 14.9368 | 26.547 | 29.397 |  | 32.2292 | 15.1 | 16.1
| 10.7917 | 266.524 | 47.94 | 58.788 | 51.846 | 73.536 |  | 32.2917 | 31.8973 | 27.5152 | 11.7993 | 14.9146 | 26.5178 | 29.3676 |  | 32.25 | 15 | 16.1
| 10.7986 | 265.352 | 47.954 | 58.807 | 51.856 | 73.562 |  | 32.3125 | 31.8769 | 27.4971 | 11.7794 | 14.8924 | 26.5043 | 29.3563 |  | 32.2708 | 14.9 | 16.1
| 10.8056 | 266.161 | 47.959 | 58.824 | 51.867 | 73.583 |  | 32.3333 | 31.8867 | 27.5022 | 11.8088 | 14.8952 | 26.5138 | 29.3592 |  | 32.2917 | 15 | 16.1
| 10.8125 | 265.917 | 47.968 | 58.84 | 51.876 | 73.604 |  | 32.3542 | 31.8549 | 27.4705 | 11.7667 | 14.8574 | 26.559 | 29.3299 |  | 32.3125 | 14.9 | 16.1
| 10.8194 | 267.313 | 47.979 | 58.859 | 51.884 | 73.625 |  | 32.375 | 31.8878 | 27.5099 | 11.7698 | 14.8806 | 26.6164 | 29.3648 |  | 32.3333 | 15.2 | 16.1
| 10.8264 | 267.363 | 47.993 | 58.881 | 51.9 | 73.657 |  | 32.3958 | 31.9292 | 27.5352 | 11.8256 | 14.901 | 26.6507 | 29.3948 |  | 32.3542 | 15.8 | 16.1
| 10.8333 | 268.87 | 48.003 | 58.904 | 51.915 | 73.689 |  | 32.4167 | 31.9016 | 27.5278 | 11.7893 | 14.8914 | 26.6455 | 29.3874 |  | 32.375 | 15.8 | 16.1
| 10.8403 | 268.136 | 48.022 | 58.932 | 51.929 | 73.729 |  | 32.4375 | 31.8852 | 27.5382 | 11.7949 | 14.8749 | 26.6446 | 29.3867 |  | 32.3958 | 16.2 | 16.1
| 10.8472 | 266.988 | 48.032 | 58.956 | 51.948 | 73.765 |  | 32.4583 | 31.824 | 27.5224 | 11.7263 | 14.8193 | 26.5544 | 29.3143 |  | 32.4167 | 16.7 | 16.1
| 10.8542 | 267.697 | 48.048 | 58.974 | 51.959 | 73.783 |  | 32.4792 | 31.8398 | 27.5382 | 11.7329 | 14.8327 | 26.5724 | 29.3437 |  | 32.4375 | 17.1 | 16.1
| 10.8611 | 267.507 | 48.053 | 58.996 | 51.968 | 73.805 |  | 32.5 | 31.8082 | 27.511 | 11.6643 | 14.8038 | 26.5431 | 29.3188 |  | 32.4583 | 17.4 | 16.1
| 10.8681 | 267.071 | 48.065 | 59.016 | 51.98 | 73.83 |  | 32.5208 | 31.8987 | 27.5766 | 11.7285 | 14.8548 | 26.6469 | 29.3912 |  | 32.4792 | 18.3 | 16.1
| 10.875 | 266.975 | 48.071 | 59.031 | 51.99 | 73.842 |  | 32.5417 | 31.8919 | 27.5766 | 11.7507 | 14.8594 | 26.6424 | 29.3934 |  | 32.5 | 17.9 | 16.1
| 10.8819 | 266.903 | 48.072 | 59.038 | 51.992 | 73.852 |  | 32.5625 | 31.8829 | 27.5585 | 11.6975 | 14.8371 | 26.6062 | 29.3822 |  | 32.5208 | 17.7 | 16.1
| 10.8889 | 268.389 | 48.075 | 59.053 | 52.003 | 73.854 |  | 32.5833 | 31.9017 | 27.5816 | 11.7425 | 14.8512 | 26.634 | 29.3987 |  | 32.5417 | 17.6 | 16.1
| 10.8958 | 270.508 | 48.092 | 59.075 | 52.018 | 73.883 |  | 32.6042 | 31.8742 | 27.5627 | 11.6464 | 14.8148 | 26.5972 | 29.3664 |  | 32.5625 | 17.9 | 16.1
| 10.9028 | 271.734 | 48.117 | 59.117 | 52.042 | 73.941 |  | 32.625 | 31.89 | 27.5734 | 11.6431 | 14.8265 | 26.6282 | 29.3909 |  | 32.5833 | 18 | 16.1
| 10.9097 | 268.832 | 48.145 | 59.156 | 52.066 | 74 |  | 32.6458 | 31.8793 | 27.5717 | 11.6393 | 14.8224 | 26.6175 | 29.3848 |  | 32.6042 | 18.7 | 16.1
| 10.9167 | 269.308 | 48.15 | 59.177 | 52.077 | 74.023 |  | 32.6667 | 31.8975 | 27.5921 | 11.5909 | 14.8314 | 26.622 | 29.4006 |  | 32.625 | 19.5 | 16.1
| 10.9236 | 270.349 | 48.161 | 59.194 | 52.093 | 74.048 |  | 32.6875 | 31.8864 | 27.5721 | 11.6305 | 14.8162 | 26.6088 | 29.392 |  | 32.6458 | 20.8 | 16.1
| 10.9306 | 270.82 | 48.184 | 59.228 | 52.117 | 74.088 |  | 32.7083 | 31.8646 | 27.5664 | 11.5389 | 14.7952 | 26.5693 | 29.3816 |  | 32.6667 | 20.8 | 16.1
| 10.9375 | 268.635 | 48.198 | 59.261 | 52.135 | 74.138 |  | 32.7292 | 31.8797 | 27.5703 | 11.5738 | 14.7993 | 26.5913 | 29.3833 |  | 32.6875 | 20.6 | 16.1
| 10.9444 | 268.182 | 48.212 | 59.283 | 52.145 | 74.153 |  | 32.75 | 31.8789 | 27.572 | 11.4868 | 14.7968 | 26.6064 | 29.3825 |  | 32.7083 | 20.5 | 16.1
| 10.9514 | 269.298 | 48.211 | 59.291 | 52.154 | 74.154 |  | 32.7708 | 31.9197 | 27.5855 | 11.4912 | 14.8101 | 26.6176 | 29.3893 |  | 32.7292 | 20.3 | 16.1
| 10.9583 | 268.86 | 48.21 | 59.307 | 52.165 | 74.164 |  | 32.7917 | 31.9122 | 27.6031 | 11.5017 | 14.8051 | 26.6058 | 29.3909 |  | 32.75 | 19.9 | 16.1
| 10.9653 | 269.646 | 48.218 | 59.323 | 52.172 | 74.172 |  | 32.8125 | 31.8471 | 27.5428 | 11.4143 | 14.7528 | 26.5164 | 29.335 |  | 32.7708 | 19.7 | 16.1
| 10.9722 | 270.505 | 48.23 | 59.347 | 52.186 | 74.192 |  | 32.8333 | 31.8734 | 27.5671 | 11.4822 | 14.7632 | 26.5654 | 29.3751 |  | 32.7917 | 19.6 | 16.1
| 10.9792 | 271.382 | 48.243 | 59.37 | 52.197 | 74.227 |  | 32.8542 | 31.8699 | 27.566 | 11.459 | 14.7555 | 26.5393 | 29.3647 |  | 32.8125 | 19.4 | 16.1
| 10.9861 | 270.839 | 48.261 | 59.401 | 52.213 | 74.256 |  | 32.875 | 31.8659 | 27.5622 | 11.4594 | 14.7647 | 26.5218 | 29.3675 |  | 32.8333 | 18.7 | 16.1
| 10.9931 | 270.958 | 48.274 | 59.425 | 52.225 | 74.286 |  | 32.8958 | 31.884 | 27.5802 | 11.4572 | 14.7624 | 26.5128 | 29.3766 |  | 32.8542 | 18.3 | 16.1
| 11 | 271.787 | 48.288 | 59.456 | 52.243 | 74.318 |  | 32.9167 | 31.8613 | 27.5577 | 11.4156 | 14.7339 | 26.4859 | 29.3517 |  | 32.875 | 17.8 | 16.1
| 11.0069 | 266.63 | 48.293 | 59.469 | 52.25 | 74.33 |  | 32.9375 | 31.8521 | 27.5531 | 11.3979 | 14.7362 | 26.4769 | 29.3449 |  | 32.8958 | 17.4 | 16.1
| 11.0139 | 264.5 | 48.27 | 59.454 | 52.232 | 74.272 |  | 32.9583 | 31.8443 | 27.5319 | 11.395 | 14.7199 | 26.4535 | 29.3282 |  | 32.9167 | 17 | 16.1
| 11.0208 | 264.361 | 48.246 | 59.435 | 52.22 | 74.216 |  | 32.9792 | 31.8402 | 27.5301 | 11.3288 | 14.7067 | 26.3929 | 29.3036 |  | 32.9375 | 16.9 | 16.1
| 11.0278 | 264.464 | 48.223 | 59.419 | 52.211 | 74.167 |  | 33 | 31.8469 | 27.5393 | 11.3403 | 14.7094 | 26.4089 | 29.3263 |  | 32.9583 | 16.7 | 16.1
| 11.0347 | 264.895 | 48.206 | 59.399 | 52.194 | 74.115 |  | 33.0208 | 31.8672 | 27.571 | 11.3491 | 14.716 | 26.4044 | 29.3466 |  | 32.9792 | 16.6 | 16.1
| 11.0417 | 265.076 | 48.194 | 59.392 | 52.184 | 74.072 |  | 33.0417 | 31.8718 | 27.5732 | 11.358 | 14.7115 | 26.4179 | 29.3579 |  | 33 | 16.3 | 16.1
| 11.0486 | 265.303 | 48.186 | 59.38 | 52.179 | 74.044 |  | 33.0625 | 31.8542 | 27.5512 | 11.3009 | 14.6919 | 26.3847 | 29.3291 |  | 33.0208 | 15.8 | 16.1
| 11.0556 | 265.869 | 48.181 | 59.384 | 52.173 | 74.028 |  | 33.0833 | 31.8519 | 27.5535 | 11.3053 | 14.6942 | 26.3891 | 29.3291 |  | 33.0417 | 15.7 | 16.1
| 11.0625 | 266.258 | 48.183 | 59.39 | 52.171 | 74.02 |  | 33.1042 | 31.8474 | 27.5535 | 11.2633 | 14.6875 | 26.3847 | 29.3381 |  | 33.0625 | 15.6 | 16.1
| 11.0694 | 265.108 | 48.181 | 59.392 | 52.18 | 74.013 |  | 33.125 | 31.8502 | 27.5497 | 11.2753 | 14.6729 | 26.3741 | 29.3252 |  | 33.0833 | 15.5 | 16.1
| 11.0764 | 265.547 | 48.183 | 59.396 | 52.172 | 73.998 |  | 33.1458 | 31.8389 | 27.5384 | 11.3284 | 14.6595 | 26.3651 | 29.3117 |  | 33.1042 | 15.4 | 16.1
| 11.0833 | 266.174 | 48.181 | 59.405 | 52.18 | 73.992 |  | 33.1667 | 31.8661 | 27.5587 | 11.2841 | 14.6751 | 26.3628 | 29.332 |  | 33.125 | 15.3 | 16.1
| 11.0903 | 263.964 | 48.189 | 59.411 | 52.18 | 73.987 |  | 33.1875 | 31.8331 | 27.5372 | 11.3384 | 14.6474 | 26.3481 | 29.3081 |  | 33.1458 | 15.3 | 16.1
| 11.0972 | 263.961 | 48.173 | 59.409 | 52.168 | 73.966 |  | 33.2083 | 31.8668 | 27.5598 | 11.2431 | 14.667 | 26.3884 | 29.3281 |  | 33.1667 | 15.2 | 16.1
| 11.1042 | 264.159 | 48.16 | 59.4 | 52.159 | 73.928 |  | 33.2292 | 31.8516 | 27.5492 | 11.2109 | 14.6371 | 26.3646 | 29.3222 |  | 33.1875 | 15 | 16.1
| 11.1111 | 263.575 | 48.154 | 59.398 | 52.152 | 73.899 |  | 33.25 | 31.8403 | 27.547 | 11.2375 | 14.6304 | 26.3533 | 29.3132 |  | 33.2083 | 14.7 | 16.1
| 11.1181 | 263.252 | 48.144 | 59.388 | 52.144 | 73.873 |  | 33.2708 | 31.8285 | 27.5214 | 11.1704 | 14.6186 | 26.3459 | 29.2946 |  | 33.2292 | 14.2 | 16.1
| 11.125 | 263.922 | 48.136 | 59.383 | 52.136 | 73.841 |  | 33.2917 | 31.8511 | 27.5346 | 11.1808 | 14.6225 | 26.3816 | 29.3102 |  | 33.25 | 13.9 | 16.1
| 11.1319 | 263.337 | 48.126 | 59.379 | 52.136 | 73.814 |  | 33.3125 | 31.8327 | 27.523 | 11.1741 | 14.6068 | 26.4691 | 29.2962 |  | 33.2708 | 14.1 | 16.1
| 11.1389 | 263.689 | 48.125 | 59.379 | 52.124 | 73.792 |  | 33.3333 | 31.8402 | 27.5235 | 11.2698 | 14.6096 | 26.4968 | 29.3015 |  | 33.2917 | 14.6 | 16.1
| 11.1458 | 263.67 | 48.123 | 59.38 | 52.126 | 73.782 |  | 33.3542 | 31.8412 | 27.5289 | 11.1621 | 14.5993 | 26.4909 | 29.3069 |  | 33.3125 | 14.8 | 16.1
| 11.1528 | 264.063 | 48.119 | 59.385 | 52.125 | 73.77 |  | 33.375 | 31.805 | 27.495 | 11.1974 | 14.5571 | 26.4413 | 29.2685 |  | 33.3333 | 15.1 | 16.1
| 11.1597 | 264.54 | 48.117 | 59.391 | 52.119 | 73.759 |  | 33.3958 | 31.8392 | 27.54 | 11.2237 | 14.5946 | 26.4772 | 29.3137 |  | 33.3542 | 15.4 | 16.1
| 11.1667 | 263.53 | 48.118 | 59.39 | 52.118 | 73.745 |  | 33.4167 | 31.8758 | 27.5628 | 11.3169 | 14.6105 | 26.5136 | 29.339 |  | 33.375 | 15.8 | 16.1
| 11.1736 | 263.388 | 48.119 | 59.393 | 52.123 | 73.736 |  | 33.4375 | 31.8078 | 27.5222 | 11.2443 | 14.5523 | 26.4506 | 29.2915 |  | 33.3958 | 15.9 | 16.1
| 11.1806 | 263.871 | 48.117 | 59.401 | 52.122 | 73.73 |  | 33.4583 | 31.8588 | 27.5679 | 11.2797 | 14.6013 | 26.4964 | 29.3467 |  | 33.4167 | 16.7 | 16.1
| 11.1875 | 264.098 | 48.119 | 59.402 | 52.114 | 73.72 |  | 33.4792 | 31.8689 | 27.5732 | 11.1893 | 14.5997 | 26.513 | 29.3499 |  | 33.4375 | 17.3 | 16.1
| 11.1944 | 264.575 | 48.113 | 59.41 | 52.123 | 73.715 |  | 33.5 | 31.8644 | 27.5819 | 11.1595 | 14.5854 | 26.4946 | 29.3541 |  | 33.4583 | 18.3 | 16.1
| 11.2014 | 263.871 | 48.12 | 59.414 | 52.118 | 73.707 |  | 33.5208 | 31.8639 | 27.5653 | 11.1629 | 14.5755 | 26.4872 | 29.3491 |  | 33.4792 | 19.2 | 16.1
| 11.2083 | 263.333 | 48.114 | 59.417 | 52.118 | 73.7 |  | 33.5417 | 31.8685 | 27.5676 | 11.1562 | 14.5644 | 26.4782 | 29.3401 |  | 33.5 | 20.3 | 16.1
| 11.2153 | 262.989 | 48.11 | 59.426 | 52.117 | 73.691 |  | 33.5625 | 31.8752 | 27.5788 | 11.1984 | 14.5599 | 26.4782 | 29.3491 |  | 33.5208 | 20.9 | 16.1
| 11.2222 | 261.852 | 48.105 | 59.418 | 52.113 | 73.669 |  | 33.5833 | 31.8911 | 27.5946 | 11.1252 | 14.5688 | 26.5097 | 29.3694 |  | 33.5417 | 21.4 | 16.1
| 11.2292 | 261.419 | 48.096 | 59.414 | 52.101 | 73.644 |  | 33.6042 | 31.9206 | 27.5679 | 11.1211 | 14.5804 | 26.3861 | 29.3787 |  | 33.5625 | 21.3 | 16.1
| 11.2361 | 266.181 | 48.104 | 59.425 | 52.107 | 73.644 |  | 33.625 | 31.927 | 27.5772 | 11.1307 | 14.5721 | 26.3929 | 29.365 |  | 33.5833 | 21.1 | 16.1
| 11.2431 | 266.09 | 48.117 | 59.445 | 52.12 | 73.677 |  | 33.6458 | 31.8885 | 27.5523 | 11.1418 | 14.5632 | 26.4019 | 29.3628 |  | 33.6042 | 21.2 | 16.1
| 11.25 | 265.578 | 48.136 | 59.477 | 52.136 | 73.701 |  | 33.6667 | 31.8546 | 27.5206 | 11.1063 | 14.5254 | 26.456 | 29.3356 |  | 33.625 | 20.4 | 16.1
| 11.2569 | 265.266 | 48.147 | 59.493 | 52.149 | 73.726 |  | 33.6875 | 31.8802 | 27.5553 | 11.1251 | 14.5419 | 26.5063 | 29.3634 |  | 33.6458 | 18.9 | 16.1
| 11.2639 | 262.885 | 48.145 | 59.496 | 52.146 | 73.725 |  | 33.7083 | 31.8517 | 27.5584 | 11.0992 | 14.5338 | 26.4734 | 29.3576 |  | 33.6667 | 19.3 | 16.1
| 11.2708 | 264.663 | 48.141 | 59.498 | 52.138 | 73.702 |  | 33.7292 | 31.8631 | 27.6285 | 11.1103 | 14.5515 | 26.4914 | 29.3734 |  | 33.6875 | 19.9 | 16.1
| 11.2778 | 265.753 | 48.139 | 59.509 | 52.149 | 73.71 |  | 33.75 | 31.8491 | 27.5989 | 11.1079 | 14.5179 | 26.4573 | 29.346 |  | 33.7083 | 20.2 | 16.1
| 11.2847 | 265.314 | 48.155 | 59.524 | 52.157 | 73.722 |  | 33.7708 | 31.8445 | 27.6033 | 11.1035 | 14.5068 | 26.4416 | 29.3505 |  | 33.7292 | 19.7 | 16.1
| 11.2917 | 265.729 | 48.163 | 59.544 | 52.166 | 73.736 |  | 33.7917 | 31.8604 | 27.6214 | 11.1079 | 14.5202 | 26.4529 | 29.3687 |  | 33.75 | 19.7 | 16.1
| 11.2986 | 263.751 | 48.162 | 59.554 | 52.167 | 73.745 |  | 33.8125 | 31.8434 | 27.6024 | 11.1315 | 14.5061 | 26.436 | 29.3517 |  | 33.7708 | 19.6 | 16.1
| 11.3056 | 263.338 | 48.157 | 59.551 | 52.166 | 73.725 |  | 33.8333 | 31.8382 | 27.5567 | 11.1091 | 14.4924 | 26.3048 | 29.3466 |  | 33.7917 | 19.7 | 16.1
| 11.3125 | 265.994 | 48.15 | 59.549 | 52.159 | 73.701 |  | 33.8542 | 31.8049 | 27.526 | 10.9749 | 14.4556 | 26.2402 | 29.3224 |  | 33.8125 | 19.6 | 16.1
| 11.3194 | 265.079 | 48.153 | 59.563 | 52.175 | 73.705 |  | 33.875 | 31.8186 | 27.5173 | 11.0712 | 14.4564 | 26.2226 | 29.3205 |  | 33.8333 | 19.3 | 16.1
| 11.3264 | 264.929 | 48.162 | 59.581 | 52.175 | 73.725 |  | 33.8958 | 31.8381 | 27.5348 | 11.108 | 14.4606 | 26.249 | 29.3333 |  | 33.8542 | 18.6 | 16.1
| 11.3333 | 264.652 | 48.166 | 59.588 | 52.181 | 73.724 |  | 33.9167 | 31.8356 | 27.5369 | 11.1187 | 14.4559 | 26.233 | 29.3307 |  | 33.875 | 18.1 | 16.1
| 11.3403 | 263.95 | 48.17 | 59.6 | 52.186 | 73.725 |  | 33.9375 | 31.8378 | 27.5392 | 11.1143 | 14.4492 | 26.2532 | 29.3284 |  | 33.8958 | 17.7 | 16.1
| 11.3472 | 263.154 | 48.168 | 59.603 | 52.186 | 73.716 |  | 33.9583 | 31.822 | 27.5256 | 11.0877 | 14.4359 | 26.2397 | 29.3104 |  | 33.9167 | 17.1 | 16.1
| 11.3542 | 262.739 | 48.161 | 59.603 | 52.178 | 73.692 |  | 33.9792 | 31.8333 | 27.5414 | 11.1032 | 14.4381 | 26.2464 | 29.3261 |  | 33.9375 | 16.7 | 16.1
| 11.3611 | 262.367 | 48.156 | 59.6 | 52.183 | 73.676 |  | 34 | 31.8401 | 27.5504 | 11.1165 | 14.4403 | 26.2577 | 29.3353 |  | 33.9583 | 16.7 | 16.1
| 11.3681 | 261.679 | 48.143 | 59.592 | 52.163 | 73.649 |  | 34.0208 | 31.8361 | 27.5376 | 11.0865 | 14.4212 | 26.2314 | 29.3246 |  | 33.9792 | 16.7 | 16.1
| 11.375 | 261.641 | 48.137 | 59.582 | 52.156 | 73.619 |  | 34.0417 | 31.87 | 27.5716 | 11.0952 | 14.45 | 26.2562 | 29.3585 |  | 34 | 16.3 | 16.1
| 11.3819 | 265.828 | 48.134 | 59.591 | 52.161 | 73.606 |  | 34.0625 | 31.8211 | 27.5297 | 11.0522 | 14.3935 | 26.2145 | 29.3097 |  | 34.0208 | 16.3 | 16.1
| 11.3889 | 265.109 | 48.152 | 59.616 | 52.178 | 73.637 |  | 34.0833 | 31.8301 | 27.5365 | 11.0744 | 14.4135 | 26.2122 | 29.3189 |  | 34.0417 | 15.8 | 16.1
| 11.3958 | 264.021 | 48.16 | 59.636 | 52.186 | 73.657 |  | 34.1042 | 31.7958 | 27.5092 | 11.0541 | 14.3754 | 26.1916 | 29.2891 |  | 34.0625 | 15.4 | 16.1
| 11.4028 | 267.114 | 48.169 | 59.644 | 52.195 | 73.662 |  | 34.125 | 31.7868 | 27.5001 | 11.0121 | 14.3576 | 26.1713 | 29.2755 |  | 34.0833 | 15.2 | 16.1
| 11.4097 | 266.807 | 48.186 | 59.673 | 52.211 | 73.691 |  | 34.1458 | 31.7709 | 27.4911 | 11.0408 | 14.3421 | 26.1646 | 29.2619 |  | 34.1042 | 14.8 | 16.1
| 11.4167 | 266.994 | 48.208 | 59.698 | 52.229 | 73.729 |  | 34.1667 | 31.7845 | 27.4934 | 11.0718 | 14.3354 | 26.1556 | 29.2732 |  | 34.125 | 14.8 | 16.1
| 11.4236 | 267.531 | 48.217 | 59.721 | 52.242 | 73.759 |  | 34.1875 | 31.7778 | 27.4911 | 11.0541 | 14.3288 | 26.1646 | 29.2687 |  | 34.1458 | 14.9 | 16.1
| 11.4306 | 268.681 | 48.238 | 59.754 | 52.26 | 73.801 |  | 34.2083 | 31.7986 | 27.5298 | 11.2512 | 14.3469 | 26.1672 | 29.3008 |  | 34.1667 | 14.9 | 16.1
| 11.4375 | 267.217 | 48.259 | 59.788 | 52.279 | 73.838 |  | 34.2292 | 31.7782 | 27.4982 | 11.0478 | 14.3136 | 26.1514 | 29.2668 |  | 34.1875 | 15.2 | 16.1
| 11.4444 | 266.425 | 48.274 | 59.805 | 52.286 | 73.868 |  | 34.25 | 31.8313 | 27.5418 | 11.0862 | 14.3522 | 26.2266 | 29.3129 |  | 34.2083 | 15 | 16.1
| 11.4514 | 265.783 | 48.274 | 59.825 | 52.296 | 73.882 |  | 34.2708 | 31.786 | 27.5327 | 11.0266 | 14.3029 | 26.1613 | 29.2746 |  | 34.2292 | 14.9 | 16.1
| 11.4583 | 264.751 | 48.277 | 59.829 | 52.3 | 73.878 |  | 34.2917 | 31.841 | 27.6168 | 11.0736 | 14.3456 | 26.2203 | 29.3271 |  | 34.25 | 15.3 | 16.1
| 11.4653 | 266.152 | 48.275 | 59.838 | 52.303 | 73.871 |  | 34.3125 | 31.8125 | 27.5973 | 11.0435 | 14.3262 | 26.219 | 29.3054 |  | 34.2708 | 15.6 | 16.1
| 11.4722 | 263.699 | 48.276 | 59.847 | 52.31 | 73.878 |  | 34.3333 | 31.765 | 27.5431 | 11.0302 | 14.2749 | 26.255 | 29.2715 |  | 34.2917 | 15.8 | 16.1
| 11.4792 | 263.659 | 48.272 | 59.844 | 52.303 | 73.852 |  | 34.3542 | 31.8195 | 27.5858 | 11.0694 | 14.3233 | 26.3135 | 29.3189 |  | 34.3125 | 16.3 | 16.1
| 11.4861 | 264.127 | 48.256 | 59.838 | 52.298 | 73.824 |  | 34.375 | 31.8221 | 27.5949 | 11.0916 | 14.3122 | 26.3114 | 29.3214 |  | 34.3333 | 16.4 | 16.1
| 11.4931 | 262.62 | 48.256 | 59.843 | 52.302 | 73.81 |  | 34.3958 | 31.8431 | 27.6244 | 11.0823 | 14.3364 | 26.3455 | 29.3467 |  | 34.3542 | 16.8 | 16.1
| 11.5 | 267.036 | 48.248 | 59.834 | 52.298 | 73.79 |  | 34.4167 | 31.8301 | 27.629 | 11.1283 | 14.3271 | 26.3344 | 29.3493 |  | 34.375 | 17.3 | 16.1
| 11.5069 | 266.223 | 48.27 | 59.863 | 52.308 | 73.812 |  | 34.4375 | 31.8272 | 27.6282 | 11.0984 | 14.3193 | 26.3382 | 29.3554 |  | 34.3958 | 18.3 | 16.1
| 11.5139 | 264.046 | 48.274 | 59.877 | 52.316 | 73.826 |  | 34.4583 | 31.7683 | 27.5829 | 11.0495 | 14.2592 | 26.2076 | 29.3058 |  | 34.4167 | 19.7 | 16.1
| 11.5208 | 265.086 | 48.278 | 59.883 | 52.325 | 73.827 |  | 34.4792 | 31.8368 | 27.5814 | 11.0944 | 14.311 | 26.1947 | 29.3516 |  | 34.4375 | 20.9 | 16.1
| 11.5278 | 266.165 | 48.285 | 59.895 | 52.327 | 73.83 |  | 34.5 | 31.8362 | 27.5769 | 11.1039 | 14.3025 | 26.1989 | 29.3534 |  | 34.4583 | 21.7 | 16.1
| 11.5347 | 263.078 | 48.29 | 59.907 | 52.323 | 73.833 |  | 34.5208 | 31.821 | 27.5776 | 11.1228 | 14.288 | 26.2943 | 29.3428 |  | 34.4792 | 22.3 | 16.1
| 11.5417 | 262.656 | 48.285 | 59.903 | 52.32 | 73.816 |  | 34.5417 | 31.8243 | 27.6124 | 11.1301 | 14.282 | 26.3245 | 29.3438 |  | 34.5 | 20.6 | 16.1
| 11.5486 | 262.139 | 48.28 | 59.899 | 52.319 | 73.799 |  | 34.5625 | 31.8039 | 27.6102 | 11.0968 | 14.2597 | 26.3065 | 29.3279 |  | 34.5208 | 18.9 | 16.1
| 11.5556 | 262.055 | 48.271 | 59.891 | 52.314 | 73.767 |  | 34.5833 | 31.8394 | 27.5819 | 11.0975 | 14.2784 | 26.2356 | 29.3496 |  | 34.5417 | 18.5 | 16.1
| 11.5625 | 263.33 | 48.265 | 59.886 | 52.303 | 73.743 |  | 34.6042 | 31.8168 | 27.6225 | 11.1264 | 14.2539 | 26.3257 | 29.3338 |  | 34.5625 | 20.3 | 16.1
| 11.5694 | 263.503 | 48.259 | 59.888 | 52.3 | 73.733 |  | 34.625 | 31.8688 | 27.6677 | 11.1618 | 14.2939 | 26.3775 | 29.3903 |  | 34.5833 | 20.4 | 16.1
| 11.5764 | 263.946 | 48.264 | 59.896 | 52.304 | 73.73 |  | 34.6458 | 31.8506 | 27.6518 | 11.113 | 14.265 | 26.3302 | 29.3745 |  | 34.6042 | 21.3 | 16.1
| 11.5833 | 262.935 | 48.265 | 59.901 | 52.307 | 73.731 |  | 34.6667 | 31.8464 | 27.6495 | 11.1324 | 14.2555 | 26.3301 | 29.3768 |  | 34.625 | 21.3 | 16.1
| 11.5903 | 263.59 | 48.271 | 59.907 | 52.305 | 73.724 |  | 34.6875 | 31.8432 | 27.628 | 11.1265 | 14.2454 | 26.3471 | 29.3555 |  | 34.6458 | 20.5 | 16.1
| 11.5972 | 263.606 | 48.268 | 59.91 | 52.305 | 73.723 |  | 34.7083 | 31.8229 | 27.6212 | 11.1 | 14.2232 | 26.3089 | 29.3442 |  | 34.6667 | 21.1 | 16.1
| 11.6042 | 262.827 | 48.27 | 59.911 | 52.306 | 73.712 |  | 34.7292 | 31.8575 | 27.6467 | 11.1358 | 14.2436 | 26.3455 | 29.3675 |  | 34.6875 | 21.9 | 16.1
| 11.6111 | 262.904 | 48.264 | 59.917 | 52.302 | 73.705 |  | 34.75 | 31.8553 | 27.6489 | 11.1158 | 14.2391 | 26.3365 | 29.3719 |  | 34.7083 | 22.5 | 16.1
| 11.6181 | 263.909 | 48.268 | 59.922 | 52.3 | 73.699 |  | 34.7708 | 31.8649 | 27.6541 | 11.1297 | 14.2441 | 26.355 | 29.3771 |  | 34.7292 | 22.3 | 16.1
| 11.625 | 262.278 | 48.265 | 59.921 | 52.303 | 73.692 |  | 34.7917 | 31.8717 | 27.6631 | 11.1297 | 14.2397 | 26.3528 | 29.3816 |  | 34.75 | 22.4 | 16.1
| 11.6319 | 261.701 | 48.259 | 59.918 | 52.298 | 73.675 |  | 34.8125 | 31.8653 | 27.6639 | 11.1132 | 14.2408 | 26.331 | 29.3755 |  | 34.7708 | 22.8 | 16.1
| 11.6389 | 261.803 | 48.25 | 59.911 | 52.293 | 73.652 |  | 34.8333 | 31.8669 | 27.6524 | 11.1203 | 14.2344 | 26.3127 | 29.3796 |  | 34.7917 | 22.2 | 16.1
| 11.6458 | 262.022 | 48.247 | 59.905 | 52.288 | 73.634 |  | 34.8542 | 31.8828 | 27.6619 | 11.1655 | 14.2285 | 26.2882 | 29.3728 |  | 34.8125 | 22.6 | 16.1
| 11.6528 | 262.771 | 48.25 | 59.913 | 52.287 | 73.629 |  | 34.875 | 31.8641 | 27.6663 | 11.1703 | 14.2154 | 26.2496 | 29.3613 |  | 34.8333 | 20.6 | 16.1
| 11.6597 | 263.786 | 48.255 | 59.92 | 52.287 | 73.628 |  | 34.8958 | 31.8753 | 27.655 | 11.1394 | 14.211 | 26.2248 | 29.3589 |  | 34.8542 | 19.2 | 16.1
| 11.6667 | 261.699 | 48.259 | 59.93 | 52.293 | 73.644 |  | 34.9167 | 31.8578 | 27.6536 | 11.1378 | 14.2009 | 26.2008 | 29.3595 |  | 34.875 | 18.6 | 16.1
| 11.6736 | 260.71 | 48.256 | 59.927 | 52.281 | 73.63 |  | 34.9375 | 31.8409 | 27.6436 | 11.1348 | 14.1736 | 26.1233 | 29.3338 |  | 34.8958 | 18.2 | 16.1
| 11.6806 | 261.719 | 48.248 | 59.913 | 52.28 | 73.605 |  | 34.9583 | 31.8654 | 27.6547 | 11.1124 | 14.1911 | 26.195 | 29.3492 |  | 34.9167 | 17.6 | 16.1
| 11.6875 | 265.23 | 48.244 | 59.907 | 52.277 | 73.592 |  | 34.9792 | 31.8563 | 27.6479 | 11.1124 | 14.1734 | 26.1545 | 29.3469 |  | 34.9375 | 17.2 | 16.1
| 11.6944 | 265.646 | 48.266 | 59.931 | 52.285 | 73.62 |  | 35 | 31.8699 | 27.6638 | 11.1434 | 14.1934 | 26.1816 | 29.3628 |  | 34.9583 | 17.1 | 16.1
| 11.7014 | 263.358 | 48.286 | 59.964 | 52.305 | 73.662 | [9 empty] | 34.9792 | 16.6 | 16.1
| 11.7083 | 263.525 | 48.288 | 59.966 | 52.311 | 73.666 | [9 empty] | 35 | 16.2 | 16.1
| 11.7153 | 263.527 | 48.29 | 59.974 | 52.311 | 73.671
| 11.7222 | 263.653 | 48.287 | 59.98 | 52.314 | 73.677
| 11.7292 | 264.746 | 48.297 | 59.996 | 52.323 | 73.685
| 11.7361 | 265.569 | 48.309 | 60.012 | 52.329 | 73.707
| 11.7431 | 263.811 | 48.322 | 60.03 | 52.339 | 73.729
| 11.75 | 263.778 | 48.324 | 60.043 | 52.344 | 73.736
| 11.7569 | 264.838 | 48.325 | 60.049 | 52.345 | 73.739
| 11.7639 | 264.478 | 48.326 | 60.059 | 52.354 | 73.747
| 11.7708 | 264.813 | 48.334 | 60.077 | 52.358 | 73.756
| 11.7778 | 264.964 | 48.337 | 60.086 | 52.366 | 73.766
| 11.7847 | 265.457 | 48.344 | 60.1 | 52.374 | 73.776
| 11.7917 | 264.459 | 48.349 | 60.114 | 52.378 | 73.784
| 11.7986 | 265.852 | 48.359 | 60.129 | 52.386 | 73.803
| 11.8056 | 266.12 | 48.366 | 60.147 | 52.392 | 73.819
| 11.8125 | 266.648 | 48.382 | 60.163 | 52.406 | 73.839
| 11.8194 | 263.305 | 48.392 | 60.192 | 52.422 | 73.875
| 11.8264 | 264.124 | 48.387 | 60.192 | 52.416 | 73.863
| 11.8333 | 263.865 | 48.383 | 60.193 | 52.419 | 73.855
| 11.8403 | 261.523 | 48.38 | 60.195 | 52.417 | 73.846
| 11.8472 | 262.173 | 48.369 | 60.183 | 52.41 | 73.806
| 11.8542 | 261.39 | 48.356 | 60.167 | 52.392 | 73.773
| 11.8611 | 264.432 | 48.346 | 60.163 | 52.39 | 73.747
| 11.8681 | 264.187 | 48.353 | 60.181 | 52.396 | 73.765
| 11.875 | 263.799 | 48.358 | 60.191 | 52.405 | 73.77
| 11.8819 | 264.092 | 48.362 | 60.202 | 52.405 | 73.766
| 11.8889 | 264.764 | 48.358 | 60.204 | 52.411 | 73.766
| 11.8958 | 263.203 | 48.358 | 60.204 | 52.408 | 73.761
| 11.9028 | 262.845 | 48.359 | 60.205 | 52.406 | 73.751
| 11.9097 | 263.687 | 48.354 | 60.208 | 52.406 | 73.74
| 11.9167 | 264.434 | 48.356 | 60.221 | 52.407 | 73.747
| 11.9236 | 264.771 | 48.366 | 60.235 | 52.415 | 73.757
| 11.9306 | 264.756 | 48.373 | 60.247 | 52.422 | 73.773
| 11.9375 | 265.671 | 48.381 | 60.264 | 52.435 | 73.793
| 11.9444 | 266.103 | 48.397 | 60.283 | 52.443 | 73.816
| 11.9514 | 266.379 | 48.41 | 60.304 | 52.452 | 73.842
| 11.9583 | 267.153 | 48.423 | 60.332 | 52.474 | 73.877
| 11.9653 | 264.182 | 48.437 | 60.355 | 52.481 | 73.909
| 11.9722 | 265.035 | 48.438 | 60.358 | 52.485 | 73.907
| 11.9792 | 265.759 | 48.444 | 60.371 | 52.49 | 73.914
| 11.9861 | 265.707 | 48.446 | 60.384 | 52.494 | 73.926
| 11.9931 | 264.894 | 48.45 | 60.396 | 52.504 | 73.934
| 12 | 266.342 | 48.453 | 60.405 | 52.506 | 73.94
| 12.0069 | 266.064 | 48.456 | 60.416 | 52.511 | 73.942
| 12.0139 | 265.828 | 48.461 | 60.429 | 52.521 | 73.956
| 12.0208 | 265.98 | 48.472 | 60.445 | 52.527 | 73.967
| 12.0278 | 265.939 | 48.479 | 60.464 | 52.532 | 73.982
| 12.0347 | 266.838 | 48.486 | 60.482 | 52.539 | 74.001
| 12.0417 | 267.281 | 48.498 | 60.498 | 52.552 | 74.02
| 12.0486 | 267.983 | 48.511 | 60.526 | 52.565 | 74.051
| 12.0556 | 265.056 | 48.524 | 60.55 | 52.58 | 74.082
| 12.0625 | 265.572 | 48.519 | 60.555 | 52.576 | 74.075
| 12.0694 | 265.36 | 48.519 | 60.555 | 52.577 | 74.064
| 12.0764 | 265.014 | 48.516 | 60.563 | 52.58 | 74.064
| 12.0833 | 265.23 | 48.517 | 60.57 | 52.582 | 74.063
| 12.0903 | 266.052 | 48.519 | 60.578 | 52.587 | 74.061
| 12.0972 | 266.806 | 48.527 | 60.596 | 52.595 | 74.072
| 12.1042 | 266.706 | 48.532 | 60.612 | 52.605 | 74.085
| 12.1111 | 266.25 | 48.539 | 60.629 | 52.611 | 74.097
| 12.1181 | 266.388 | 48.545 | 60.639 | 52.611 | 74.109
| 12.125 | 266.382 | 48.551 | 60.65 | 52.619 | 74.117
| 12.1319 | 266.055 | 48.551 | 60.665 | 52.627 | 74.119
| 12.1389 | 265.669 | 48.556 | 60.676 | 52.633 | 74.124
| 12.1458 | 266.165 | 48.562 | 60.685 | 52.635 | 74.135
| 12.1528 | 266.283 | 48.567 | 60.704 | 52.636 | 74.144
| 12.1597 | 266.149 | 48.574 | 60.714 | 52.645 | 74.15
| 12.1667 | 265.778 | 48.576 | 60.725 | 52.656 | 74.154
| 12.1736 | 266.011 | 48.578 | 60.736 | 52.657 | 74.159
| 12.1806 | 266.01 | 48.578 | 60.747 | 52.661 | 74.16
| 12.1875 | 266.1 | 48.585 | 60.755 | 52.668 | 74.164
| 12.1944 | 265.229 | 48.584 | 60.766 | 52.671 | 74.168
| 12.2014 | 265.077 | 48.585 | 60.771 | 52.67 | 74.161
| 12.2083 | 264.901 | 48.587 | 60.78 | 52.664 | 74.158
| 12.2153 | 264.303 | 48.585 | 60.78 | 52.664 | 74.146
| 12.2222 | 264.386 | 48.575 | 60.78 | 52.658 | 74.125
| 12.2292 | 265.446 | 48.57 | 60.775 | 52.658 | 74.114
| 12.2361 | 265.884 | 48.573 | 60.789 | 52.66 | 74.116
| 12.2431 | 264.693 | 48.58 | 60.799 | 52.668 | 74.116
| 12.25 | 264.838 | 48.58 | 60.806 | 52.67 | 74.121
| 12.2569 | 264.363 | 48.579 | 60.808 | 52.665 | 74.11
| 12.2639 | 266.052 | 48.574 | 60.81 | 52.659 | 74.097
| 12.2708 | 266.004 | 48.582 | 60.826 | 52.671 | 74.111
| 12.2778 | 265.097 | 48.585 | 60.841 | 52.678 | 74.118
| 12.2847 | 264.528 | 48.585 | 60.844 | 52.679 | 74.117
| 12.2917 | 266.395 | 48.581 | 60.849 | 52.673 | 74.105
| 12.2986 | 268.214 | 48.594 | 60.87 | 52.686 | 74.122
| 12.3056 | 267.108 | 48.61 | 60.902 | 52.702 | 74.164
| 12.3125 | 267.039 | 48.625 | 60.924 | 52.71 | 74.188
| 12.3194 | 265.452 | 48.632 | 60.941 | 52.716 | 74.201
| 12.3264 | 265.498 | 48.629 | 60.941 | 52.713 | 74.201
| 12.3333 | 265.037 | 48.628 | 60.942 | 52.713 | 74.191
| 12.3403 | 265.225 | 48.626 | 60.95 | 52.715 | 74.185
| 12.3472 | 265.619 | 48.618 | 60.949 | 52.708 | 74.169
| 12.3542 | 265.331 | 48.616 | 60.952 | 52.705 | 74.159
| 12.3611 | 264.536 | 48.616 | 60.958 | 52.708 | 74.153
| 12.3681 | 264.245 | 48.612 | 60.961 | 52.706 | 74.148
| 12.375 | 263.86 | 48.609 | 60.963 | 52.701 | 74.134
| 12.3819 | 264.446 | 48.607 | 60.968 | 52.699 | 74.129
| 12.3889 | 265.051 | 48.607 | 60.974 | 52.706 | 74.125
| 12.3958 | 263.864 | 48.613 | 60.979 | 52.697 | 74.122
| 12.4028 | 263.931 | 48.614 | 60.984 | 52.698 | 74.117
| 12.4097 | 262.926 | 48.606 | 60.981 | 52.695 | 74.102
| 12.4792 | 263.906 | 48.549 | 60.951 | 52.626 | 73.929
| 12.4861 | 264.712 | 48.558 | 60.971 | 52.638 | 73.952
| 12.4931 | 265.015 | 48.571 | 60.987 | 52.641 | 73.966
| 12.5 | 265.095 | 48.58 | 61.004 | 52.645 | 73.987
| 12.5069 | 265.158 | 48.591 | 61.021 | 52.651 | 74.009
| 12.5139 | 264.993 | 48.601 | 61.034 | 52.657 | 74.023
| 12.5208 | 261.326 | 48.591 | 61.039 | 52.653 | 74.018
| 12.5278 | 261.51 | 48.579 | 61.019 | 52.638 | 73.984
| 12.5347 | 261.037 | 48.562 | 61.004 | 52.621 | 73.952
| 12.5417 | 261.024 | 48.55 | 60.989 | 52.612 | 73.916
| 12.5486 | 261.335 | 48.539 | 60.985 | 52.604 | 73.888
| 12.5556 | 261.042 | 48.537 | 60.983 | 52.599 | 73.877
| 12.5625 | 260.838 | 48.529 | 60.974 | 52.591 | 73.853
| 12.5694 | 260.929 | 48.522 | 60.967 | 52.582 | 73.831
| 12.5764 | 260.711 | 48.516 | 61.207 | 52.575 | 73.812
| 12.5833 | 261.491 | 48.505 | 61.248 | 52.572 | 73.796
| 12.5903 | 263.745 | 48.509 | 61.264 | 52.582 | 73.8
| 12.5972 | 264.014 | 48.522 | 61.287 | 52.592 | 73.826
| 12.6042 | 262.611 | 48.54 | 61.303 | 52.601 | 73.854
| 12.6111 | 264.003 | 48.541 | 61.312 | 52.603 | 73.862
| 12.6181 | 264.121 | 48.549 | 61.322 | 52.609 | 73.877
| 12.625 | 264.614 | 48.551 | 61.321 | 52.616 | 73.89
| 12.6319 | 264.889 | 48.557 | 61.308 | 52.617 | 73.905
| 12.6389 | 265.592 | 48.562 | 61.245 | 52.631 | 73.93
| 12.6458 | 264.837 | 48.57 | 61.216 | 52.644 | 73.945
| 12.6528 | 266.102 | 48.571 | 61.183 | 52.646 | 73.964
| 12.6597 | 267.774 | 48.577 | 61.204 | 52.66 | 73.997
| 12.6667 | 259.588 | 48.593 | 61.223 | 52.672 | 74.027
| 12.6736 | 259.333 | 48.563 | 61.182 | 52.652 | 73.977
| 12.6806 | 259.707 | 48.538 | 61.156 | 52.625 | 73.91
| 12.6875 | 260.34 | 48.513 | 61.127 | 52.61 | 73.859
| 12.6944 | 259 | 48.501 | 61.113 | 52.599 | 73.829
| 12.7014 | 259.286 | 48.485 | 61.092 | 52.574 | 73.784
| 12.7083 | 258.865 | 48.46 | 61.07 | 52.556 | 73.737
| 12.7153 | 259.237 | 48.441 | 61.056 | 52.533 | 73.697
| 12.7222 | 259.802 | 48.432 | 61.042 | 52.527 | 73.666
| 12.7292 | 260.488 | 48.421 | 61.034 | 52.512 | 73.634
| 12.7361 | 256.811 | 48.407 | 61.014 | 52.497 | 73.61
| 12.7431 | 257.933 | 48.39 | 60.991 | 52.48 | 73.558
| 12.75 | 258.238 | 48.379 | 60.968 | 52.464 | 73.521
| 12.7569 | 259.013 | 48.371 | 60.953 | 52.441 | 73.488
| 12.7639 | 259.282 | 48.364 | 60.937 | 52.436 | 73.47
| 12.7708 | 259.285 | 48.364 | 60.93 | 52.416 | 73.452
| 12.7778 | 259.267 | 48.36 | 60.922 | 52.405 | 73.429
| 12.7847 | 258.7 | 48.348 | 60.916 | 52.398 | 73.421
| 12.7917 | 261.509 | 48.328 | 60.897 | 52.386 | 73.379
| 12.7986 | 262.134 | 48.326 | 60.902 | 52.38 | 73.379
| 12.8056 | 262.383 | 48.334 | 60.918 | 52.382 | 73.395
| 12.8125 | 261.061 | 48.342 | 60.931 | 52.389 | 73.41
| 12.8194 | 262.038 | 48.351 | 60.94 | 52.39 | 73.42
| 12.8264 | 262.226 | 48.351 | 60.953 | 52.389 | 73.431
| 12.8333 | 262.278 | 48.349 | 60.965 | 52.397 | 73.446
| 12.8403 | 263.05 | 48.357 | 60.978 | 52.396 | 73.462
| 12.8472 | 259.006 | 48.363 | 60.99 | 52.399 | 73.477
| 12.8542 | 259.12 | 48.351 | 60.974 | 52.385 | 73.448
| 12.8611 | 259.661 | 48.335 | 60.959 | 52.374 | 73.422
| 12.8681 | 260.238 | 48.33 | 60.942 | 52.367 | 73.407
| 12.875 | 259.984 | 48.315 | 60.939 | 52.361 | 73.396
| 12.8819 | 259.882 | 48.324 | 60.935 | 52.36 | 73.39
| 12.8889 | 258.691 | 48.317 | 60.924 | 52.345 | 73.372
| 12.8958 | 258.833 | 48.3 | 60.917 | 52.338 | 73.344
| 12.9028 | 259.525 | 48.29 | 60.908 | 52.321 | 73.32
| 12.9097 | 259.638 | 48.281 | 60.897 | 52.318 | 73.303
| 12.9167 | 260.582 | 48.277 | 60.895 | 52.316 | 73.292
| 12.9236 | 260.463 | 48.276 | 60.901 | 52.314 | 73.289
| 12.9306 | 258.72 | 48.276 | 60.911 | 52.307 | 73.285
| 12.9375 | 259.797 | 48.266 | 60.904 | 52.303 | 73.269
| 12.9444 | 259.874 | 48.262 | 60.91 | 52.298 | 73.261
| 12.9514 | 260.428 | 48.259 | 60.918 | 52.297 | 73.265
| 12.9583 | 260.882 | 48.267 | 60.927 | 52.297 | 73.268
| 12.9653 | 259.505 | 48.272 | 60.94 | 52.303 | 73.277
| 12.9722 | 259.951 | 48.266 | 60.937 | 52.299 | 73.275
| 12.9792 | 260.014 | 48.261 | 60.936 | 52.287 | 73.263
| 12.9861 | 261.204 | 48.26 | 60.941 | 52.281 | 73.258
| 12.9931 | 260.782 | 48.257 | 60.944 | 52.282 | 73.255
| 13 | 261.13 | 48.257 | 60.953 | 52.285 | 73.258
| 13.0069 | 262.119 | 48.267 | 60.969 | 52.287 | 73.269
| 13.0139 | 260.886 | 48.268 | 60.983 | 52.29 | 73.282
| 13.0208 | 261.429 | 48.273 | 60.992 | 52.292 | 73.288
| 13.0278 | 261.307 | 48.271 | 60.998 | 52.292 | 73.288
| 13.0347 | 261.619 | 48.269 | 61.01 | 52.29 | 73.294
| 13.0417 | 261.584 | 48.27 | 61.017 | 52.291 | 73.296
| 13.0486 | 262.121 | 48.276 | 61.03 | 52.301 | 73.306
| 13.0556 | 262.073 | 48.279 | 61.042 | 52.302 | 73.319
| 13.0625 | 262.747 | 48.286 | 61.058 | 52.309 | 73.329
| 13.0694 | 263.031 | 48.294 | 61.075 | 52.313 | 73.345
| 13.0764 | 259.503 | 48.303 | 61.092 | 52.318 | 73.365
| 13.0833 | 259.57 | 48.291 | 61.083 | 52.312 | 73.348
| 13.0903 | 260.512 | 48.279 | 61.074 | 52.306 | 73.32
| 13.0972 | 259.984 | 48.271 | 61.068 | 52.293 | 73.302
| 13.1042 | 260.248 | 48.262 | 61.063 | 52.291 | 73.284
| 13.1111 | 260.343 | 48.255 | 61.055 | 52.284 | 73.275
| 13.1181 | 260.101 | 48.256 | 61.059 | 52.285 | 73.27
| 13.125 | 260.764 | 48.252 | 61.057 | 52.281 | 73.258
| 13.1319 | 260.441 | 48.252 | 61.057 | 52.278 | 73.245
| 13.1389 | 260.969 | 48.249 | 61.063 | 52.275 | 73.239
| 13.1458 | 260.412 | 48.246 | 61.068 | 52.273 | 73.238
| 13.1528 | 260.251 | 48.246 | 61.072 | 52.27 | 73.232
| 13.1597 | 261.058 | 48.244 | 61.072 | 52.268 | 73.231
| 13.1667 | 260.896 | 48.234 | 61.075 | 52.266 | 73.217
| 13.1736 | 260.434 | 48.236 | 61.077 | 52.261 | 73.213
| 13.1806 | 260.087 | 48.234 | 61.079 | 52.259 | 73.206
| 13.1875 | 260.542 | 48.231 | 61.08 | 52.254 | 73.201
| 13.1944 | 260.365 | 48.23 | 61.084 | 52.258 | 73.197
| 13.2014 | 260.277 | 48.226 | 61.083 | 52.251 | 73.193
| 13.2083 | 261.266 | 48.224 | 61.089 | 52.25 | 73.185
| 13.2153 | 260.252 | 48.22 | 61.089 | 52.248 | 73.184
| 13.2222 | 259.865 | 48.219 | 61.092 | 52.243 | 73.174
| 13.2292 | 261.797 | 48.215 | 61.092 | 52.241 | 73.17
| 13.2361 | 262.004 | 48.22 | 61.107 | 52.246 | 73.179
| 13.2431 | 261.905 | 48.227 | 61.122 | 52.249 | 73.198
| 13.25 | 262.412 | 48.238 | 61.139 | 52.256 | 73.211
| 13.2569 | 262.108 | 48.241 | 61.157 | 52.26 | 73.236
| 13.2639 | 262.328 | 48.248 | 61.17 | 52.266 | 73.247
| 13.2708 | 261.633 | 48.253 | 61.179 | 52.27 | 73.252
| 13.2778 | 260.935 | 48.251 | 61.185 | 52.269 | 73.253
| 13.2847 | 261.008 | 48.245 | 61.185 | 52.268 | 73.249
| 13.2917 | 261.192 | 48.235 | 61.183 | 52.262 | 73.237
| 13.2986 | 260.043 | 48.231 | 61.183 | 52.256 | 73.224
| 13.3056 | 259.859 | 48.224 | 61.183 | 52.248 | 73.21
| 13.3125 | 259.33 | 48.213 | 61.173 | 52.246 | 73.195
| 13.3194 | 259.368 | 48.208 | 61.169 | 52.237 | 73.17
| 13.3264 | 258.934 | 48.193 | 61.152 | 52.228 | 73.145
| 13.3333 | 258.082 | 48.184 | 61.146 | 52.216 | 73.123
| 13.3403 | 261.088 | 48.166 | 61.129 | 52.204 | 73.089
| 13.3472 | 260.624 | 48.175 | 61.137 | 52.202 | 73.093
| 13.3542 | 260.625 | 48.174 | 61.145 | 52.203 | 73.096
| 13.3611 | 260.399 | 48.176 | 61.148 | 52.202 | 73.097
| 13.3681 | 259.964 | 48.176 | 61.149 | 52.203 | 73.092
| 13.375 | 259.291 | 48.172 | 61.151 | 52.196 | 73.086
| 13.3819 | 258.663 | 48.164 | 61.146 | 52.187 | 73.074
| 13.3889 | 258.586 | 48.151 | 61.133 | 52.178 | 73.042
| 13.3958 | 258.602 | 48.141 | 61.126 | 52.175 | 73.027
| 13.4028 | 258.307 | 48.137 | 61.116 | 52.157 | 73.009
| 13.4097 | 260.27 | 48.129 | 61.111 | 52.151 | 72.989
| 13.4167 | 260.359 | 48.13 | 61.117 | 52.15 | 72.995
| 13.4236 | 261.29 | 48.138 | 61.127 | 52.153 | 73.012
| 13.4306 | 260.528 | 48.146 | 61.138 | 52.157 | 73.021
| 13.4375 | 259.46 | 48.148 | 61.144 | 52.155 | 73.025
| 13.4444 | 259.258 | 48.14 | 61.138 | 52.15 | 73.013
| 13.4514 | 259.181 | 48.133 | 61.131 | 52.141 | 72.999
| 13.4583 | 259.694 | 48.127 | 61.131 | 52.136 | 72.988
| 13.4653 | 259.461 | 48.12 | 61.128 | 52.134 | 72.983
| 13.4722 | 259.647 | 48.118 | 61.128 | 52.129 | 72.977
| 13.4792 | 259.216 | 48.115 | 61.124 | 52.12 | 72.961
| 13.4861 | 257.554 | 48.108 | 61.119 | 52.116 | 72.948
| 13.4931 | 257.324 | 48.098 | 61.101 | 52.102 | 72.916
| 13.5 | 258.07 | 48.081 | 61.085 | 52.086 | 72.884
| 13.5069 | 258.964 | 48.072 | 61.07 | 52.074 | 72.868
| 13.5139 | 258.956 | 48.071 | 61.071 | 52.074 | 72.863
| 13.5208 | 259.332 | 48.067 | 61.076 | 52.074 | 72.858
| 13.5278 | 258.109 | 48.069 | 61.078 | 52.063 | 72.859
| 13.5347 | 258.166 | 48.062 | 61.068 | 52.057 | 72.842
| 13.5417 | 259.026 | 48.057 | 61.093 | 52.052 | 72.832
| 13.5486 | 259.373 | 48.055 | 61.308 | 52.046 | 72.829
| 13.5556 | 259.733 | 48.06 | 61.315 | 52.048 | 72.838
| 13.5625 | 259.572 | 48.065 | 61.314 | 52.051 | 72.864
| 13.5694 | 259.832 | 48.072 | 61.272 | 52.044 | 72.863
| 13.5764 | 259.934 | 48.074 | 61.223 | 52.046 | 72.868
| 13.5833 | 260.047 | 48.078 | 61.162 | 52.047 | 72.878
| 13.5903 | 258.293 | 48.079 | 61.166 | 52.047 | 72.891
| 13.5972 | 254.655 | 48.059 | 61.143 | 52.027 | 72.853
| 13.6042 | 254.492 | 48.024 | 61.095 | 52.002 | 72.783
| 13.6111 | 254.241 | 47.993 | 61.055 | 51.976 | 72.719
| 13.6181 | 253.251 | 47.971 | 61.019 | 51.944 | 72.662
| 13.625 | 257.257 | 47.962 | 60.997 | 51.932 | 72.628
| 13.6319 | 257.622 | 47.955 | 60.991 | 51.93 | 72.622
| 13.6389 | 257.784 | 47.963 | 60.997 | 51.925 | 72.624
| 13.6458 | 257.934 | 47.961 | 61.012 | 51.925 | 72.623
| 13.6528 | 258.042 | 47.966 | 61.011 | 51.921 | 72.631
| 13.6597 | 258.349 | 47.968 | 61.009 | 51.921 | 72.642
| 13.6667 | 257.95 | 47.967 | 61.004 | 51.917 | 72.637
| 13.6736 | 257.982 | 47.961 | 61.009 | 51.913 | 72.637
| 13.6806 | 258.668 | 47.96 | 61.008 | 51.911 | 72.636
| 13.6875 | 258.634 | 47.961 | 61.015 | 51.911 | 72.64
| 13.6944 | 257.609 | 47.958 | 61.01 | 51.905 | 72.642
| 13.7014 | 257.679 | 47.957 | 61.007 | 51.904 | 72.642
| 13.7083 | 257.615 | 47.953 | 61.006 | 51.903 | 72.635
| 13.7153 | 258.497 | 47.945 | 61.002 | 51.897 | 72.638
| 13.7222 | 259.044 | 47.948 | 61.005 | 51.894 | 72.64
| 13.7292 | 260.155 | 47.949 | 61.014 | 51.899 | 72.648
| 13.7361 | 258.461 | 47.958 | 61.025 | 51.898 | 72.669
| 13.7431 | 259.081 | 47.959 | 61.025 | 51.895 | 72.674
| 13.75 | 258.566 | 47.956 | 61.036 | 51.902 | 72.683
| 13.7569 | 259.56 | 47.959 | 61.035 | 51.898 | 72.691
| 13.7639 | 258.704 | 47.965 | 61.053 | 51.903 | 72.705
| 13.7708 | 259.156 | 47.965 | 61.059 | 51.899 | 72.714
| 13.7778 | 260.06 | 47.964 | 61.066 | 51.908 | 72.723
| 13.7847 | 260.082 | 47.965 | 61.074 | 51.907 | 72.731
| 13.7917 | 260.053 | 47.973 | 61.086 | 51.912 | 72.74
| 13.7986 | 259.862 | 47.979 | 61.098 | 51.907 | 72.753
| 13.8056 | 260.106 | 47.981 | 61.109 | 51.911 | 72.768
| 13.8125 | 261.213 | 47.982 | 61.117 | 51.914 | 72.783
| 13.8194 | 260.618 | 47.984 | 61.129 | 51.914 | 72.794
| 13.8264 | 259.768 | 47.992 | 61.144 | 51.913 | 72.811
| 13.8333 | 260.318 | 47.995 | 61.154 | 51.924 | 72.825
| 13.8403 | 260.041 | 47.996 | 61.163 | 51.917 | 72.834
| 13.8472 | 260.336 | 47.996 | 61.172 | 51.923 | 72.849
| 13.8542 | 260.925 | 47.999 | 61.183 | 51.927 | 72.858
| 13.8611 | 260.682 | 48.002 | 61.199 | 51.929 | 72.872
| 13.8681 | 260.579 | 48.007 | 61.209 | 51.936 | 72.885
| 13.875 | 260.61 | 48.009 | 61.223 | 51.94 | 72.894
| 13.8819 | 261.047 | 48.011 | 61.229 | 51.941 | 72.9
| 13.8889 | 258.089 | 48.007 | 61.237 | 51.935 | 72.907
| 13.8958 | 258.62 | 48 | 61.229 | 51.924 | 72.89
| 13.9028 | 258.74 | 47.988 | 61.222 | 51.918 | 72.864
| 13.9097 | 259.062 | 47.977 | 61.216 | 51.909 | 72.851
| 13.9167 | 259.404 | 47.971 | 61.214 | 51.911 | 72.844
| 13.9236 | 259.329 | 47.969 | 61.221 | 51.903 | 72.839
| 13.9306 | 258.224 | 47.962 | 61.221 | 51.898 | 72.831
| 13.9375 | 258.884 | 47.958 | 61.218 | 51.892 | 72.824
| 13.9444 | 258.868 | 47.957 | 61.219 | 51.896 | 72.819
| 13.9514 | 259.824 | 47.951 | 61.222 | 51.89 | 72.813
| 13.9583 | 259.631 | 47.954 | 61.228 | 51.884 | 72.818
| 13.9653 | 260.936 | 47.955 | 61.239 | 51.886 | 72.82
| 13.9722 | 261.382 | 47.961 | 61.253 | 51.899 | 72.838
| 13.9792 | 261.659 | 47.971 | 61.278 | 51.901 | 72.863
| 13.9861 | 261.429 | 47.98 | 61.3 | 51.909 | 72.887
| 13.9931 | 261.327 | 47.983 | 61.314 | 51.913 | 72.907
| 14 | 262.288 | 47.992 | 61.33 | 51.916 | 72.927
| 14.0069 | 259.153 | 48.002 | 61.356 | 51.921 | 72.948
| 14.0139 | 260.176 | 47.993 | 61.351 | 51.917 | 72.944
| 14.0208 | 261.026 | 47.977 | 61.338 | 51.911 | 72.916
| 14.0278 | 260.413 | 47.971 | 61.337 | 51.901 | 72.905
| 14.0347 | 261.54 | 47.976 | 61.348 | 51.906 | 72.912
| 14.0417 | 260.747 | 47.979 | 61.362 | 51.903 | 72.925
| 14.0486 | 261.089 | 47.978 | 61.373 | 51.904 | 72.929
| 14.0556 | 261.499 | 47.987 | 61.385 | 51.909 | 72.944
| 14.0625 | 261.808 | 47.991 | 61.401 | 51.912 | 72.959
| 14.0694 | 261.523 | 48.002 | 61.419 | 51.915 | 72.977
| 14.0764 | 261.692 | 48.007 | 61.432 | 51.915 | 72.989
| 14.0833 | 262.761 | 48.01 | 61.453 | 51.925 | 73.006
| 14.0903 | 262.243 | 48.014 | 61.47 | 51.927 | 73.026
| 14.0972 | 263.133 | 48.024 | 61.488 | 51.938 | 73.04
| 14.1042 | 263.971 | 48.035 | 61.509 | 51.945 | 73.062
| 14.1111 | 263.664 | 48.043 | 61.537 | 51.953 | 73.098
| 14.1181 | 264.048 | 48.054 | 61.565 | 51.967 | 73.129
| 14.125 | 264.742 | 48.071 | 61.595 | 51.974 | 73.155
| 14.1319 | 261.901 | 48.074 | 61.609 | 51.981 | 73.174
| 14.1389 | 261.775 | 48.067 | 61.611 | 51.977 | 73.164
| 14.1458 | 261.348 | 48.066 | 61.613 | 51.975 | 73.159
| 14.1528 | 261.689 | 48.06 | 61.618 | 51.973 | 73.152
| 14.1597 | 261.151 | 48.051 | 61.618 | 51.964 | 73.144
| 14.1667 | 260.978 | 48.047 | 61.619 | 51.959 | 73.131
| 14.1736 | 261.529 | 48.048 | 61.619 | 51.959 | 73.123
| 14.1806 | 262.084 | 48.045 | 61.626 | 51.956 | 73.12
| 14.1875 | 261.558 | 48.041 | 61.632 | 51.951 | 73.114
| 14.1944 | 261.562 | 48.04 | 61.637 | 51.949 | 73.114
| 14.2014 | 261.429 | 48.04 | 61.639 | 51.947 | 73.106
| 14.2083 | 261.709 | 48.034 | 61.645 | 51.944 | 73.103
| 14.2153 | 260.821 | 48.029 | 61.646 | 51.935 | 73.096
| 14.2222 | 261.685 | 48.025 | 61.645 | 51.936 | 73.085
| 14.2292 | 262.996 | 48.027 | 61.65 | 51.935 | 73.08
| 14.2361 | 262.72 | 48.029 | 61.667 | 51.934 | 73.094
| 14.2431 | 262.925 | 48.038 | 61.683 | 51.941 | 73.108
| 14.25 | 263.408 | 48.045 | 61.697 | 51.945 | 73.131
| 14.2569 | 264.072 | 48.05 | 61.709 | 51.952 | 73.156
| 14.2639 | 263.811 | 48.058 | 61.723 | 51.957 | 73.174
| 14.2708 | 264.012 | 48.066 | 61.737 | 51.962 | 73.19
| 14.2778 | 263.699 | 48.074 | 61.749 | 51.969 | 73.205
| 14.2847 | 263.725 | 48.078 | 61.765 | 51.969 | 73.222
| 14.2917 | 264.173 | 48.079 | 61.786 | 51.976 | 73.237
| 14.2986 | 263.803 | 48.085 | 61.802 | 51.98 | 73.253
| 14.3056 | 263.237 | 48.09 | 61.82 | 51.983 | 73.26
| 14.3125 | 263.009 | 48.088 | 61.832 | 51.979 | 73.267
| 14.3194 | 262.823 | 48.09 | 61.838 | 51.983 | 73.269
| 14.3264 | 262.441 | 48.079 | 61.843 | 51.977 | 73.267
| 14.3333 | 261.967 | 48.077 | 61.846 | 51.976 | 73.259
| 14.3403 | 262.366 | 48.072 | 61.847 | 51.973 | 73.25
| 14.3472 | 262.339 | 48.072 | 61.848 | 51.966 | 73.246
| 14.3542 | 261.712 | 48.063 | 61.85 | 51.96 | 73.231
| 14.3611 | 260.537 | 48.052 | 61.846 | 51.952 | 73.214
| 14.3681 | 260.412 | 48.042 | 61.834 | 51.944 | 73.195
| 14.375 | 259.886 | 48.029 | 61.828 | 51.929 | 73.162
| 14.3819 | 259.665 | 48.014 | 61.814 | 51.919 | 73.135
| 14.3889 | 259.126 | 47.998 | 61.794 | 51.899 | 73.097
| 14.3958 | 258.23 | 47.98 | 61.78 | 51.892 | 73.058
| 14.4028 | 262.231 | 47.97 | 61.77 | 51.883 | 73.039
| 14.4097 | 261.062 | 47.981 | 61.782 | 51.888 | 73.043
| 14.4167 | 260.351 | 47.981 | 61.787 | 51.886 | 73.046
| 14.4236 | 263.699 | 47.976 | 61.786 | 51.873 | 73.038
| 14.4306 | 260.162 | 47.987 | 61.807 | 51.885 | 73.059
| 14.4375 | 260.254 | 47.98 | 61.803 | 51.872 | 73.056
| 14.4444 | 261.149 | 47.975 | 61.8 | 51.867 | 73.043
| 14.4514 | 259.336 | 47.966 | 61.797 | 51.856 | 73.027
| 14.4583 | 260.076 | 47.958 | 61.79 | 51.85 | 73.012
| 14.4653 | 259.767 | 47.947 | 61.781 | 51.837 | 72.989
| 14.4722 | 258.967 | 47.939 | 61.768 | 51.82 | 72.965
| 14.4792 | 258.643 | 47.926 | 61.761 | 51.811 | 72.949
| 14.4861 | 258.104 | 47.915 | 61.74 | 51.797 | 72.918
| 14.4931 | 257.92 | 47.902 | 61.729 | 51.786 | 72.886
| 14.5 | 256.453 | 47.883 | 61.707 | 51.764 | 72.856
| 14.5069 | 255.957 | 47.862 | 61.677 | 51.741 | 72.803
| 14.5139 | 256.636 | 47.833 | 61.648 | 51.723 | 72.756
| 14.5208 | 257.651 | 47.823 | 61.629 | 51.7 | 72.724
| 14.5278 | 258.168 | 47.813 | 61.617 | 51.694 | 72.704
| 14.5347 | 258.648 | 47.81 | 61.617 | 51.683 | 72.692
| 14.5417 | 258.008 | 47.809 | 61.613 | 51.67 | 72.681
| 14.5486 | 256.166 | 47.796 | 61.594 | 51.66 | 72.658
| 14.5556 | 256.032 | 47.777 | 61.572 | 51.638 | 72.62
| 14.5625 | 257.691 | 47.756 | 61.553 | 51.621 | 72.587
| 14.5694 | 258.822 | 47.758 | 61.546 | 51.614 | 72.574
| 14.5764 | 257.824 | 47.75 | 61.544 | 51.605 | 72.564
| 14.5833 | 259.411 | 47.746 | 61.543 | 51.597 | 72.563
| 14.5903 | 258.668 | 47.745 | 61.545 | 51.589 | 72.567
| 14.5972 | 257.277 | 47.739 | 61.537 | 51.578 | 72.552
| 14.6042 | 258.334 | 47.731 | 61.536 | 51.571 | 72.537
| 14.6111 | 258.348 | 47.726 | 61.53 | 51.564 | 72.532
| 14.6181 | 258.758 | 47.719 | 61.532 | 51.557 | 72.531
| 14.625 | 259.641 | 47.72 | 61.528 | 51.558 | 72.532
| 14.6319 | 260.27 | 47.726 | 61.541 | 51.555 | 72.545
| 14.6389 | 260.764 | 47.73 | 61.555 | 51.554 | 72.565
| 14.6458 | 258.696 | 47.737 | 61.564 | 51.552 | 72.578
| 14.6528 | 258.94 | 47.729 | 61.561 | 51.541 | 72.576
| 14.6597 | 258.73 | 47.722 | 61.56 | 51.538 | 72.574
| 14.6667 | 259.837 | 47.721 | 61.56 | 51.536 | 72.568
| 14.6736 | 260.813 | 47.721 | 61.57 | 51.531 | 72.582
| 14.6806 | 261.054 | 47.728 | 61.579 | 51.537 | 72.6
| 14.6875 | 260.68 | 47.73 | 61.591 | 51.533 | 72.61
| 14.6944 | 260.06 | 47.729 | 61.597 | 51.533 | 72.619
| 14.7014 | 259.988 | 47.726 | 61.602 | 51.534 | 72.627
| 14.7083 | 260.328 | 47.726 | 61.61 | 51.529 | 72.634
| 14.7153 | 260.172 | 47.727 | 61.62 | 51.527 | 72.637
| 14.7222 | 259.144 | 47.725 | 61.627 | 51.519 | 72.645
| 14.7292 | 259.083 | 47.721 | 61.621 | 51.515 | 72.638
| 14.7361 | 258.588 | 47.706 | 61.615 | 51.508 | 72.616
| 14.7431 | 259.492 | 47.699 | 61.609 | 51.499 | 72.61
| 14.75 | 260.253 | 47.693 | 61.609 | 51.489 | 72.61
| 14.7569 | 259.461 | 47.694 | 61.616 | 51.489 | 72.607
| 14.7639 | 259.233 | 47.691 | 61.615 | 51.484 | 72.601
| 14.7708 | 259.33 | 47.683 | 61.611 | 51.473 | 72.597
| 14.7778 | 260.611 | 47.68 | 61.613 | 51.472 | 72.6
| 14.7847 | 260.041 | 47.684 | 61.62 | 51.467 | 72.6
| 14.7917 | 259.962 | 47.675 | 61.627 | 51.464 | 72.601
| 14.7986 | 259.887 | 47.677 | 61.633 | 51.462 | 72.603
| 14.8056 | 260.019 | 47.669 | 61.634 | 51.452 | 72.598
| 14.8125 | 259.677 | 47.663 | 61.632 | 51.453 | 72.6
| 14.8194 | 260.307 | 47.658 | 61.634 | 51.446 | 72.595
| 14.8264 | 260.056 | 47.658 | 61.635 | 51.442 | 72.598
| 14.8333 | 260.872 | 47.658 | 61.643 | 51.438 | 72.602
| 14.8403 | 260.126 | 47.653 | 61.649 | 51.435 | 72.604
| 14.8472 | 260.338 | 47.65 | 61.656 | 51.436 | 72.609
| 14.8542 | 261.253 | 47.653 | 61.664 | 51.429 | 72.619
| 14.8611 | 261.368 | 47.652 | 61.674 | 51.428 | 72.625
| 14.8681 | 260.598 | 47.651 | 61.682 | 51.427 | 72.634
| 14.875 | 261.099 | 47.652 | 61.689 | 51.426 | 72.636
| 14.8819 | 259.697 | 47.652 | 61.692 | 51.423 | 72.634
| 14.8889 | 259.393 | 47.64 | 61.694 | 51.414 | 72.633
| 14.8958 | 261.049 | 47.63 | 61.685 | 51.404 | 72.606
| 14.9028 | 260.176 | 47.629 | 61.693 | 51.407 | 72.616
| 14.9097 | 261.202 | 47.628 | 61.7 | 51.406 | 72.625
| 14.9167 | 260.684 | 47.631 | 61.713 | 51.398 | 72.633
| 14.9236 | 260.667 | 47.63 | 61.722 | 51.402 | 72.64
| 14.9306 | 260.849 | 47.628 | 61.731 | 51.4 | 72.646
| 14.9375 | 261.333 | 47.634 | 61.742 | 51.402 | 72.657
| 14.9444 | 261.862 | 47.631 | 61.753 | 51.399 | 72.666
| 14.9514 | 262.442 | 47.636 | 61.77 | 51.402 | 72.682
| 14.9583 | 262.645 | 47.644 | 61.79 | 51.403 | 72.697
| 14.9653 | 262.392 | 47.65 | 61.806 | 51.41 | 72.714
| 14.9722 | 262.105 | 47.653 | 61.823 | 51.412 | 72.733
| 14.9792 | 262.767 | 47.655 | 61.839 | 51.41 | 72.75
| 14.9861 | 262.776 | 47.659 | 61.861 | 51.424 | 72.764
| 14.9931 | 262.244 | 47.659 | 61.872 | 51.416 | 72.776
| 15 | 262.644 | 47.662 | 61.89 | 51.43 | 72.787
| 15.0069 | 261.481 | 47.665 | 61.907 | 51.429 | 72.802
| 15.0139 | 262.376 | 47.666 | 61.916 | 51.427 | 72.811
| 15.0208 | 262.319 | 47.663 | 61.923 | 51.424 | 72.811
| 15.0278 | 262.278 | 47.659 | 61.933 | 51.421 | 72.818
| 15.0347 | 262.153 | 47.658 | 61.943 | 51.423 | 72.82
| 15.0417 | 261.894 | 47.659 | 61.949 | 51.413 | 72.816
| 15.0486 | 260.825 | 47.651 | 61.955 | 51.409 | 72.812
| 15.0556 | 261.293 | 47.647 | 61.95 | 51.408 | 72.8
| 15.0625 | 261.905 | 47.643 | 61.961 | 51.407 | 72.801
| 15.0694 | 261.025 | 47.642 | 61.965 | 51.402 | 72.803
| 15.0764 | 261.559 | 47.64 | 61.971 | 51.4 | 72.798
| 15.0833 | 261.503 | 47.639 | 61.977 | 51.399 | 72.797
| 15.0903 | 262.488 | 47.636 | 61.986 | 51.394 | 72.795
| 15.0972 | 261.772 | 47.635 | 61.999 | 51.393 | 72.799
| 15.1042 | 262.042 | 47.638 | 62.009 | 51.392 | 72.806
| 15.1111 | 262.258 | 47.639 | 62.017 | 51.394 | 72.814
| 15.1181 | 262.463 | 47.636 | 62.039 | 51.393 | 72.821
| 15.125 | 262.09 | 47.638 | 62.04 | 51.387 | 72.828
| 15.1319 | 262.112 | 47.634 | 62.055 | 51.388 | 72.831
| 15.1389 | 262.599 | 47.635 | 62.066 | 51.387 | 72.836
| 15.1458 | 262.1 | 47.636 | 62.074 | 51.385 | 72.836
| 15.1528 | 262.011 | 47.634 | 62.085 | 51.391 | 72.842
| 15.1597 | 262.815 | 47.636 | 62.094 | 51.383 | 72.846
| 15.1667 | 262.11 | 47.638 | 62.106 | 51.384 | 72.85
| 15.1736 | 261.478 | 47.631 | 62.119 | 51.384 | 72.85
| 15.1806 | 261.756 | 47.629 | 62.122 | 51.381 | 72.852
| 15.1875 | 261.833 | 47.624 | 62.128 | 51.379 | 72.844
| 15.1944 | 261.684 | 47.625 | 62.134 | 51.378 | 72.85
| 15.2014 | 261.769 | 47.623 | 62.145 | 51.376 | 72.842
| 15.2083 | 262.019 | 47.618 | 62.148 | 51.37 | 72.84
| 15.2153 | 261.828 | 47.619 | 62.153 | 51.367 | 72.839
| 15.2222 | 260.791 | 47.611 | 62.155 | 51.357 | 72.835
| 15.2292 | 261.727 | 47.607 | 62.158 | 51.353 | 72.826
| 15.2361 | 262.262 | 47.604 | 62.16 | 51.354 | 72.815
| 15.2431 | 262.736 | 47.603 | 62.178 | 51.352 | 72.823
| 15.25 | 262.99 | 47.606 | 62.191 | 51.353 | 72.839
| 15.2569 | 262.613 | 47.61 | 62.209 | 51.362 | 72.851
| 15.2639 | 262.349 | 47.616 | 62.228 | 51.359 | 72.859
| 15.2708 | 262.985 | 47.617 | 62.235 | 51.359 | 72.871
| 15.2778 | 263.295 | 47.618 | 62.249 | 51.363 | 72.878
| 15.2847 | 262.536 | 47.618 | 62.262 | 51.36 | 72.886
| 15.2917 | 263.063 | 47.615 | 62.269 | 51.36 | 72.886
| 15.2986 | 262.578 | 47.616 | 62.282 | 51.361 | 72.89
| 15.3056 | 262.634 | 47.61 | 62.296 | 51.361 | 72.895
| 15.3125 | 262.786 | 47.613 | 62.305 | 51.361 | 72.894
| 15.3194 | 262.745 | 47.611 | 62.313 | 51.359 | 72.903
| 15.3264 | 262.367 | 47.615 | 62.328 | 51.361 | 72.907
| 15.3333 | 261.723 | 47.611 | 62.335 | 51.361 | 72.912
| 15.3403 | 260.649 | 47.608 | 62.335 | 51.352 | 72.897
| 15.3472 | 260.316 | 47.594 | 62.326 | 51.343 | 72.878
| 15.3542 | 260.583 | 47.584 | 62.319 | 51.332 | 72.851
| 15.3611 | 259.495 | 47.567 | 62.307 | 51.316 | 72.824
| 15.3681 | 258.545 | 47.553 | 62.292 | 51.304 | 72.792
| 15.375 | 258.649 | 47.533 | 62.27 | 51.293 | 72.752
| 15.3819 | 260.521 | 47.525 | 62.257 | 51.279 | 72.736
| 15.3889 | 260.438 | 47.519 | 62.252 | 51.274 | 72.728
| 15.3958 | 260.397 | 47.518 | 62.243 | 51.268 | 72.72
| 15.4028 | 260.08 | 47.513 | 62.246 | 51.264 | 72.709
| 15.4097 | 260.349 | 47.508 | 62.243 | 51.254 | 72.7
| 15.4167 | 260.112 | 47.506 | 62.244 | 51.244 | 72.691
| 15.4236 | 259.72 | 47.498 | 62.242 | 51.236 | 72.675
| 15.4306 | 259.67 | 47.485 | 62.234 | 51.221 | 72.652
| 15.4375 | 258.979 | 47.477 | 62.225 | 51.212 | 72.631
| 15.4444 | 258.38 | 47.465 | 62.215 | 51.198 | 72.605
| 15.4514 | 258.308 | 47.447 | 62.199 | 51.186 | 72.575
| 15.4583 | 257.61 | 47.435 | 62.186 | 51.165 | 72.546
| 15.4653 | 261.14 | 47.42 | 62.17 | 51.153 | 72.515
| 15.4722 | 262.549 | 47.425 | 62.19 | 51.152 | 72.525
| 15.4792 | 260.171 | 47.434 | 62.204 | 51.157 | 72.544
| 15.4861 | 259.994 | 47.425 | 62.207 | 51.153 | 72.541
| 15.4931 | 260.22 | 47.426 | 62.204 | 51.145 | 72.531
| 15.5 | 259.646 | 47.424 | 62.21 | 51.138 | 72.531
| 15.5069 | 259.07 | 47.412 | 62.205 | 51.131 | 72.516
| 15.5139 | 259.276 | 47.399 | 62.198 | 51.122 | 72.505
| 15.5208 | 259.365 | 47.397 | 62.195 | 51.114 | 72.493
| 15.5278 | 258.662 | 47.391 | 62.195 | 51.107 | 72.484
| 15.5347 | 258.969 | 47.38 | 62.186 | 51.09 | 72.461
| 15.5417 | 258.25 | 47.371 | 62.174 | 51.083 | 72.445
| 15.5486 | 259.525 | 47.363 | 62.168 | 51.07 | 72.423
| 15.5556 | 261.398 | 47.359 | 62.173 | 51.071 | 72.431
| 15.5625 | 260.06 | 47.366 | 62.188 | 51.069 | 72.446
| 15.5694 | 260.134 | 47.369 | 62.203 | 51.073 | 72.455
| 15.5764 | 258.303 | 47.37 | 62.204 | 51.058 | 72.45
| 15.5833 | 258.773 | 47.357 | 62.194 | 51.053 | 72.434
| 15.5903 | 260.206 | 47.347 | 62.191 | 51.044 | 72.421
| 15.5972 | 260.003 | 47.346 | 62.197 | 51.044 | 72.422
| 15.6042 | 260.635 | 47.341 | 62.204 | 51.047 | 72.428
| 15.6111 | 260.625 | 47.346 | 62.217 | 51.042 | 72.435
| 15.6181 | 261.566 | 47.346 | 62.223 | 51.037 | 72.445
| 15.625 | 261.29 | 47.355 | 62.246 | 51.045 | 72.467
| 15.6319 | 261.318 | 47.358 | 62.255 | 51.048 | 72.481
| 15.6389 | 261.784 | 47.363 | 62.272 | 51.05 | 72.493
| 15.6458 | 261.928 | 47.366 | 62.285 | 51.047 | 72.505
| 15.6528 | 261.756 | 47.369 | 62.301 | 51.055 | 72.521
| 15.6597 | 261.437 | 47.373 | 62.316 | 51.053 | 72.542
| 15.6667 | 258.246 | 47.376 | 62.334 | 51.053 | 72.551
| 15.6736 | 258.088 | 47.365 | 62.32 | 51.043 | 72.532
| 15.6806 | 258.914 | 47.342 | 62.306 | 51.032 | 72.499
| 15.7083 | 259.079 | 47.305 | 62.276 | 50.991 | 72.424
| 15.7153 | 258.101 | 47.304 | 62.274 | 50.981 | 72.414
| 15.7222 | 258.762 | 47.29 | 62.264 | 50.972 | 72.395
| 15.7292 | 258.763 | 47.282 | 62.262 | 50.963 | 72.384
| 15.7361 | 258.356 | 47.272 | 62.251 | 50.954 | 72.369
| 15.7431 | 258.341 | 47.264 | 62.252 | 50.941 | 72.357
| 15.75 | 258.501 | 47.257 | 62.245 | 50.926 | 72.343
| 15.7569 | 257.869 | 47.248 | 62.239 | 50.927 | 72.323
| 15.7639 | 256.832 | 47.235 | 62.222 | 50.919 | 72.296
| 15.7708 | 257.259 | 47.223 | 62.208 | 50.898 | 72.27
| 15.7778 | 257.171 | 47.209 | 62.198 | 50.889 | 72.245
| 15.7847 | 257.753 | 47.204 | 62.187 | 50.871 | 72.228
| 15.7917 | 258.168 | 47.195 | 62.185 | 50.869 | 72.216
| 15.7986 | 257.807 | 47.185 | 62.183 | 50.86 | 72.203
| 15.8056 | 257.786 | 47.179 | 62.174 | 50.847 | 72.194
| 15.8125 | 258.014 | 47.175 | 62.176 | 50.843 | 72.182
| 15.8194 | 258.217 | 47.167 | 62.174 | 50.836 | 72.176
| 15.8264 | 258.692 | 47.165 | 62.175 | 50.821 | 72.173
| 15.8333 | 258.306 | 47.164 | 62.176 | 50.825 | 72.171
| 15.8403 | 259.119 | 47.16 | 62.179 | 50.821 | 72.167
| 15.8472 | 259.55 | 47.157 | 62.188 | 50.812 | 72.172
| 15.8542 | 258.863 | 47.161 | 62.192 | 50.82 | 72.176
| 15.8611 | 259.477 | 47.157 | 62.203 | 50.812 | 72.179
| 15.8681 | 259.834 | 47.154 | 62.206 | 50.808 | 72.187
| 15.875 | 259.517 | 47.154 | 62.215 | 50.806 | 72.194
| 15.8819 | 258.536 | 47.153 | 62.215 | 50.799 | 72.19
| 15.8889 | 258.057 | 47.142 | 62.221 | 50.806 | 72.184
| 15.8958 | 259.705 | 47.132 | 62.212 | 50.791 | 72.172
| 15.9028 | 260.576 | 47.13 | 62.219 | 50.78 | 72.168
| 15.9097 | 260.112 | 47.134 | 62.235 | 50.79 | 72.182
| 15.9167 | 260.295 | 47.136 | 62.25 | 50.785 | 72.196
| 15.9236 | 260.648 | 47.135 | 62.259 | 50.789 | 72.209
| 15.9306 | 260.343 | 47.144 | 62.277 | 50.79 | 72.224
| 15.9375 | 261.2 | 47.147 | 62.29 | 50.789 | 72.233
| 15.9444 | 260.993 | 47.152 | 62.311 | 50.804 | 72.253
| 15.9514 | 261.947 | 47.154 | 62.329 | 50.807 | 72.276
| 15.9583 | 261.825 | 47.163 | 62.35 | 50.809 | 72.299
| 15.9653 | 262.745 | 47.174 | 62.377 | 50.82 | 72.326
| 15.9722 | 262.484 | 47.188 | 62.406 | 50.826 | 72.351
| 15.9792 | 262.754 | 47.193 | 62.433 | 50.841 | 72.386
| 15.9861 | 263.394 | 47.206 | 62.459 | 50.847 | 72.412
| 15.9931 | 263.612 | 47.211 | 62.487 | 50.859 | 72.437
| 16 | 260.653 | 47.212 | 62.497 | 50.855 | 72.444
| 16.0069 | 261.152 | 47.205 | 62.496 | 50.848 | 72.428
| 16.0139 | 261.865 | 47.197 | 62.501 | 50.844 | 72.423
| 16.0208 | 261.591 | 47.198 | 62.515 | 50.846 | 72.428
| 16.0278 | 260.728 | 47.197 | 62.523 | 50.843 | 72.434
| 16.0347 | 261.367 | 47.193 | 62.538 | 50.842 | 72.43
| 16.0417 | 261.699 | 47.192 | 62.55 | 50.841 | 72.435
| 16.0486 | 261.706 | 47.194 | 62.566 | 50.845 | 72.44
| 16.0556 | 261.736 | 47.193 | 62.586 | 50.846 | 72.446
| 16.0625 | 261.828 | 47.198 | 62.614 | 50.845 | 72.457
| 16.0694 | 261.565 | 47.203 | 62.63 | 50.844 | 72.459
| 16.0764 | 261.379 | 47.201 | 62.649 | 50.844 | 72.466
| 16.0833 | 261.443 | 47.197 | 62.663 | 50.845 | 72.465
| 16.0903 | 261.391 | 47.198 | 62.671 | 50.844 | 72.464
| 16.0972 | 262.164 | 47.194 | 62.685 | 50.845 | 72.473
| 16.1042 | 260.78 | 47.204 | 62.702 | 50.847 | 72.483
| 16.1111 | 261.378 | 47.2 | 62.713 | 50.85 | 72.484
| 16.1181 | 260.825 | 47.199 | 62.718 | 50.844 | 72.478
| 16.125 | 261.608 | 47.193 | 62.724 | 50.845 | 72.477
| 16.1319 | 260.589 | 47.19 | 62.73 | 50.841 | 72.472
| 16.1389 | 260.975 | 47.188 | 62.738 | 50.835 | 72.467
| 16.1458 | 260.617 | 47.185 | 62.741 | 50.836 | 72.465
| 16.1528 | 261.316 | 47.183 | 62.752 | 50.831 | 72.461
| 16.1597 | 261.213 | 47.183 | 62.76 | 50.832 | 72.463
| 16.1667 | 260.936 | 47.18 | 62.771 | 50.828 | 72.46
| 16.1736 | 260.625 | 47.18 | 62.775 | 50.824 | 72.458
| 16.1806 | 260.266 | 47.176 | 62.778 | 50.824 | 72.449
| 16.1875 | 260.225 | 47.168 | 62.774 | 50.817 | 72.439
| 16.1944 | 260.331 | 47.163 | 62.782 | 50.814 | 72.426
| 16.2014 | 260.168 | 47.156 | 62.781 | 50.808 | 72.42
| 16.2083 | 259.585 | 47.152 | 62.785 | 50.804 | 72.41
| 16.2153 | 259.371 | 47.15 | 62.785 | 50.793 | 72.395
| 16.2222 | 258.763 | 47.137 | 62.778 | 50.785 | 72.376
| 16.2292 | 259.917 | 47.128 | 62.77 | 50.77 | 72.352
| 16.2361 | 259.544 | 47.122 | 62.772 | 50.768 | 72.344
| 16.2431 | 258.723 | 47.116 | 62.77 | 50.761 | 72.335
| 16.25 | 260.487 | 47.111 | 62.77 | 50.755 | 72.322
| 16.2569 | 258.951 | 47.107 | 62.774 | 50.754 | 72.323
| 16.2639 | 259.789 | 47.104 | 62.776 | 50.746 | 72.307
| 16.2708 | 259.301 | 47.1 | 62.778 | 50.742 | 72.301
| 16.2778 | 259.247 | 47.096 | 62.782 | 50.737 | 72.295
| 16.2847 | 259.588 | 47.09 | 62.782 | 50.736 | 72.29
| 16.2917 | 259.538 | 47.086 | 62.783 | 50.726 | 72.276
| 16.2986 | 260.681 | 47.077 | 62.771 | 50.72 | 72.258
| 16.3056 | 261.389 | 47.076 | 62.783 | 50.716 | 72.261
| 16.3125 | 261.754 | 47.084 | 62.805 | 50.725 | 72.28
| 16.3194 | 260.156 | 47.09 | 62.821 | 50.726 | 72.298
| 16.3264 | 259.695 | 47.093 | 62.835 | 50.722 | 72.302
| 16.3333 | 259.912 | 47.086 | 62.835 | 50.718 | 72.295
| 16.3403 | 261.254 | 47.085 | 62.839 | 50.718 | 72.292
| 16.3472 | 261.092 | 47.09 | 62.856 | 50.722 | 72.308
| 16.3542 | 261.412 | 47.092 | 62.874 | 50.724 | 72.323
| 16.3611 | 260.658 | 47.094 | 62.879 | 50.721 | 72.322
| 16.3681 | 260.293 | 47.089 | 62.89 | 50.717 | 72.324
| 16.375 | 259.837 | 47.085 | 62.894 | 50.72 | 72.321
| 16.3819 | 259.301 | 47.079 | 62.896 | 50.716 | 72.31
| 16.3889 | 259.628 | 47.074 | 62.898 | 50.709 | 72.304
| 16.3958 | 259.043 | 47.071 | 62.892 | 50.701 | 72.295
| 16.4028 | 259.302 | 47.065 | 62.896 | 50.702 | 72.287
| 16.4097 | 258.894 | 47.057 | 62.893 | 50.692 | 72.269
| 16.4167 | 258.565 | 47.049 | 62.888 | 50.69 | 72.258
| 16.4236 | 258.589 | 47.038 | 62.882 | 50.674 | 72.234
| 16.4306 | 258.875 | 47.032 | 62.877 | 50.667 | 72.222
| 16.4375 | 259.973 | 47.028 | 62.877 | 50.661 | 72.212
| 16.4444 | 258.928 | 47.028 | 62.884 | 50.657 | 72.212
| 16.4514 | 259.093 | 47.026 | 62.882 | 50.658 | 72.206
| 16.4583 | 258.946 | 47.023 | 62.887 | 50.657 | 72.2
| 16.4653 | 258.732 | 47.02 | 62.886 | 50.644 | 72.191
| 16.4722 | 259.906 | 47.015 | 62.894 | 50.643 | 72.185
| 16.4792 | 259.034 | 47.018 | 62.894 | 50.643 | 72.188
| 16.4861 | 258.231 | 47.011 | 62.892 | 50.633 | 72.181
| 16.4931 | 257.892 | 47 | 62.885 | 50.624 | 72.163
| 16.5 | 258.674 | 46.995 | 62.885 | 50.614 | 72.151
| 16.5069 | 259.47 | 46.99 | 62.882 | 50.61 | 72.139
| 16.5139 | 259.558 | 46.991 | 62.888 | 50.608 | 72.141
| 16.5208 | 259.696 | 46.994 | 62.898 | 50.607 | 72.151
| 16.5278 | 259.543 | 46.992 | 62.903 | 50.603 | 72.152
| 16.5347 | 259.104 | 46.994 | 62.911 | 50.601 | 72.153
| 16.5417 | 258.817 | 46.991 | 62.91 | 50.593 | 72.148
| 16.5486 | 257.482 | 46.981 | 62.908 | 50.589 | 72.131
| 16.5556 | 256.992 | 46.97 | 62.897 | 50.575 | 72.112
| 16.5625 | 258.487 | 46.956 | 62.882 | 50.566 | 72.091
| 16.5694 | 258.644 | 46.956 | 62.885 | 50.558 | 72.079
| 16.5764 | 259.186 | 46.953 | 62.887 | 50.554 | 72.076
| 16.5833 | 259.353 | 46.951 | 62.887 | 50.55 | 72.076
| 16.5903 | 260.22 | 46.948 | 62.898 | 50.551 | 72.076
| 16.5972 | 260.835 | 46.956 | 62.91 | 50.555 | 72.087
| 16.6042 | 260.438 | 46.956 | 62.919 | 50.548 | 72.096
| 16.6111 | 259.765 | 46.961 | 62.934 | 50.55 | 72.102
| 16.6181 | 260.742 | 46.961 | 62.943 | 50.551 | 72.115
| 16.625 | 259.607 | 46.964 | 62.953 | 50.547 | 72.123
| 16.6319 | 260.483 | 46.965 | 62.961 | 50.552 | 72.128
| 16.6389 | 260.88 | 46.966 | 62.976 | 50.553 | 72.14
| 16.6458 | 261.19 | 46.973 | 62.993 | 50.56 | 72.156
| 16.6528 | 257.685 | 46.979 | 63.007 | 50.553 | 72.171
| 16.6597 | 258.044 | 46.965 | 62.999 | 50.544 | 72.154
| 16.6667 | 258.367 | 46.954 | 62.991 | 50.536 | 72.131
| 16.6736 | 257.949 | 46.945 | 62.976 | 50.523 | 72.115
| 16.6806 | 257.59 | 46.934 | 62.975 | 50.512 | 72.098
| 16.6875 | 258.422 | 46.923 | 62.96 | 50.507 | 72.071
| 16.6944 | 257.93 | 46.917 | 62.955 | 50.493 | 72.062
| 16.7014 | 258.512 | 46.907 | 62.957 | 50.488 | 72.048
| 16.7083 | 258.266 | 46.905 | 62.953 | 50.484 | 72.039
| 16.7153 | 257.521 | 46.904 | 62.958 | 50.478 | 72.033
| 16.7222 | 258.034 | 46.896 | 62.953 | 50.474 | 72.026
| 16.7292 | 257.599 | 46.895 | 62.957 | 50.465 | 72.024
| 16.7361 | 258.089 | 46.893 | 62.957 | 50.462 | 72.013
| 16.7431 | 257.831 | 46.889 | 62.958 | 50.452 | 72.012
| 16.75 | 258.869 | 46.884 | 62.961 | 50.449 | 72.005
| 16.7569 | 258.558 | 46.882 | 62.961 | 50.441 | 72.004
| 16.7639 | 257.875 | 46.878 | 62.965 | 50.438 | 72.005
| 16.7708 | 256.1 | 46.869 | 62.954 | 50.431 | 71.981
| 16.7778 | 255.729 | 46.847 | 62.929 | 50.407 | 71.942
| 16.7847 | 256.149 | 46.835 | 62.916 | 50.4 | 71.911
| 16.7917 | 256.223 | 46.825 | 62.906 | 50.387 | 71.891
| 16.7986 | 256.556 | 46.814 | 62.894 | 50.377 | 71.87
| 16.8056 | 256.457 | 46.803 | 62.89 | 50.359 | 71.854
| 16.8125 | 256.479 | 46.8 | 62.882 | 50.355 | 71.841
| 16.8194 | 256.807 | 46.793 | 62.878 | 50.35 | 71.827
| 16.8264 | 258.197 | 46.788 | 62.875 | 50.346 | 71.813
| 16.8333 | 257.686 | 46.787 | 62.876 | 50.342 | 71.814
| 16.8403 | 258.356 | 46.781 | 62.882 | 50.336 | 71.814
| 16.8472 | 258.602 | 46.782 | 62.889 | 50.338 | 71.82
| 16.8542 | 259.258 | 46.785 | 62.901 | 50.341 | 71.827
| 16.8611 | 259.186 | 46.792 | 62.918 | 50.34 | 71.842
| 16.8681 | 259.743 | 46.796 | 62.937 | 50.348 | 71.86
| 16.875 | 259.359 | 46.797 | 62.947 | 50.35 | 71.876
| 16.8819 | 259.017 | 46.804 | 62.96 | 50.349 | 71.889
| 16.8889 | 259.229 | 46.806 | 62.978 | 50.353 | 71.899
| 16.8958 | 257.086 | 46.797 | 62.987 | 50.355 | 71.906
| 16.9028 | 257.764 | 46.793 | 62.981 | 50.345 | 71.892
| 16.9097 | 258.973 | 46.78 | 62.977 | 50.339 | 71.875
| 16.9167 | 258.545 | 46.778 | 62.978 | 50.331 | 71.873
| 16.9236 | 260.005 | 46.777 | 62.99 | 50.332 | 71.876
| 16.9306 | 260.104 | 46.78 | 63.007 | 50.338 | 71.893
| 16.9375 | 261.122 | 46.794 | 63.031 | 50.349 | 71.918
| 16.9444 | 262.16 | 46.807 | 63.064 | 50.354 | 71.943
| 16.9514 | 259.905 | 46.817 | 63.089 | 50.361 | 71.976
| 16.9583 | 260.709 | 46.82 | 63.103 | 50.365 | 71.989
| 16.9653 | 260.385 | 46.817 | 63.116 | 50.363 | 71.996
| 16.9722 | 261.446 | 46.823 | 63.132 | 50.369 | 72.01
| 16.9792 | 261.451 | 46.826 | 63.151 | 50.369 | 72.024
| 16.9861 | 261.891 | 46.835 | 63.177 | 50.383 | 72.045
| 16.9931 | 262.13 | 46.842 | 63.204 | 50.391 | 72.068
| 17 | 262.054 | 46.853 | 63.227 | 50.404 | 72.097
| 17.0069 | 262.534 | 46.861 | 63.259 | 50.408 | 72.119
| 17.0139 | 259.572 | 46.862 | 63.268 | 50.411 | 72.125
| 17.0208 | 259.278 | 46.854 | 63.27 | 50.404 | 72.11
| 17.0278 | 259.371 | 46.848 | 63.27 | 50.397 | 72.095
| 17.0347 | 260.062 | 46.843 | 63.274 | 50.401 | 72.089
| 17.0417 | 259.592 | 46.835 | 63.279 | 50.391 | 72.086
| 17.0486 | 259.462 | 46.831 | 63.289 | 50.393 | 72.08
| 17.0556 | 259.592 | 46.83 | 63.293 | 50.39 | 72.077
| 17.0625 | 259.924 | 46.832 | 63.302 | 50.391 | 72.072
| 17.0694 | 260.034 | 46.829 | 63.311 | 50.388 | 72.069
| 17.0764 | 259.465 | 46.833 | 63.319 | 50.386 | 72.069
| 17.0833 | 260.383 | 46.826 | 63.329 | 50.389 | 72.067
| 17.0903 | 260.613 | 46.825 | 63.339 | 50.39 | 72.069
| 17.0972 | 260.435 | 46.832 | 63.356 | 50.392 | 72.074
| 17.1042 | 260.486 | 46.833 | 63.369 | 50.394 | 72.081
| 17.1111 | 260.098 | 46.837 | 63.38 | 50.394 | 72.088
| 17.1181 | 259.831 | 46.838 | 63.396 | 50.393 | 72.086
| 17.125 | 260.547 | 46.839 | 63.406 | 50.398 | 72.091
| 17.1319 | 260.512 | 46.838 | 63.42 | 50.4 | 72.102
| 17.1389 | 260.806 | 46.842 | 63.437 | 50.404 | 72.111
| 17.1458 | 260.711 | 46.846 | 63.463 | 50.407 | 72.12
| 17.1528 | 260.834 | 46.847 | 63.481 | 50.416 | 72.13
| 17.1597 | 260.645 | 46.853 | 63.494 | 50.417 | 72.141
| 17.1667 | 260.865 | 46.858 | 63.509 | 50.418 | 72.148
| 17.1736 | 261.302 | 46.861 | 63.526 | 50.426 | 72.153
| 17.1806 | 260.591 | 46.861 | 63.54 | 50.432 | 72.163
| 17.1875 | 260.6 | 46.859 | 63.551 | 50.429 | 72.163
| 17.1944 | 260.395 | 46.86 | 63.564 | 50.431 | 72.161
| 17.2014 | 259.657 | 46.862 | 63.573 | 50.43 | 72.163
| 17.2083 | 259.704 | 46.857 | 63.58 | 50.428 | 72.159
| 17.2153 | 258.888 | 46.853 | 63.582 | 50.423 | 72.148
| 17.2222 | 257.621 | 46.841 | 63.579 | 50.415 | 72.119
| 17.2292 | 258.795 | 46.826 | 63.562 | 50.406 | 72.089
| 17.2361 | 259.188 | 46.821 | 63.564 | 50.401 | 72.074
| 17.2431 | 260.327 | 46.815 | 63.563 | 50.397 | 72.064
| 17.25 | 259.809 | 46.817 | 63.581 | 50.397 | 72.067
| 17.2569 | 258.609 | 46.824 | 63.597 | 50.405 | 72.072
| 17.2639 | 257.438 | 46.814 | 63.591 | 50.398 | 72.06
| 17.2708 | 260.088 | 46.804 | 63.585 | 50.392 | 72.037
| 17.2778 | 260.383 | 46.813 | 63.597 | 50.393 | 72.046
| 17.2847 | 260.269 | 46.815 | 63.619 | 50.392 | 72.052
| 17.2917 | 258.34 | 46.814 | 63.624 | 50.4 | 72.057
| 17.2986 | 257.581 | 46.808 | 63.626 | 50.392 | 72.041
| 17.3056 | 257.372 | 46.796 | 63.617 | 50.383 | 72.018
| 17.3125 | 260.628 | 46.794 | 63.622 | 50.382 | 72.013
| 17.3194 | 259.685 | 46.802 | 63.64 | 50.386 | 72.027
| 17.3264 | 259.512 | 46.803 | 63.657 | 50.389 | 72.029
| 17.3333 | 257.769 | 46.8 | 63.656 | 50.384 | 72.024
| 17.3403 | 257.465 | 46.794 | 63.659 | 50.377 | 72.011
| 17.3472 | 257.294 | 46.785 | 63.653 | 50.368 | 71.994
| 17.3542 | 259.227 | 46.782 | 63.659 | 50.371 | 71.983
| 17.3611 | 259.259 | 46.787 | 63.668 | 50.371 | 71.99
| 17.3681 | 259.412 | 46.785 | 63.677 | 50.373 | 71.988
| 17.375 | 259.113 | 46.787 | 63.682 | 50.372 | 71.985
| 17.3819 | 259.277 | 46.787 | 63.69 | 50.367 | 71.982
| 17.3889 | 260.444 | 46.783 | 63.701 | 50.369 | 71.984
| 17.3958 | 260.21 | 46.796 | 63.714 | 50.373 | 71.998
| 17.4028 | 259.036 | 46.793 | 63.729 | 50.375 | 71.997
| 17.4097 | 258.309 | 46.79 | 63.732 | 50.374 | 71.993
| 17.4167 | 258.25 | 46.789 | 63.733 | 50.37 | 71.984
| 17.4236 | 258.452 | 46.784 | 63.735 | 50.365 | 71.976
| 17.4306 | 257.307 | 46.777 | 63.734 | 50.36 | 71.966
| 17.4375 | 256.651 | 46.766 | 63.726 | 50.353 | 71.943
| 17.4444 | 256.522 | 46.758 | 63.719 | 50.343 | 71.916
| 17.4514 | 256.67 | 46.745 | 63.703 | 50.33 | 71.885
| 17.4583 | 255.872 | 46.73 | 63.685 | 50.32 | 71.853
| 17.4653 | 256.541 | 46.719 | 63.668 | 50.308 | 71.825
| 17.4722 | 256.333 | 46.71 | 63.659 | 50.297 | 71.8
| 17.4792 | 255.905 | 46.701 | 63.65 | 50.286 | 71.775
| 17.4861 | 255.66 | 46.693 | 63.646 | 50.283 | 71.758
| 17.4931 | 256.175 | 46.691 | 63.637 | 50.271 | 71.738
| 17.5 | 256.076 | 46.682 | 63.627 | 50.263 | 71.719
| 17.5069 | 256.641 | 46.677 | 63.624 | 50.258 | 71.708
| 17.5139 | 256.691 | 46.677 | 63.627 | 50.251 | 71.699
| 17.5208 | 256.398 | 46.676 | 63.627 | 50.249 | 71.697
| 17.5278 | 256.635 | 46.678 | 63.629 | 50.245 | 71.691
| 17.5347 | 256.454 | 46.669 | 63.627 | 50.239 | 71.68
| 17.5417 | 255.708 | 46.669 | 63.622 | 50.23 | 71.671
| 17.5486 | 255.731 | 46.658 | 63.616 | 50.225 | 71.652
| 17.5556 | 255.507 | 46.65 | 63.608 | 50.212 | 71.637
| 17.5625 | 255.576 | 46.641 | 63.599 | 50.207 | 71.622
| 17.5694 | 256.744 | 46.64 | 63.6 | 50.203 | 71.61
| 17.5764 | 256.539 | 46.635 | 63.598 | 50.202 | 71.605
| 17.5833 | 256.464 | 46.636 | 63.6 | 50.195 | 71.596
| 17.5903 | 256.953 | 46.633 | 63.603 | 50.196 | 71.601
| 17.5972 | 256.274 | 46.635 | 63.611 | 50.191 | 71.603
| 17.6042 | 256.806 | 46.638 | 63.608 | 50.187 | 71.606
| 17.6111 | 257.103 | 46.636 | 63.616 | 50.194 | 71.609
| 17.6181 | 256.629 | 46.633 | 63.616 | 50.194 | 71.607
| 17.625 | 257.83 | 46.638 | 63.615 | 50.188 | 71.613
| 17.6319 | 258.456 | 46.641 | 63.624 | 50.186 | 71.617
| 17.6389 | 258.648 | 46.648 | 63.64 | 50.196 | 71.633
| 17.6458 | 257.693 | 46.656 | 63.659 | 50.2 | 71.659
| 17.6528 | 258.259 | 46.658 | 63.674 | 50.205 | 71.669
| 17.6597 | 258.246 | 46.663 | 63.688 | 50.207 | 71.677
| 17.6667 | 259 | 46.664 | 63.701 | 50.207 | 71.687
| 17.6736 | 258.128 | 46.67 | 63.72 | 50.213 | 71.697
| 17.6806 | 258.76 | 46.672 | 63.739 | 50.217 | 71.717
| 17.6875 | 258.525 | 46.681 | 63.758 | 50.228 | 71.729
| 17.6944 | 258.488 | 46.687 | 63.777 | 50.225 | 71.743
| 17.7014 | 255.242 | 46.68 | 63.773 | 50.226 | 71.735
| 17.7083 | 255.078 | 46.665 | 63.753 | 50.208 | 71.702
| 17.7153 | 254.709 | 46.643 | 63.733 | 50.195 | 71.665
| 17.7222 | 255.539 | 46.637 | 63.728 | 50.188 | 71.636
| 17.7292 | 255.888 | 46.627 | 63.721 | 50.181 | 71.621
| 17.7361 | 255.918 | 46.618 | 63.714 | 50.176 | 71.606
| 17.7431 | 255.723 | 46.62 | 63.715 | 50.168 | 71.591
| 17.75 | 256.155 | 46.612 | 63.712 | 50.16 | 71.579
| 17.7569 | 256.256 | 46.606 | 63.713 | 50.153 | 71.571
| 17.7639 | 256.699 | 46.603 | 63.719 | 50.159 | 71.571
| 17.7708 | 256.487 | 46.602 | 63.727 | 50.157 | 71.576
| 17.7778 | 253.917 | 46.602 | 63.733 | 50.149 | 71.573
| 17.7847 | 256.536 | 46.593 | 63.734 | 50.147 | 71.562
| 17.7917 | 256.065 | 46.589 | 63.738 | 50.147 | 71.563
| 17.7986 | 257.118 | 46.59 | 63.746 | 50.138 | 71.559
| 17.8056 | 256.309 | 46.589 | 63.746 | 50.146 | 71.554
| 17.8125 | 256.097 | 46.578 | 63.747 | 50.138 | 71.542
| 17.8194 | 256.319 | 46.578 | 63.752 | 50.136 | 71.541
| 17.8264 | 256.848 | 46.575 | 63.753 | 50.139 | 71.54
| 17.8333 | 256.831 | 46.576 | 63.762 | 50.141 | 71.532
| 17.8403 | 256.991 | 46.573 | 63.766 | 50.135 | 71.538
| 17.8472 | 257.615 | 46.58 | 63.782 | 50.141 | 71.542
| 17.8542 | 257.433 | 46.582 | 63.797 | 50.146 | 71.553
| 17.8611 | 258.829 | 46.59 | 63.814 | 50.154 | 71.569
| 17.8681 | 258.453 | 46.596 | 63.838 | 50.169 | 71.58
| 17.875 | 259.873 | 46.601 | 63.855 | 50.171 | 71.595
| 17.8819 | 261.218 | 46.613 | 63.883 | 50.186 | 71.626
| 17.8889 | 259.141 | 46.631 | 63.931 | 50.208 | 71.672
| 17.8958 | 259.959 | 46.646 | 63.955 | 50.215 | 71.704
| 17.9028 | 261.077 | 46.65 | 63.983 | 50.223 | 71.727
| 17.9097 | 261.23 | 46.665 | 64.01 | 50.239 | 71.76
| 17.9167 | 261.348 | 46.675 | 64.034 | 50.257 | 71.792
| 17.9236 | 262.418 | 46.697 | 64.063 | 50.266 | 71.835
| 17.9306 | 259.839 | 46.716 | 64.097 | 50.287 | 71.885
| 17.9375 | 259.875 | 46.711 | 64.109 | 50.295 | 71.891
| 17.9444 | 259.991 | 46.713 | 64.119 | 50.295 | 71.889
| 17.9514 | 259.797 | 46.713 | 64.135 | 50.297 | 71.897
| 17.9583 | 260.086 | 46.716 | 64.15 | 50.305 | 71.907
| 17.9653 | 261.321 | 46.718 | 64.179 | 50.31 | 71.919
| 17.9722 | 260.859 | 46.726 | 64.201 | 50.324 | 71.932
| 17.9792 | 258.769 | 46.73 | 64.226 | 50.33 | 71.946
| 17.9861 | 258.684 | 46.723 | 64.226 | 50.325 | 71.932
| 17.9931 | 258.64 | 46.719 | 64.242 | 50.322 | 71.92
| 18 | 259.222 | 46.72 | 64.249 | 50.327 | 71.917
| 18.0069 | 260.121 | 46.723 | 64.264 | 50.335 | 71.927
| 18.0139 | 260.681 | 46.729 | 64.296 | 50.339 | 71.94
| 18.0208 | 261.234 | 46.741 | 64.324 | 50.354 | 71.964
| 18.0278 | 261.46 | 46.755 | 64.356 | 50.367 | 71.986
| 18.0347 | 261.405 | 46.765 | 64.388 | 50.377 | 72.013
| 18.0417 | 262.029 | 46.778 | 64.419 | 50.386 | 72.035
| 18.0486 | 258.481 | 46.785 | 64.445 | 50.395 | 72.053
| 18.0556 | 258.935 | 46.775 | 64.447 | 50.395 | 72.04
| 18.0625 | 259.573 | 46.775 | 64.455 | 50.393 | 72.027
| 18.0694 | 259.001 | 46.767 | 64.465 | 50.392 | 72.022
| 18.0764 | 258.885 | 46.764 | 64.473 | 50.399 | 72.012
| 18.0833 | 259.298 | 46.763 | 64.483 | 50.4 | 72.006
| 18.0903 | 260.303 | 46.767 | 64.497 | 50.401 | 72.002
| 18.0972 | 260.14 | 46.772 | 64.515 | 50.411 | 72.013
| 18.1042 | 260.494 | 46.777 | 64.538 | 50.419 | 72.024
| 18.1111 | 259.836 | 46.781 | 64.553 | 50.417 | 72.035
| 18.1181 | 259.529 | 46.782 | 64.572 | 50.427 | 72.035
| 18.125 | 260.746 | 46.79 | 64.59 | 50.432 | 72.041
| 18.1319 | 260.666 | 46.797 | 64.612 | 50.44 | 72.052
| 18.1389 | 261.72 | 46.807 | 64.636 | 50.452 | 72.075
| 18.1458 | 261.154 | 46.82 | 64.669 | 50.461 | 72.097
| 18.1528 | 261.352 | 46.824 | 64.692 | 50.471 | 72.114
| 18.1597 | 261.21 | 46.834 | 64.718 | 50.478 | 72.125
| 18.1667 | 261.239 | 46.839 | 64.736 | 50.483 | 72.135
| 18.1736 | 260.54 | 46.844 | 64.754 | 50.494 | 72.145
| 18.1806 | 259.872 | 46.847 | 64.775 | 50.502 | 72.15
| 18.1875 | 260.052 | 46.852 | 64.787 | 50.503 | 72.148
| 18.1944 | 260.043 | 46.846 | 64.802 | 50.507 | 72.155
| 18.2014 | 259.97 | 46.85 | 64.816 | 50.518 | 72.152
| 18.2083 | 259.348 | 46.852 | 64.825 | 50.515 | 72.15
| 18.2153 | 258.745 | 46.85 | 64.831 | 50.515 | 72.139
| 18.2222 | 258.633 | 46.843 | 64.834 | 50.515 | 72.124
| 18.2292 | 259.195 | 46.84 | 64.841 | 50.516 | 72.109
| 18.2361 | 259.837 | 46.845 | 64.853 | 50.524 | 72.108
| 18.2431 | 261.044 | 46.85 | 64.872 | 50.528 | 72.119
| 18.25 | 261.283 | 46.864 | 64.903 | 50.538 | 72.14
| 18.2569 | 259.8 | 46.873 | 64.925 | 50.55 | 72.162
| 18.2639 | 261.003 | 46.872 | 64.928 | 50.549 | 72.15
| 18.2708 | 262.396 | 46.88 | 64.954 | 50.56 | 72.168
| 18.2778 | 261.78 | 46.897 | 64.987 | 50.575 | 72.197
| 18.2847 | 260.514 | 46.907 | 65.015 | 50.584 | 72.217
| 18.2917 | 260.097 | 46.909 | 65.031 | 50.588 | 72.218
| 18.2986 | 258.466 | 46.903 | 65.036 | 50.593 | 72.208
| 18.3056 | 260.38 | 46.893 | 65.031 | 50.59 | 72.184
| 18.3125 | 260.614 | 46.896 | 65.038 | 50.589 | 72.177
| 18.3194 | 262.046 | 46.907 | 65.067 | 50.602 | 72.198
| 18.3264 | 261.281 | 46.922 | 65.098 | 50.617 | 72.231
| 18.3333 | 261.896 | 46.933 | 65.128 | 50.629 | 72.247
| 18.3403 | 261.105 | 46.946 | 65.154 | 50.636 | 72.269
| 18.3472 | 260.906 | 46.948 | 65.174 | 50.648 | 72.275
| 18.3542 | 260.975 | 46.952 | 65.193 | 50.652 | 72.29
| 18.3611 | 260.892 | 46.956 | 65.206 | 50.656 | 72.287
| 18.3681 | 260.13 | 46.957 | 65.218 | 50.659 | 72.287
| 18.375 | 260.02 | 46.958 | 65.224 | 50.662 | 72.286
| 18.3819 | 260.165 | 46.96 | 65.238 | 50.668 | 72.278
| 18.3889 | 260.468 | 46.964 | 65.25 | 50.672 | 72.284
| 18.3958 | 259.488 | 46.964 | 65.263 | 50.672 | 72.285
| 18.4028 | 259.263 | 46.964 | 65.27 | 50.67 | 72.28
| 18.4097 | 259.817 | 46.964 | 65.274 | 50.675 | 72.266
| 18.4167 | 259.15 | 46.961 | 65.282 | 50.673 | 72.257
| 18.4236 | 259.13 | 46.957 | 65.282 | 50.676 | 72.245
| 18.4306 | 258.605 | 46.954 | 65.278 | 50.674 | 72.229
| 18.4375 | 258.906 | 46.947 | 65.277 | 50.67 | 72.212
| 18.4444 | 257.979 | 46.948 | 65.278 | 50.674 | 72.206
| 18.4514 | 257.545 | 46.946 | 65.28 | 50.667 | 72.192
| 18.4583 | 257.62 | 46.937 | 65.274 | 50.661 | 72.173
| 18.4653 | 257.336 | 46.927 | 65.267 | 50.661 | 72.146
| 18.4722 | 257.07 | 46.921 | 65.259 | 50.656 | 72.124
| 18.4792 | 257.244 | 46.917 | 65.251 | 50.646 | 72.104
| 18.4861 | 256.373 | 46.91 | 65.247 | 50.635 | 72.09
| 18.4931 | 257.467 | 46.904 | 65.235 | 50.636 | 72.067
| 18.5 | 256.384 | 46.902 | 65.232 | 50.633 | 72.049
| 18.5069 | 256.621 | 46.9 | 65.23 | 50.626 | 72.031
| 18.5139 | 256.9 | 46.895 | 65.227 | 50.622 | 72.025
| 18.5208 | 256.629 | 46.892 | 65.223 | 50.616 | 72.006
| 18.5278 | 257.944 | 46.89 | 65.225 | 50.611 | 71.995
| 18.5347 | 258.849 | 46.888 | 65.227 | 50.616 | 71.997
| 18.5417 | 257.941 | 46.899 | 65.235 | 50.62 | 72.003
| 18.5486 | 256.91 | 46.896 | 65.246 | 50.615 | 72.002
| 18.5556 | 255.989 | 46.898 | 65.239 | 50.615 | 71.991
| 18.5625 | 256.129 | 46.888 | 65.232 | 50.612 | 71.967
| 18.5694 | 256.392 | 46.883 | 65.222 | 50.598 | 71.948
| 18.5764 | 257.317 | 46.875 | 65.218 | 50.602 | 71.94
| 18.5833 | 257.553 | 46.876 | 65.225 | 50.601 | 71.943
| 18.5903 | 257.399 | 46.879 | 65.231 | 50.6 | 71.944
| 18.5972 | 257.427 | 46.882 | 65.231 | 50.593 | 71.94
| 18.6042 | 257.581 | 46.88 | 65.235 | 50.601 | 71.935
| 18.6111 | 257.054 | 46.879 | 65.244 | 50.593 | 71.931
| 18.6181 | 257.081 | 46.878 | 65.244 | 50.599 | 71.93
| 18.625 | 258.281 | 46.881 | 65.247 | 50.598 | 71.93
| 18.6319 | 258.512 | 46.885 | 65.255 | 50.597 | 71.931
| 18.6389 | 258.86 | 46.893 | 65.27 | 50.6 | 71.941
| 18.6458 | 258.338 | 46.899 | 65.281 | 50.609 | 71.957
| 18.6528 | 259.22 | 46.905 | 65.299 | 50.612 | 71.971
| 18.6597 | 258.463 | 46.913 | 65.31 | 50.619 | 71.983
| 18.6667 | 258.298 | 46.916 | 65.323 | 50.62 | 71.993
| 18.6736 | 257.219 | 46.912 | 65.329 | 50.624 | 72.001
| 18.6806 | 257.137 | 46.917 | 65.335 | 50.618 | 71.997
| 18.6875 | 257.112 | 46.915 | 65.335 | 50.619 | 71.993
| 18.6944 | 256.968 | 46.912 | 65.34 | 50.618 | 71.988
| 18.7014 | 257.335 | 46.912 | 65.34 | 50.614 | 71.982
| 18.7083 | 257.409 | 46.911 | 65.348 | 50.617 | 71.983
| 18.7153 | 257.693 | 46.911 | 65.355 | 50.615 | 71.986
| 18.7222 | 257.025 | 46.917 | 65.366 | 50.618 | 71.994
| 18.7292 | 258.165 | 46.92 | 65.375 | 50.623 | 72.002
| 18.7361 | 257.18 | 46.926 | 65.389 | 50.623 | 72.009
| 18.7431 | 256.287 | 46.922 | 65.383 | 50.62 | 72.001
| 18.75 | 256.635 | 46.916 | 65.378 | 50.62 | 71.987
| 18.7569 | 257.012 | 46.914 | 65.377 | 50.617 | 71.976
| 18.7639 | 257.076 | 46.909 | 65.383 | 50.616 | 71.976
| 18.7708 | 256.694 | 46.916 | 65.389 | 50.607 | 71.979
| 18.7778 | 256.528 | 46.914 | 65.396 | 50.612 | 71.978
| 18.7847 | 257.746 | 46.918 | 65.399 | 50.614 | 71.981
| 18.7917 | 257.833 | 46.916 | 65.41 | 50.62 | 71.984
| 18.7986 | 257.961 | 46.922 | 65.416 | 50.615 | 71.991
| 18.8056 | 258.761 | 46.926 | 65.434 | 50.624 | 71.999
| 18.8125 | 259.075 | 46.936 | 65.448 | 50.631 | 72.016
| 18.8194 | 258.902 | 46.938 | 65.466 | 50.635 | 72.03
| 18.8264 | 259.647 | 46.946 | 65.484 | 50.647 | 72.043
| 18.8333 | 259.322 | 46.954 | 65.502 | 50.649 | 72.063
| 18.8403 | 259.98 | 46.965 | 65.524 | 50.665 | 72.084
| 18.8472 | 257.879 | 46.978 | 65.553 | 50.669 | 72.114
| 18.8542 | 258.108 | 46.971 | 65.555 | 50.671 | 72.109
| 18.8611 | 258.548 | 46.971 | 65.554 | 50.668 | 72.096
| 18.8681 | 258.841 | 46.971 | 65.562 | 50.67 | 72.1
| 18.875 | 258.989 | 46.973 | 65.572 | 50.678 | 72.104
| 18.8819 | 259.158 | 46.98 | 65.592 | 50.687 | 72.117
| 18.8889 | 259.536 | 46.989 | 65.608 | 50.69 | 72.129
| 18.8958 | 259.354 | 46.987 | 65.619 | 50.698 | 72.141
| 18.9028 | 257.142 | 46.992 | 65.631 | 50.7 | 72.143
| 18.9097 | 258.452 | 46.986 | 65.631 | 50.699 | 72.135
| 18.9167 | 259.03 | 46.984 | 65.634 | 50.702 | 72.129
| 18.9236 | 259.487 | 46.989 | 65.648 | 50.707 | 72.138
| 18.9306 | 259.879 | 46.997 | 65.665 | 50.711 | 72.154
| 18.9375 | 260.189 | 47.006 | 65.684 | 50.725 | 72.174
| 18.9444 | 260.892 | 47.013 | 65.71 | 50.73 | 72.197
| 18.9514 | 260.173 | 47.03 | 65.74 | 50.749 | 72.226
| 18.9583 | 260.447 | 47.039 | 65.763 | 50.755 | 72.247
| 18.9653 | 260.535 | 47.047 | 65.785 | 50.765 | 72.272
| 18.9722 | 261.328 | 47.058 | 65.816 | 50.785 | 72.295
| 18.9792 | 261.317 | 47.072 | 65.848 | 50.796 | 72.327
| 18.9861 | 261.066 | 47.08 | 65.868 | 50.804 | 72.347
| 18.9931 | 258.857 | 47.083 | 65.879 | 50.811 | 72.351
| 19 | 259.004 | 47.071 | 65.883 | 50.807 | 72.339
| 19.0069 | 260.362 | 47.071 | 65.887 | 50.801 | 72.329
| 19.0139 | 260.016 | 47.075 | 65.902 | 50.802 | 72.337
| 19.0208 | 259.89 | 47.077 | 65.92 | 50.813 | 72.351
| 19.0278 | 260.564 | 47.083 | 65.936 | 50.815 | 72.363
| 19.0347 | 260.854 | 47.096 | 65.95 | 50.824 | 72.372
| 19.0417 | 260.844 | 47.092 | 65.972 | 50.833 | 72.383
| 19.0486 | 260.977 | 47.098 | 65.989 | 50.834 | 72.39
| 19.0556 | 260.923 | 47.107 | 66.008 | 50.843 | 72.408
| 19.0625 | 261.347 | 47.121 | 66.033 | 50.853 | 72.431
| 19.0694 | 261.683 | 47.129 | 66.059 | 50.861 | 72.444
| 19.0764 | 261.084 | 47.141 | 66.085 | 50.875 | 72.465
| 19.0833 | 261.763 | 47.142 | 66.104 | 50.878 | 72.484
| 19.0903 | 261.745 | 47.15 | 66.13 | 50.891 | 72.501
| 19.0972 | 262.851 | 47.164 | 66.158 | 50.902 | 72.525
| 19.1042 | 262.943 | 47.175 | 66.19 | 50.911 | 72.556
| 19.1111 | 261.993 | 47.183 | 66.215 | 50.925 | 72.58
| 19.1181 | 261.53 | 47.193 | 66.235 | 50.932 | 72.589
| 19.125 | 262.085 | 47.197 | 66.258 | 50.942 | 72.603
| 19.1319 | 261.921 | 47.204 | 66.281 | 50.949 | 72.611
| 19.1389 | 262.229 | 47.209 | 66.298 | 50.962 | 72.627
| 19.1458 | 261.779 | 47.214 | 66.316 | 50.961 | 72.636
| 19.1528 | 262.02 | 47.218 | 66.334 | 50.975 | 72.647
| 19.1597 | 261.407 | 47.22 | 66.36 | 50.979 | 72.66
| 19.1667 | 261.804 | 47.229 | 66.373 | 50.989 | 72.672
| 19.1736 | 261.59 | 47.233 | 66.399 | 50.992 | 72.676
| 19.1806 | 261.637 | 47.237 | 66.411 | 51.002 | 72.68
| 19.1875 | 260.676 | 47.238 | 66.425 | 51.001 | 72.685
| 19.1944 | 260.714 | 47.239 | 66.431 | 51.007 | 72.683
| 19.2014 | 260.698 | 47.239 | 66.442 | 51.007 | 72.68
| 19.2083 | 260.62 | 47.238 | 66.455 | 51.01 | 72.677
| 19.2153 | 259.254 | 47.238 | 66.458 | 51.009 | 72.675
| 19.2222 | 258.69 | 47.231 | 66.453 | 51.005 | 72.653
| 19.2292 | 261.128 | 47.223 | 66.453 | 51 | 72.637
| 19.2361 | 260.401 | 47.229 | 66.464 | 51.008 | 72.641
| 19.2431 | 260.262 | 47.231 | 66.481 | 51.009 | 72.637
| 19.25 | 260.105 | 47.234 | 66.487 | 51.013 | 72.646
| 19.2569 | 260.143 | 47.239 | 66.505 | 51.025 | 72.645
| 19.2639 | 259.909 | 47.238 | 66.506 | 51.022 | 72.639
| 19.2708 | 260.176 | 47.235 | 66.514 | 51.017 | 72.629
| 19.2778 | 260.917 | 47.231 | 66.515 | 51.021 | 72.621
| 19.2847 | 260.639 | 47.237 | 66.534 | 51.021 | 72.634
| 19.2917 | 259.93 | 47.243 | 66.548 | 51.024 | 72.642
| 19.2986 | 258.575 | 47.244 | 66.552 | 51.028 | 72.635
| 19.3056 | 257.994 | 47.235 | 66.546 | 51.02 | 72.618
| 19.3125 | 261.329 | 47.22 | 66.538 | 51.013 | 72.59
| 19.3194 | 261.483 | 47.231 | 66.553 | 51.02 | 72.601
| 19.3264 | 260.663 | 47.24 | 66.57 | 51.032 | 72.615
| 19.3333 | 260.085 | 47.246 | 66.584 | 51.029 | 72.619
| 19.3403 | 258.997 | 47.243 | 66.594 | 51.032 | 72.62
| 19.3472 | 258.928 | 47.243 | 66.595 | 51.032 | 72.616
| 19.3542 | 259.947 | 47.241 | 66.6 | 51.03 | 72.608
| 19.3611 | 259.144 | 47.245 | 66.605 | 51.033 | 72.604
| 19.3681 | 258.659 | 47.244 | 66.612 | 51.036 | 72.6
| 19.375 | 258.525 | 47.242 | 66.615 | 51.034 | 72.592
| 19.3819 | 258.647 | 47.235 | 66.613 | 51.029 | 72.582
| 19.3889 | 259.486 | 47.233 | 66.621 | 51.03 | 72.574
| 19.3958 | 258.45 | 47.233 | 66.624 | 51.029 | 72.573
| 19.4028 | 258.272 | 47.23 | 66.619 | 51.027 | 72.561
| 19.4097 | 257.801 | 47.223 | 66.609 | 51.019 | 72.538
| 19.4167 | 257.795 | 47.212 | 66.603 | 51.011 | 72.516
| 19.4236 | 256.848 | 47.206 | 66.592 | 51.005 | 72.494
| 19.4306 | 260.028 | 47.2 | 66.585 | 50.999 | 72.476
| 19.4375 | 259.322 | 47.208 | 66.604 | 51.009 | 72.493
| 19.4444 | 257.993 | 47.217 | 66.614 | 51.01 | 72.501
| 19.4514 | 259.119 | 47.218 | 66.621 | 51.006 | 72.498
| 19.4583 | 258.298 | 47.218 | 66.626 | 51.006 | 72.499
| 19.4653 | 258.174 | 47.222 | 66.634 | 51.012 | 72.493
| 19.4722 | 258.039 | 47.222 | 66.631 | 51.009 | 72.496
| 19.4792 | 257.436 | 47.218 | 66.632 | 51.003 | 72.487
| 19.4861 | 257.811 | 47.21 | 66.633 | 51.004 | 72.478
| 19.4931 | 257.34 | 47.21 | 66.635 | 50.995 | 72.469
| 19.5 | 258.375 | 47.208 | 66.632 | 50.996 | 72.461
| 19.5069 | 259.149 | 47.208 | 66.633 | 50.986 | 72.45
| 19.5139 | 257.458 | 47.207 | 66.633 | 50.995 | 72.456
| 19.5208 | 257.707 | 47.202 | 66.634 | 50.984 | 72.439
| 19.5278 | 258.24 | 47.198 | 66.626 | 50.984 | 72.426
| 19.5347 | 257.137 | 47.194 | 66.621 | 50.979 | 72.419
| 19.5417 | 257.424 | 47.195 | 66.62 | 50.977 | 72.415
| 19.5486 | 256.302 | 47.195 | 66.62 | 50.972 | 72.406
| 19.5556 | 257.13 | 47.197 | 66.629 | 50.974 | 72.41
| 19.5625 | 257.467 | 47.195 | 66.634 | 50.975 | 72.413
| 19.5694 | 258.237 | 47.194 | 66.63 | 50.976 | 72.412
| 19.5764 | 257.821 | 47.194 | 66.637 | 50.973 | 72.411
| 19.5833 | 258.691 | 47.194 | 66.642 | 50.968 | 72.406
| 19.5903 | 258.192 | 47.199 | 66.646 | 50.973 | 72.412
| 19.5972 | 257.585 | 47.198 | 66.656 | 50.973 | 72.414
| 19.6042 | 258.008 | 47.2 | 66.658 | 50.971 | 72.415
| 19.6111 | 257.445 | 47.193 | 66.659 | 50.971 | 72.407
| 19.6181 | 257.453 | 47.197 | 66.665 | 50.967 | 72.41
| 19.625 | 257.36 | 47.198 | 66.669 | 50.97 | 72.412
| 19.6319 | 257.313 | 47.198 | 66.676 | 50.969 | 72.412
| 19.6389 | 257.322 | 47.192 | 66.678 | 50.963 | 72.404
| 19.6458 | 258.375 | 47.192 | 66.679 | 50.961 | 72.409
| 19.6528 | 258.7 | 47.198 | 66.694 | 50.965 | 72.419
| 19.6597 | 259.01 | 47.204 | 66.709 | 50.975 | 72.43
| 19.6667 | 257.96 | 47.211 | 66.717 | 50.973 | 72.44
| 19.6736 | 258.322 | 47.213 | 66.727 | 50.976 | 72.447
| 19.6806 | 258.669 | 47.211 | 66.735 | 50.975 | 72.449
| 19.6875 | 257.048 | 47.207 | 66.736 | 50.974 | 72.448
| 19.6944 | 257.49 | 47.205 | 66.732 | 50.966 | 72.434
| 19.7014 | 257.584 | 47.198 | 66.726 | 50.957 | 72.421
| 19.7083 | 256.763 | 47.189 | 66.721 | 50.954 | 72.407
| 19.7153 | 257.226 | 47.187 | 66.718 | 50.953 | 72.4
| 19.7222 | 257.104 | 47.183 | 66.715 | 50.946 | 72.392
| 19.7292 | 257.577 | 47.18 | 66.72 | 50.943 | 72.388
| 19.7361 | 257.347 | 47.185 | 66.723 | 50.945 | 72.387
| 19.7431 | 258.476 | 47.183 | 66.727 | 50.949 | 72.391
| 19.75 | 257.659 | 47.184 | 66.735 | 50.945 | 72.391
| 19.7569 | 257.096 | 47.181 | 66.732 | 50.938 | 72.387
| 19.7639 | 257.311 | 47.177 | 66.734 | 50.938 | 72.379
| 19.7708 | 257.615 | 47.177 | 66.724 | 50.94 | 72.379
| 19.7778 | 257.729 | 47.179 | 66.717 | 50.943 | 72.379
| 19.7847 | 257.736 | 47.18 | 66.712 | 50.939 | 72.388
| 19.7917 | 258.326 | 47.176 | 66.713 | 50.933 | 72.386
| 19.7986 | 259.142 | 47.181 | 66.722 | 50.936 | 72.396
| 19.8056 | 258.286 | 47.184 | 66.738 | 50.943 | 72.4
| 19.8125 | 259.546 | 47.191 | 66.76 | 50.943 | 72.414
| 19.8194 | 258.975 | 47.196 | 66.766 | 50.946 | 72.428
| 19.8264 | 258.723 | 47.2 | 66.789 | 50.951 | 72.441
| 19.8333 | 259.399 | 47.202 | 66.803 | 50.955 | 72.456
| 19.8403 | 259.747 | 47.212 | 66.819 | 50.961 | 72.473
| 19.8472 | 257.569 | 47.213 | 66.838 | 50.964 | 72.482
| 19.8542 | 258.331 | 47.207 | 66.837 | 50.964 | 72.475
| 19.8611 | 258.413 | 47.202 | 66.845 | 50.96 | 72.472
| 19.8681 | 258.474 | 47.206 | 66.858 | 50.967 | 72.478
| 19.875 | 258.661 | 47.21 | 66.866 | 50.961 | 72.48
| 19.8819 | 258.348 | 47.208 | 66.875 | 50.965 | 72.482
| 19.8889 | 257.836 | 47.211 | 66.885 | 50.963 | 72.482
| 19.8958 | 257.959 | 47.209 | 66.893 | 50.964 | 72.48
| 19.9028 | 256.442 | 47.202 | 66.89 | 50.964 | 72.465
| 19.9097 | 256.765 | 47.188 | 66.877 | 50.95 | 72.443
| 19.9167 | 257.71 | 47.179 | 66.875 | 50.945 | 72.427
| 19.9236 | 255.983 | 47.181 | 66.873 | 50.941 | 72.416
| 19.9306 | 255.9 | 47.166 | 66.858 | 50.932 | 72.391
| 19.9375 | 257.003 | 47.156 | 66.852 | 50.927 | 72.374
| 19.9444 | 257.443 | 47.159 | 66.861 | 50.923 | 72.365
| 19.9514 | 258.816 | 47.159 | 66.867 | 50.93 | 72.374
| 19.9583 | 259.019 | 47.172 | 66.886 | 50.933 | 72.383
| 19.9653 | 259.324 | 47.182 | 66.904 | 50.944 | 72.411
| 19.9722 | 259.407 | 47.186 | 66.924 | 50.952 | 72.427
| 19.9792 | 260.258 | 47.196 | 66.947 | 50.954 | 72.448
| 19.9861 | 260.19 | 47.209 | 66.978 | 50.962 | 72.474
| 19.9931 | 260.475 | 47.221 | 67.005 | 50.976 | 72.507
| 20 | 257.826 | 47.22 | 67.021 | 50.976 | 72.51
| 20.0069 | 258.293 | 47.214 | 67.025 | 50.978 | 72.502
| 20.0139 | 258.593 | 47.213 | 67.028 | 50.975 | 72.502
| 20.0208 | 258.876 | 47.215 | 67.042 | 50.979 | 72.51
| 20.0278 | 258.882 | 47.22 | 67.059 | 50.986 | 72.523
| 20.0347 | 258.891 | 47.228 | 67.073 | 50.986 | 72.534
| 20.0417 | 259.473 | 47.226 | 67.093 | 50.998 | 72.545
| 20.0486 | 257.764 | 47.23 | 67.11 | 51.004 | 72.552
| 20.0556 | 258.313 | 47.222 | 67.107 | 50.997 | 72.536
| 20.0625 | 258.119 | 47.216 | 67.107 | 50.993 | 72.528
| 20.0694 | 257.977 | 47.214 | 67.11 | 50.99 | 72.517
| 20.0764 | 258.175 | 47.211 | 67.112 | 50.989 | 72.508
| 20.0833 | 258.285 | 47.205 | 67.117 | 50.989 | 72.5
| 20.0903 | 258.332 | 47.212 | 67.122 | 50.993 | 72.497
| 20.0972 | 258.206 | 47.213 | 67.14 | 50.997 | 72.505
| 20.1042 | 258.071 | 47.212 | 67.145 | 50.997 | 72.501
| 20.1111 | 258.401 | 47.218 | 67.161 | 50.999 | 72.508
| 20.1181 | 258.519 | 47.219 | 67.17 | 51.001 | 72.511
| 20.125 | 258.798 | 47.224 | 67.184 | 51.006 | 72.518
| 20.1319 | 258.928 | 47.224 | 67.198 | 51.012 | 72.52
| 20.1389 | 258.272 | 47.226 | 67.209 | 51.01 | 72.525
| 20.1458 | 258.082 | 47.228 | 67.215 | 51.011 | 72.524
| 20.1528 | 258.221 | 47.224 | 67.223 | 51.016 | 72.523
| 20.1597 | 258.598 | 47.229 | 67.234 | 51.015 | 72.524
| 20.1667 | 258.895 | 47.234 | 67.253 | 51.022 | 72.531
| 20.1736 | 258.94 | 47.234 | 67.262 | 51.03 | 72.54
| 20.1806 | 258.368 | 47.238 | 67.272 | 51.031 | 72.541
| 20.1875 | 258.302 | 47.236 | 67.282 | 51.03 | 72.543
| 20.1944 | 258.189 | 47.239 | 67.293 | 51.036 | 72.542
| 20.2014 | 258.735 | 47.243 | 67.308 | 51.039 | 72.548
| 20.2083 | 258.728 | 47.24 | 67.315 | 51.038 | 72.55
| 20.2153 | 258.271 | 47.244 | 67.33 | 51.039 | 72.557
| 20.2222 | 259.58 | 47.242 | 67.338 | 51.045 | 72.551
| 20.2292 | 260.271 | 47.245 | 67.357 | 51.051 | 72.561
| 20.2361 | 260.22 | 47.263 | 67.383 | 51.063 | 72.587
| 20.2431 | 261.292 | 47.272 | 67.409 | 51.074 | 72.614
| 20.25 | 260.938 | 47.288 | 67.44 | 51.089 | 72.644
| 20.2569 | 260.369 | 47.301 | 67.47 | 51.096 | 72.669
| 20.2639 | 258.506 | 47.309 | 67.494 | 51.109 | 72.684
| 20.2708 | 259.218 | 47.308 | 67.507 | 51.11 | 72.688
| 20.2778 | 258.336 | 47.303 | 67.509 | 51.113 | 72.682
| 20.2847 | 257.802 | 47.298 | 67.512 | 51.106 | 72.671
| 20.2917 | 257.448 | 47.293 | 67.513 | 51.103 | 72.657
| 20.2986 | 258.155 | 47.287 | 67.512 | 51.102 | 72.64
| 20.3056 | 259.474 | 47.279 | 67.505 | 51.097 | 72.62
| 20.3125 | 260.106 | 47.284 | 67.516 | 51.104 | 72.625
| 20.3194 | 258.687 | 47.288 | 67.537 | 51.111 | 72.635
| 20.3264 | 258.711 | 47.292 | 67.549 | 51.112 | 72.642
| 20.3333 | 258.484 | 47.296 | 67.556 | 51.114 | 72.635
| 20.3403 | 257.114 | 47.291 | 67.559 | 51.111 | 72.632
| 20.3472 | 259.111 | 47.287 | 67.559 | 51.109 | 72.615
| 20.3542 | 259.026 | 47.292 | 67.578 | 51.115 | 72.625
| 20.3611 | 259.112 | 47.303 | 67.594 | 51.122 | 72.635
| 20.3681 | 258.565 | 47.303 | 67.599 | 51.125 | 72.64
| 20.375 | 258.737 | 47.301 | 67.609 | 51.123 | 72.636
| 20.3819 | 259.57 | 47.304 | 67.614 | 51.124 | 72.635
| 20.3889 | 262.258 | 47.315 | 67.639 | 51.13 | 72.654
| 20.3958 | 261.247 | 47.335 | 67.686 | 51.146 | 72.703
| 20.4028 | 261.003 | 47.351 | 67.718 | 51.165 | 72.735
| 20.4097 | 260.385 | 47.365 | 67.744 | 51.179 | 72.759
| 20.4167 | 259.668 | 47.368 | 67.763 | 51.188 | 72.769
| 20.4236 | 258.51 | 47.369 | 67.771 | 51.182 | 72.767
| 20.4306 | 259.924 | 47.365 | 67.776 | 51.189 | 72.762
| 20.4375 | 260.444 | 47.372 | 67.792 | 51.196 | 72.778
| 20.4444 | 259.371 | 47.379 | 67.816 | 51.199 | 72.789
| 20.4514 | 259.421 | 47.373 | 67.823 | 51.201 | 72.79
| 20.4583 | 260.103 | 47.375 | 67.83 | 51.202 | 72.788
| 20.4653 | 259.256 | 47.386 | 67.842 | 51.212 | 72.795
| 20.4722 | 258.438 | 47.383 | 67.856 | 51.215 | 72.797
| 20.4792 | 258.611 | 47.385 | 67.865 | 51.213 | 72.801
| 20.4861 | 257.734 | 47.383 | 67.869 | 51.213 | 72.79
| 20.4931 | 257.969 | 47.376 | 67.875 | 51.211 | 72.78
| 20.5 | 258.699 | 47.374 | 67.874 | 51.212 | 72.773
| 20.5069 | 258.779 | 47.38 | 67.88 | 51.209 | 72.775
| 20.5139 | 255.77 | 47.383 | 67.896 | 51.222 | 72.779
| 20.5208 | 255.425 | 47.376 | 67.893 | 51.208 | 72.759
| 20.5278 | 255.87 | 47.352 | 67.867 | 51.2 | 72.718
| 20.5347 | 255.343 | 47.35 | 67.857 | 51.181 | 72.686
| 20.5417 | 255.15 | 47.332 | 67.832 | 51.178 | 72.655
| 20.5486 | 255.442 | 47.324 | 67.82 | 51.161 | 72.629
| 20.5556 | 256.165 | 47.318 | 67.813 | 51.153 | 72.603
| 20.5625 | 256.951 | 47.315 | 67.811 | 51.161 | 72.596
| 20.5694 | 257.407 | 47.318 | 67.82 | 51.155 | 72.594
| 20.5764 | 258.019 | 47.322 | 67.826 | 51.155 | 72.6
| 20.5833 | 254.912 | 47.323 | 67.829 | 51.162 | 72.606
| 20.5903 | 252.711 | 47.312 | 67.815 | 51.146 | 72.572
| 20.5972 | 257.308 | 47.309 | 67.815 | 51.138 | 72.561
| 20.6042 | 257.416 | 47.309 | 67.818 | 51.146 | 72.567
| 20.6111 | 258.027 | 47.315 | 67.836 | 51.146 | 72.575
| 20.6181 | 257.73 | 47.324 | 67.842 | 51.146 | 72.578
| 20.625 | 257.829 | 47.33 | 67.855 | 51.155 | 72.593
| 20.6319 | 257.239 | 47.335 | 67.872 | 51.155 | 72.611
| 20.6389 | 257.275 | 47.336 | 67.877 | 51.16 | 72.614
| 20.6458 | 257.813 | 47.338 | 67.888 | 51.168 | 72.617
| 20.6528 | 256.554 | 47.341 | 67.894 | 51.166 | 72.623
| 20.6597 | 256.453 | 47.34 | 67.897 | 51.16 | 72.617
| 20.6667 | 256.035 | 47.337 | 67.896 | 51.155 | 72.61
| 20.6736 | 256.898 | 47.33 | 67.894 | 51.153 | 72.598
| 20.6806 | 258.666 | 47.335 | 67.904 | 51.16 | 72.604
| 20.6875 | 258.307 | 47.352 | 67.932 | 51.172 | 72.641
| 20.6944 | 258.815 | 47.361 | 67.959 | 51.185 | 72.664
| 20.7014 | 258.748 | 47.374 | 67.984 | 51.19 | 72.693
| 20.7083 | 258.648 | 47.382 | 68.004 | 51.205 | 72.714
| 20.7153 | 258.674 | 47.389 | 68.027 | 51.205 | 72.732
| 20.7222 | 257.609 | 47.392 | 68.043 | 51.215 | 72.745
| 20.7292 | 257.689 | 47.401 | 68.053 | 51.215 | 72.749
| 20.7361 | 256.962 | 47.396 | 68.065 | 51.227 | 72.755
| 20.7431 | 256.559 | 47.396 | 68.064 | 51.219 | 72.747
| 20.75 | 256.054 | 47.387 | 68.065 | 51.218 | 72.733
| 20.7569 | 259.686 | 47.393 | 68.085 | 51.233 | 72.75
| 20.7639 | 259.413 | 47.416 | 68.117 | 51.24 | 72.792
| 20.7708 | 259.689 | 47.431 | 68.151 | 51.259 | 72.828
| 20.7778 | 258.822 | 47.444 | 68.186 | 51.272 | 72.858
| 20.7847 | 259.122 | 47.451 | 68.211 | 51.278 | 72.883
| 20.7917 | 258.036 | 47.455 | 68.226 | 51.282 | 72.886
| 20.7986 | 258.515 | 47.452 | 68.239 | 51.285 | 72.892
| 20.8056 | 259.65 | 47.461 | 68.258 | 51.296 | 72.908
| 20.8125 | 259.685 | 47.47 | 68.28 | 51.304 | 72.924
| 20.8194 | 258.884 | 47.475 | 68.299 | 51.31 | 72.937
| 20.8264 | 259.753 | 47.481 | 68.32 | 51.32 | 72.948
| 20.8333 | 259.075 | 47.491 | 68.348 | 51.331 | 72.97
| 20.8403 | 259.278 | 47.493 | 68.361 | 51.335 | 72.977
| 20.8472 | 260.653 | 47.501 | 68.382 | 51.352 | 72.994
| 20.8542 | 261.715 | 47.515 | 68.415 | 51.359 | 73.021
| 20.8611 | 262.726 | 47.537 | 68.46 | 51.383 | 73.066
| 20.8681 | 263.321 | 47.555 | 68.507 | 51.402 | 73.116
| 20.875 | 265.01 | 47.584 | 68.562 | 51.432 | 73.174
| 20.8819 | 265.606 | 47.617 | 68.622 | 51.457 | 73.238
| 20.8889 | 265.993 | 47.645 | 68.692 | 51.494 | 73.318
| 20.8958 | 263.328 | 47.667 | 68.746 | 51.516 | 73.362
| 20.9028 | 261.634 | 47.674 | 68.776 | 51.531 | 73.381
| 20.9097 | 262.446 | 47.673 | 68.791 | 51.533 | 73.387
| 20.9167 | 262.261 | 47.672 | 68.815 | 51.548 | 73.398
| 20.9236 | 262.888 | 47.68 | 68.837 | 51.551 | 73.409
| 20.9306 | 263.201 | 47.687 | 68.867 | 51.57 | 73.424
| 20.9375 | 264.133 | 47.698 | 68.902 | 51.58 | 73.45
| 20.9444 | 264.533 | 47.714 | 68.934 | 51.599 | 73.482
| 20.9514 | 265.607 | 47.736 | 68.985 | 51.62 | 73.52
| 20.9583 | 266.11 | 47.758 | 69.043 | 51.637 | 73.572
| 20.9653 | 266.185 | 47.785 | 69.092 | 51.668 | 73.629
| 20.9722 | 260.824 | 47.801 | 69.144 | 51.691 | 73.669
| 20.9792 | 257.894 | 47.78 | 69.126 | 51.671 | 73.624
| 20.9861 | 259.179 | 47.742 | 69.093 | 51.65 | 73.56
| 20.9931 | 257.29 | 47.716 | 69.067 | 51.636 | 73.498
| 21 | 257.649 | 47.691 | 69.037 | 51.623 | 73.432
| 21.0069 | 257.963 | 47.676 | 69.013 | 51.608 | 73.386
| 21.0139 | 257.585 | 47.664 | 69.004 | 51.592 | 73.344
| 21.0208 | 257.915 | 47.654 | 68.985 | 51.585 | 73.308
| 21.0278 | 258.407 | 47.649 | 68.981 | 51.587 | 73.289
| 21.0347 | 258.096 | 47.645 | 68.982 | 51.574 | 73.269
| 21.0417 | 259.097 | 47.642 | 68.982 | 51.573 | 73.254
| 21.0486 | 258.716 | 47.648 | 68.991 | 51.575 | 73.252
| 21.0556 | 259.653 | 47.645 | 68.994 | 51.578 | 73.243
| 21.0625 | 260.076 | 47.653 | 69.006 | 51.576 | 73.244
| 21.0694 | 259.739 | 47.657 | 69.023 | 51.586 | 73.256
| 21.0764 | 260.446 | 47.659 | 69.032 | 51.586 | 73.258
| 21.0833 | 260.078 | 47.663 | 69.055 | 51.594 | 73.266
| 21.0903 | 260.185 | 47.674 | 69.072 | 51.603 | 73.276
| 21.0972 | 260.758 | 47.674 | 69.091 | 51.613 | 73.286
| 21.1042 | 260.776 | 47.687 | 69.112 | 51.618 | 73.295
| 21.1111 | 260.818 | 47.696 | 69.142 | 51.627 | 73.312
| 21.1181 | 260.485 | 47.705 | 69.163 | 51.64 | 73.326
| 21.125 | 261.444 | 47.709 | 69.184 | 51.642 | 73.342
| 21.1319 | 260.92 | 47.714 | 69.199 | 51.658 | 73.351
| 21.1389 | 258.338 | 47.717 | 69.217 | 51.66 | 73.355
| 21.1458 | 258.541 | 47.707 | 69.215 | 51.652 | 73.33
| 21.1528 | 258.723 | 47.703 | 69.212 | 51.652 | 73.311
| 21.1597 | 258.255 | 47.692 | 69.218 | 51.652 | 73.296
| 21.1667 | 258.988 | 47.695 | 69.219 | 51.656 | 73.287
| 21.1736 | 258.649 | 47.698 | 69.225 | 51.658 | 73.281
| 21.1806 | 258.736 | 47.694 | 69.232 | 51.654 | 73.274
| 21.1875 | 259.12 | 47.694 | 69.238 | 51.664 | 73.266
| 21.1944 | 259.554 | 47.699 | 69.248 | 51.666 | 73.265
| 21.2014 | 259.982 | 47.702 | 69.258 | 51.671 | 73.265
| 21.2083 | 259.146 | 47.708 | 69.276 | 51.674 | 73.265
| 21.2153 | 258.786 | 47.707 | 69.285 | 51.68 | 73.269
| 21.2222 | 261.745 | 47.713 | 69.3 | 51.686 | 73.266
| 21.2292 | 259.599 | 47.721 | 69.318 | 51.689 | 73.273
| 21.2361 | 259.59 | 47.718 | 69.326 | 51.694 | 73.271
| 21.2431 | 259.58 | 47.723 | 69.338 | 51.696 | 73.27
| 21.25 | 259.81 | 47.731 | 69.356 | 51.703 | 73.28
| 21.2569 | 259.906 | 47.734 | 69.376 | 51.711 | 73.281
| 21.2639 | 259.049 | 47.74 | 69.392 | 51.718 | 73.289
| 21.2708 | 259.377 | 47.741 | 69.399 | 51.723 | 73.296
| 21.2778 | 258.609 | 47.746 | 69.41 | 51.724 | 73.285
| 21.2847 | 257.868 | 47.738 | 69.412 | 51.723 | 73.28
| 21.2917 | 257.504 | 47.734 | 69.411 | 51.728 | 73.257
| 21.2986 | 256.784 | 47.727 | 69.412 | 51.725 | 73.244
| 21.3056 | 260.375 | 47.728 | 69.411 | 51.725 | 73.233
| 21.3125 | 259.934 | 47.745 | 69.435 | 51.736 | 73.246
| 21.3194 | 259.115 | 47.748 | 69.456 | 51.741 | 73.26
| 21.3264 | 258.289 | 47.753 | 69.467 | 51.744 | 73.258
| 21.3333 | 258.294 | 47.754 | 69.474 | 51.748 | 73.256
| 21.3403 | 257.451 | 47.756 | 69.479 | 51.75 | 73.252
| 21.3472 | 257.258 | 47.753 | 69.478 | 51.747 | 73.235
| 21.3542 | 259.743 | 47.745 | 69.474 | 51.742 | 73.221
| 21.3611 | 259.492 | 47.758 | 69.49 | 51.752 | 73.231
| 21.3681 | 257.837 | 47.761 | 69.507 | 51.756 | 73.234
| 21.375 | 258.196 | 47.763 | 69.51 | 51.761 | 73.231
| 21.3819 | 257.911 | 47.761 | 69.516 | 51.761 | 73.221
| 21.3889 | 257.524 | 47.763 | 69.523 | 51.766 | 73.211
| 21.3958 | 256.492 | 47.759 | 69.52 | 51.758 | 73.207
| 21.4028 | 256.23 | 47.747 | 69.516 | 51.758 | 73.18
| 21.4097 | 256.071 | 47.741 | 69.5 | 51.747 | 73.158
| 21.4167 | 258.359 | 47.731 | 69.49 | 51.744 | 73.127
| 21.4236 | 260.686 | 47.736 | 69.497 | 51.742 | 73.125
| 21.4306 | 257.18 | 47.75 | 69.514 | 51.754 | 73.134
| 21.4375 | 256.3 | 47.749 | 69.513 | 51.753 | 73.134
| 21.4444 | 255.275 | 47.748 | 69.514 | 51.751 | 73.122
| 21.4514 | 255.188 | 47.736 | 69.501 | 51.74 | 73.097
| 21.4583 | 254.464 | 47.728 | 69.487 | 51.737 | 73.068
| 21.4653 | 254.704 | 47.721 | 69.47 | 51.727 | 73.042
| 21.4722 | 253.534 | 47.706 | 69.455 | 51.714 | 73.008
| 21.4792 | 253.358 | 47.7 | 69.437 | 51.705 | 72.978
| 21.4861 | 258.509 | 47.689 | 69.419 | 51.698 | 72.944
| 21.4931 | 261.381 | 47.72 | 69.462 | 51.719 | 73
| 21.5 | 261.098 | 47.761 | 69.527 | 51.749 | 73.074
| 21.5069 | 261.259 | 47.789 | 69.584 | 51.78 | 73.146
| 21.5139 | 262.818 | 47.823 | 69.642 | 51.806 | 73.215
| 21.5208 | 261.828 | 47.858 | 69.702 | 51.834 | 73.288
| 21.5278 | 261.532 | 47.877 | 69.752 | 51.86 | 73.346
| 21.5347 | 261.599 | 47.894 | 69.8 | 51.877 | 73.385
| 21.5417 | 261.305 | 47.912 | 69.834 | 51.893 | 73.427
| 21.5486 | 262.933 | 47.927 | 69.873 | 51.916 | 73.462
| 21.5556 | 262.706 | 47.945 | 69.916 | 51.936 | 73.505
| 21.5625 | 259.098 | 47.966 | 69.96 | 51.961 | 73.545
| 21.5694 | 258.658 | 47.971 | 69.984 | 51.963 | 73.559
| 21.5764 | 260.54 | 47.961 | 69.988 | 51.964 | 73.556
| 21.5833 | 260.721 | 47.967 | 70.006 | 51.975 | 73.558
| 21.5903 | 259.722 | 47.978 | 70.031 | 51.991 | 73.577
| 21.5972 | 259.483 | 47.987 | 70.049 | 52.001 | 73.59
| 21.6042 | 260.276 | 47.991 | 70.076 | 52.001 | 73.603
| 21.6111 | 260.014 | 48.001 | 70.093 | 52.02 | 73.622
| 21.6181 | 260.384 | 48.01 | 70.121 | 52.024 | 73.638
| 21.625 | 259.676 | 48.018 | 70.147 | 52.033 | 73.654
| 21.6319 | 259.355 | 48.027 | 70.164 | 52.042 | 73.667
| 21.6389 | 260.39 | 48.035 | 70.183 | 52.049 | 73.678
| 21.6458 | 260.519 | 48.041 | 70.204 | 52.064 | 73.687
| 21.6528 | 260.626 | 48.051 | 70.226 | 52.071 | 73.694
| 21.6597 | 260.984 | 48.059 | 70.249 | 52.082 | 73.719
| 21.6667 | 260.296 | 48.07 | 70.281 | 52.096 | 73.735
| 21.6736 | 260.352 | 48.08 | 70.303 | 52.1 | 73.75
| 21.6806 | 260.535 | 48.089 | 70.329 | 52.119 | 73.774
| 21.6875 | 261.196 | 48.094 | 70.352 | 52.13 | 73.783
| 21.6944 | 261.308 | 48.106 | 70.369 | 52.137 | 73.798
| 21.7014 | 262.446 | 48.12 | 70.402 | 52.154 | 73.816
| 21.7083 | 262.548 | 48.133 | 70.443 | 52.167 | 73.853
| 21.7153 | 263.236 | 48.152 | 70.476 | 52.187 | 73.89
| 21.7222 | 263.292 | 48.168 | 70.52 | 52.208 | 73.931
| 21.7292 | 262.397 | 48.189 | 70.557 | 52.22 | 73.963
| 21.7361 | 262.218 | 48.199 | 70.588 | 52.239 | 73.99
| 21.7431 | 263.137 | 48.21 | 70.615 | 52.258 | 74.012
| 21.75 | 262.386 | 48.217 | 70.646 | 52.265 | 74.032
| 21.7569 | 262.524 | 48.226 | 70.68 | 52.277 | 74.053
| 21.7639 | 262.321 | 48.239 | 70.708 | 52.291 | 74.075
| 21.7708 | 262.275 | 48.25 | 70.735 | 52.304 | 74.098
| 21.7778 | 261.271 | 48.255 | 70.758 | 52.311 | 74.11
| 21.7847 | 261.449 | 48.258 | 70.776 | 52.326 | 74.115
| 21.7917 | 262.785 | 48.265 | 70.795 | 52.332 | 74.123
| 21.7986 | 263.37 | 48.273 | 70.828 | 52.345 | 74.143
| 21.8056 | 264.272 | 48.288 | 70.862 | 52.368 | 74.17
| 21.8125 | 263.888 | 48.304 | 70.899 | 52.379 | 74.208
| 21.8194 | 263.626 | 48.319 | 70.937 | 52.399 | 74.238
| 21.8264 | 263.671 | 48.335 | 70.976 | 52.414 | 74.27
| 21.8333 | 263.798 | 48.352 | 71.004 | 52.426 | 74.299
| 21.8403 | 264.653 | 48.357 | 71.035 | 52.436 | 74.317
| 21.8472 | 264.035 | 48.368 | 71.07 | 52.452 | 74.337
| 21.8542 | 265.028 | 48.385 | 71.107 | 52.468 | 74.363
| 21.8611 | 264.846 | 48.398 | 71.145 | 52.488 | 74.394
| 21.8681 | 264.945 | 48.414 | 71.185 | 52.507 | 74.435
| 21.875 | 265.149 | 48.432 | 71.23 | 52.526 | 74.467
| 21.8819 | 265.626 | 48.447 | 71.271 | 52.539 | 74.501
| 21.8889 | 262.713 | 48.459 | 71.31 | 52.554 | 74.529
| 21.8958 | 263.211 | 48.464 | 71.323 | 52.566 | 74.532
| 21.9028 | 263.844 | 48.462 | 71.345 | 52.572 | 74.53
| 21.9097 | 264.385 | 48.467 | 71.37 | 52.578 | 74.539
| 21.9167 | 263.895 | 48.472 | 71.396 | 52.589 | 74.549
| 21.9236 | 264.528 | 48.485 | 71.424 | 52.602 | 74.572
| 21.9306 | 265.092 | 48.5 | 71.456 | 52.617 | 74.595
| 21.9375 | 266.273 | 48.513 | 71.495 | 52.637 | 74.618
| 21.9444 | 267.691 | 48.533 | 71.541 | 52.656 | 74.658
| 21.9514 | 260.731 | 48.543 | 71.573 | 52.666 | 74.677
| 21.9583 | 258.224 | 48.528 | 71.56 | 52.651 | 74.641
| 21.9653 | 258.458 | 48.492 | 71.532 | 52.634 | 74.567
| 21.9722 | 259.213 | 48.471 | 71.504 | 52.62 | 74.512
| 21.9792 | 260.795 | 48.458 | 71.491 | 52.616 | 74.475
| 21.9861 | 261.566 | 48.455 | 71.496 | 52.617 | 74.459
| 21.9931 | 262.072 | 48.463 | 71.501 | 52.614 | 74.459
| 22 | 259.282 | 48.465 | 71.521 | 52.62 | 74.459
| 22.0069 | 256.71 | 48.454 | 71.509 | 52.613 | 74.427
| 22.0139 | 257.292 | 48.431 | 71.476 | 52.593 | 74.367
| 22.0208 | 257.87 | 48.416 | 71.45 | 52.577 | 74.316
| 22.0278 | 256.774 | 48.393 | 71.424 | 52.566 | 74.269
| 22.0347 | 257.039 | 48.377 | 71.4 | 52.548 | 74.223
| 22.0417 | 258.145 | 48.37 | 71.381 | 52.533 | 74.184
| 22.0486 | 257.648 | 48.362 | 71.366 | 52.525 | 74.156
| 22.0556 | 256.642 | 48.35 | 71.353 | 52.52 | 74.125
| 22.0625 | 257.016 | 48.341 | 71.332 | 52.512 | 74.089
| 22.0694 | 257.191 | 48.334 | 71.319 | 52.502 | 74.063
| 22.0764 | 257.532 | 48.331 | 71.312 | 52.492 | 74.037
| 22.0833 | 258.035 | 48.324 | 71.294 | 52.487 | 74.02
| 22.0903 | 256.852 | 48.321 | 71.273 | 52.481 | 73.996
| 22.0972 | 257.604 | 48.311 | 71.25 | 52.482 | 73.983
| 22.1042 | 257.845 | 48.311 | 71.237 | 52.472 | 73.964
| 22.1111 | 257.352 | 48.31 | 71.235 | 52.474 | 73.953
| 22.1181 | 257.683 | 48.307 | 71.229 | 52.469 | 73.935
| 22.125 | 259.002 | 48.306 | 71.228 | 52.47 | 73.921
| 22.1319 | 258.335 | 48.312 | 71.241 | 52.47 | 73.933
| 22.1389 | 258.452 | 48.317 | 71.253 | 52.474 | 73.936
| 22.1458 | 258.437 | 48.322 | 71.262 | 52.478 | 73.94
| 22.1528 | 258.206 | 48.33 | 71.271 | 52.482 | 73.939
| 22.1597 | 258.199 | 48.326 | 71.282 | 52.488 | 73.944
| 22.1667 | 258.94 | 48.332 | 71.288 | 52.488 | 73.942
| 22.1736 | 258.264 | 48.332 | 71.302 | 52.489 | 73.943
| 22.1806 | 257.905 | 48.331 | 71.307 | 52.495 | 73.943
| 22.1875 | 258.255 | 48.331 | 71.308 | 52.497 | 73.935
| 22.1944 | 257.943 | 48.331 | 71.315 | 52.498 | 73.925
| 22.2014 | 257.413 | 48.327 | 71.314 | 52.493 | 73.916
| 22.2083 | 256.688 | 48.325 | 71.314 | 52.494 | 73.907
| 22.2153 | 256.544 | 48.319 | 71.307 | 52.496 | 73.887
| 22.2222 | 259.648 | 48.315 | 71.304 | 52.486 | 73.865
| 22.2292 | 259.716 | 48.327 | 71.322 | 52.497 | 73.882
| 22.2361 | 260.505 | 48.343 | 71.351 | 52.516 | 73.913
| 22.2431 | 260.329 | 48.359 | 71.384 | 52.529 | 73.944
| 22.25 | 259.968 | 48.373 | 71.413 | 52.54 | 73.974
| 22.2569 | 258.408 | 48.381 | 71.433 | 52.551 | 73.988
| 22.2639 | 258.168 | 48.38 | 71.439 | 52.551 | 73.983
| 22.2708 | 258.187 | 48.376 | 71.44 | 52.558 | 73.975
| 22.2778 | 258.264 | 48.371 | 71.448 | 52.553 | 73.965
| 22.2847 | 256.377 | 48.367 | 71.438 | 52.554 | 73.953
| 22.2917 | 259.238 | 48.369 | 71.451 | 52.555 | 73.949
| 22.2986 | 259.732 | 48.38 | 71.468 | 52.563 | 73.965
| 22.3056 | 258.375 | 48.396 | 71.495 | 52.575 | 73.991
| 22.3125 | 257.807 | 48.4 | 71.5 | 52.579 | 73.988
| 22.3194 | 257.23 | 48.394 | 71.502 | 52.574 | 73.974
| 22.3264 | 257.324 | 48.388 | 71.495 | 52.578 | 73.957
| 22.3333 | 259.965 | 48.38 | 71.493 | 52.579 | 73.94
| 22.3403 | 259.39 | 48.397 | 71.509 | 52.582 | 73.957
| 22.3472 | 260.66 | 48.409 | 71.537 | 52.598 | 73.977
| 22.3542 | 260.654 | 48.428 | 71.571 | 52.612 | 74.017
| 22.3611 | 261.361 | 48.443 | 71.604 | 52.627 | 74.044
| 22.3681 | 260.584 | 48.455 | 71.629 | 52.636 | 74.068
| 22.375 | 259.82 | 48.461 | 71.651 | 52.647 | 74.084
| 22.3819 | 260.253 | 48.467 | 71.666 | 52.655 | 74.094
| 22.3889 | 259.902 | 48.469 | 71.687 | 52.663 | 74.103
| 22.3958 | 260.7 | 48.482 | 71.702 | 52.673 | 74.118
| 22.4028 | 259.696 | 48.489 | 71.728 | 52.679 | 74.134
| 22.4097 | 260.176 | 48.499 | 71.74 | 52.69 | 74.143
| 22.4167 | 259.569 | 48.501 | 71.761 | 52.696 | 74.153
| 22.4236 | 259.243 | 48.505 | 71.767 | 52.702 | 74.155
| 22.4306 | 257.964 | 48.501 | 71.773 | 52.701 | 74.146
| 22.4375 | 257.662 | 48.494 | 71.765 | 52.696 | 74.135
| 22.4444 | 256.747 | 48.487 | 71.764 | 52.69 | 74.111
| 22.4514 | 258.701 | 48.487 | 71.767 | 52.695 | 74.099
| 22.4583 | 259.06 | 48.492 | 71.78 | 52.694 | 74.112
| 22.4653 | 257.868 | 48.496 | 71.792 | 52.706 | 74.114
| 22.4722 | 258.185 | 48.499 | 71.794 | 52.705 | 74.107
| 22.4792 | 257.359 | 48.497 | 71.791 | 52.703 | 74.103
| 22.4861 | 257.963 | 48.495 | 71.794 | 52.706 | 74.083
| 22.4931 | 257.819 | 48.493 | 71.795 | 52.701 | 74.08
| 22.5 | 258.503 | 48.49 | 71.794 | 52.699 | 74.074
| 22.5069 | 258.676 | 48.49 | 71.797 | 52.704 | 74.068
| 22.5139 | 259.443 | 48.499 | 71.811 | 52.709 | 74.076
| 22.5208 | 259.044 | 48.505 | 71.825 | 52.713 | 74.094
| 22.5278 | 258.997 | 48.512 | 71.833 | 52.723 | 74.097
| 22.5347 | 259.965 | 48.521 | 71.849 | 52.73 | 74.11
| 22.5417 | 260.816 | 48.528 | 71.867 | 52.731 | 74.123
| 22.5486 | 260.683 | 48.543 | 71.895 | 52.747 | 74.151
| 22.5556 | 259.949 | 48.555 | 71.915 | 52.752 | 74.181
| 22.5625 | 260.331 | 48.561 | 71.937 | 52.762 | 74.199
| 22.5694 | 259.453 | 48.569 | 71.956 | 52.774 | 74.213
| 22.5764 | 260.767 | 48.573 | 71.969 | 52.78 | 74.22
| 22.6597 | 257.188 | 48.583 | 72.066 | 52.802 | 74.231
| 22.6667 | 258.328 | 48.58 | 72.062 | 52.801 | 74.211
| 22.6736 | 258.538 | 48.578 | 72.056 | 52.798 | 74.202
| 22.6806 | 257.237 | 48.579 | 72.059 | 52.798 | 74.201
| 22.6875 | 257.555 | 48.577 | 72.056 | 52.794 | 74.189
| 22.6944 | 257.803 | 48.573 | 72.051 | 52.788 | 74.172
| 22.7014 | 257.67 | 48.566 | 72.042 | 52.782 | 74.167
| 22.7083 | 258.16 | 48.573 | 72.044 | 52.783 | 74.166
| 22.7153 | 258.484 | 48.572 | 72.052 | 52.779 | 74.165
| 22.7222 | 258.701 | 48.578 | 72.056 | 52.786 | 74.166
| 22.7292 | 258.051 | 48.58 | 72.065 | 52.784 | 74.172
| 22.7361 | 258.799 | 48.579 | 72.062 | 52.784 | 74.167
| 22.7431 | 258.152 | 48.581 | 72.066 | 52.783 | 74.17
| 22.75 | 258.902 | 48.578 | 72.071 | 52.788 | 74.172
| 22.7569 | 259.257 | 48.588 | 72.079 | 52.785 | 74.171
| 22.7639 | 259.933 | 48.595 | 72.092 | 52.795 | 74.193
| 22.7708 | 259.89 | 48.605 | 72.114 | 52.8 | 74.213
| 22.7778 | 259.924 | 48.608 | 72.132 | 52.807 | 74.23
| 22.7847 | 259.26 | 48.618 | 72.138 | 52.81 | 74.239
| 22.7917 | 259.496 | 48.619 | 72.153 | 52.816 | 74.248
| 22.7986 | 259.962 | 48.628 | 72.171 | 52.821 | 74.27
| 22.8056 | 259.952 | 48.632 | 72.193 | 52.828 | 74.285
| 22.8125 | 260.621 | 48.642 | 72.203 | 52.835 | 74.302
| 22.8194 | 260.565 | 48.65 | 72.225 | 52.847 | 74.319
| 22.8264 | 257.361 | 48.651 | 72.237 | 52.849 | 74.332
| 22.8333 | 258.005 | 48.644 | 72.227 | 52.837 | 74.307
| 22.8403 | 258.974 | 48.631 | 72.219 | 52.837 | 74.285
| 22.8472 | 258.805 | 48.63 | 72.218 | 52.834 | 74.276
| 22.8542 | 258.588 | 48.63 | 72.223 | 52.831 | 74.277
| 22.8611 | 259.546 | 48.633 | 72.23 | 52.831 | 74.282
| 22.8681 | 258.798 | 48.629 | 72.235 | 52.831 | 74.286
| 22.875 | 256.303 | 48.628 | 72.228 | 52.824 | 74.262
| 22.8819 | 257.304 | 48.611 | 72.21 | 52.817 | 74.24
| 22.8889 | 257.17 | 48.602 | 72.2 | 52.808 | 74.221
| 22.8958 | 254.723 | 48.597 | 72.188 | 52.798 | 74.203
| 22.9028 | 259.113 | 48.593 | 72.181 | 52.795 | 74.191
| 22.9097 | 258.936 | 48.601 | 72.189 | 52.799 | 74.2
| 22.9167 | 259.42 | 48.606 | 72.204 | 52.799 | 74.208
| 22.9236 | 260.496 | 48.612 | 72.215 | 52.808 | 74.228
| 22.9306 | 257.721 | 48.625 | 72.24 | 52.814 | 74.252
| 22.9375 | 258.551 | 48.625 | 72.244 | 52.813 | 74.255
| 22.9444 | 259.549 | 48.623 | 72.247 | 52.815 | 74.257
| 22.9514 | 259.679 | 48.629 | 72.255 | 52.816 | 74.27
| 22.9583 | 260.721 | 48.635 | 72.274 | 52.82 | 74.284
| 22.9653 | 257.417 | 48.64 | 72.291 | 52.829 | 74.301
| 22.9722 | 256.35 | 48.635 | 72.283 | 52.825 | 74.292
| 22.9792 | 256.005 | 48.617 | 72.265 | 52.815 | 74.257
| 22.9861 | 256.487 | 48.606 | 72.247 | 52.801 | 74.235
| 22.9931 | 256.803 | 48.6 | 72.24 | 52.789 | 74.21
| 23 | 256.859 | 48.59 | 72.223 | 52.783 | 74.19
| 23.0069 | 257.794 | 48.586 | 72.216 | 52.775 | 74.179
| 23.0139 | 257.871 | 48.588 | 72.22 | 52.774 | 74.174
| 23.0208 | 257.759 | 48.583 | 72.215 | 52.773 | 74.169
| 23.0278 | 257.207 | 48.583 | 72.217 | 52.767 | 74.164
| 23.0347 | 258.288 | 48.577 | 72.216 | 52.765 | 74.16
| 23.0417 | 257.951 | 48.582 | 72.215 | 52.767 | 74.159
| 23.0486 | 257.641 | 48.582 | 72.22 | 52.765 | 74.157
| 23.0556 | 257.652 | 48.582 | 72.22 | 52.759 | 74.159
| 23.0625 | 258.255 | 48.58 | 72.222 | 52.759 | 74.162
| 23.0694 | 257.548 | 48.575 | 72.22 | 52.756 | 74.164
| 23.0764 | 257.938 | 48.58 | 72.225 | 52.757 | 74.157
| 23.0833 | 257.714 | 48.573 | 72.227 | 52.752 | 74.158
| 23.0903 | 258.13 | 48.578 | 72.228 | 52.749 | 74.157
| 23.0972 | 258.067 | 48.577 | 72.229 | 52.743 | 74.155
| 23.1042 | 258.123 | 48.578 | 72.236 | 52.744 | 74.163
| 23.1111 | 258.063 | 48.577 | 72.238 | 52.747 | 74.16
| 23.1181 | 257.983 | 48.574 | 72.239 | 52.749 | 74.164
| 23.125 | 258.265 | 48.576 | 72.241 | 52.743 | 74.16
| 23.1319 | 257.99 | 48.578 | 72.247 | 52.741 | 74.162
| 23.1389 | 257.913 | 48.577 | 72.246 | 52.742 | 74.167
| 23.1458 | 258.544 | 48.575 | 72.255 | 52.742 | 74.17
| 23.1528 | 259.016 | 48.58 | 72.263 | 52.741 | 74.18
| 23.1597 | 258.141 | 48.585 | 72.273 | 52.742 | 74.192
| 23.1667 | 258.071 | 48.584 | 72.28 | 52.743 | 74.192
| 23.1736 | 258.843 | 48.588 | 72.284 | 52.749 | 74.199
| 23.1806 | 258.467 | 48.59 | 72.294 | 52.746 | 74.204
| 23.1875 | 258.212 | 48.59 | 72.301 | 52.744 | 74.204
| 23.1944 | 257.921 | 48.59 | 72.307 | 52.739 | 74.209
| 23.2014 | 258.225 | 48.591 | 72.31 | 52.746 | 74.214
| 23.2083 | 258.395 | 48.59 | 72.317 | 52.744 | 74.216
| 23.2153 | 256.777 | 48.585 | 72.317 | 52.745 | 74.213
| 23.2222 | 256.637 | 48.577 | 72.308 | 52.736 | 74.194
| 23.2292 | 256.281 | 48.57 | 72.297 | 52.729 | 74.173
| 23.2361 | 257.53 | 48.561 | 72.285 | 52.716 | 74.157
| 23.2431 | 257.524 | 48.559 | 72.286 | 52.716 | 74.15
| 23.25 | 256.949 | 48.558 | 72.286 | 52.712 | 74.148
| 23.2569 | 257.302 | 48.557 | 72.293 | 52.711 | 74.15
| 23.2639 | 256.85 | 48.557 | 72.293 | 52.706 | 74.146
| 23.2708 | 259.3 | 48.545 | 72.281 | 52.701 | 74.127
| 23.2778 | 258.415 | 48.553 | 72.289 | 52.703 | 74.137
| 23.2847 | 257.191 | 48.557 | 72.295 | 52.7 | 74.147
| 23.2917 | 256.763 | 48.55 | 72.292 | 52.697 | 74.137
| 23.2986 | 255.48 | 48.539 | 72.281 | 52.686 | 74.118
| 23.3056 | 257.068 | 48.534 | 72.279 | 52.685 | 74.115
| 23.3125 | 259.679 | 48.544 | 72.285 | 52.683 | 74.116
| 23.3194 | 259.072 | 48.552 | 72.309 | 52.692 | 74.151
| 23.3264 | 258.534 | 48.563 | 72.327 | 52.695 | 74.173
| 23.3333 | 258.306 | 48.566 | 72.335 | 52.7 | 74.182
| 23.3403 | 257.349 | 48.563 | 72.343 | 52.702 | 74.189
| 23.3472 | 256.444 | 48.558 | 72.334 | 52.693 | 74.173
| 23.3542 | 256.976 | 48.55 | 72.329 | 52.686 | 74.159
| 23.3611 | 256.55 | 48.543 | 72.318 | 52.677 | 74.148
| 23.3681 | 256.844 | 48.537 | 72.308 | 52.675 | 74.131
| 23.375 | 257.556 | 48.533 | 72.31 | 52.668 | 74.131
| 23.3819 | 257.346 | 48.533 | 72.312 | 52.668 | 74.125
| 23.3889 | 257.952 | 48.536 | 72.307 | 52.666 | 74.128
| 23.3958 | 256.269 | 48.532 | 72.314 | 52.662 | 74.13
| 23.4028 | 256.889 | 48.528 | 72.309 | 52.658 | 74.121
| 23.4097 | 256.658 | 48.525 | 72.307 | 52.649 | 74.109
| 23.4167 | 259.486 | 48.513 | 72.302 | 52.644 | 74.094
| 23.4236 | 260.522 | 48.526 | 72.321 | 52.652 | 74.124
| 23.4306 | 259.809 | 48.541 | 72.346 | 52.659 | 74.149
| 23.4375 | 259.555 | 48.551 | 72.37 | 52.667 | 74.184
| 23.4444 | 259.629 | 48.561 | 72.391 | 52.674 | 74.203
| 23.4514 | 259.23 | 48.568 | 72.407 | 52.68 | 74.221
| 23.4583 | 259.195 | 48.567 | 72.417 | 52.68 | 74.232
| 23.4653 | 259.074 | 48.569 | 72.428 | 52.682 | 74.241
| 23.4722 | 258.81 | 48.57 | 72.437 | 52.684 | 74.251
| 23.4792 | 258.922 | 48.573 | 72.444 | 52.684 | 74.254
| 23.4861 | 259.246 | 48.571 | 72.456 | 52.685 | 74.261
| 23.4931 | 259.48 | 48.57 | 72.463 | 52.682 | 74.266
| 23.5 | 258.795 | 48.573 | 72.473 | 52.69 | 74.271
| 23.5069 | 260.073 | 48.578 | 72.49 | 52.688 | 74.285
| 23.5139 | 260.16 | 48.586 | 72.501 | 52.694 | 74.303
| 23.5208 | 260.751 | 48.596 | 72.525 | 52.705 | 74.33
| 23.5278 | 260.698 | 48.604 | 72.551 | 52.711 | 74.356
| 23.5347 | 260.74 | 48.62 | 72.575 | 52.726 | 74.389
| 23.5417 | 260.968 | 48.622 | 72.598 | 52.728 | 74.41
| 23.5486 | 260.674 | 48.628 | 72.621 | 52.736 | 74.433
| 23.5556 | 260.378 | 48.633 | 72.641 | 52.739 | 74.443
| 23.5625 | 260.355 | 48.637 | 72.648 | 52.744 | 74.453
| 23.5694 | 260.395 | 48.641 | 72.664 | 52.744 | 74.467
| 23.5764 | 261.345 | 48.641 | 72.686 | 52.753 | 74.484
| 23.5833 | 262.196 | 48.656 | 72.711 | 52.76 | 74.506
| 23.5903 | 261.484 | 48.663 | 72.739 | 52.768 | 74.533
| 23.5972 | 261.564 | 48.671 | 72.766 | 52.775 | 74.551
| 23.6042 | 261.391 | 48.678 | 72.788 | 52.782 | 74.578
| 23.6111 | 261.105 | 48.681 | 72.81 | 52.787 | 74.596
| 23.6181 | 261.009 | 48.688 | 72.83 | 52.793 | 74.612
| 23.625 | 261.354 | 48.69 | 72.845 | 52.792 | 74.621
| 23.6319 | 261.43 | 48.695 | 72.861 | 52.8 | 74.63
| 23.6389 | 261.431 | 48.701 | 72.882 | 52.803 | 74.649
| 23.6458 | 258.421 | 48.696 | 72.891 | 52.806 | 74.652
| 23.6528 | 258.133 | 48.682 | 72.875 | 52.794 | 74.618
| 23.6597 | 258.807 | 48.667 | 72.866 | 52.781 | 74.592
| 23.6667 | 260.182 | 48.661 | 72.865 | 52.778 | 74.581
| 23.6736 | 259.739 | 48.665 | 72.878 | 52.779 | 74.588
| 23.6806 | 259.598 | 48.662 | 72.882 | 52.773 | 74.591
| 23.6875 | 259.078 | 48.658 | 72.88 | 52.767 | 74.581
| 23.6944 | 258.928 | 48.657 | 72.884 | 52.765 | 74.569
| 23.7014 | 259.332 | 48.657 | 72.881 | 52.761 | 74.567
| 23.7083 | 259.921 | 48.65 | 72.89 | 52.756 | 74.568
| 23.7153 | 260.455 | 48.656 | 72.899 | 52.764 | 74.573
| 23.7222 | 260.376 | 48.659 | 72.92 | 52.76 | 74.593
| 23.7292 | 260.307 | 48.667 | 72.928 | 52.76 | 74.6
| 23.7361 | 260.318 | 48.667 | 72.946 | 52.763 | 74.612
| 23.7431 | 260.327 | 48.673 | 72.955 | 52.766 | 74.62
| 23.75 | 260.342 | 48.673 | 72.964 | 52.765 | 74.625
| 23.7569 | 260.107 | 48.676 | 72.976 | 52.765 | 74.632
| 23.7639 | 260.263 | 48.671 | 72.981 | 52.763 | 74.635
| 23.7708 | 260.421 | 48.673 | 72.993 | 52.76 | 74.64
| 23.7778 | 260.301 | 48.674 | 73.002 | 52.765 | 74.638
| 23.7847 | 259.907 | 48.67 | 73.004 | 52.756 | 74.642
| 23.7917 | 259.708 | 48.667 | 73.011 | 52.755 | 74.638
| 23.7986 | 260.057 | 48.664 | 73.011 | 52.752 | 74.634
| 23.8056 | 260.739 | 48.664 | 73.025 | 52.755 | 74.643
| 23.8125 | 260.94 | 48.672 | 73.032 | 52.757 | 74.656
| 23.8194 | 260.899 | 48.677 | 73.052 | 52.761 | 74.669
| 23.8264 | 260.948 | 48.685 | 73.068 | 52.762 | 74.687
| 23.8333 | 261.066 | 48.685 | 73.086 | 52.769 | 74.704
| 23.8403 | 258.527 | 48.677 | 73.092 | 52.763 | 74.7
| 23.8472 | 259.062 | 48.665 | 73.078 | 52.752 | 74.672
| 23.8542 | 259.191 | 48.657 | 73.075 | 52.745 | 74.658
| 23.8611 | 256.549 | 48.648 | 73.066 | 52.741 | 74.643
| 23.8681 | 257.081 | 48.635 | 73.045 | 52.717 | 74.608
| 23.875 | 257.437 | 48.616 | 73.023 | 52.702 | 74.573
| 23.8819 | 256.801 | 48.597 | 73.004 | 52.69 | 74.543
| 23.8889 | 257.391 | 48.586 | 72.982 | 52.675 | 74.511
| 23.8958 | 255.211 | 48.575 | 72.963 | 52.665 | 74.484
| 23.9028 | 259.259 | 48.568 | 72.954 | 52.656 | 74.469
| 23.9097 | 259.087 | 48.568 | 72.953 | 52.653 | 74.473
| 23.9167 | 259.898 | 48.576 | 72.963 | 52.654 | 74.478
| 23.9236 | 260.329 | 48.583 | 72.98 | 52.652 | 74.495
| 23.9306 | 259.977 | 48.59 | 72.989 | 52.653 | 74.511
| 23.9375 | 257.917 | 48.594 | 73.007 | 52.659 | 74.529
| 23.9444 | 257.886 | 48.583 | 73.001 | 52.653 | 74.518
| 23.9514 | 258.145 | 48.579 | 72.992 | 52.644 | 74.501
| 23.9583 | 259.62 | 48.571 | 72.985 | 52.633 | 74.491
| 23.9653 | 259.158 | 48.569 | 72.987 | 52.632 | 74.494
| 23.9722 | 260.414 | 48.573 | 72.997 | 52.633 | 74.502
| 23.9792 | 260.286 | 48.577 | 73.012 | 52.63 | 74.515
| 23.9861 | 260.748 | 48.584 | 73.03 | 52.639 | 74.539
| 23.9931 | 260.824 | 48.588 | 73.045 | 52.65 | 74.555
| 24 | 258.251 | 48.59 | 73.055 | 52.64 | 74.561
| 24.0069 | 257.357 | 48.575 | 73.038 | 52.627 | 74.536
| 24.0139 | 257.783 | 48.561 | 73.028 | 52.616 | 74.51
| 24.0208 | 258.794 | 48.556 | 73.014 | 52.607 | 74.499
| 24.0278 | 258.733 | 48.547 | 73.01 | 52.602 | 74.487
| 24.0347 | 258.575 | 48.544 | 73.007 | 52.594 | 74.479
| 24.0417 | 258.846 | 48.537 | 73.007 | 52.586 | 74.469
| 24.0486 | 258.463 | 48.535 | 73.006 | 52.582 | 74.465
| 24.0556 | 258.856 | 48.534 | 73.007 | 52.577 | 74.46
| 24.0625 | 258.452 | 48.533 | 73.005 | 52.58 | 74.461
| 24.0694 | 258.93 | 48.531 | 73.008 | 52.572 | 74.457
| 24.0764 | 259.01 | 48.528 | 73.011 | 52.572 | 74.459
| 24.0833 | 259.442 | 48.528 | 73.018 | 52.573 | 74.464
| 24.0903 | 259.539 | 48.532 | 73.022 | 52.568 | 74.467
| 24.0972 | 259.85 | 48.533 | 73.033 | 52.57 | 74.48
| 24.1042 | 259.793 | 48.534 | 73.046 | 52.569 | 74.489
| 24.1111 | 259.332 | 48.538 | 73.055 | 52.566 | 74.499
| 24.1181 | 259.357 | 48.537 | 73.061 | 52.568 | 74.508
| 24.125 | 259.593 | 48.538 | 73.073 | 52.564 | 74.508
| 24.1319 | 260.148 | 48.537 | 73.079 | 52.564 | 74.509
| 24.1389 | 259.507 | 48.539 | 73.086 | 52.561 | 74.516
| 24.1458 | 260.214 | 48.537 | 73.093 | 52.564 | 74.525
| 24.1528 | 259.866 | 48.537 | 73.102 | 52.565 | 74.532
| 24.1597 | 260.043 | 48.539 | 73.113 | 52.564 | 74.535
| 24.1667 | 259.482 | 48.54 | 73.119 | 52.566 | 74.539
| 24.1736 | 259.416 | 48.539 | 73.124 | 52.563 | 74.542
| 24.1806 | 259.892 | 48.535 | 73.134 | 52.568 | 74.546
| 24.1875 | 259.068 | 48.535 | 73.135 | 52.559 | 74.545
| 24.1944 | 259.211 | 48.531 | 73.139 | 52.556 | 74.539
| 24.2014 | 258.969 | 48.528 | 73.137 | 52.547 | 74.534
| 24.2083 | 258.293 | 48.523 | 73.141 | 52.542 | 74.529
| 24.2153 | 258.195 | 48.517 | 73.139 | 52.54 | 74.525
| 24.2222 | 259.589 | 48.511 | 73.133 | 52.533 | 74.506
| 24.2292 | 260.061 | 48.514 | 73.14 | 52.527 | 74.513
| 24.2361 | 259.69 | 48.514 | 73.147 | 52.527 | 74.518
| 24.2431 | 258.604 | 48.507 | 73.149 | 52.524 | 74.512
| 24.25 | 259.513 | 48.5 | 73.15 | 52.519 | 74.509
| 24.2569 | 257.371 | 48.505 | 73.15 | 52.514 | 74.505
| 24.2639 | 258.67 | 48.487 | 73.131 | 52.505 | 74.478
| 24.2708 | 257.919 | 48.483 | 73.129 | 52.491 | 74.467
| 24.2778 | 256.696 | 48.472 | 73.12 | 52.481 | 74.45
| 24.2847 | 256.911 | 48.461 | 73.102 | 52.473 | 74.424
| 24.2917 | 256.375 | 48.452 | 73.092 | 52.464 | 74.405
| 24.2986 | 259.294 | 48.444 | 73.079 | 52.448 | 74.383
| 24.3056 | 257.82 | 48.451 | 73.085 | 52.449 | 74.391
| 24.3125 | 259.231 | 48.446 | 73.083 | 52.446 | 74.387
| 24.3194 | 257.706 | 48.446 | 73.09 | 52.442 | 74.391
| 24.3264 | 258.273 | 48.442 | 73.088 | 52.442 | 74.388
| 24.3333 | 257.741 | 48.436 | 73.082 | 52.435 | 74.377
| 24.3403 | 256.446 | 48.425 | 73.073 | 52.423 | 74.364
| 24.3472 | 256.034 | 48.416 | 73.058 | 52.413 | 74.336
| 24.3542 | 256.288 | 48.402 | 73.035 | 52.394 | 74.306
| 24.3611 | 255.893 | 48.385 | 73.016 | 52.38 | 74.276
| 24.3681 | 258.364 | 48.383 | 73.009 | 52.374 | 74.271
| 24.375 | 258.136 | 48.39 | 73.019 | 52.381 | 74.282
| 24.3819 | 259.843 | 48.397 | 73.026 | 52.378 | 74.293
| 24.3889 | 258.559 | 48.399 | 73.039 | 52.375 | 74.311
| 24.3958 | 257.723 | 48.403 | 73.048 | 52.377 | 74.319
| 24.4028 | 258.242 | 48.4 | 73.053 | 52.378 | 74.32
| 24.4097 | 260.066 | 48.405 | 73.055 | 52.375 | 74.326
| 24.4167 | 259.997 | 48.41 | 73.069 | 52.378 | 74.345
| 24.4236 | 260.057 | 48.416 | 73.087 | 52.38 | 74.364
| 24.4306 | 259.417 | 48.417 | 73.104 | 52.38 | 74.374
| 24.4375 | 259.148 | 48.42 | 73.113 | 52.382 | 74.386
| 24.4444 | 259.04 | 48.421 | 73.12 | 52.382 | 74.396
| 24.4514 | 259.109 | 48.42 | 73.126 | 52.378 | 74.398
| 24.4583 | 258.173 | 48.419 | 73.131 | 52.377 | 74.401
| 24.4653 | 258.938 | 48.411 | 73.132 | 52.377 | 74.395
| 24.4722 | 257.254 | 48.405 | 73.132 | 52.365 | 74.385
| 24.4792 | 258.21 | 48.397 | 73.122 | 52.359 | 74.372
| 24.4861 | 257.62 | 48.391 | 73.116 | 52.357 | 74.362
| 24.4931 | 257.049 | 48.386 | 73.111 | 52.343 | 74.347
| 24.5 | 257.691 | 48.377 | 73.105 | 52.338 | 74.332
| 24.5069 | 258.526 | 48.373 | 73.104 | 52.335 | 74.326
| 24.5139 | 258.633 | 48.372 | 73.103 | 52.332 | 74.33
| 24.5208 | 258.719 | 48.377 | 73.11 | 52.329 | 74.332
| 24.5278 | 259.313 | 48.375 | 73.118 | 52.328 | 74.333
| 24.5347 | 258.87 | 48.377 | 73.125 | 52.326 | 74.342
| 24.5417 | 259.037 | 48.379 | 73.132 | 52.327 | 74.351
| 24.5486 | 259.254 | 48.377 | 73.139 | 52.325 | 74.358
| 24.5556 | 257.46 | 48.374 | 73.137 | 52.316 | 74.347
| 24.5625 | 257.19 | 48.363 | 73.125 | 52.302 | 74.327
| 24.5694 | 257.755 | 48.353 | 73.121 | 52.299 | 74.309
| 24.5764 | 258.077 | 48.35 | 73.115 | 52.293 | 74.305
| 24.5833 | 258.328 | 48.348 | 73.119 | 52.293 | 74.305
| 24.5903 | 258.341 | 48.353 | 73.125 | 52.29 | 74.313
| 24.5972 | 258.006 | 48.352 | 73.132 | 52.292 | 74.314
| 24.6042 | 258.336 | 48.346 | 73.129 | 52.281 | 74.308
| 24.6111 | 257.857 | 48.341 | 73.124 | 52.276 | 74.304
| 24.6181 | 258.645 | 48.335 | 73.124 | 52.27 | 74.291
| 24.625 | 258.36 | 48.338 | 73.125 | 52.267 | 74.296
| 24.6319 | 258.576 | 48.335 | 73.129 | 52.263 | 74.302
| 24.6389 | 258.484 | 48.333 | 73.127 | 52.264 | 74.301
| 24.6458 | 258.058 | 48.332 | 73.132 | 52.259 | 74.303
| 24.6528 | 258.166 | 48.333 | 73.131 | 52.259 | 74.303
| 24.6597 | 259.034 | 48.328 | 73.136 | 52.26 | 74.303
| 24.6667 | 259.465 | 48.335 | 73.145 | 52.252 | 74.315
| 24.6736 | 259.378 | 48.332 | 73.158 | 52.251 | 74.329
| 24.6806 | 259.412 | 48.342 | 73.173 | 52.258 | 74.338
| 24.6875 | 258.75 | 48.344 | 73.183 | 52.26 | 74.351
| 24.6944 | 259.461 | 48.344 | 73.187 | 52.261 | 74.362
| 24.7014 | 259.015 | 48.349 | 73.207 | 52.264 | 74.37
| 24.7083 | 258.946 | 48.35 | 73.212 | 52.264 | 74.376
| 24.7153 | 259.405 | 48.345 | 73.221 | 52.262 | 74.384
| 24.7222 | 259.608 | 48.349 | 73.236 | 52.26 | 74.392
| 24.7292 | 259.771 | 48.35 | 73.247 | 52.266 | 74.402
| 24.7361 | 259.913 | 48.355 | 73.257 | 52.266 | 74.411
| 24.7431 | 259.633 | 48.353 | 73.272 | 52.262 | 74.419
| 24.75 | 259.882 | 48.357 | 73.282 | 52.27 | 74.428
| 24.7569 | 258.12 | 48.36 | 73.295 | 52.265 | 74.437
| 24.7639 | 257.879 | 48.347 | 73.288 | 52.259 | 74.419
| 24.7708 | 257.792 | 48.338 | 73.286 | 52.243 | 74.399
| 24.7778 | 257.439 | 48.326 | 73.272 | 52.237 | 74.383
| 24.7847 | 256.754 | 48.315 | 73.263 | 52.225 | 74.365
| 24.7917 | 257.61 | 48.307 | 73.256 | 52.209 | 74.344
| 24.7986 | 258.346 | 48.305 | 73.249 | 52.211 | 74.334
| 24.8056 | 258.176 | 48.301 | 73.247 | 52.197 | 74.325
| 24.8125 | 258.663 | 48.3 | 73.251 | 52.197 | 74.324
| 24.8194 | 258.904 | 48.295 | 73.258 | 52.197 | 74.329
| 24.8264 | 258.382 | 48.296 | 73.263 | 52.199 | 74.33
| 24.8333 | 259.129 | 48.301 | 73.27 | 52.195 | 74.33
| 24.8403 | 259.326 | 48.3 | 73.279 | 52.194 | 74.344
| 24.8472 | 259.58 | 48.308 | 73.29 | 52.192 | 74.351
| 24.8542 | 259.192 | 48.306 | 73.304 | 52.197 | 74.367
| 24.8611 | 259.648 | 48.31 | 73.319 | 52.197 | 74.373
| 24.8681 | 259.413 | 48.312 | 73.331 | 52.206 | 74.387
| 24.875 | 260.169 | 48.318 | 73.342 | 52.21 | 74.4
| 24.8819 | 260.055 | 48.321 | 73.36 | 52.21 | 74.412
| 24.8889 | 260.248 | 48.325 | 73.378 | 52.219 | 74.426
| 24.8958 | 260.45 | 48.33 | 73.39 | 52.224 | 74.441
| 24.9028 | 260.112 | 48.334 | 73.409 | 52.224 | 74.451
| 24.9097 | 258.794 | 48.334 | 73.418 | 52.226 | 74.458
| 24.9167 | 259.009 | 48.324 | 73.418 | 52.218 | 74.447
| 24.9236 | 260.238 | 48.321 | 73.424 | 52.221 | 74.446
| 24.9306 | 260.512 | 48.33 | 73.435 | 52.226 | 74.461
| 24.9375 | 257.983 | 48.336 | 73.458 | 52.228 | 74.479
| 24.9444 | 258.602 | 48.325 | 73.461 | 52.221 | 74.471
| 24.9514 | 259.791 | 48.322 | 73.462 | 52.217 | 74.465
| 24.9583 | 260.092 | 48.325 | 73.475 | 52.227 | 74.471
| 24.9653 | 260.974 | 48.327 | 73.488 | 52.226 | 74.482
| 24.9722 | 258.171 | 48.337 | 73.507 | 52.227 | 74.506
| 24.9792 | 259.153 | 48.33 | 73.509 | 52.221 | 74.49
| 24.9861 | 258.834 | 48.322 | 73.502 | 52.216 | 74.482
| 24.9931 | 259.56 | 48.321 | 73.507 | 52.213 | 74.474
| 25 | 259.785 | 48.32 | 73.513 | 52.213 | 74.478
| 25.0069 | 259.958 | 48.324 | 73.526 | 52.221 | 74.489
| 25.0139 | 260.286 | 48.332 | 73.539 | 52.217 | 74.499
| 25.0208 | 261.153 | 48.329 | 73.556 | 52.222 | 74.512
| 25.0278 | 260.533 | 48.337 | 73.578 | 52.222 | 74.523
| 25.0347 | 260.459 | 48.341 | 73.59 | 52.229 | 74.535
| 25.0417 | 261.399 | 48.343 | 73.608 | 52.23 | 74.551
| 25.0486 | 260.989 | 48.352 | 73.627 | 52.24 | 74.567
| 25.0556 | 258.184 | 48.355 | 73.644 | 52.238 | 74.578
| 25.0625 | 258.369 | 48.343 | 73.634 | 52.228 | 74.564
| 25.0694 | 258.774 | 48.33 | 73.629 | 52.219 | 74.539
| 25.0764 | 258.536 | 48.323 | 73.619 | 52.213 | 74.522
| 25.0833 | 259.028 | 48.319 | 73.622 | 52.207 | 74.514
| 25.0903 | 259.071 | 48.31 | 73.626 | 52.206 | 74.51
| 25.0972 | 257.079 | 48.313 | 73.621 | 52.203 | 74.503
| 25.1042 | 256.883 | 48.299 | 73.615 | 52.193 | 74.476
| 25.1111 | 256.949 | 48.284 | 73.584 | 52.174 | 74.44
| 25.1181 | 257.368 | 48.27 | 73.573 | 52.163 | 74.414
| 25.125 | 256.593 | 48.261 | 73.556 | 52.154 | 74.389
| 25.1319 | 257.003 | 48.254 | 73.542 | 52.141 | 74.366
| 25.1389 | 257.05 | 48.242 | 73.529 | 52.129 | 74.343
| 25.1458 | 256.807 | 48.232 | 73.513 | 52.124 | 74.326
| 25.1528 | 256.915 | 48.226 | 73.501 | 52.109 | 74.302
| 25.1597 | 256.717 | 48.221 | 73.491 | 52.106 | 74.281
| 25.1667 | 256.514 | 48.211 | 73.482 | 52.094 | 74.271
| 25.1736 | 256.491 | 48.205 | 73.474 | 52.096 | 74.254
| 25.1806 | 256.725 | 48.198 | 73.461 | 52.076 | 74.234
| 25.1875 | 256.486 | 48.189 | 73.455 | 52.073 | 74.221
| 25.1944 | 256.833 | 48.183 | 73.446 | 52.067 | 74.208
| 25.2014 | 256.963 | 48.181 | 73.442 | 52.056 | 74.193
| 25.2083 | 257.002 | 48.179 | 73.431 | 52.052 | 74.186
| 25.2153 | 257.186 | 48.172 | 73.427 | 52.043 | 74.179
| 25.2222 | 258.432 | 48.169 | 73.425 | 52.041 | 74.176
| 25.2292 | 259.175 | 48.178 | 73.439 | 52.045 | 74.19
| 25.2361 | 259.137 | 48.186 | 73.456 | 52.05 | 74.211
| 25.2431 | 259.078 | 48.198 | 73.475 | 52.059 | 74.233
| 25.25 | 260.256 | 48.192 | 73.479 | 52.051 | 74.234
| 25.2569 | 260.378 | 48.204 | 73.498 | 52.059 | 74.259
| 25.2639 | 260.011 | 48.214 | 73.524 | 52.073 | 74.29
| 25.2708 | 260.339 | 48.223 | 73.545 | 52.077 | 74.305
| 25.2778 | 259.295 | 48.222 | 73.554 | 52.078 | 74.316
| 25.2847 | 259.275 | 48.228 | 73.567 | 52.083 | 74.329
| 25.2917 | 259.664 | 48.226 | 73.585 | 52.08 | 74.336
| 25.2986 | 259.392 | 48.232 | 73.587 | 52.085 | 74.347
| 25.3056 | 258.88 | 48.228 | 73.598 | 52.084 | 74.347
| 25.3125 | 258.337 | 48.227 | 73.605 | 52.079 | 74.339
| 25.3194 | 258.123 | 48.218 | 73.601 | 52.08 | 74.332
| 25.3264 | 257.948 | 48.213 | 73.596 | 52.071 | 74.327
| 25.3333 | 257.557 | 48.206 | 73.597 | 52.07 | 74.315
| 25.3403 | 257.395 | 48.196 | 73.59 | 52.057 | 74.304
| 25.3472 | 257.36 | 48.19 | 73.587 | 52.049 | 74.286
| 25.3542 | 257.443 | 48.183 | 73.577 | 52.04 | 74.272
| 25.3611 | 256.971 | 48.18 | 73.574 | 52.038 | 74.26
| 25.3681 | 256.874 | 48.17 | 73.56 | 52.029 | 74.239
| 25.375 | 259.505 | 48.166 | 73.558 | 52.026 | 74.234
| 25.3819 | 259.153 | 48.177 | 73.579 | 52.037 | 74.253
| 25.3889 | 259.355 | 48.183 | 73.595 | 52.037 | 74.265
| 25.3958 | 259.01 | 48.189 | 73.602 | 52.037 | 74.277
| 25.4028 | 258.4 | 48.189 | 73.616 | 52.04 | 74.287
| 25.4097 | 257.471 | 48.188 | 73.611 | 52.035 | 74.28
| 25.4167 | 257.679 | 48.182 | 73.614 | 52.023 | 74.27
| 25.4236 | 256.499 | 48.172 | 73.605 | 52.017 | 74.255
| 25.4306 | 255.973 | 48.162 | 73.593 | 52.005 | 74.238
| 25.4375 | 255.462 | 48.15 | 73.577 | 51.996 | 74.212
| 25.4444 | 254.791 | 48.131 | 73.559 | 51.986 | 74.186
| 25.4514 | 255.097 | 48.117 | 73.539 | 51.965 | 74.149
| 25.4583 | 256.628 | 48.108 | 73.517 | 51.954 | 74.119
| 25.4653 | 256.058 | 48.099 | 73.507 | 51.949 | 74.106
| 25.4722 | 256.172 | 48.102 | 73.502 | 51.939 | 74.101
| 25.4792 | 255.707 | 48.095 | 73.498 | 51.941 | 74.098
| 25.4861 | 255.029 | 48.094 | 73.488 | 51.924 | 74.081
| 25.4931 | 254.807 | 48.084 | 73.474 | 51.917 | 74.062
| 25.5 | 254.818 | 48.071 | 73.457 | 51.9 | 74.034
| 25.5069 | 254.402 | 48.06 | 73.435 | 51.889 | 74.009
| 25.5139 | 254.896 | 48.045 | 73.42 | 51.874 | 73.984
| 25.5208 | 253.604 | 48.037 | 73.397 | 51.866 | 73.959
| 25.5278 | 252.921 | 48.024 | 73.376 | 51.851 | 73.928
| 25.5347 | 253.493 | 48.009 | 73.345 | 51.831 | 73.899
| 25.5417 | 253.277 | 47.995 | 73.321 | 51.814 | 73.865
| 25.5486 | 252.915 | 47.985 | 73.295 | 51.804 | 73.841
| 25.5556 | 258.613 | 47.985 | 73.296 | 51.801 | 73.849
| 25.5625 | 258.372 | 48.017 | 73.333 | 51.818 | 73.898
| 25.5694 | 259.316 | 48.035 | 73.366 | 51.829 | 73.947
| 25.5764 | 258.605 | 48.051 | 73.397 | 51.836 | 73.999
| 25.5833 | 258.79 | 48.068 | 73.425 | 51.848 | 74.027
| 25.5903 | 258.56 | 48.08 | 73.457 | 51.86 | 74.068
| 25.5972 | 259.26 | 48.09 | 73.482 | 51.87 | 74.099
| 25.6042 | 259.368 | 48.101 | 73.506 | 51.876 | 74.129
| 25.6111 | 259.634 | 48.1 | 73.526 | 51.878 | 74.154
| 25.6181 | 259.198 | 48.11 | 73.551 | 51.884 | 74.18
| 25.625 | 259.303 | 48.119 | 73.571 | 51.889 | 74.201
| 25.6319 | 259.188 | 48.123 | 73.596 | 51.898 | 74.226
| 25.6389 | 258.812 | 48.132 | 73.616 | 51.903 | 74.247
| 25.6458 | 259.651 | 48.138 | 73.635 | 51.908 | 74.264
| 25.6528 | 259.807 | 48.139 | 73.659 | 51.915 | 74.28
| 25.6597 | 260.142 | 48.147 | 73.677 | 51.92 | 74.303
| 25.6667 | 260.276 | 48.151 | 73.696 | 51.923 | 74.324
| 25.6736 | 258.878 | 48.159 | 73.719 | 51.927 | 74.344
| 25.6806 | 259.078 | 48.162 | 73.737 | 51.934 | 74.358
| 25.6875 | 259.387 | 48.161 | 73.753 | 51.928 | 74.366
| 25.6944 | 259.461 | 48.168 | 73.771 | 51.927 | 74.38
| 25.7014 | 258.967 | 48.168 | 73.786 | 51.94 | 74.394
| 25.7083 | 259.404 | 48.172 | 73.803 | 51.942 | 74.407
| 25.7153 | 259.647 | 48.177 | 73.823 | 51.95 | 74.426
| 25.7222 | 259.465 | 48.183 | 73.84 | 51.956 | 74.433
| 25.7292 | 260.329 | 48.188 | 73.864 | 51.96 | 74.451
| 25.7361 | 259.71 | 48.192 | 73.886 | 51.965 | 74.469
| 25.7431 | 259.43 | 48.197 | 73.908 | 51.968 | 74.49
| 25.75 | 259.947 | 48.202 | 73.925 | 51.968 | 74.502
| 25.7569 | 258.912 | 48.202 | 73.94 | 51.972 | 74.514
| 25.7639 | 259.269 | 48.206 | 73.958 | 51.974 | 74.517
| 25.7708 | 259.004 | 48.206 | 73.967 | 51.972 | 74.526
| 25.7778 | 259.42 | 48.207 | 73.981 | 51.975 | 74.537
| 25.7847 | 259.95 | 48.212 | 74.004 | 51.981 | 74.547
| 25.7917 | 259.101 | 48.216 | 74.018 | 51.981 | 74.555
| 25.7986 | 258.753 | 48.216 | 74.036 | 51.982 | 74.566
| 25.8056 | 259.552 | 48.221 | 74.045 | 51.984 | 74.577
| 25.8125 | 259.535 | 48.221 | 74.066 | 51.987 | 74.583
| 25.8194 | 259.664 | 48.224 | 74.083 | 51.991 | 74.593
| 25.8264 | 259.634 | 48.223 | 74.102 | 51.995 | 74.607
| 25.8333 | 259.978 | 48.23 | 74.121 | 52 | 74.623
| 25.8403 | 261.062 | 48.239 | 74.146 | 52.006 | 74.641
| 25.8472 | 261.484 | 48.25 | 74.17 | 52.014 | 74.662
| 25.8542 | 261.724 | 48.261 | 74.201 | 52.025 | 74.693
| 25.8611 | 261.926 | 48.274 | 74.234 | 52.039 | 74.718
| 25.8681 | 262.364 | 48.283 | 74.266 | 52.046 | 74.748
| 25.875 | 262.908 | 48.289 | 74.3 | 52.052 | 74.775
| 25.8819 | 262.989 | 48.303 | 74.332 | 52.072 | 74.805
| 25.8889 | 263.064 | 48.309 | 74.364 | 52.083 | 74.831
| 25.8958 | 263.273 | 48.325 | 74.391 | 52.086 | 74.851
| 25.9028 | 262.637 | 48.324 | 74.42 | 52.098 | 74.865
| 25.9097 | 261.828 | 48.322 | 74.428 | 52.097 | 74.864
| 25.9167 | 262.643 | 48.322 | 74.446 | 52.104 | 74.866
| 25.9236 | 262.844 | 48.326 | 74.465 | 52.108 | 74.881
| 25.9306 | 263.029 | 48.331 | 74.492 | 52.118 | 74.899
| 25.9375 | 263.523 | 48.343 | 74.525 | 52.129 | 74.925
| 25.9444 | 264.094 | 48.353 | 74.555 | 52.143 | 74.951
| 25.9514 | 264.316 | 48.366 | 74.593 | 52.158 | 74.983
| 25.9583 | 242.372 | 48.188 | 74.373 | 52.01 | 74.682
| 25.9653 | 258.263 | 47.968 | 73.983 | 51.836 | 74.126
| 25.9722 | 258.495 | 47.994 | 74.01 | 51.847 | 74.152
| 25.9792 | 258.607 | 48.03 | 74.039 | 51.871 | 74.196
| 25.9861 | 258.745 | 48.063 | 74.069 | 51.885 | 74.235
| 25.9931 | 259.547 | 48.084 | 74.091 | 51.895 | 74.273
| 26 | 259.466 | 48.099 | 74.118 | 51.906 | 74.307
| 26.0069 | 259.866 | 48.113 | 74.14 | 51.912 | 74.335
| 26.0139 | 260.223 | 48.128 | 74.164 | 51.919 | 74.368
| 26.0208 | 261.052 | 48.142 | 74.192 | 51.931 | 74.397
| 26.0278 | 260.749 | 48.155 | 74.22 | 51.943 | 74.429
| 26.0347 | 260.909 | 48.168 | 74.244 | 51.949 | 74.451
| 26.0417 | 261.545 | 48.175 | 74.273 | 51.969 | 74.48
| 26.0486 | 257.914 | 48.173 | 74.283 | 51.97 | 74.487
| 26.0556 | 258.359 | 48.164 | 74.278 | 51.961 | 74.47
| 26.0625 | 258.805 | 48.157 | 74.28 | 51.961 | 74.46
| 26.0694 | 259.012 | 48.159 | 74.287 | 51.951 | 74.452
| 26.0764 | 258.225 | 48.153 | 74.295 | 51.959 | 74.45
| 26.0833 | 259.244 | 48.152 | 74.302 | 51.963 | 74.45
| 26.0903 | 259.281 | 48.152 | 74.312 | 51.962 | 74.451
| 26.0972 | 259.096 | 48.155 | 74.328 | 51.962 | 74.45
| 26.1042 | 258.662 | 48.154 | 74.338 | 51.967 | 74.455
| 26.1111 | 259.266 | 48.156 | 74.35 | 51.97 | 74.456
| 26.1181 | 258.95 | 48.157 | 74.365 | 51.971 | 74.458
| 26.125 | 259.077 | 48.163 | 74.377 | 51.976 | 74.462
| 26.1319 | 258.825 | 48.162 | 74.386 | 51.978 | 74.464
| 26.1389 | 258.83 | 48.164 | 74.401 | 51.986 | 74.462
| 26.1458 | 258.793 | 48.161 | 74.412 | 51.982 | 74.464
| 26.1528 | 259.304 | 48.164 | 74.424 | 51.989 | 74.459
| 26.1597 | 258.569 | 48.169 | 74.435 | 51.996 | 74.466
| 26.1667 | 259.551 | 48.172 | 74.45 | 51.997 | 74.465
| 26.1736 | 258.75 | 48.167 | 74.463 | 52.009 | 74.467
| 26.1806 | 259.931 | 48.171 | 74.48 | 52.004 | 74.469
| 26.1875 | 259.671 | 48.179 | 74.493 | 52.02 | 74.479
| 26.1944 | 260.25 | 48.185 | 74.513 | 52.022 | 74.489
| 26.2014 | 259.898 | 48.192 | 74.533 | 52.032 | 74.497
| 26.2083 | 259.757 | 48.197 | 74.553 | 52.046 | 74.509
| 26.2153 | 258.591 | 48.199 | 74.566 | 52.047 | 74.514
| 26.2222 | 258.065 | 48.199 | 74.576 | 52.047 | 74.515
| 26.2292 | 258.855 | 48.194 | 74.583 | 52.05 | 74.503
| 26.2361 | 259.669 | 48.197 | 74.591 | 52.053 | 74.505
| 26.2431 | 258.589 | 48.201 | 74.609 | 52.059 | 74.507
| 26.25 | 257.939 | 48.204 | 74.618 | 52.057 | 74.507
| 26.2569 | 257.103 | 48.197 | 74.622 | 52.062 | 74.496
| 26.2639 | 260.072 | 48.198 | 74.631 | 52.064 | 74.489
| 26.2708 | 259.289 | 48.205 | 74.651 | 52.072 | 74.505
| 26.2778 | 258.193 | 48.21 | 74.669 | 52.079 | 74.511
| 26.2847 | 258.098 | 48.214 | 74.683 | 52.078 | 74.507
| 26.2917 | 257.224 | 48.204 | 74.677 | 52.078 | 74.496
| 26.2986 | 259.904 | 48.203 | 74.683 | 52.082 | 74.484
| 26.3056 | 261.914 | 48.214 | 74.702 | 52.09 | 74.498
| 26.3125 | 261.558 | 48.24 | 74.748 | 52.112 | 74.535
| 26.3194 | 261.482 | 48.257 | 74.786 | 52.13 | 74.579
| 26.3264 | 261.683 | 48.274 | 74.825 | 52.142 | 74.612
| 26.3333 | 260.66 | 48.284 | 74.855 | 52.156 | 74.636
| 26.3403 | 259.575 | 48.292 | 74.879 | 52.164 | 74.647
| 26.3472 | 259.258 | 48.29 | 74.896 | 52.172 | 74.654
| 26.3542 | 261.512 | 48.292 | 74.906 | 52.175 | 74.651
| 26.3611 | 260.848 | 48.303 | 74.936 | 52.183 | 74.67
| 26.3681 | 261.333 | 48.315 | 74.961 | 52.199 | 74.692
| 26.375 | 259.664 | 48.32 | 74.987 | 52.211 | 74.705
| 26.3819 | 142.779 | 48.169 | 74.803 | 52.081 | 74.444
| 26.3889 | 259.923 | 47.81 | 74.184 | 51.797 | 73.587
| 26.3958 | 258.091 | 47.865 | 74.242 | 51.84 | 73.658
| 26.4028 | 257.984 | 47.935 | 74.305 | 51.88 | 73.753
| 26.4097 | 257.189 | 47.981 | 74.357 | 51.902 | 73.826
| 26.4167 | 257.497 | 48.016 | 74.388 | 51.925 | 73.882
| 26.4236 | 257.683 | 48.045 | 74.418 | 51.936 | 73.935
| 26.4306 | 257.908 | 48.066 | 74.447 | 51.951 | 73.978
| 26.4375 | 257.805 | 48.082 | 74.471 | 51.964 | 74.015
| 26.4444 | 257.8 | 48.093 | 74.494 | 51.972 | 74.042
| 26.4514 | 257.036 | 48.109 | 74.514 | 51.985 | 74.069
| 26.4583 | 256.689 | 48.111 | 74.535 | 51.995 | 74.092
| 26.4653 | 257.359 | 48.122 | 74.544 | 52 | 74.108
| 26.4722 | 256.559 | 48.125 | 74.554 | 52.006 | 74.115
| 26.4792 | 256.833 | 48.125 | 74.563 | 52.007 | 74.118
| 26.4861 | 255.664 | 48.123 | 74.566 | 52.012 | 74.115
| 26.4931 | 255.277 | 48.12 | 74.562 | 52.013 | 74.109
| 26.5 | 254.972 | 48.114 | 74.557 | 52.007 | 74.094
| 26.5069 | 254.78 | 48.108 | 74.551 | 52.003 | 74.077
| 26.5139 | 254.348 | 48.108 | 74.547 | 52.002 | 74.069
| 26.5208 | 254.587 | 48.1 | 74.543 | 52 | 74.058
| 26.5278 | 254.375 | 48.098 | 74.534 | 51.994 | 74.043
| 26.5347 | 254.526 | 48.091 | 74.531 | 51.994 | 74.022
| 26.5417 | 253.553 | 48.087 | 74.529 | 51.988 | 74.012
| 26.5486 | 254.139 | 48.084 | 74.52 | 51.98 | 74
| 26.5556 | 253.536 | 48.082 | 74.513 | 51.979 | 73.988
| 26.5625 | 254.442 | 48.079 | 74.509 | 51.977 | 73.977
| 26.5694 | 254.107 | 48.077 | 74.506 | 51.979 | 73.969
| 26.5764 | 254.412 | 48.076 | 74.501 | 51.978 | 73.958
| 26.5833 | 254.341 | 48.079 | 74.506 | 51.977 | 73.955
| 26.5903 | 254.817 | 48.085 | 74.506 | 51.976 | 73.96
| 26.5972 | 254.745 | 48.083 | 74.514 | 51.977 | 73.961
| 26.6042 | 254.349 | 48.088 | 74.515 | 51.981 | 73.965
| 26.6111 | 254.498 | 48.088 | 74.517 | 51.982 | 73.957
| 26.6181 | 254.205 | 48.089 | 74.519 | 51.98 | 73.958
| 26.625 | 255.297 | 48.087 | 74.521 | 51.976 | 73.955
| 26.6319 | 255.748 | 48.09 | 74.525 | 51.986 | 73.965
| 26.6389 | 255.031 | 48.097 | 74.532 | 51.987 | 73.967
| 26.6458 | 254.834 | 48.099 | 74.546 | 51.991 | 73.977
| 26.6528 | 255.275 | 48.102 | 74.552 | 51.994 | 73.984
| 26.6597 | 255.354 | 48.103 | 74.558 | 51.993 | 73.99
| 26.6667 | 255.525 | 48.112 | 74.571 | 52.002 | 73.996
| 26.6736 | 255.93 | 48.113 | 74.579 | 52.002 | 74.006
| 26.6806 | 260.076 | 48.124 | 74.595 | 52.012 | 74.021
| 26.6875 | 258.35 | 48.146 | 74.639 | 52.032 | 74.073
| 26.6944 | 259.278 | 48.177 | 74.69 | 52.058 | 74.13
| 26.7014 | 257.907 | 48.197 | 74.733 | 52.082 | 74.181
| 26.7083 | 257.629 | 48.213 | 74.763 | 52.093 | 74.213
| 26.7153 | 257.62 | 48.223 | 74.787 | 52.103 | 74.239
| 26.7222 | 257.967 | 48.234 | 74.814 | 52.118 | 74.264
| 26.7292 | 257.699 | 48.239 | 74.842 | 52.119 | 74.287
| 26.7361 | 258.388 | 48.247 | 74.862 | 52.13 | 74.306
| 26.7431 | 258.409 | 48.253 | 74.891 | 52.139 | 74.327
| 26.75 | 258.844 | 48.266 | 74.92 | 52.158 | 74.355
| 26.7569 | 258.717 | 48.274 | 74.949 | 52.166 | 74.379
| 26.7639 | 258.894 | 48.285 | 74.979 | 52.18 | 74.402
| 26.7708 | 137.134 | 48.241 | 74.946 | 52.138 | 74.343
| 26.7778 | 259.567 | 47.94 | 74.442 | 51.901 | 73.647
| 26.7847 | 258.812 | 47.992 | 74.505 | 51.943 | 73.733
| 26.7917 | 259.975 | 48.055 | 74.593 | 51.99 | 73.85
| 26.7986 | 259.895 | 48.116 | 74.665 | 52.03 | 73.944
| 26.8056 | 260.06 | 48.159 | 74.732 | 52.057 | 74.038
| 26.8125 | 259.708 | 48.195 | 74.782 | 52.092 | 74.113
| 26.8194 | 259.486 | 48.217 | 74.837 | 52.11 | 74.17
| 26.8264 | 260.479 | 48.236 | 74.882 | 52.131 | 74.224
| 26.8333 | 260.301 | 48.263 | 74.925 | 52.153 | 74.274
| 26.8403 | 261.33 | 48.29 | 74.974 | 52.174 | 74.333
| 26.8472 | 139.568 | 48.107 | 74.758 | 52.041 | 74.039
| 26.8542 | 260.124 | 47.781 | 74.176 | 51.78 | 73.24
| 26.8611 | 259.399 | 47.849 | 74.261 | 51.827 | 73.356
| 26.8681 | 259.354 | 47.94 | 74.364 | 51.887 | 73.505
| 26.875 | 258.711 | 48.007 | 74.447 | 51.926 | 73.637
| 26.8819 | 259.375 | 48.061 | 74.514 | 51.962 | 73.734
| 26.8889 | 259.98 | 48.1 | 74.574 | 51.988 | 73.824
| 26.8958 | 258.669 | 48.13 | 74.633 | 52.026 | 73.897
| 26.9028 | 259.103 | 48.159 | 74.678 | 52.046 | 73.962
| 26.9097 | 257.556 | 48.178 | 74.721 | 52.065 | 74.012
| 26.9167 | 258.247 | 48.185 | 74.747 | 52.076 | 74.041
| 26.9236 | 258.509 | 48.198 | 74.78 | 52.093 | 74.074
| 26.9306 | 259.191 | 48.21 | 74.817 | 52.107 | 74.113
| 26.9375 | 259.53 | 48.23 | 74.859 | 52.128 | 74.156
| 26.9444 | 259.649 | 48.248 | 74.901 | 52.152 | 74.206
| 26.9514 | 258.533 | 48.267 | 74.947 | 52.184 | 74.248
| 26.9583 | 259.409 | 48.276 | 74.983 | 52.189 | 74.281
| 26.9653 | 139.214 | 48.125 | 74.809 | 52.066 | 74.028
| 26.9722 | 259.973 | 47.81 | 74.257 | 51.82 | 73.272
| 26.9792 | 259.892 | 47.885 | 74.357 | 51.874 | 73.398
| 26.9861 | 260.586 | 47.975 | 74.461 | 51.933 | 73.552
| 26.9931 | 257.54 | 48.046 | 74.558 | 51.993 | 73.687
| 27 | 257.257 | 48.086 | 74.612 | 52.016 | 73.762
| 27.0069 | 255.192 | 48.109 | 74.653 | 52.025 | 73.812
| 27.0139 | 255.533 | 48.115 | 74.674 | 52.038 | 73.842
| 27.0208 | 255.88 | 48.127 | 74.693 | 52.052 | 73.859
| 27.0278 | 255.684 | 48.137 | 74.715 | 52.06 | 73.891
| 27.0347 | 256.207 | 48.142 | 74.736 | 52.076 | 73.912
| 27.0417 | 257.597 | 48.152 | 74.753 | 52.076 | 73.931
| 27.0486 | 257.423 | 48.167 | 74.785 | 52.091 | 73.956
| 27.0556 | 257.267 | 48.181 | 74.818 | 52.109 | 73.994
| 27.0625 | 257.234 | 48.193 | 74.852 | 52.124 | 74.026
| 27.0694 | 257.629 | 48.207 | 74.881 | 52.135 | 74.057
| 27.0764 | 257.952 | 48.22 | 74.909 | 52.152 | 74.086
| 27.0833 | 257.962 | 48.231 | 74.942 | 52.162 | 74.114
| 27.0903 | 257.639 | 48.241 | 74.975 | 52.177 | 74.138
| 27.0972 | 42.752 | 48.245 | 74.997 | 52.185 | 74.153
| 27.1042 | 259.356 | 47.79 | 74.284 | 51.818 | 73.181
| 27.1111 | 259.118 | 47.828 | 74.309 | 51.846 | 73.209
| 27.1181 | 258.815 | 47.918 | 74.422 | 51.906 | 73.367
| 27.125 | 258.84 | 47.996 | 74.512 | 51.962 | 73.501
| 27.1319 | 258.44 | 48.052 | 74.592 | 52 | 73.611
| 27.1389 | 258.129 | 48.091 | 74.667 | 52.032 | 73.704
| 27.1458 | 258.092 | 48.132 | 74.718 | 52.061 | 73.779
| 27.1528 | 258.735 | 48.159 | 74.769 | 52.089 | 73.847
| 27.1597 | 258.783 | 48.182 | 74.816 | 52.112 | 73.907
| 27.1667 | 258.741 | 48.203 | 74.861 | 52.135 | 73.959
| 27.1736 | 258.57 | 48.219 | 74.906 | 52.153 | 74.013
| 27.1806 | 258.309 | 48.236 | 74.949 | 52.171 | 74.053
| 27.1875 | 258.374 | 48.253 | 74.984 | 52.193 | 74.091
| 27.1944 | 238.244 | 47.984 | 74.639 | 51.989 | 73.616
| 27.2014 | 257.325 | 47.859 | 74.378 | 51.882 | 73.238
| 27.2083 | 257.499 | 47.925 | 74.462 | 51.931 | 73.353
| 27.2153 | 256.423 | 47.992 | 74.538 | 51.98 | 73.466
| 27.2222 | 256.955 | 48.045 | 74.61 | 52.018 | 73.558
| 27.2292 | 256.788 | 48.088 | 74.665 | 52.044 | 73.641
| 27.2361 | 257.242 | 48.12 | 74.719 | 52.071 | 73.707
| 27.2431 | 257.127 | 48.143 | 74.765 | 52.091 | 73.767
| 27.25 | 256.172 | 48.161 | 74.801 | 52.109 | 73.812
| 27.2569 | 257.399 | 48.179 | 74.837 | 52.126 | 73.849
| 27.2639 | 255.913 | 48.19 | 74.867 | 52.14 | 73.886
| 27.2708 | 255.715 | 48.199 | 74.89 | 52.152 | 73.911
| 27.2778 | 255.712 | 48.206 | 74.913 | 52.159 | 73.928
| 27.2847 | 255.2 | 48.214 | 74.93 | 52.17 | 73.938
| 27.2917 | 255.164 | 48.214 | 74.945 | 52.179 | 73.948
| 27.2986 | 254.91 | 48.217 | 74.963 | 52.186 | 73.955
| 27.3056 | 254.888 | 48.219 | 74.977 | 52.194 | 73.96
| 27.3125 | 254.823 | 48.219 | 74.982 | 52.192 | 73.964
| 27.3194 | 253.679 | 48.217 | 74.985 | 52.193 | 73.957
| 27.3264 | 63.656 | 48.176 | 74.951 | 52.159 | 73.892
| 27.3333 | 257.992 | 47.857 | 74.419 | 51.902 | 73.162
| 27.3403 | 257.289 | 47.922 | 74.492 | 51.948 | 73.268
| 27.3472 | 256.099 | 47.988 | 74.581 | 51.996 | 73.39
| 27.3542 | 258.118 | 48.047 | 74.643 | 52.034 | 73.487
| 27.3611 | 257.72 | 48.1 | 74.714 | 52.074 | 73.585
| 27.3681 | 257.37 | 48.138 | 74.773 | 52.1 | 73.669
| 27.375 | 256.929 | 48.168 | 74.829 | 52.134 | 73.738
| 27.3819 | 257.142 | 48.19 | 74.869 | 52.145 | 73.791
| 27.3889 | 256.229 | 48.207 | 74.905 | 52.163 | 73.838
| 27.3958 | 255.581 | 48.22 | 74.933 | 52.182 | 73.87
| 27.4028 | 255.108 | 48.227 | 74.961 | 52.188 | 73.893
| 27.4097 | 254.742 | 48.232 | 74.984 | 52.199 | 73.91
| 27.4167 | 254.498 | 48.236 | 74.994 | 52.204 | 73.92
| 27.4236 | 257.048 | 48.003 | 74.661 | 52.024 | 73.457
| 27.4306 | 260.773 | 48.013 | 74.644 | 52.027 | 73.433
| 27.4375 | 260.285 | 48.095 | 74.757 | 52.091 | 73.583
| 27.4444 | 259.827 | 48.166 | 74.848 | 52.141 | 73.714
| 27.4514 | 259.194 | 48.217 | 74.933 | 52.183 | 73.828
| 27.4583 | 42.224 | 48.256 | 75.011 | 52.214 | 73.917
| 27.4653 | 260.244 | 47.874 | 74.416 | 51.91 | 73.113
| 27.4722 | 259.287 | 47.919 | 74.461 | 51.939 | 73.175
| 27.4792 | 259.149 | 48.007 | 74.575 | 52.003 | 73.332
| 27.4861 | 258.308 | 48.076 | 74.669 | 52.058 | 73.473
| 27.4931 | 257.97 | 48.135 | 74.753 | 52.096 | 73.589
| 27.5 | 259.505 | 48.182 | 74.827 | 52.126 | 73.69
| 27.5069 | 259.812 | 48.221 | 74.897 | 52.162 | 73.787
| 27.5139 | 258.774 | 48.257 | 74.963 | 52.195 | 73.871
| 27.5208 | 138.922 | 48.172 | 74.897 | 52.13 | 73.773
| 27.5278 | 258.934 | 47.916 | 74.449 | 51.926 | 73.156
| 27.5347 | 259.342 | 47.985 | 74.545 | 51.981 | 73.292
| 27.5417 | 259.034 | 48.066 | 74.661 | 52.037 | 73.457
| 27.5486 | 258.111 | 48.134 | 74.75 | 52.092 | 73.589
| 27.5556 | 258.928 | 48.185 | 74.831 | 52.131 | 73.693
| 27.5625 | 259.523 | 48.228 | 74.905 | 52.161 | 73.791
| 27.5694 | 258.913 | 48.265 | 74.977 | 52.197 | 73.888
| 27.5764 | 138.482 | 48.045 | 74.695 | 52.023 | 73.508
| 27.5833 | 259.851 | 47.769 | 74.195 | 51.801 | 72.819
| 27.5903 | 259.164 | 47.861 | 74.317 | 51.872 | 72.994
| 27.5972 | 258.676 | 47.964 | 74.447 | 51.939 | 73.18
| 27.6042 | 258.086 | 48.039 | 74.549 | 51.992 | 73.342
| 27.6111 | 257.953 | 48.104 | 74.639 | 52.037 | 73.465
| 27.6181 | 257.939 | 48.152 | 74.715 | 52.075 | 73.571
| 27.625 | 257.811 | 48.183 | 74.78 | 52.102 | 73.662
| 27.6319 | 257.981 | 48.218 | 74.841 | 52.132 | 73.742
| 27.6389 | 256.107 | 48.241 | 74.893 | 52.158 | 73.809
| 27.6458 | 256.153 | 48.254 | 74.938 | 52.183 | 73.862
| 27.6528 | 256.908 | 48.27 | 74.981 | 52.198 | 73.903
| 27.6597 | 137.614 | 48.091 | 74.763 | 52.071 | 73.607
| 27.6667 | 259.613 | 47.823 | 74.287 | 51.846 | 72.938
| 27.6736 | 258.75 | 47.907 | 74.403 | 51.916 | 73.102
| 27.6806 | 259.12 | 48.006 | 74.52 | 51.973 | 73.275
| 27.6875 | 258.77 | 48.077 | 74.631 | 52.024 | 73.417
| 27.6944 | 258.348 | 48.139 | 74.718 | 52.074 | 73.548
| 27.7014 | 259.272 | 48.182 | 74.797 | 52.109 | 73.655
| 27.7083 | 258.641 | 48.223 | 74.865 | 52.137 | 73.747
| 27.7153 | 258.53 | 48.25 | 74.93 | 52.162 | 73.823
| 27.7222 | 258.758 | 48.276 | 74.991 | 52.197 | 73.896
| 27.7292 | 245.566 | 47.945 | 74.523 | 51.929 | 73.263
| 27.7361 | 259.057 | 47.889 | 74.387 | 51.884 | 73.054
| 27.7431 | 259.302 | 47.973 | 74.506 | 51.945 | 73.223
| 27.75 | 258.41 | 48.049 | 74.61 | 52.002 | 73.37
| 27.7569 | 259.835 | 48.116 | 74.699 | 52.051 | 73.496
| 27.7639 | 261.097 | 48.168 | 74.786 | 52.098 | 73.616
| 27.7708 | 261.35 | 48.223 | 74.886 | 52.142 | 73.742
| 27.7778 | 260.642 | 48.268 | 74.965 | 52.184 | 73.847
| 27.7847 | 138.684 | 48.064 | 74.722 | 52.022 | 73.507
| 27.7917 | 258.981 | 47.795 | 74.248 | 51.813 | 72.85
| 27.7986 | 260.23 | 47.88 | 74.362 | 51.879 | 73.004
| 27.8056 | 260.066 | 47.979 | 74.49 | 51.951 | 73.208
| 27.8125 | 260.572 | 48.056 | 74.607 | 52.013 | 73.384
| 27.8194 | 261.007 | 48.125 | 74.704 | 52.059 | 73.531
| 27.8264 | 261.037 | 48.18 | 74.794 | 52.102 | 73.664
| 27.8333 | 261.541 | 48.227 | 74.886 | 52.144 | 73.785
| 27.8403 | 262.157 | 48.272 | 74.974 | 52.188 | 73.892
| 27.8472 | 141.407 | 47.979 | 74.599 | 51.963 | 73.368
| 27.8542 | 259.9 | 47.718 | 74.125 | 51.757 | 72.703
| 27.8611 | 259.334 | 47.814 | 74.251 | 51.827 | 72.881
| 27.8681 | 258.782 | 47.917 | 74.388 | 51.903 | 73.075
| 27.875 | 259.479 | 47.999 | 74.495 | 51.956 | 73.229
| 27.8819 | 259.763 | 48.07 | 74.594 | 52.003 | 73.367
| 27.8889 | 259.43 | 48.122 | 74.681 | 52.041 | 73.488
| 27.8958 | 259.884 | 48.164 | 74.765 | 52.084 | 73.594
| 27.9028 | 259.1 | 48.2 | 74.836 | 52.121 | 73.687
| 27.9097 | 257.384 | 48.228 | 74.906 | 52.142 | 73.762
| 27.9167 | 257.492 | 48.245 | 74.954 | 52.164 | 73.811
| 27.9236 | 176.843 | 48.257 | 75.002 | 52.363 | 73.857
| 27.9306 | 248.06 | 47.795 | 74.33 | 51.822 | 72.931
| 27.9375 | 260.71 | 47.77 | 74.228 | 51.8 | 72.781
| 27.9444 | 261.109 | 47.878 | 74.379 | 51.876 | 72.985
| 27.9514 | 260.731 | 47.984 | 74.51 | 51.95 | 73.174
| 27.9583 | 260.943 | 48.066 | 74.632 | 52.005 | 73.342
| 27.9653 | 256.405 | 48.128 | 74.735 | 52.054 | 73.479
| 27.9722 | 256.507 | 48.157 | 74.791 | 52.08 | 73.549
| 27.9792 | 255.744 | 48.172 | 74.826 | 52.103 | 73.598
| 27.9861 | 256.41 | 48.184 | 74.868 | 52.113 | 73.637
| 27.9931 | 256.677 | 48.204 | 74.915 | 52.131 | 73.686
| 28 | 256.91 | 48.219 | 74.958 | 52.153 | 73.73
| 28.0069 | 41.324 | 48.237 | 75.002 | 52.173 | 73.77
| 28.0139 | 248.403 | 47.717 | 74.237 | 51.761 | 72.714
| 28.0208 | 259.548 | 47.699 | 74.145 | 51.735 | 72.579
| 28.0278 | 258.942 | 47.814 | 74.291 | 51.822 | 72.785
| 28.0347 | 259.215 | 47.919 | 74.417 | 51.889 | 72.976
| 28.0417 | 259.031 | 47.994 | 74.532 | 51.947 | 73.131
| 28.0486 | 258.31 | 48.058 | 74.619 | 51.986 | 73.259
| 28.0556 | 258.548 | 48.102 | 74.706 | 52.027 | 73.371
| 28.0625 | 259.092 | 48.142 | 74.779 | 52.062 | 73.47
| 28.0694 | 259.066 | 48.178 | 74.849 | 52.094 | 73.563
| 28.0764 | 258.85 | 48.211 | 74.919 | 52.131 | 73.635
| 28.0833 | 258.117 | 48.238 | 74.98 | 52.156 | 73.711
| 28.0903 | 142.419 | 48.013 | 74.701 | 51.981 | 73.325
| 28.0972 | 259.468 | 47.774 | 74.265 | 51.791 | 72.72
| 28.1042 | 259.044 | 47.863 | 74.395 | 51.861 | 72.881
| 28.1111 | 258.998 | 47.957 | 74.518 | 51.932 | 73.059
| 28.1181 | 258.293 | 48.029 | 74.623 | 51.982 | 73.202
| 28.125 | 259.095 | 48.087 | 74.71 | 52.027 | 73.319
| 28.1319 | 258.467 | 48.136 | 74.787 | 52.066 | 73.429
| 28.1389 | 258.74 | 48.17 | 74.86 | 52.101 | 73.512
| 28.1458 | 258.465 | 48.203 | 74.927 | 52.13 | 73.594
| 28.1528 | 258.999 | 48.226 | 74.989 | 52.161 | 73.667
| 28.1597 | 247.856 | 47.884 | 74.503 | 51.891 | 72.989
| 28.1667 | 259.281 | 47.851 | 74.406 | 51.859 | 72.848
| 28.1736 | 258.98 | 47.941 | 74.53 | 51.935 | 73.017
| 28.1806 | 259.052 | 48.027 | 74.641 | 51.991 | 73.171
| 28.1875 | 258.677 | 48.09 | 74.739 | 52.043 | 73.302
| 28.1944 | 258.388 | 48.137 | 74.821 | 52.075 | 73.407
| 28.2014 | 258.944 | 48.175 | 74.892 | 52.112 | 73.498
| 28.2083 | 258.106 | 48.209 | 74.96 | 52.143 | 73.58
| 28.2153 | 41.658 | 48.138 | 74.906 | 52.088 | 73.494
| 28.2222 | 260.427 | 47.678 | 74.154 | 51.725 | 72.461
| 28.2292 | 259.67 | 47.761 | 74.25 | 51.786 | 72.588
| 28.2361 | 259.39 | 47.876 | 74.399 | 51.869 | 72.805
| 28.2431 | 260.196 | 47.975 | 74.533 | 51.937 | 72.985
| 28.25 | 259.598 | 48.047 | 74.642 | 51.991 | 73.134
| 28.2569 | 258.574 | 48.109 | 74.735 | 52.037 | 73.27
| 28.2639 | 259.087 | 48.15 | 74.811 | 52.075 | 73.377
| 28.2708 | 259.624 | 48.193 | 74.894 | 52.113 | 73.491
| 28.2778 | 259.807 | 48.23 | 74.974 | 52.15 | 73.593
| 28.2847 | 143.423 | 47.973 | 74.644 | 51.948 | 73.143
| 28.2917 | 260.071 | 47.751 | 74.233 | 51.77 | 72.573
| 28.2986 | 258.976 | 47.848 | 74.37 | 51.844 | 72.759
| 28.3056 | 258.691 | 47.944 | 74.496 | 51.913 | 72.944
| 28.3125 | 258.498 | 48.019 | 74.601 | 51.968 | 73.095
| 28.3194 | 257.869 | 48.078 | 74.689 | 52.011 | 73.206
| 28.3264 | 257.246 | 48.118 | 74.763 | 52.052 | 73.296
| 28.3333 | 256.691 | 48.154 | 74.831 | 52.082 | 73.387
| 28.3403 | 256.053 | 48.177 | 74.884 | 52.104 | 73.434
| 28.3472 | 255.413 | 48.194 | 74.929 | 52.125 | 73.482
| 28.3542 | 258.501 | 48.204 | 74.966 | 52.144 | 73.522
| 28.3611 | 42.014 | 48.143 | 74.926 | 52.102 | 73.45
| 28.3681 | 259.219 | 47.713 | 74.212 | 51.754 | 72.463
| 28.375 | 258.307 | 47.79 | 74.305 | 51.809 | 72.591
| 28.3819 | 260.632 | 47.898 | 74.44 | 51.886 | 72.783
| 28.3889 | 258.842 | 47.997 | 74.567 | 51.954 | 72.97
| 28.3958 | 259.697 | 48.067 | 74.673 | 52.007 | 73.118
| 28.4028 | 258.479 | 48.124 | 74.771 | 52.05 | 73.253
| 28.4097 | 257.667 | 48.173 | 74.851 | 52.089 | 73.36
| 28.4167 | 257.955 | 48.205 | 74.921 | 52.12 | 73.446
| 28.4236 | 258.341 | 48.236 | 74.988 | 52.149 | 73.532
| 28.4306 | 218.981 | 47.895 | 74.513 | 51.878 | 72.883
| 28.4375 | 255.286 | 47.787 | 74.295 | 51.792 | 72.567
| 28.4444 | 254.2 | 47.863 | 74.387 | 51.845 | 72.706
| 28.4514 | 254.733 | 47.933 | 74.477 | 51.897 | 72.833
| 28.4583 | 254.7 | 47.991 | 74.55 | 51.934 | 72.938
| 28.4653 | 253.871 | 48.035 | 74.611 | 51.961 | 73.023
| 28.4722 | 254.401 | 48.064 | 74.653 | 51.983 | 73.089
| 28.4792 | 253.616 | 48.088 | 74.692 | 52.003 | 73.145
| 28.4861 | 253.599 | 48.101 | 74.727 | 52.013 | 73.189
| 28.4931 | 260.712 | 48.125 | 74.776 | 52.038 | 73.252
| 28.5 | 259.693 | 48.185 | 74.877 | 52.087 | 73.384
| 28.5069 | 259.294 | 48.23 | 74.962 | 52.124 | 73.497
| 28.5139 | 140.546 | 48.081 | 74.789 | 52.009 | 73.255
| 28.5208 | 259.11 | 47.87 | 74.416 | 51.841 | 72.732
| 28.5278 | 258.6 | 47.95 | 74.529 | 51.905 | 72.885
| 28.5347 | 258.048 | 48.031 | 74.641 | 51.967 | 73.038
| 28.5417 | 257.523 | 48.103 | 74.74 | 52.014 | 73.179
| 28.5486 | 256.892 | 48.153 | 74.823 | 52.049 | 73.292
| 28.5556 | 257.791 | 48.191 | 74.895 | 52.083 | 73.388
| 28.5625 | 258.018 | 48.227 | 74.961 | 52.11 | 73.472
| 28.5694 | 41.108 | 48.14 | 74.885 | 52.041 | 73.364
| 28.5764 | 259.591 | 47.701 | 74.159 | 51.691 | 72.362
| 28.5833 | 258.702 | 47.787 | 74.261 | 51.753 | 72.509
| 28.5903 | 258.71 | 47.898 | 74.409 | 51.828 | 72.726
| 28.5972 | 257.563 | 47.993 | 74.533 | 51.889 | 72.904
| 28.6042 | 256.898 | 48.061 | 74.627 | 51.937 | 73.043
| 28.6111 | 256.973 | 48.11 | 74.708 | 51.974 | 73.157
| 28.6181 | 257.645 | 48.15 | 74.779 | 52.007 | 73.259
| 28.625 | 257.08 | 48.185 | 74.847 | 52.04 | 73.345
| 28.6319 | 257.271 | 48.216 | 74.911 | 52.065 | 73.431
| 28.6389 | 256.486 | 48.241 | 74.968 | 52.088 | 73.504
| 28.6458 | 40.759 | 48.134 | 74.864 | 52.004 | 73.351
| 28.6528 | 260.273 | 47.689 | 74.132 | 51.653 | 72.346
| 28.6597 | 259.195 | 47.782 | 74.24 | 51.713 | 72.496
| 28.6667 | 259.459 | 47.899 | 74.396 | 51.799 | 72.718
| 28.6736 | 259.087 | 47.999 | 74.526 | 51.867 | 72.91
| 28.6806 | 257.882 | 48.077 | 74.641 | 51.924 | 73.072
| 28.6875 | 258.334 | 48.127 | 74.727 | 51.965 | 73.203
| 28.6944 | 258.517 | 48.175 | 74.81 | 51.998 | 73.314
| 28.7014 | 257.895 | 48.215 | 74.885 | 52.032 | 73.417
| 28.7083 | 258.83 | 48.248 | 74.961 | 52.068 | 73.508
| 28.7153 | 40.869 | 48.154 | 74.878 | 51.994 | 73.388
| 28.7222 | 259.024 | 47.713 | 74.154 | 51.645 | 72.394
| 28.7292 | 259.289 | 47.794 | 74.256 | 51.703 | 72.535
| 28.7361 | 258.701 | 47.904 | 74.404 | 51.783 | 72.742
| 28.7431 | 258.03 | 47.999 | 74.521 | 51.848 | 72.921
| 28.75 | 258.357 | 48.071 | 74.621 | 51.898 | 73.064
| 28.7569 | 257.918 | 48.116 | 74.711 | 51.932 | 73.189
| 28.7639 | 258.094 | 48.164 | 74.791 | 51.965 | 73.291
| 28.7708 | 258.047 | 48.2 | 74.858 | 51.995 | 73.389
| 28.7778 | 258.136 | 48.231 | 74.927 | 52.032 | 73.478
| 28.7847 | 258.018 | 48.258 | 74.997 | 52.059 | 73.56
| 28.7917 | 247.712 | 47.871 | 74.436 | 51.757 | 72.785
| 28.7986 | 258.137 | 47.862 | 74.386 | 51.751 | 72.706
| 28.8056 | 258.387 | 47.952 | 74.52 | 51.817 | 72.89
| 28.8125 | 258.315 | 48.038 | 74.638 | 51.879 | 73.053
| 28.8194 | 258.341 | 48.104 | 74.73 | 51.922 | 73.189
| 28.8264 | 258.2 | 48.152 | 74.82 | 51.97 | 73.306
| 28.8333 | 258.868 | 48.197 | 74.897 | 52.003 | 73.412
| 28.8403 | 259.942 | 48.239 | 74.98 | 52.039 | 73.515
| 28.8472 | 142.018 | 47.921 | 74.558 | 51.786 | 72.934
| 28.8542 | 259.683 | 47.733 | 74.197 | 51.632 | 72.427
| 28.8611 | 260.214 | 47.841 | 74.345 | 51.714 | 72.641
| 28.8681 | 259.735 | 47.946 | 74.491 | 51.794 | 72.849
| 28.875 | 259.927 | 48.036 | 74.61 | 51.856 | 73.028
| 28.8819 | 259.61 | 48.109 | 74.725 | 51.914 | 73.183
| 28.8889 | 258.662 | 48.169 | 74.826 | 51.954 | 73.314
| 28.8958 | 259.587 | 48.205 | 74.906 | 51.994 | 73.418
| 28.9028 | 259.829 | 48.243 | 74.984 | 52.026 | 73.522
| 28.9097 | 142.888 | 47.874 | 74.484 | 51.74 | 72.832
| 28.9167 | 259.689 | 47.688 | 74.129 | 51.586 | 72.34
| 28.9236 | 259.147 | 47.797 | 74.277 | 51.669 | 72.542
| 28.9306 | 258.215 | 47.906 | 74.413 | 51.749 | 72.747
| 28.9375 | 259.262 | 47.99 | 74.524 | 51.8 | 72.912
| 28.9444 | 259.612 | 48.053 | 74.629 | 51.849 | 73.059
| 28.9514 | 259.894 | 48.111 | 74.729 | 51.897 | 73.193
| 28.9583 | 260.627 | 48.159 | 74.821 | 51.945 | 73.325
| 28.9653 | 260.955 | 48.21 | 74.914 | 51.985 | 73.442
| 28.9722 | 26.114 | 48.25 | 75.005 | 52.028 | 73.552
| 28.9792 | 260.327 | 47.787 | 74.33 | 51.662 | 72.625
| 28.9861 | 259.523 | 47.793 | 74.298 | 51.661 | 72.569
| 28.9931 | 259.751 | 47.898 | 74.449 | 51.744 | 72.782
| 29 | 260.333 | 47.995 | 74.579 | 51.814 | 72.976
| 29.0069 | 260.825 | 48.074 | 74.7 | 51.876 | 73.138
| 29.0139 | 260.887 | 48.137 | 74.809 | 51.93 | 73.283
| 29.0208 | 261.048 | 48.194 | 74.914 | 51.975 | 73.422
| 29.0278 | 24.928 | 48.24 | 75.011 | 52.021 | 73.55
| 29.0347 | 260.937 | 47.73 | 74.261 | 51.617 | 72.527
| 29.0417 | 257.197 | 47.739 | 74.23 | 51.623 | 72.508
| 29.0486 | 260.156 | 47.839 | 74.369 | 51.7 | 72.717
| 29.0556 | 260.617 | 47.948 | 74.509 | 51.777 | 72.933
| 29.0625 | 260.794 | 48.045 | 74.634 | 51.837 | 73.104
| 29.0694 | 259.932 | 48.113 | 74.745 | 51.893 | 73.258
| 29.0764 | 260.023 | 48.162 | 74.854 | 51.941 | 73.395
| 29.0833 | 260.827 | 48.196 | 74.953 | 51.983 | 73.547
| 29.0903 | 89.392 | 48.091 | 74.895 | 51.926 | 73.45
| 29.0972 | 259.887 | 47.671 | 74.224 | 51.605 | 72.523
| 29.1042 | 258.968 | 47.724 | 74.336 | 51.669 | 72.66
| 29.1111 | 258.783 | 47.799 | 74.478 | 51.742 | 72.858
| 29.1181 | 258.914 | 47.857 | 74.6 | 51.813 | 73.02
| 29.125 | 258.165 | 47.893 | 74.705 | 51.855 | 73.156
| 29.1319 | 258.174 | 47.917 | 74.789 | 51.9 | 73.263
| 29.1389 | 258.134 | 47.937 | 74.873 | 51.935 | 73.358
| 29.1458 | 258.532 | 47.953 | 74.949 | 51.968 | 73.444
| 29.1528 | 142.923 | 47.916 | 74.96 | 51.952 | 73.438
| 29.1597 | 260.033 | 47.546 | 74.365 | 51.662 | 72.598
| 29.1667 | 259.575 | 47.61 | 74.471 | 51.725 | 72.731
| 29.1736 | 258.342 | 47.686 | 74.605 | 51.795 | 72.915
| 29.1806 | 258.349 | 47.748 | 74.716 | 51.855 | 73.063
| 29.1875 | 258.148 | 47.791 | 74.811 | 51.903 | 73.189
| 29.1944 | 257.724 | 47.828 | 74.897 | 51.943 | 73.296
| 29.2014 | 258.05 | 47.849 | 74.973 | 51.977 | 73.386
| 29.2083 | 248.273 | 47.642 | 74.712 | 51.807 | 73.02
| 29.2153 | 258.811 | 47.485 | 74.402 | 51.674 | 72.579
| 29.2222 | 259.901 | 47.57 | 74.534 | 51.746 | 72.75
| 29.2292 | 259.364 | 47.651 | 74.662 | 51.818 | 72.931
| 29.2361 | 258.791 | 47.723 | 74.774 | 51.873 | 73.088
| 29.2431 | 257.689 | 47.771 | 74.87 | 51.924 | 73.214
| 29.25 | 257.464 | 47.81 | 74.954 | 51.96 | 73.313
| 29.2569 | 141.787 | 47.772 | 74.948 | 51.93 | 73.294
| 29.2639 | 262.117 | 47.416 | 74.337 | 51.637 | 72.45
| 29.2708 | 261.214 | 47.511 | 74.461 | 51.709 | 72.627
| 29.2778 | 261.27 | 47.619 | 74.621 | 51.8 | 72.85
| 29.2847 | 260.7 | 47.706 | 74.756 | 51.87 | 73.045
| 29.2917 | 260.306 | 47.778 | 74.871 | 51.926 | 73.208
| 29.2986 | 259.115 | 47.822 | 74.97 | 51.976 | 73.338
| 29.3056 | 249.068 | 47.604 | 74.684 | 51.794 | 72.949
| 29.3125 | 258.899 | 47.461 | 74.372 | 51.664 | 72.517
| 29.3194 | 258.497 | 47.543 | 74.496 | 51.736 | 72.692
| 29.3264 | 257.373 | 47.626 | 74.607 | 51.801 | 72.86
| 29.3333 | 259.323 | 47.687 | 74.693 | 51.843 | 72.989
| 29.3403 | 258.113 | 47.74 | 74.779 | 51.895 | 73.112
| 29.3472 | 257.285 | 47.789 | 74.852 | 51.93 | 73.224
| 29.3542 | 257.947 | 47.814 | 74.915 | 51.966 | 73.309
| 29.3611 | 257.978 | 47.846 | 74.97 | 51.992 | 73.387
| 29.3681 | 144.678 | 47.751 | 74.881 | 51.93 | 73.268
| 29.375 | 259.215 | 47.392 | 74.225 | 51.622 | 72.378
| 29.3819 | 261.024 | 47.48 | 74.327 | 51.687 | 72.537
| 29.3889 | 261.101 | 47.599 | 74.475 | 51.774 | 72.761
| 29.3958 | 259.284 | 47.688 | 74.596 | 51.848 | 72.947
| 29.4028 | 259.185 | 47.753 | 74.695 | 51.9 | 73.097
| 29.4097 | 259.682 | 47.805 | 74.769 | 51.943 | 73.228
| 29.4167 | 258.547 | 47.843 | 74.84 | 51.986 | 73.338
| 29.4236 | 259.044 | 47.878 | 74.9 | 52.019 | 73.431
| 29.4306 | 258.376 | 47.908 | 74.949 | 52.048 | 73.509
| 29.4375 | 258.5 | 47.927 | 74.991 | 52.079 | 73.584
| 29.4444 | 248.91 | 47.587 | 74.488 | 51.8 | 72.915
| 29.4514 | 258.667 | 47.449 | 74.153 | 51.671 | 72.48
| 29.4583 | 257.744 | 47.554 | 74.261 | 51.747 | 72.664
| 29.4653 | 257.631 | 47.648 | 74.361 | 51.815 | 72.849
| 29.4722 | 257.34 | 47.726 | 74.428 | 51.87 | 72.991
| 29.4792 | 257.222 | 47.779 | 74.485 | 51.909 | 73.112
| 29.4861 | 258.324 | 47.83 | 74.531 | 51.949 | 73.225
| 29.4931 | 256.84 | 47.865 | 74.563 | 51.983 | 73.314
| 29.5 | 257.831 | 47.899 | 74.582 | 52.008 | 73.396
| 29.5069 | 257.503 | 47.927 | 74.603 | 52.036 | 73.468
| 29.5139 | 258.029 | 47.955 | 74.619 | 52.066 | 73.539
| 29.5208 | 258.035 | 47.986 | 74.63 | 52.099 | 73.621
| 29.5278 | 258.721 | 48.011 | 74.64 | 52.128 | 73.69
| 29.5347 | 258.051 | 48.038 | 74.644 | 52.151 | 73.755
| 29.5417 | 258.358 | 48.058 | 74.642 | 52.174 | 73.806
| 29.5486 | 258.334 | 48.073 | 74.633 | 52.193 | 73.859
| 29.5556 | 257.894 | 48.088 | 74.619 | 52.215 | 73.904
| 29.5625 | 257.479 | 48.107 | 74.605 | 52.234 | 73.95
| 29.5694 | 258.728 | 48.125 | 74.583 | 52.253 | 73.988
| 29.5764 | 258.047 | 48.138 | 74.564 | 52.271 | 74.03
| 29.5833 | 258.688 | 48.152 | 74.543 | 52.296 | 74.073
| 29.5903 | 258.284 | 48.175 | 74.516 | 52.312 | 74.112
| 29.5972 | 258.161 | 48.184 | 74.49 | 52.326 | 74.148
| 29.6042 | 257.355 | 48.199 | 74.457 | 52.34 | 74.177
| 29.6111 | 257.688 | 48.211 | 74.418 | 52.354 | 74.209
| 29.6181 | 258.519 | 48.22 | 74.376 | 52.368 | 74.237
| 29.625 | 258.239 | 48.236 | 74.338 | 52.384 | 74.275
| 29.6319 | 258.573 | 48.251 | 74.301 | 52.397 | 74.305
| 29.6389 | 256.525 | 48.254 | 74.245 | 52.408 | 74.321
| 29.6458 | 257.461 | 48.257 | 74.181 | 52.414 | 74.328
| 29.6528 | 257.317 | 48.261 | 74.115 | 52.423 | 74.342
| 29.6597 | 257.829 | 48.266 | 74.058 | 52.429 | 74.36
| 29.6667 | 257.018 | 48.28 | 73.997 | 52.442 | 74.382
| 29.6736 | 257.424 | 48.281 | 73.927 | 52.446 | 74.392
| 29.6806 | 258.087 | 48.286 | 73.858 | 52.449 | 74.411
| 29.6875 | 257.803 | 48.298 | 73.789 | 52.458 | 74.431
| 29.6944 | 257.922 | 48.305 | 73.725 | 52.471 | 74.456
| 29.7014 | 257.572 | 48.312 | 73.652 | 52.482 | 74.481
| 29.7083 | 258.614 | 48.325 | 73.582 | 52.492 | 74.5
| 29.7153 | 257.91 | 48.329 | 73.51 | 52.504 | 74.53
| 29.7222 | 258.811 | 48.337 | 73.435 | 52.511 | 74.554
| 29.7292 | 259.043 | 48.349 | 73.366 | 52.518 | 74.582
| 29.7361 | 258.004 | 48.354 | 73.29 | 52.535 | 74.612
| 29.7431 | 258.315 | 48.364 | 73.211 | 52.541 | 74.628
| 29.75 | 259.775 | 48.372 | 73.133 | 52.554 | 74.651
| 29.7569 | 259.014 | 48.383 | 73.061 | 52.566 | 74.683
| 29.7639 | 258.486 | 48.396 | 72.977 | 52.576 | 74.712
| 29.7708 | 258.678 | 48.4 | 72.89 | 52.583 | 74.731
| 29.7778 | 258.273 | 48.402 | 72.802 | 52.594 | 74.744
| 29.7847 | 257.232 | 48.403 | 72.703 | 52.595 | 74.762
| 29.7917 | 257.762 | 48.404 | 72.603 | 52.601 | 74.761
| 29.7986 | 257.815 | 48.403 | 72.502 | 52.603 | 74.767
| 29.8056 | 258.13 | 48.407 | 72.397 | 52.611 | 74.775
| 29.8125 | 258.598 | 48.413 | 72.307 | 52.616 | 74.792
| 29.8194 | 259.522 | 48.422 | 72.211 | 52.625 | 74.811
| 29.8264 | 259.22 | 48.431 | 72.122 | 52.636 | 74.839
| 29.8333 | 259.693 | 48.444 | 72.027 | 52.648 | 74.862
| 29.8403 | 260.087 | 48.454 | 71.936 | 52.658 | 74.891
| 29.8472 | 257.532 | 48.461 | 71.841 | 52.669 | 74.912
| 29.8542 | 257.525 | 48.455 | 71.722 | 52.665 | 74.911
| 29.8611 | 257.834 | 48.457 | 71.609 | 52.665 | 74.91
| 29.8681 | 258.595 | 48.457 | 71.506 | 52.671 | 74.917
| 29.875 | 259.261 | 48.462 | 71.398 | 52.68 | 74.932
| 29.8819 | 257.118 | 48.462 | 71.284 | 52.678 | 74.94
| 29.8889 | 256.634 | 48.461 | 71.163 | 52.681 | 74.931
| 29.8958 | 256.529 | 48.458 | 71.043 | 52.678 | 74.927
| 29.9028 | 255.087 | 48.452 | 70.92 | 52.673 | 74.92
| 29.9097 | 256.909 | 48.443 | 70.788 | 52.664 | 74.893
| 29.9167 | 257.161 | 48.438 | 70.665 | 52.658 | 74.888
| 29.9236 | 257.935 | 48.441 | 70.548 | 52.66 | 74.891
| 29.9306 | 258.396 | 48.445 | 70.441 | 52.666 | 74.908
| 29.9375 | 258.776 | 48.463 | 70.335 | 52.678 | 74.925
| 29.9444 | 259.696 | 48.472 | 70.242 | 52.689 | 74.962
| 29.9514 | 41.765 | 48.49 | 70.152 | 52.699 | 74.994
| 29.9583 | 259.755 | 48.067 | 69.356 | 52.343 | 74.094
| 29.9653 | 260.736 | 48.078 | 69.21 | 52.342 | 74.037
| 29.9722 | 260.065 | 48.162 | 69.2 | 52.392 | 74.184
| 29.9792 | 260.697 | 48.234 | 69.177 | 52.442 | 74.32
| 29.9861 | 260.558 | 48.295 | 69.136 | 52.49 | 74.443
| 29.9931 | 261.606 | 48.342 | 69.08 | 52.523 | 74.543
| 30 | 257.341 | 48.364 | 69.007 | 52.539 | 74.609
| 30.0069 | 257.791 | 48.369 | 68.9 | 52.541 | 74.637
| 30.0139 | 257.344 | 48.369 | 68.797 | 52.547 | 74.66
| 30.0208 | 258.043 | 48.373 | 68.689 | 52.557 | 74.694
| 30.0278 | 257.418 | 48.382 | 68.585 | 52.559 | 74.715
| 30.0347 | 257.639 | 48.389 | 68.481 | 52.57 | 74.739
| 30.0417 | 258.107 | 48.394 | 68.38 | 52.583 | 74.767
| 30.0486 | 258.561 | 48.407 | 68.275 | 52.589 | 74.795
| 30.0556 | 258.632 | 48.415 | 68.173 | 52.599 | 74.826
| 30.0625 | 258.061 | 48.426 | 68.075 | 52.604 | 74.852
| 30.0694 | 258.784 | 48.431 | 67.962 | 52.612 | 74.874
| 30.0764 | 258.407 | 48.439 | 67.861 | 52.624 | 74.897
| 30.0833 | 259.068 | 48.443 | 67.756 | 52.631 | 74.916
| 30.0903 | 259.7 | 48.453 | 67.656 | 52.638 | 74.948
| 30.0972 | 259.497 | 48.461 | 67.559 | 52.649 | 74.979
| 30.1042 | 252.351 | 48.469 | 67.459 | 52.654 | 74.995
| 30.1111 | 257.848 | 48.456 | 67.319 | 52.644 | 74.969
| 30.1181 | 257.912 | 48.454 | 67.209 | 52.65 | 74.978
| 30.125 | 256.728 | 48.461 | 67.101 | 52.652 | 74.986
| 30.1319 | 257.846 | 48.46 | 66.991 | 52.658 | 74.989
| 30.1389 | 256.824 | 48.464 | 66.882 | 52.66 | 74.992
| 30.1458 | 257.045 | 48.46 | 66.765 | 52.651 | 74.995
| 30.1528 | 255.264 | 48.408 | 66.564 | 52.601 | 74.878
| 30.1597 | 255.054 | 48.39 | 66.419 | 52.588 | 74.831
| 30.1667 | 254.699 | 48.389 | 66.303 | 52.586 | 74.821
| 30.1736 | 255.367 | 48.391 | 66.184 | 52.582 | 74.81
| 30.1806 | 254.09 | 48.388 | 66.064 | 52.578 | 74.806
| 30.1875 | 254.552 | 48.384 | 65.942 | 52.568 | 74.79
| 30.1944 | 254.189 | 48.385 | 65.819 | 52.566 | 74.787
| 30.2014 | 254.24 | 48.377 | 65.697 | 52.558 | 74.773
| 30.2083 | 257.571 | 48.38 | 65.587 | 52.562 | 74.769
| 30.2153 | 257.744 | 48.396 | 65.494 | 52.568 | 74.801
| 30.2222 | 257.743 | 48.411 | 65.407 | 52.579 | 74.835
| 30.2292 | 258.137 | 48.426 | 65.319 | 52.586 | 74.871
| 30.2361 | 257.904 | 48.436 | 65.227 | 52.603 | 74.908
| 30.2431 | 258.153 | 48.445 | 65.133 | 52.607 | 74.931
| 30.25 | 256.428 | 48.449 | 65.035 | 52.614 | 74.945
| 30.2569 | 255.752 | 48.447 | 64.933 | 52.615 | 74.959
| 30.2639 | 256.705 | 48.441 | 64.812 | 52.607 | 74.95
| 30.2708 | 257.394 | 48.442 | 64.712 | 52.612 | 74.955
| 30.2778 | 258.96 | 48.453 | 64.621 | 52.62 | 74.975
| 30.2847 | 143.431 | 48.383 | 64.421 | 52.558 | 74.876
| 30.2917 | 259.411 | 48.066 | 63.766 | 52.294 | 74.103
| 30.2986 | 258.336 | 48.127 | 63.759 | 52.329 | 74.193
| 30.3056 | 257.294 | 48.191 | 63.739 | 52.364 | 74.305
| 30.3125 | 256.189 | 48.239 | 63.693 | 52.4 | 74.387
| 30.3194 | 256.455 | 48.27 | 63.623 | 52.416 | 74.45
| 30.3264 | 254.872 | 48.289 | 63.54 | 52.422 | 74.493
| 30.3333 | 257.035 | 48.296 | 63.445 | 52.429 | 74.525
| 30.3403 | 256.98 | 48.316 | 63.358 | 52.442 | 74.573
| 30.3472 | 256.262 | 48.331 | 63.272 | 52.454 | 74.608
| 30.3542 | 255.876 | 48.336 | 63.171 | 52.459 | 74.635
| 30.3611 | 255.748 | 48.338 | 63.072 | 52.463 | 74.65
| 30.3681 | 255.969 | 48.341 | 62.963 | 52.467 | 74.662
| 30.375 | 255.638 | 48.347 | 62.866 | 52.468 | 74.684
| 30.3819 | 255.802 | 48.352 | 62.759 | 52.475 | 74.699
| 30.3889 | 256.147 | 48.356 | 62.66 | 52.479 | 74.716
| 30.3958 | 255.082 | 48.361 | 62.561 | 52.479 | 74.734
| 30.4028 | 254.923 | 48.362 | 62.451 | 52.483 | 74.742
| 30.4097 | 254.359 | 48.359 | 62.342 | 52.481 | 74.742
| 30.4167 | 253.577 | 48.354 | 62.224 | 52.476 | 74.734
| 30.4236 | 254.208 | 48.346 | 62.102 | 52.467 | 74.72
| 30.4306 | 253.737 | 48.342 | 61.982 | 52.462 | 74.715
| 30.4375 | 257.587 | 48.347 | 61.87 | 52.468 | 74.716
| 30.4444 | 256.749 | 48.364 | 61.777 | 52.473 | 74.751
| 30.4514 | 259.024 | 48.373 | 61.676 | 52.482 | 74.781
| 30.4583 | 258.976 | 48.395 | 61.594 | 52.499 | 74.833
| 30.4653 | 255.787 | 48.404 | 61.507 | 52.512 | 74.865
| 30.4722 | 256.091 | 48.404 | 61.399 | 52.509 | 74.869
| 30.4792 | 255.141 | 48.402 | 61.295 | 52.509 | 74.875
| 30.4861 | 254.121 | 48.4 | 61.193 | 52.507 | 74.87
| 30.4931 | 254.349 | 48.392 | 61.08 | 52.496 | 74.856
| 30.5 | 254.547 | 48.384 | 60.977 | 52.494 | 74.839
| 30.5069 | 254.553 | 48.38 | 60.872 | 52.485 | 74.825
| 30.5139 | 256.12 | 48.38 | 60.78 | 52.487 | 74.829
| 30.5208 | 255.31 | 48.384 | 60.697 | 52.486 | 74.841
| 30.5278 | 256.013 | 48.396 | 60.61 | 52.483 | 74.85
| 30.5347 | 255.638 | 48.395 | 60.52 | 52.486 | 74.856
| 30.5417 | 256.472 | 48.399 | 60.448 | 52.494 | 74.872
| 30.5486 | 256.662 | 48.407 | 60.375 | 52.497 | 74.886
| 30.5556 | 256.025 | 48.412 | 60.304 | 52.503 | 74.908
| 30.5625 | 256.174 | 48.414 | 60.227 | 52.502 | 74.918
| 30.5694 | 256.147 | 48.417 | 60.152 | 52.508 | 74.933
| 30.5764 | 253.945 | 48.418 | 60.072 | 52.498 | 74.927
| 30.5833 | 254.492 | 48.402 | 59.989 | 52.49 | 74.909
| 30.5903 | 253.421 | 48.395 | 59.906 | 52.48 | 74.892
| 30.5972 | 260.209 | 48.386 | 59.828 | 52.469 | 74.871
| 30.6042 | 261.595 | 48.416 | 59.802 | 52.493 | 74.932
| 30.6111 | 40.992 | 48.442 | 59.772 | 52.507 | 75.001
| 30.6181 | 259.185 | 47.967 | 59.081 | 52.112 | 73.964
| 30.625 | 259.299 | 47.996 | 59.111 | 52.118 | 73.963
| 30.6319 | 259.288 | 48.094 | 59.162 | 52.18 | 74.124
| 30.6389 | 258.354 | 48.166 | 59.171 | 52.224 | 74.261
| 30.6458 | 258.973 | 48.22 | 59.16 | 52.257 | 74.371
| 30.6528 | 257.837 | 48.261 | 59.138 | 52.288 | 74.467
| 30.6597 | 258.394 | 48.288 | 59.11 | 52.308 | 74.54
| 30.6667 | 258.307 | 48.318 | 59.083 | 52.324 | 74.614
| 30.6736 | 258.087 | 48.333 | 59.053 | 52.339 | 74.68
| 30.6806 | 258.793 | 48.352 | 59.024 | 52.363 | 74.739
| 30.6875 | 259.219 | 48.376 | 58.988 | 52.38 | 74.798
| 30.6944 | 259.849 | 48.397 | 58.961 | 52.403 | 74.862
| 30.7014 | 260.145 | 48.42 | 58.938 | 52.425 | 74.924
| 30.7083 | 260.445 | 48.441 | 58.911 | 52.447 | 74.989
| 30.7153 | 248.248 | 48.056 | 58.391 | 52.131 | 74.234
| 30.7222 | 260.829 | 47.956 | 58.276 | 52.042 | 73.91
| 30.7292 | 260.108 | 48.048 | 58.335 | 52.105 | 74.076
| 30.7361 | 259.674 | 48.13 | 58.362 | 52.16 | 74.231
| 30.7431 | 257.83 | 48.188 | 58.363 | 52.197 | 74.353
| 30.75 | 257.391 | 48.233 | 58.343 | 52.222 | 74.447
| 30.7569 | 257.591 | 48.257 | 58.322 | 52.238 | 74.519
| 30.7639 | 257.37 | 48.278 | 58.298 | 52.255 | 74.581
| 30.7708 | 257.239 | 48.303 | 58.273 | 52.272 | 74.637
| 30.7778 | 258.208 | 48.31 | 58.258 | 52.294 | 74.688
| 30.7847 | 258.161 | 48.331 | 58.249 | 52.306 | 74.742
| 30.7917 | 258.448 | 48.348 | 58.237 | 52.327 | 74.799
| 30.7986 | 258.522 | 48.368 | 58.236 | 52.345 | 74.848
| 30.8056 | 257.75 | 48.378 | 58.224 | 52.357 | 74.898
| 30.8125 | 259.006 | 48.39 | 58.219 | 52.375 | 74.939
| 30.8194 | 259.255 | 48.406 | 58.219 | 52.385 | 74.983
| 30.8264 | 142.991 | 48.216 | 57.99 | 52.23 | 74.663
| 30.8333 | 260.356 | 47.907 | 57.666 | 51.971 | 73.874
| 30.8403 | 256.534 | 47.992 | 57.749 | 52.03 | 74.02
| 30.8472 | 257.193 | 48.066 | 57.787 | 52.079 | 74.157
| 30.8542 | 257.172 | 48.128 | 57.814 | 52.113 | 74.271
| 30.8611 | 257.932 | 48.175 | 57.828 | 52.146 | 74.369
| 30.8681 | 257.747 | 48.213 | 57.834 | 52.17 | 74.452
| 30.875 | 258.101 | 48.241 | 57.849 | 52.201 | 74.531
| 30.8819 | 258.526 | 48.269 | 57.857 | 52.225 | 74.608
| 30.8889 | 259.445 | 48.293 | 57.866 | 52.247 | 74.684
| 30.8958 | 259.763 | 48.315 | 57.877 | 52.271 | 74.746
| 30.9028 | 258.859 | 48.331 | 57.882 | 52.293 | 74.808
| 30.9097 | 256.994 | 48.341 | 57.882 | 52.305 | 74.843
| 30.9167 | 255.97 | 48.336 | 57.87 | 52.308 | 74.853
| 30.9236 | 256.385 | 48.329 | 57.858 | 52.311 | 74.856
| 30.9306 | 256.978 | 48.332 | 57.85 | 52.317 | 74.864
| 30.9375 | 257.766 | 48.333 | 57.851 | 52.322 | 74.885
| 30.9444 | 259.076 | 48.348 | 57.852 | 52.334 | 74.915
| 30.9514 | 259.868 | 48.365 | 57.851 | 52.355 | 74.954
| 30.9583 | 41.373 | 48.381 | 57.866 | 52.374 | 75.004
| 30.9653 | 260.074 | 47.995 | 57.443 | 52.05 | 74.179
| 30.9722 | 260.179 | 48.027 | 57.493 | 52.067 | 74.18
| 30.9792 | 260.396 | 48.106 | 57.552 | 52.125 | 74.331
| 30.9861 | 260.258 | 48.18 | 57.593 | 52.175 | 74.468
| 30.9931 | 260.945 | 48.237 | 57.624 | 52.211 | 74.588
| 31 | 258.17 | 48.27 | 57.646 | 52.246 | 74.675
| 31.0069 | 258.822 | 48.292 | 57.656 | 52.26 | 74.74
| 31.0139 | 259.516 | 48.315 | 57.668 | 52.282 | 74.798
| 31.0208 | 259.138 | 48.332 | 57.682 | 52.304 | 74.86
| 31.0278 | 259.523 | 48.35 | 57.693 | 52.322 | 74.915
| 31.0347 | 260.044 | 48.364 | 57.705 | 52.337 | 74.964
| 31.0417 | 143.722 | 48.319 | 57.655 | 52.301 | 74.925
| 31.0486 | 259.139 | 48.054 | 57.381 | 52.081 | 74.297
| 31.0556 | 258.94 | 48.104 | 57.441 | 52.122 | 74.386
| 31.0625 | 259.383 | 48.169 | 57.484 | 52.167 | 74.503
| 31.0694 | 259.894 | 48.215 | 57.52 | 52.209 | 74.603
| 31.0764 | 259.717 | 48.256 | 57.537 | 52.239 | 74.697
| 31.0833 | 259.551 | 48.288 | 57.565 | 52.265 | 74.78
| 31.0903 | 256.93 | 48.316 | 57.585 | 52.289 | 74.847
| 31.0972 | 256.475 | 48.327 | 57.59 | 52.308 | 74.881
| 31.1042 | 256.962 | 48.327 | 57.588 | 52.312 | 74.906
| 31.1111 | 257.611 | 48.337 | 57.592 | 52.32 | 74.927
| 31.1181 | 257.259 | 48.337 | 57.594 | 52.324 | 74.945
| 31.125 | 257.038 | 48.341 | 57.597 | 52.331 | 74.969
| 31.1319 | 256.729 | 48.346 | 57.601 | 52.337 | 74.981
| 31.1389 | 107.678 | 48.35 | 57.598 | 52.347 | 74.998
| 31.1458 | 258.806 | 48.147 | 57.38 | 52.173 | 74.543
| 31.1528 | 258.844 | 48.175 | 57.423 | 52.194 | 74.587
| 31.1597 | 258.63 | 48.222 | 57.452 | 52.225 | 74.672
| 31.1667 | 258.673 | 48.258 | 57.477 | 52.255 | 74.745
| 31.1736 | 258.074 | 48.286 | 57.489 | 52.285 | 74.805
| 31.1806 | 257.508 | 48.302 | 57.501 | 52.301 | 74.856
| 31.1875 | 257.586 | 48.321 | 57.506 | 52.311 | 74.899
| 31.1944 | 257.055 | 48.33 | 57.516 | 52.318 | 74.934
| 31.2014 | 256.823 | 48.341 | 57.52 | 52.325 | 74.96
| 31.2083 | 256.795 | 48.343 | 57.523 | 52.338 | 74.98
| 31.2153 | 41.751 | 48.347 | 57.518 | 52.34 | 74.993
| 31.2222 | 260.359 | 47.924 | 57.082 | 51.99 | 74.071
| 31.2292 | 258.838 | 47.966 | 57.142 | 52.012 | 74.1
| 31.2361 | 258.138 | 48.047 | 57.202 | 52.073 | 74.251
| 31.2431 | 257.835 | 48.113 | 57.242 | 52.117 | 74.371
| 31.25 | 257.643 | 48.159 | 57.26 | 52.147 | 74.463
| 31.2569 | 256.066 | 48.194 | 57.28 | 52.165 | 74.535
| 31.2639 | 257.208 | 48.219 | 57.293 | 52.191 | 74.606
| 31.2708 | 261.87 | 48.245 | 57.31 | 52.212 | 74.671
| 31.2778 | 261.021 | 48.288 | 57.355 | 52.253 | 74.775
| 31.2847 | 260.353 | 48.32 | 57.386 | 52.285 | 74.872
| 31.2917 | 259.442 | 48.342 | 57.405 | 52.307 | 74.944
| 31.2986 | 258.259 | 48.355 | 57.418 | 52.329 | 74.99
| 31.3056 | 247.305 | 48.022 | 57.06 | 52.058 | 74.345
| 31.3125 | 261.985 | 47.953 | 57.029 | 51.995 | 74.08
| 31.3194 | 263.083 | 48.051 | 57.116 | 52.066 | 74.262
| 31.3264 | 261.704 | 48.143 | 57.183 | 52.136 | 74.453
| 31.3333 | 261.376 | 48.212 | 57.231 | 52.186 | 74.599
| 31.3403 | 260.992 | 48.259 | 57.264 | 52.228 | 74.716
| 31.3472 | 259.821 | 48.296 | 57.292 | 52.25 | 74.811
| 31.3542 | 259.418 | 48.319 | 57.315 | 52.279 | 74.88
| 31.3611 | 259.462 | 48.334 | 57.333 | 52.298 | 74.932
| 31.3681 | 259.841 | 48.352 | 57.344 | 52.321 | 74.985
| 31.375 | 248.647 | 48.084 | 57.058 | 52.1 | 74.482
| 31.3819 | 259.66 | 48.007 | 57.017 | 52.038 | 74.231
| 31.3889 | 259.097 | 48.079 | 57.084 | 52.096 | 74.364
| 31.3958 | 257.884 | 48.145 | 57.125 | 52.141 | 74.489
| 31.4028 | 257.244 | 48.183 | 57.144 | 52.165 | 74.575
| 31.4097 | 257.562 | 48.216 | 57.158 | 52.188 | 74.638
| 31.4167 | 257.179 | 48.237 | 57.175 | 52.209 | 74.692
| 31.4236 | 256.61 | 48.25 | 57.186 | 52.219 | 74.737
| 31.4306 | 256.748 | 48.264 | 57.194 | 52.236 | 74.771
| 31.4375 | 256.997 | 48.272 | 57.201 | 52.244 | 74.802
| 31.4444 | 257.065 | 48.282 | 57.209 | 52.255 | 74.839
| 31.4514 | 256.916 | 48.286 | 57.211 | 52.264 | 74.866
| 31.4583 | 259.309 | 48.297 | 57.218 | 52.274 | 74.887
| 31.4653 | 259.167 | 48.322 | 57.242 | 52.299 | 74.951
| 31.4722 | 41.731 | 48.341 | 57.251 | 52.316 | 75.001
| 31.4792 | 259.769 | 47.941 | 56.847 | 51.981 | 74.135
| 31.4861 | 259.476 | 47.978 | 56.904 | 52.004 | 74.167
| 31.4931 | 259.122 | 48.059 | 56.961 | 52.061 | 74.314
| 31.5 | 259.829 | 48.127 | 57.002 | 52.108 | 74.447
| 31.5069 | 260.08 | 48.18 | 57.03 | 52.146 | 74.557
| 31.5139 | 259.895 | 48.229 | 57.062 | 52.188 | 74.661
| 31.5208 | 256.341 | 48.263 | 57.094 | 52.219 | 74.759
| 31.5278 | 257.459 | 48.273 | 57.109 | 52.229 | 74.813
| 31.5347 | 257.37 | 48.289 | 57.12 | 52.244 | 74.852
| 31.5417 | 257.512 | 48.297 | 57.132 | 52.257 | 74.897
| 31.5486 | 258.198 | 48.315 | 57.147 | 52.277 | 74.94
| 31.5556 | 256.933 | 48.321 | 57.156 | 52.294 | 74.971
| 31.5625 | 255.662 | 48.325 | 57.16 | 52.299 | 74.997
| 31.5694 | 248.779 | 47.99 | 56.809 | 52.022 | 74.334
| 31.5764 | 260.027 | 47.935 | 56.78 | 51.969 | 74.106
| 31.5833 | 259.386 | 48.023 | 56.851 | 52.033 | 74.266
| 31.5903 | 259.626 | 48.1 | 56.9 | 52.082 | 74.412
| 31.5972 | 259.465 | 48.158 | 56.937 | 52.129 | 74.537
| 31.6042 | 259.169 | 48.203 | 56.966 | 52.163 | 74.642
| 31.6111 | 259.684 | 48.233 | 56.99 | 52.185 | 74.728
| 31.6181 | 259.283 | 48.267 | 57.01 | 52.214 | 74.808
| 31.625 | 260.878 | 48.293 | 57.039 | 52.233 | 74.887
| 31.6319 | 260.187 | 48.321 | 57.069 | 52.267 | 74.968
| 31.6389 | 144.097 | 48.122 | 56.849 | 52.103 | 74.639
| 31.6458 | 259.164 | 47.859 | 56.614 | 51.881 | 73.958
| 31.6528 | 259.375 | 47.941 | 56.696 | 51.94 | 74.099
| 31.6597 | 258.606 | 48.021 | 56.747 | 52.002 | 74.255
| 31.6667 | 258.629 | 48.087 | 56.787 | 52.042 | 74.38
| 31.6944 | 257.171 | 48.203 | 56.864 | 52.137 | 74.695
| 31.7014 | 251.719 | 48.209 | 56.871 | 52.137 | 74.725
| 31.7083 | 251.148 | 48.186 | 56.844 | 52.131 | 74.689
| 31.7153 | 250.58 | 48.162 | 56.821 | 52.109 | 74.648
| 31.7222 | 251.03 | 48.145 | 56.801 | 52.091 | 74.616
| 31.7292 | 250.306 | 48.131 | 56.785 | 52.085 | 74.593
| 31.7361 | 251.375 | 48.125 | 56.773 | 52.076 | 74.568
| 31.7431 | 251.182 | 48.112 | 56.755 | 52.067 | 74.551
| 31.75 | 251.127 | 48.106 | 56.739 | 52.057 | 74.533
| 31.7569 | 251.706 | 48.101 | 56.724 | 52.047 | 74.522
| 31.7639 | 251.876 | 48.096 | 56.711 | 52.038 | 74.513
| 31.7708 | 252.035 | 48.095 | 56.701 | 52.038 | 74.507
| 31.7778 | 252.595 | 48.096 | 56.692 | 52.028 | 74.506
| 31.7847 | 252.193 | 48.095 | 56.681 | 52.028 | 74.509
| 31.7917 | 252.08 | 48.093 | 56.676 | 52.02 | 74.503
| 31.7986 | 251.985 | 48.093 | 56.665 | 52.023 | 74.501
| 31.8056 | 251.895 | 48.087 | 56.656 | 52.017 | 74.497
| 31.8125 | 252.239 | 48.086 | 56.644 | 52.012 | 74.497
| 31.8194 | 251.683 | 48.082 | 56.629 | 52.006 | 74.488
| 31.8264 | 251.585 | 48.076 | 56.618 | 52.002 | 74.485
| 31.8333 | 251.732 | 48.071 | 56.608 | 51.995 | 74.47
| 31.8403 | 252.254 | 48.069 | 56.598 | 51.988 | 74.464
| 31.8472 | 252.269 | 48.066 | 56.588 | 51.985 | 74.47
| 31.8542 | 250.112 | 48.069 | 56.58 | 51.979 | 74.463
| 31.8611 | 250.231 | 48.044 | 56.552 | 51.961 | 74.429
| 31.8681 | 249.428 | 48.032 | 56.534 | 51.944 | 74.402
| 31.875 | 249.259 | 48.015 | 56.509 | 51.933 | 74.371
| 31.8819 | 250.228 | 48.004 | 56.492 | 51.919 | 74.346
| 31.8889 | 250.425 | 47.998 | 56.478 | 51.907 | 74.325
| 31.8958 | 250.488 | 47.99 | 56.465 | 51.907 | 74.313
| 31.9028 | 249.932 | 47.988 | 56.45 | 51.892 | 74.299
| 31.9097 | 249.552 | 47.975 | 56.429 | 51.881 | 74.276
| 31.9167 | 249.343 | 47.961 | 56.407 | 51.87 | 74.246
| 31.9236 | 250.484 | 47.955 | 56.392 | 51.854 | 74.228
| 31.9306 | 250.157 | 47.948 | 56.379 | 51.847 | 74.215
| 31.9375 | 249.885 | 47.947 | 56.366 | 51.843 | 74.206
| 31.9444 | 251.221 | 47.946 | 56.355 | 51.833 | 74.197
| 31.9514 | 252.095 | 47.949 | 56.35 | 51.834 | 74.203
| 31.9583 | 248.372 | 47.948 | 56.341 | 51.831 | 74.208
| 31.9653 | 249.265 | 47.931 | 56.316 | 51.814 | 74.182
| 31.9722 | 250.082 | 47.918 | 56.298 | 51.804 | 74.159
| 31.9792 | 249.852 | 47.912 | 56.289 | 51.792 | 74.14
| 31.9861 | 248.9 | 47.903 | 56.271 | 51.782 | 74.125
| 31.9931 | 249.315 | 47.893 | 56.251 | 51.767 | 74.104
| 32 | 248.032 | 47.877 | 56.229 | 51.756 | 74.071
| 32.0069 | 247.061 | 47.864 | 56.209 | 51.743 | 74.04
| 32.0139 | 247.211 | 47.846 | 56.184 | 51.722 | 74.001
| 32.0208 | 250.911 | 47.829 | 56.161 | 51.704 | 73.968
| 32.0278 | 249.881 | 47.832 | 56.152 | 51.699 | 73.964
| 32.0347 | 249.997 | 47.832 | 56.146 | 51.699 | 73.967
| 32.0417 | 250.129 | 47.834 | 56.137 | 51.696 | 73.973
| 32.0486 | 249.657 | 47.832 | 56.126 | 51.691 | 73.972
| 32.0556 | 250.149 | 47.831 | 56.116 | 51.684 | 73.969
| 32.0625 | 250.226 | 47.827 | 56.11 | 51.676 | 73.969
| 32.0694 | 250.009 | 47.828 | 56.098 | 51.675 | 73.964
| 32.0764 | 249.609 | 47.822 | 56.089 | 51.668 | 73.962
| 32.0833 | 250.174 | 47.817 | 56.081 | 51.662 | 73.953
| 32.0903 | 249.926 | 47.812 | 56.072 | 51.655 | 73.954
| 32.0972 | 250.187 | 47.814 | 56.063 | 51.657 | 73.958
| 32.1042 | 250.628 | 47.816 | 56.062 | 51.651 | 73.954
| 32.1111 | 250.488 | 47.812 | 56.055 | 51.652 | 73.962
| 32.1181 | 249.851 | 47.81 | 56.042 | 51.646 | 73.965
| 32.125 | 249.942 | 47.808 | 56.034 | 51.639 | 73.96
| 32.1319 | 250.032 | 47.797 | 56.03 | 51.633 | 73.953
| 32.1389 | 250.331 | 47.793 | 56.017 | 51.625 | 73.944
| 32.1458 | 249.791 | 47.791 | 56.005 | 51.625 | 73.943
| 32.1528 | 249.586 | 47.785 | 55.999 | 51.617 | 73.93
| 32.1597 | 249.424 | 47.778 | 55.986 | 51.609 | 73.921
| 32.1667 | 250.204 | 47.774 | 55.977 | 51.607 | 73.911
| 32.1736 | 249.055 | 47.769 | 55.964 | 51.598 | 73.907
| 32.1806 | 248.786 | 47.763 | 55.95 | 51.589 | 73.894
| 32.1875 | 248.242 | 47.757 | 55.939 | 51.578 | 73.877
| 32.1944 | 251.422 | 47.749 | 55.928 | 51.572 | 73.867
| 32.2014 | 250.817 | 47.758 | 55.933 | 51.579 | 73.886
| 32.2083 | 250.562 | 47.759 | 55.926 | 51.578 | 73.898
| 32.2153 | 251.566 | 47.767 | 55.925 | 51.58 | 73.908
| 32.2222 | 251.573 | 47.765 | 55.918 | 51.577 | 73.915
| 32.2292 | 252.018 | 47.77 | 55.917 | 51.582 | 73.928
| 32.2361 | 251.85 | 47.774 | 55.922 | 51.579 | 73.94
| 32.2431 | 251.211 | 47.775 | 55.916 | 51.586 | 73.95
| 32.25 | 250.938 | 47.771 | 55.911 | 51.581 | 73.953
| 32.2569 | 250.241 | 47.768 | 55.904 | 51.577 | 73.951
| 32.2639 | 247.04 | 47.755 | 55.887 | 51.561 | 73.931
| 32.2708 | 250.827 | 47.748 | 55.878 | 51.557 | 73.918
| 32.2778 | 250.066 | 47.747 | 55.871 | 51.554 | 73.915
| 32.2847 | 248.063 | 47.734 | 55.859 | 51.545 | 73.898
| 32.2917 | 249.882 | 47.726 | 55.843 | 51.532 | 73.876
| 32.2986 | 249.115 | 47.724 | 55.833 | 51.531 | 73.872
| 32.3056 | 249.131 | 47.716 | 55.827 | 51.523 | 73.864
| 32.3125 | 247.932 | 47.708 | 55.811 | 51.515 | 73.842
| 32.3194 | 248.887 | 47.695 | 55.793 | 51.496 | 73.812
| 32.3264 | 247.993 | 47.69 | 55.776 | 51.49 | 73.793
| 32.3333 | 250.13 | 47.675 | 55.761 | 51.475 | 73.774
| 32.3403 | 252.003 | 47.68 | 55.762 | 51.478 | 73.783
| 32.3472 | 250.514 | 47.688 | 55.764 | 51.481 | 73.8
| 32.3542 | 250.575 | 47.69 | 55.756 | 51.482 | 73.81
| 32.3611 | 251.623 | 47.696 | 55.755 | 51.482 | 73.825
| 32.3681 | 251.352 | 47.703 | 55.758 | 51.486 | 73.839
| 32.375 | 250.501 | 47.703 | 55.755 | 51.486 | 73.85
| 32.3819 | 251.387 | 47.701 | 55.75 | 51.481 | 73.854
| 32.3889 | 251.025 | 47.706 | 55.75 | 51.486 | 73.861
| 32.3958 | 250.113 | 47.707 | 55.746 | 51.486 | 73.872
| 32.4028 | 250.831 | 47.703 | 55.738 | 51.478 | 73.87
| 32.4097 | 249.737 | 47.697 | 55.734 | 51.479 | 73.86
| 32.4167 | 249.385 | 47.688 | 55.72 | 51.459 | 73.846
| 32.4236 | 249.585 | 47.674 | 55.71 | 51.456 | 73.831
| 32.4306 | 249.736 | 47.676 | 55.702 | 51.451 | 73.825
| 32.4375 | 248.817 | 47.665 | 55.689 | 51.442 | 73.812
| 32.4444 | 249.555 | 47.666 | 55.679 | 51.429 | 73.797
| 32.4514 | 247.726 | 47.653 | 55.666 | 51.42 | 73.781
| 32.4583 | 248.623 | 47.64 | 55.649 | 51.413 | 73.758
| 32.4653 | 248.435 | 47.631 | 55.632 | 51.402 | 73.732
| 32.4722 | 247.986 | 47.619 | 55.616 | 51.389 | 73.714
| 32.4792 | 248.069 | 47.61 | 55.602 | 51.378 | 73.689
| 32.4861 | 248.166 | 47.597 | 55.586 | 51.359 | 73.675
| 32.4931 | 247.249 | 47.589 | 55.571 | 51.353 | 73.649
| 32.5 | 248.143 | 47.582 | 55.556 | 51.338 | 73.63
| 32.5069 | 248.685 | 47.576 | 55.541 | 51.33 | 73.616
| 32.5139 | 249.109 | 47.577 | 55.536 | 51.328 | 73.607
| 32.5208 | 248.667 | 47.574 | 55.526 | 51.318 | 73.606
| 32.5278 | 249.561 | 47.571 | 55.523 | 51.319 | 73.607
| 32.5347 | 248.734 | 47.573 | 55.514 | 51.314 | 73.614
| 32.5417 | 249.305 | 47.571 | 55.511 | 51.307 | 73.612
| 32.5486 | 249.686 | 47.572 | 55.503 | 51.307 | 73.614
| 32.5556 | 249.742 | 47.57 | 55.5 | 51.308 | 73.618
| 32.5625 | 249.431 | 47.57 | 55.494 | 51.304 | 73.619
| 32.5694 | 249.612 | 47.569 | 55.486 | 51.301 | 73.621
| 32.5764 | 249.908 | 47.571 | 55.485 | 51.301 | 73.631
| 32.5833 | 250.504 | 47.573 | 55.482 | 51.3 | 73.637
| 32.5903 | 251.585 | 47.578 | 55.486 | 51.303 | 73.661
| 32.5972 | 250.281 | 47.583 | 55.49 | 51.306 | 73.677
| 32.6042 | 250.407 | 47.585 | 55.487 | 51.308 | 73.687
| 32.6111 | 251.261 | 47.585 | 55.487 | 51.305 | 73.701
| 32.6181 | 251.634 | 47.593 | 55.493 | 51.306 | 73.718
| 32.625 | 251.5 | 47.597 | 55.496 | 51.312 | 73.739
| 32.6319 | 248.475 | 47.588 | 55.489 | 51.307 | 73.738
| 32.6389 | 249.101 | 47.575 | 55.47 | 51.297 | 73.71
| 32.6458 | 249.176 | 47.572 | 55.463 | 51.288 | 73.709
| 32.6528 | 247.831 | 47.562 | 55.453 | 51.281 | 73.694
| 32.6597 | 247.504 | 47.548 | 55.439 | 51.271 | 73.671
| 32.6667 | 248.718 | 47.543 | 55.423 | 51.257 | 73.646
| 32.6736 | 248.516 | 47.533 | 55.413 | 51.247 | 73.636
| 32.6806 | 249.647 | 47.533 | 55.411 | 51.245 | 73.634
| 32.6875 | 249.493 | 47.538 | 55.406 | 51.241 | 73.645
| 32.6944 | 249.757 | 47.535 | 55.4 | 51.242 | 73.642
| 32.7014 | 249.362 | 47.535 | 55.395 | 51.237 | 73.649
| 32.7083 | 250.125 | 47.533 | 55.391 | 51.233 | 73.647
| 32.7153 | 250.122 | 47.536 | 55.388 | 51.237 | 73.649
| 32.7222 | 249.303 | 47.537 | 55.389 | 51.239 | 73.657
| 32.7292 | 250.075 | 47.536 | 55.389 | 51.232 | 73.661
| 32.7361 | 249.794 | 47.539 | 55.378 | 51.233 | 73.663
| 32.7431 | 248.943 | 47.53 | 55.374 | 51.231 | 73.661
| 32.75 | 249.254 | 47.53 | 55.371 | 51.228 | 73.663
| 32.7569 | 250.756 | 47.531 | 55.368 | 51.224 | 73.668
| 32.7639 | 247.986 | 47.539 | 55.369 | 51.226 | 73.685
| 32.7708 | 247.757 | 47.525 | 55.36 | 51.221 | 73.67
| 32.7778 | 248.039 | 47.511 | 55.341 | 51.205 | 73.639
| 32.7847 | 247.244 | 47.498 | 55.326 | 51.194 | 73.609
| 32.7917 | 247.51 | 47.484 | 55.308 | 51.18 | 73.577
| 32.7986 | 247.829 | 47.472 | 55.291 | 51.167 | 73.554
| 32.8056 | 247.693 | 47.463 | 55.282 | 51.153 | 73.526
| 32.8125 | 248.427 | 47.455 | 55.269 | 51.147 | 73.517
| 32.8194 | 248.181 | 47.452 | 55.261 | 51.14 | 73.511
| 32.8264 | 247.806 | 47.452 | 55.258 | 51.138 | 73.507
| 32.8333 | 248.573 | 47.452 | 55.247 | 51.136 | 73.507
| 32.8403 | 249.511 | 47.452 | 55.244 | 51.129 | 73.505
| 32.8472 | 250.27 | 47.458 | 55.246 | 51.131 | 73.515
| 32.8542 | 250.221 | 47.461 | 55.245 | 51.136 | 73.534
| 32.8611 | 248.017 | 47.466 | 55.244 | 51.136 | 73.54
| 32.8681 | 249.21 | 47.462 | 55.24 | 51.129 | 73.539
| 32.875 | 249.066 | 47.458 | 55.234 | 51.128 | 73.53
| 32.8819 | 250.044 | 47.455 | 55.233 | 51.13 | 73.54
| 32.8889 | 250.289 | 47.455 | 55.232 | 51.132 | 73.546
| 32.8958 | 249.97 | 47.462 | 55.232 | 51.129 | 73.556
| 32.9028 | 250.619 | 47.463 | 55.235 | 51.133 | 73.568
| 32.9097 | 249.047 | 47.458 | 55.231 | 51.129 | 73.568
| 32.9167 | 249.114 | 47.457 | 55.224 | 51.128 | 73.558
| 32.9236 | 249.119 | 47.454 | 55.222 | 51.124 | 73.559
| 32.9306 | 249.146 | 47.447 | 55.214 | 51.126 | 73.553
| 32.9375 | 250.235 | 47.448 | 55.211 | 51.119 | 73.554
| 32.9444 | 250.609 | 47.452 | 55.213 | 51.116 | 73.565
| 32.9514 | 249.183 | 47.46 | 55.222 | 51.123 | 73.58
| 32.9583 | 250.317 | 47.455 | 55.218 | 51.125 | 73.587
| 32.9653 | 251.115 | 47.461 | 55.217 | 51.128 | 73.594
| 32.9722 | 249.812 | 47.462 | 55.22 | 51.132 | 73.607
| 32.9792 | 250.268 | 47.463 | 55.219 | 51.133 | 73.605
| 32.9861 | 250.197 | 47.463 | 55.219 | 51.133 | 73.617
| 32.9931 | 251.154 | 47.465 | 55.222 | 51.133 | 73.623
| 33 | 249.98 | 47.461 | 55.223 | 51.136 | 73.626
| 33.0069 | 250.589 | 47.462 | 55.218 | 51.129 | 73.632
| 33.0139 | 249.646 | 47.46 | 55.215 | 51.133 | 73.63
| 33.0208 | 250.315 | 47.463 | 55.219 | 51.134 | 73.629
| 33.0278 | 251.789 | 47.459 | 55.214 | 51.127 | 73.638
| 33.0347 | 251.294 | 47.466 | 55.222 | 51.134 | 73.652
| 33.0417 | 251.748 | 47.474 | 55.222 | 51.139 | 73.668
| 33.0486 | 249.142 | 47.476 | 55.229 | 51.146 | 73.681
| 33.0556 | 249.36 | 47.462 | 55.217 | 51.13 | 73.662
| 33.0625 | 249.057 | 47.454 | 55.211 | 51.124 | 73.644
| 33.0694 | 249.234 | 47.447 | 55.201 | 51.116 | 73.626
| 33.0764 | 249.597 | 47.442 | 55.199 | 51.116 | 73.616
| 33.0833 | 249.234 | 47.442 | 55.192 | 51.115 | 73.611
| 33.0903 | 250.023 | 47.437 | 55.192 | 51.107 | 73.605
| 33.0972 | 249.897 | 47.439 | 55.185 | 51.105 | 73.606
| 33.1042 | 249.835 | 47.436 | 55.185 | 51.109 | 73.603
| 33.1111 | 249.217 | 47.438 | 55.185 | 51.109 | 73.608
| 33.1181 | 249.996 | 47.437 | 55.179 | 51.105 | 73.606
| 33.125 | 249.454 | 47.432 | 55.175 | 51.105 | 73.598
| 33.1319 | 249.721 | 47.426 | 55.173 | 51.099 | 73.597
| 33.1389 | 248.735 | 47.426 | 55.169 | 51.098 | 73.591
| 33.1458 | 249.79 | 47.424 | 55.167 | 51.096 | 73.588
| 33.1528 | 249.616 | 47.425 | 55.166 | 51.095 | 73.585
| 33.1597 | 249.4 | 47.422 | 55.162 | 51.092 | 73.582
| 33.1667 | 249.712 | 47.42 | 55.159 | 51.09 | 73.583
| 33.1736 | 249.619 | 47.416 | 55.155 | 51.088 | 73.572
| 33.1806 | 249.073 | 47.41 | 55.153 | 51.086 | 73.57
| 33.1875 | 249.707 | 47.41 | 55.148 | 51.079 | 73.559
| 33.1944 | 248.736 | 47.403 | 55.14 | 51.077 | 73.55
| 33.2014 | 248.655 | 47.401 | 55.135 | 51.071 | 73.54
| 33.2083 | 248.652 | 47.397 | 55.126 | 51.063 | 73.531
| 33.2153 | 249.751 | 47.395 | 55.119 | 51.06 | 73.518
| 33.2222 | 248.927 | 47.387 | 55.119 | 51.062 | 73.511
| 33.2292 | 249.209 | 47.388 | 55.114 | 51.055 | 73.507
| 33.2361 | 249.201 | 47.388 | 55.114 | 51.054 | 73.504
| 33.2431 | 248.99 | 47.382 | 55.106 | 51.052 | 73.499
| 33.25 | 248.778 | 47.384 | 55.106 | 51.054 | 73.494
| 33.2569 | 249.305 | 47.379 | 55.101 | 51.048 | 73.486
| 33.2639 | 247.945 | 47.375 | 55.095 | 51.048 | 73.478
| 33.2708 | 250.777 | 47.375 | 55.094 | 51.043 | 73.472
| 33.2778 | 249.363 | 47.386 | 55.098 | 51.044 | 73.499
| 33.2847 | 249.279 | 47.385 | 55.098 | 51.048 | 73.499
| 33.2917 | 248.414 | 47.383 | 55.097 | 51.047 | 73.496
| 33.2986 | 247.358 | 47.375 | 55.087 | 51.037 | 73.485
| 33.3056 | 251.442 | 47.377 | 55.087 | 51.038 | 73.476
| 33.3125 | 251.175 | 47.388 | 55.098 | 51.048 | 73.502
| 33.3194 | 252.174 | 47.395 | 55.106 | 51.057 | 73.529
| 33.3264 | 252.287 | 47.407 | 55.118 | 51.069 | 73.561
| 33.3333 | 251.826 | 47.416 | 55.124 | 51.079 | 73.58
| 33.3403 | 250.645 | 47.424 | 55.13 | 51.083 | 73.6
| 33.3472 | 250.063 | 47.421 | 55.132 | 51.083 | 73.6
| 33.3542 | 249.314 | 47.418 | 55.13 | 51.081 | 73.597
| 33.3611 | 250.546 | 47.412 | 55.123 | 51.08 | 73.586
| 33.3681 | 249.51 | 47.406 | 55.121 | 51.072 | 73.587
| 33.375 | 249.666 | 47.401 | 55.12 | 51.065 | 73.57
| 33.3819 | 249.911 | 47.404 | 55.114 | 51.069 | 73.571
| 33.3889 | 249.939 | 47.406 | 55.12 | 51.074 | 73.575
| 33.3958 | 248.515 | 47.405 | 55.118 | 51.072 | 73.582
| 33.4028 | 249.354 | 47.401 | 55.114 | 51.068 | 73.572
| 33.4097 | 248.201 | 47.394 | 55.107 | 51.06 | 73.556
| 33.4167 | 248.012 | 47.388 | 55.095 | 51.056 | 73.541
| 33.4236 | 248.131 | 47.38 | 55.085 | 51.051 | 73.527
| 33.4306 | 247.658 | 47.373 | 55.08 | 51.044 | 73.504
| 33.4375 | 247.209 | 47.363 | 55.067 | 51.035 | 73.484
| 33.4444 | 246.787 | 47.355 | 55.059 | 51.022 | 73.459
| 33.4514 | 247.007 | 47.344 | 55.045 | 51.014 | 73.436
| 33.4583 | 247.744 | 47.337 | 55.036 | 51.009 | 73.419
| 33.4653 | 247.385 | 47.332 | 55.03 | 51.002 | 73.41
| 33.4722 | 246.996 | 47.328 | 55.015 | 50.994 | 73.393
| 33.4792 | 246.937 | 47.322 | 55.007 | 50.983 | 73.373
| 33.4861 | 246.042 | 47.317 | 54.995 | 50.98 | 73.353
| 33.4931 | 245.855 | 47.306 | 54.983 | 50.966 | 73.321
| 33.5 | 246.726 | 47.292 | 54.965 | 50.963 | 73.305
| 33.5069 | 248.388 | 47.291 | 54.964 | 50.947 | 73.295
| 33.5139 | 247.82 | 47.29 | 54.96 | 50.95 | 73.296
| 33.5208 | 247.855 | 47.293 | 54.959 | 50.943 | 73.297
| 33.5278 | 247.814 | 47.298 | 54.957 | 50.942 | 73.304
| 33.5347 | 246.781 | 47.297 | 54.948 | 50.942 | 73.297
| 33.5417 | 247.478 | 47.294 | 54.941 | 50.936 | 73.291
| 33.5486 | 247.216 | 47.289 | 54.943 | 50.933 | 73.287
| 33.5556 | 247.213 | 47.29 | 54.936 | 50.934 | 73.285
| 33.5625 | 248.364 | 47.289 | 54.936 | 50.927 | 73.284
| 33.5694 | 248.691 | 47.288 | 54.931 | 50.928 | 73.291
| 33.5764 | 248.858 | 47.292 | 54.936 | 50.93 | 73.298
| 33.5833 | 248.863 | 47.298 | 54.933 | 50.937 | 73.314
| 33.5903 | 248.946 | 47.301 | 54.94 | 50.934 | 73.325
| 33.5972 | 248.454 | 47.305 | 54.937 | 50.936 | 73.332
| 33.6042 | 248.349 | 47.301 | 54.936 | 50.936 | 73.33
| 33.6111 | 248.464 | 47.3 | 54.937 | 50.933 | 73.33
| 33.6181 | 248.534 | 47.3 | 54.932 | 50.929 | 73.333
| 33.625 | 248.747 | 47.302 | 54.937 | 50.931 | 73.338
| 33.6319 | 248.273 | 47.302 | 54.94 | 50.932 | 73.338
| 33.6389 | 248.611 | 47.304 | 54.936 | 50.934 | 73.343
| 33.6458 | 250.226 | 47.305 | 54.937 | 50.938 | 73.349
| 33.6528 | 250.352 | 47.31 | 54.942 | 50.945 | 73.366
| 33.6597 | 251.136 | 47.32 | 54.951 | 50.953 | 73.391
| 33.6667 | 244.199 | 47.329 | 54.956 | 50.961 | 73.418
| 33.6736 | 245.69 | 47.298 | 54.931 | 50.94 | 73.363
| 33.6806 | 243.074 | 47.275 | 54.906 | 50.919 | 73.31
| 33.6875 | 241.51 | 47.241 | 54.871 | 50.888 | 73.232
| 33.6944 | 241.408 | 47.207 | 54.834 | 50.853 | 73.149
| 33.7014 | 241.384 | 47.173 | 54.799 | 50.825 | 73.072
| 33.7083 | 241.264 | 47.144 | 54.767 | 50.802 | 72.998
| 33.7153 | 241.22 | 47.121 | 54.74 | 50.774 | 72.936
| 33.7222 | 241.001 | 47.105 | 54.708 | 50.75 | 72.874
| 33.7292 | 241.527 | 47.086 | 54.675 | 50.723 | 72.814
| 33.7361 | 241.299 | 47.064 | 54.648 | 50.703 | 72.762
| 33.7431 | 241.309 | 47.048 | 54.624 | 50.68 | 72.714
| 33.75 | 241.439 | 47.031 | 54.593 | 50.659 | 72.67
| 33.7569 | 241.966 | 47.022 | 54.571 | 50.639 | 72.631
| 33.7639 | 240.155 | 47.006 | 54.544 | 50.625 | 72.583
| 33.7708 | 240.317 | 46.986 | 54.52 | 50.6 | 72.534
| 33.7778 | 240.199 | 46.967 | 54.495 | 50.573 | 72.488
| 33.7847 | 240.773 | 46.953 | 54.471 | 50.561 | 72.446
| 33.7917 | 242.757 | 46.938 | 54.448 | 50.541 | 72.408
| 33.7986 | 243.637 | 46.937 | 54.442 | 50.536 | 72.403
| 33.8056 | 243.508 | 46.943 | 54.435 | 50.535 | 72.409
| 33.8125 | 244.476 | 46.941 | 54.433 | 50.534 | 72.413
| 33.8194 | 244.389 | 46.941 | 54.424 | 50.529 | 72.414
| 33.8264 | 244.654 | 46.945 | 54.421 | 50.524 | 72.411
| 33.8333 | 244.093 | 46.94 | 54.415 | 50.519 | 72.416
| 33.8403 | 244.864 | 46.946 | 54.411 | 50.514 | 72.422
| 33.8472 | 244.223 | 46.945 | 54.416 | 50.519 | 72.429
| 33.8542 | 241.871 | 46.948 | 54.412 | 50.522 | 72.432
| 33.8611 | 242.168 | 46.928 | 54.392 | 50.503 | 72.401
| 33.8681 | 242.396 | 46.916 | 54.379 | 50.491 | 72.373
| 33.875 | 242.318 | 46.903 | 54.365 | 50.482 | 72.35
| 33.8819 | 243.604 | 46.891 | 54.359 | 50.475 | 72.327
| 33.8889 | 243.514 | 46.893 | 54.355 | 50.467 | 72.319
| 33.8958 | 244.312 | 46.889 | 54.348 | 50.462 | 72.316
| 33.9028 | 243.729 | 46.887 | 54.344 | 50.46 | 72.312
| 33.9097 | 242.353 | 46.885 | 54.343 | 50.463 | 72.304
| 33.9167 | 243.369 | 46.884 | 54.328 | 50.455 | 72.295
| 33.9236 | 243.365 | 46.872 | 54.322 | 50.442 | 72.278
| 33.9306 | 244.285 | 46.874 | 54.321 | 50.444 | 72.278
| 33.9375 | 244.248 | 46.872 | 54.322 | 50.445 | 72.28
| 33.9444 | 242.515 | 46.873 | 54.322 | 50.446 | 72.282
| 33.9514 | 242.354 | 46.865 | 54.309 | 50.438 | 72.26
| 33.9583 | 242.759 | 46.856 | 54.301 | 50.428 | 72.24
| 33.9653 | 244.169 | 46.846 | 54.292 | 50.422 | 72.231
| 33.9722 | 244.747 | 46.848 | 54.295 | 50.42 | 72.231
| 33.9792 | 244.682 | 46.846 | 54.291 | 50.419 | 72.232
| 33.9861 | 243.708 | 46.847 | 54.287 | 50.415 | 72.228
| 33.9931 | 244.05 | 46.84 | 54.281 | 50.407 | 72.218
| 34 | 243.719 | 46.839 | 54.281 | 50.41 | 72.213
| 34.0069 | 243.828 | 46.837 | 54.278 | 50.407 | 72.213
| 34.0139 | 244.116 | 46.835 | 54.277 | 50.41 | 72.21
| 34.0208 | 244.449 | 46.839 | 54.278 | 50.409 | 72.206
| 34.0278 | 244.845 | 46.838 | 54.28 | 50.411 | 72.222
| 34.0347 | 245.573 | 46.843 | 54.286 | 50.413 | 72.228
| 34.0417 | 245.505 | 46.849 | 54.29 | 50.418 | 72.241
| 34.0486 | 244.881 | 46.853 | 54.3 | 50.423 | 72.261
| 34.0556 | 245.935 | 46.858 | 54.301 | 50.431 | 72.271
| 34.0625 | 245.418 | 46.864 | 54.311 | 50.427 | 72.282
| 34.0694 | 245.802 | 46.866 | 54.315 | 50.437 | 72.293
| 34.0764 | 243.163 | 46.87 | 54.319 | 50.449 | 72.304
| 34.0833 | 243.17 | 46.859 | 54.314 | 50.438 | 72.293
| 34.0903 | 243.033 | 46.851 | 54.305 | 50.431 | 72.266
| 34.0972 | 243.389 | 46.843 | 54.298 | 50.425 | 72.244
| 34.1042 | 243.512 | 46.833 | 54.289 | 50.419 | 72.232
| 34.1111 | 243.957 | 46.832 | 54.285 | 50.411 | 72.215
| 34.1181 | 244.174 | 46.827 | 54.283 | 50.414 | 72.208
| 34.125 | 243.744 | 46.82 | 54.281 | 50.41 | 72.197
| 34.1319 | 243.032 | 46.822 | 54.278 | 50.407 | 72.19
| 34.1389 | 243.322 | 46.814 | 54.273 | 50.399 | 72.176
| 34.1458 | 243.7 | 46.813 | 54.269 | 50.401 | 72.167
| 34.1528 | 243.709 | 46.81 | 54.262 | 50.399 | 72.16
| 34.1597 | 243.953 | 46.803 | 54.257 | 50.391 | 72.147
| 34.1667 | 243.312 | 46.799 | 54.256 | 50.394 | 72.141
| 34.1736 | 243.292 | 46.795 | 54.249 | 50.383 | 72.131
| 34.1806 | 243.333 | 46.797 | 54.248 | 50.382 | 72.126
| 34.1875 | 242.919 | 46.791 | 54.244 | 50.377 | 72.111
| 34.1944 | 243.678 | 46.787 | 54.241 | 50.378 | 72.1
| 34.2014 | 243.744 | 46.782 | 54.236 | 50.365 | 72.095
| 34.2083 | 243.272 | 46.784 | 54.236 | 50.369 | 72.087
| 34.2153 | 244.903 | 46.783 | 54.234 | 50.362 | 72.08
| 34.2222 | 245.141 | 46.785 | 54.237 | 50.367 | 72.09
| 34.2292 | 245.452 | 46.792 | 54.242 | 50.379 | 72.102
| 34.2361 | 245.402 | 46.801 | 54.25 | 50.378 | 72.116
| 34.2431 | 245.198 | 46.803 | 54.256 | 50.388 | 72.131
| 34.25 | 244.864 | 46.812 | 54.26 | 50.392 | 72.141
| 34.2569 | 244.956 | 46.814 | 54.263 | 50.394 | 72.151
| 34.2639 | 244.097 | 46.814 | 54.267 | 50.394 | 72.153
| 34.2708 | 243.829 | 46.812 | 54.264 | 50.395 | 72.147
| 34.2778 | 243.562 | 46.801 | 54.258 | 50.393 | 72.132
| 34.2847 | 242.809 | 46.797 | 54.25 | 50.386 | 72.12
| 34.2917 | 243.232 | 46.79 | 54.245 | 50.381 | 72.096
| 34.2986 | 242.01 | 46.78 | 54.234 | 50.37 | 72.08
| 34.3056 | 241.778 | 46.777 | 54.227 | 50.366 | 72.058
| 34.3125 | 241.882 | 46.764 | 54.216 | 50.352 | 72.031
| 34.3194 | 241.804 | 46.753 | 54.205 | 50.346 | 72
| 34.3264 | 240.562 | 46.738 | 54.187 | 50.334 | 71.97
| 34.3333 | 244.613 | 46.736 | 54.186 | 50.329 | 71.951
| 34.3403 | 244.033 | 46.748 | 54.194 | 50.334 | 71.97
| 34.3472 | 243.49 | 46.753 | 54.198 | 50.341 | 71.982
| 34.3542 | 243.225 | 46.755 | 54.195 | 50.338 | 71.981
| 34.3611 | 242.429 | 46.751 | 54.19 | 50.339 | 71.973
| 34.3681 | 242.102 | 46.747 | 54.176 | 50.326 | 71.956
| 34.375 | 241.624 | 46.739 | 54.171 | 50.322 | 71.938
| 34.3819 | 240.66 | 46.731 | 54.156 | 50.313 | 71.915
| 34.3889 | 243.595 | 46.724 | 54.157 | 50.306 | 71.905
| 34.3958 | 242.327 | 46.727 | 54.153 | 50.312 | 71.907
| 34.4028 | 241.502 | 46.718 | 54.15 | 50.306 | 71.89
| 34.4097 | 241.416 | 46.716 | 54.139 | 50.297 | 71.877
| 34.4167 | 239.763 | 46.704 | 54.126 | 50.286 | 71.847
| 34.4236 | 240.074 | 46.69 | 54.108 | 50.272 | 71.814
| 34.4306 | 242.373 | 46.678 | 54.093 | 50.256 | 71.781
| 34.4375 | 242.233 | 46.675 | 54.09 | 50.257 | 71.778
| 34.4444 | 243.606 | 46.682 | 54.096 | 50.261 | 71.784
| 34.4514 | 243.264 | 46.691 | 54.098 | 50.262 | 71.799
| 34.4583 | 242.6 | 46.695 | 54.101 | 50.266 | 71.811
| 34.4653 | 242.863 | 46.697 | 54.1 | 50.265 | 71.816
| 34.4722 | 242.072 | 46.698 | 54.1 | 50.269 | 71.821
| 34.4792 | 242.096 | 46.7 | 54.096 | 50.265 | 71.817
| 34.4861 | 241.409 | 46.695 | 54.089 | 50.26 | 71.811
| 34.4931 | 242.064 | 46.69 | 54.085 | 50.258 | 71.8
| 34.5 | 242.281 | 46.686 | 54.083 | 50.253 | 71.795
| 34.5069 | 243.011 | 46.69 | 54.082 | 50.247 | 71.792
| 34.5139 | 243.09 | 46.691 | 54.078 | 50.252 | 71.793
| 34.5208 | 244.26 | 46.691 | 54.084 | 50.255 | 71.811
| 34.5278 | 244.894 | 46.702 | 54.093 | 50.266 | 71.829
| 34.5347 | 244.967 | 46.715 | 54.104 | 50.272 | 71.854
| 34.5417 | 246.277 | 46.724 | 54.116 | 50.285 | 71.887
| 34.5486 | 246.634 | 46.744 | 54.132 | 50.3 | 71.926
| 34.5556 | 246.013 | 46.757 | 54.144 | 50.315 | 71.954
| 34.5625 | 242.638 | 46.771 | 54.155 | 50.323 | 71.989
| 34.5694 | 242.089 | 46.763 | 54.148 | 50.317 | 71.978
| 34.5764 | 241.701 | 46.745 | 54.137 | 50.308 | 71.95
| 34.5833 | 242.545 | 46.737 | 54.128 | 50.295 | 71.929
| 34.5903 | 243.492 | 46.729 | 54.125 | 50.292 | 71.915
| 34.5972 | 242.966 | 46.728 | 54.119 | 50.291 | 71.911
| 34.6042 | 244 | 46.731 | 54.117 | 50.29 | 71.906
| 34.6111 | 244.007 | 46.729 | 54.118 | 50.291 | 71.916
| 34.6181 | 243.41 | 46.737 | 54.12 | 50.294 | 71.921
| 34.625 | 242.911 | 46.737 | 54.117 | 50.295 | 71.924
| 34.6319 | 242.978 | 46.734 | 54.121 | 50.293 | 71.926
| 34.6389 | 243.349 | 46.735 | 54.119 | 50.286 | 71.922
| 34.6458 | 244.103 | 46.738 | 54.115 | 50.292 | 71.932
| 34.6528 | 243.228 | 46.742 | 54.12 | 50.294 | 71.931
| 34.6597 | 244.086 | 46.737 | 54.118 | 50.296 | 71.932
| 34.6667 | 244.035 | 46.74 | 54.117 | 50.3 | 71.932
| 34.6736 | 243.891 | 46.739 | 54.117 | 50.298 | 71.939
| 34.6806 | 244.434 | 46.741 | 54.118 | 50.301 | 71.945
| 34.6875 | 244.132 | 46.744 | 54.122 | 50.302 | 71.959
| 34.6944 | 244.702 | 46.747 | 54.125 | 50.309 | 71.962
| 34.7014 | 243.824 | 46.75 | 54.127 | 50.309 | 71.969
| 34.7083 | 243.832 | 46.749 | 54.128 | 50.309 | 71.971
| 34.7153 | 243.371 | 46.749 | 54.124 | 50.305 | 71.973
| 34.7222 | 242.964 | 46.749 | 54.121 | 50.302 | 71.97
| 34.7292 | 242.132 | 46.743 | 54.116 | 50.301 | 71.958
| 34.7361 | 243.023 | 46.735 | 54.113 | 50.294 | 71.94
| 34.7431 | 242.71 | 46.735 | 54.104 | 50.287 | 71.935
| 34.75 | 242.612 | 46.724 | 54.098 | 50.283 | 71.93
| 34.7569 | 242.835 | 46.725 | 54.097 | 50.284 | 71.923
| 34.7639 | 243.311 | 46.729 | 54.094 | 50.279 | 71.919
| 34.7708 | 242.802 | 46.723 | 54.087 | 50.283 | 71.914
| 34.7778 | 241.961 | 46.724 | 54.089 | 50.274 | 71.908
| 34.7847 | 242.352 | 46.716 | 54.081 | 50.275 | 71.898
| 34.7917 | 242.221 | 46.715 | 54.077 | 50.268 | 71.887
| 34.7986 | 242.929 | 46.712 | 54.073 | 50.269 | 71.883
| 34.8056 | 243.459 | 46.711 | 54.072 | 50.268 | 71.884
| 34.8125 | 243.766 | 46.72 | 54.073 | 50.267 | 71.885
| 34.8194 | 243.446 | 46.719 | 54.074 | 50.273 | 71.893
| 34.8264 | 243.649 | 46.725 | 54.074 | 50.27 | 71.901
| 34.8333 | 243.529 | 46.723 | 54.075 | 50.269 | 71.907
| 34.8403 | 243.938 | 46.729 | 54.083 | 50.275 | 71.912
| 34.8472 | 241.11 | 46.734 | 54.081 | 50.281 | 71.924
| 34.8542 | 242.091 | 46.723 | 54.078 | 50.277 | 71.913
| 34.8611 | 243.071 | 46.716 | 54.072 | 50.27 | 71.898
| 34.8681 | 243.066 | 46.715 | 54.067 | 50.266 | 71.889
| 34.875 | 243.856 | 46.712 | 54.065 | 50.268 | 71.884
| 34.8819 | 243.778 | 46.713 | 54.064 | 50.265 | 71.88
| 34.8889 | 244.1 | 46.711 | 54.069 | 50.268 | 71.877
| 34.8958 | 243.876 | 46.718 | 54.063 | 50.269 | 71.882
| 34.9028 | 243.831 | 46.718 | 54.068 | 50.267 | 71.884
| 34.9097 | 243.336 | 46.718 | 54.066 | 50.265 | 71.882
| 34.9167 | 241.427 | 46.707 | 54.057 | 50.263 | 71.869
| 34.9236 | 242.358 | 46.698 | 54.049 | 50.255 | 71.843
| 34.9306 | 241.65 | 46.691 | 54.041 | 50.248 | 71.82
| 34.9375 | 242.229 | 46.68 | 54.033 | 50.243 | 71.799
| 34.9444 | 242.439 | 46.678 | 54.025 | 50.232 | 71.787
| 34.9514 | 242.819 | 46.676 | 54.021 | 50.233 | 71.783
| 34.9583 | 243.484 | 46.677 | 54.025 | 50.235 | 71.785
| 34.9653 | 243.993 | 46.678 | 54.027 | 50.231 | 71.786
| 34.9722 | 241.857 | 46.682 | 54.025 | 50.233 | 71.788
| 34.9792 | 243.055 | 46.676 | 54.017 | 50.228 | 71.774
| 34.9861 | 242.844 | 46.667 | 54.012 | 50.221 | 71.763
| 34.9931 | 243.064 | 46.666 | 54.01 | 50.224 | 71.764
| 35 | 244.25 | 46.67 | 54.011 | 50.232 | 71.766

## Weather - Data - Temp
Parameter | Date | Air temperature | Soil temperature [-0.2 m] | Soil temperature [-0.8 m]
Unit | - | °C | °C | °C
| 2014-01-01 | 0.8 | 3.3 | 6.7
| 2014-01-01 00:30 | 0.4 | 3.3 | 6.7
| 2014-01-01 01:00 | -0.2 | 2.8 | 6.7
| 2014-01-01 01:30 | -0.7 | 2.8 | 6.7
| 2014-01-01 02:00 | -0.6 | 2.8 | 6.7
| 2014-01-01 02:30 | -0.4 | 2.8 | 6.7
| 2014-01-01 03:00 | 0 | 2.8 | 6.7
| 2014-01-01 03:30 | 0.6 | 2.8 | 6.7
| 2014-01-01 04:00 | 0.9 | 2.8 | 6.7
| 2014-01-01 04:30 | 1.3 | 2.8 | 6.7
| 2014-01-01 05:00 | 1.4 | 2.8 | 6.7
| 2014-01-01 05:30 | 2.8 | 2.8 | 6.1
| 2014-01-01 06:00 | 3.7 | 2.8 | 6.1
| 2014-01-01 06:30 | 4.1 | 2.8 | 6.1
| 2014-01-01 07:00 | 4.3 | 2.8 | 6.1
| 2014-01-01 07:30 | 4.2 | 2.8 | 6.1
| 2014-01-01 08:00 | 4.2 | 2.8 | 6.1
| 2014-01-01 08:30 | 4.3 | 2.8 | 6.1
| 2014-01-01 09:00 | 4.8 | 2.8 | 6.1
| 2014-01-01 09:30 | 5.4 | 2.8 | 6.1
| 2014-01-01 10:00 | 5.4 | 2.8 | 6.1
| 2014-01-01 10:30 | 5.7 | 2.8 | 6.1
| 2014-01-01 11:00 | 6 | 2.8 | 6.1
| 2014-01-01 11:30 | 6.5 | 2.8 | 6.1
| 2014-01-01 12:00 | 7.1 | 3.3 | 6.1
| 2014-01-01 12:30 | 7.9 | 3.3 | 6.1
| 2014-01-01 13:00 | 7.4 | 3.3 | 6.1
| 2014-01-01 13:30 | 8.4 | 3.3 | 6.1
| 2014-01-01 14:00 | 9.2 | 3.3 | 6.1
| 2014-01-01 14:30 | 9.3 | 3.3 | 6.1
| 2014-01-01 15:00 | 9.1 | 3.3 | 6.1
| 2014-01-01 15:30 | 8.1 | 3.9 | 6.1
| 2014-01-01 16:00 | 7.8 | 3.9 | 6.1
| 2014-01-01 16:30 | 7.4 | 3.9 | 6.1
| 2014-01-01 17:00 | 7.3 | 3.9 | 6.1
| 2014-01-01 17:30 | 6.8 | 3.9 | 6.1
| 2014-01-01 18:00 | 6.2 | 3.9 | 6.1
| 2014-01-01 18:30 | 6.4 | 3.9 | 6.1
| 2014-01-01 19:00 | 7.7 | 3.9 | 6.1
| 2014-01-01 19:30 | 8.2 | 3.9 | 6.1
| 2014-01-01 20:00 | 8 | 3.9 | 6.1
| 2014-01-01 20:30 | 8.4 | 3.9 | 6.1
| 2014-01-01 21:00 | 8.3 | 3.9 | 6.1
| 2014-01-01 21:30 | 8.4 | 3.9 | 6.1
| 2014-01-01 22:00 | 7.6 | 3.9 | 6.1
| 2014-01-01 22:30 | 6.5 | 3.9 | 6.1
| 2014-01-01 23:00 | 6.2 | 3.9 | 6.1
| 2014-01-01 23:30 | 5.8 | 3.9 | 6.1
| 2014-01-02 | 5.8 | 3.9 | 6.1
| 2014-01-02 00:30 | 5.8 | 3.9 | 6.1
| 2014-01-02 01:00 | 6 | 3.9 | 6.1
| 2014-01-02 01:30 | 6.3 | 3.9 | 6.1
| 2014-01-02 02:00 | 6.7 | 3.9 | 6.1
| 2014-01-02 02:30 | 7.3 | 3.9 | 6.1
| 2014-01-02 03:00 | 6.9 | 3.9 | 6.1
| 2014-01-02 03:30 | 6.7 | 3.9 | 6.1
| 2014-01-02 04:00 | 6.6 | 3.9 | 6.1
| 2014-01-02 04:30 | 6.7 | 3.9 | 6.1
| 2014-01-02 05:00 | 6.9 | 4.4 | 6.1
| 2014-01-02 05:30 | 6.6 | 4.4 | 6.1
| 2014-01-02 06:00 | 6.5 | 4.4 | 6.1
| 2014-01-02 06:30 | 6.6 | 4.4 | 6.1
| 2014-01-02 07:00 | 6.6 | 4.4 | 6.1
| 2014-01-02 07:30 | 6.6 | 4.4 | 6.1
| 2014-01-02 08:00 | 6.7 | 4.4 | 6.1
| 2014-01-02 08:30 | 7 | 4.4 | 6.1
| 2014-01-02 09:00 | 7.7 | 4.4 | 6.1
| 2014-01-02 09:30 | 8.3 | 4.4 | 6.1
| 2014-01-02 10:00 | 8.7 | 4.4 | 6.1
| 2014-01-02 10:30 | 8.7 | 4.4 | 6.1
| 2014-01-02 11:00 | 9 | 4.4 | 6.1
| 2014-01-02 11:30 | 9.3 | 4.4 | 6.1
| 2014-01-02 12:00 | 9.5 | 4.4 | 6.1
| 2014-01-02 12:30 | 9.6 | 4.4 | 6.1
| 2014-01-02 13:00 | 9.7 | 4.4 | 6.1
| 2014-01-02 13:30 | 9.8 | 5 | 6.1
| 2014-01-02 14:00 | 9.8 | 5 | 6.1
| 2014-01-02 14:30 | 9.9 | 5 | 6.1
| 2014-01-02 15:00 | 10.4 | 5 | 6.1
| 2014-01-02 15:30 | 10 | 5 | 6.1
| 2014-01-02 16:00 | 9.3 | 5 | 6.1
| 2014-01-02 16:30 | 8.2 | 5 | 6.1
| 2014-01-02 17:00 | 7.8 | 5 | 6.1
| 2014-01-02 17:30 | 7.6 | 5.6 | 6.1
| 2014-01-02 18:00 | 7.1 | 5.6 | 6.1
| 2014-01-02 18:30 | 6.7 | 5.6 | 6.1
| 2014-01-02 19:00 | 6.4 | 5.6 | 6.1
| 2014-01-02 19:30 | 6.1 | 5.6 | 6.1
| 2014-01-02 20:00 | 6 | 5.6 | 6.1
| 2014-01-02 20:30 | 6.2 | 5 | 6.1
| 2014-01-02 21:00 | 6.3 | 5 | 6.1
| 2014-01-02 21:30 | 6.5 | 5 | 6.1
| 2014-01-02 22:00 | 6.7 | 5 | 6.1
| 2014-01-02 22:30 | 7.1 | 5 | 6.1
| 2014-01-02 23:00 | 7.1 | 5 | 6.1
| 2014-01-02 23:30 | 6.9 | 5 | 6.1
| 2014-01-03 | 6.8 | 5 | 6.1
| 2014-01-03 00:30 | 6.7 | 5 | 6.1
| 2014-01-03 01:00 | 6.7 | 5 | 6.1
| 2014-01-03 01:30 | 6.6 | 5 | 6.1
| 2014-01-03 02:00 | 6.8 | 5 | 6.1
| 2014-01-03 02:30 | 6.6 | 5 | 6.1
| 2014-01-03 03:00 | 7.2 | 5 | 6.1
| 2014-01-03 03:30 | 6.8 | 4.4 | 6.1
| 2014-01-03 04:00 | 6.4 | 4.4 | 6.1
| 2014-01-03 04:30 | 6.9 | 4.4 | 6.1
| 2014-01-03 05:00 | 5.9 | 4.4 | 6.1
| 2014-01-03 05:30 | 5.3 | 4.4 | 6.1
| 2014-01-03 06:00 | 5.2 | 4.4 | 6.1
| 2014-01-03 06:30 | 5.6 | 4.4 | 6.1
| 2014-01-03 07:00 | 5.4 | 4.4 | 6.1
| 2014-01-03 07:30 | 6.1 | 4.4 | 6.1
| 2014-01-03 08:00 | 6.4 | 4.4 | 6.1
| 2014-01-03 08:30 | 5.7 | 4.4 | 6.1
| 2014-01-03 09:00 | 5.8 | 4.4 | 6.1
| 2014-01-03 09:30 | 6.7 | 4.4 | 6.1
| 2014-01-03 10:00 | 6.9 | 4.4 | 6.1
| 2014-01-03 10:30 | 7.7 | 4.4 | 6.1
| 2014-01-03 11:00 | 8.2 | 4.4 | 6.1
| 2014-01-03 11:30 | 8.7 | 4.4 | 6.1
| 2014-01-03 12:00 | 8.7 | 4.4 | 6.1
| 2014-01-03 12:30 | 8.9 | 4.4 | 6.1
| 2014-01-03 13:00 | 8.7 | 4.4 | 6.1
| 2014-01-03 13:30 | 8.7 | 4.4 | 6.1
| 2014-01-03 14:00 | 8.8 | 4.4 | 6.1
| 2014-01-03 14:30 | 9 | 5 | 6.1
| 2014-01-03 15:00 | 9 | 5 | 6.1
| 2014-01-03 15:30 | 9.1 | 5 | 6.1
| 2014-01-03 16:00 | 9.5 | 5 | 6.1
| 2014-01-03 16:30 | 9.4 | 5 | 6.1
| 2014-01-03 17:00 | 9.3 | 5 | 6.1
| 2014-01-03 17:30 | 9.5 | 5 | 6.1
| 2014-01-03 18:00 | 9.7 | 5 | 6.1
| 2014-01-03 18:30 | 9.9 | 5 | 6.1
| 2014-01-03 19:00 | 10.1 | 5 | 6.1
| 2014-01-03 19:30 | 9.9 | 5 | 6.1
| 2014-01-03 20:00 | 9.6 | 5 | 6.1
| 2014-01-03 20:30 | 9.3 | 5 | 6.1
| 2014-01-03 21:00 | 9.5 | 5.6 | 6.1
| 2014-01-03 21:30 | 9.4 | 5.6 | 6.1
| 2014-01-03 22:00 | 9.2 | 5.6 | 6.1
| 2014-01-03 22:30 | 9.2 | 5.6 | 6.1
| 2014-01-03 23:00 | 9.3 | 5.6 | 6.1
| 2014-01-03 23:30 | 9.9 | 5.6 | 6.1
| 2014-01-04 | 9.7 | 5.6 | 6.1
| 2014-01-04 00:30 | 9.4 | 5.6 | 6.1
| 2014-01-04 01:00 | 9.3 | 5.6 | 6.1
| 2014-01-04 01:30 | 9.1 | 5.6 | 6.1
| 2014-01-04 02:00 | 8.7 | 5.6 | 6.1
| 2014-01-04 02:30 | 8.2 | 5.6 | 6.1
| 2014-01-04 03:00 | 7.8 | 5.6 | 6.1
| 2014-01-04 03:30 | 6.6 | 5.6 | 6.1
| 2014-01-04 04:00 | 6.7 | 5.6 | 6.1
| 2014-01-04 04:30 | 6.4 | 5.6 | 6.1
| 2014-01-04 05:00 | 6.9 | 5 | 6.1
| 2014-01-04 05:30 | 7 | 5 | 6.1
| 2014-01-04 06:00 | 6.3 | 5 | 6.1
| 2014-01-04 06:30 | 5.8 | 5 | 6.1
| 2014-01-04 07:00 | 5.3 | 5 | 6.1
| 2014-01-04 07:30 | 4.9 | 5 | 6.1
| 2014-01-04 08:00 | 4.7 | 5 | 6.1
| 2014-01-04 08:30 | 4.5 | 5 | 6.1
| 2014-01-04 09:00 | 4.3 | 5 | 6.1
| 2014-01-04 09:30 | 4.5 | 5 | 6.1
| 2014-01-04 10:00 | 5.2 | 5 | 6.1
| 2014-01-04 10:30 | 5.8 | 5 | 6.1
| 2014-01-04 11:00 | 6.8 | 5 | 6.1
| 2014-01-04 11:30 | 7.2 | 5 | 6.1
| 2014-01-04 12:00 | 8.1 | 5 | 6.1
| 2014-01-04 12:30 | 8.6 | 5 | 6.1
| 2014-01-04 13:00 | 8.7 | 5 | 6.1
| 2014-01-04 13:30 | 9 | 5 | 6.1
| 2014-01-04 14:00 | 8.6 | 5 | 6.1
| 2014-01-04 14:30 | 7.3 | 5 | 6.1
| 2014-01-04 15:00 | 7.1 | 5 | 6.1
| 2014-01-04 15:30 | 6.7 | 5 | 6.1
| 2014-01-04 16:00 | 6.3 | 5 | 6.1
| 2014-01-04 16:30 | 6.1 | 5 | 6.1
| 2014-01-04 17:00 | 6.1 | 5 | 6.1
| 2014-01-04 17:30 | 5.9 | 5 | 6.1
| 2014-01-04 18:00 | 6 | 5 | 6.1
| 2014-01-04 18:30 | 5.8 | 5 | 6.1
| 2014-01-04 19:00 | 5.8 | 5 | 6.1
| 2014-01-04 19:30 | 5.6 | 5 | 6.1
| 2014-01-04 20:00 | 6.1 | 5 | 6.1
| 2014-01-04 20:30 | 6.3 | 5 | 6.1
| 2014-01-04 21:00 | 6.2 | 5 | 6.1
| 2014-01-04 21:30 | 6.6 | 5 | 6.1
| 2014-01-04 22:00 | 6.7 | 5 | 6.1
| 2014-01-04 22:30 | 6.5 | 5 | 6.1
| 2014-01-04 23:00 | 6.2 | 5 | 6.1
| 2014-01-04 23:30 | 6.2 | 5 | 6.1
| 2014-01-05 | 6.2 | 5 | 6.1
| 2014-01-05 00:30 | 6.5 | 5 | 6.1
| 2014-01-05 01:00 | 5.4 | 5 | 6.1
| 2014-01-05 01:30 | 5 | 5 | 6.1
| 2014-01-05 02:00 | 4.7 | 5 | 6.1
| 2014-01-05 02:30 | 3.9 | 5 | 6.1
| 2014-01-05 03:00 | 3.9 | 5 | 6.1
| 2014-01-05 03:30 | 4.3 | 5 | 6.1
| 2014-01-05 04:00 | 5.6 | 5 | 6.1
| 2014-01-05 04:30 | 6.1 | 5 | 6.1
| 2014-01-05 05:00 | 6.2 | 5 | 6.1
| 2014-01-05 05:30 | 6.1 | 5 | 6.1
| 2014-01-05 06:00 | 6.1 | 5 | 6.1
| 2014-01-05 06:30 | 6.1 | 5 | 6.1
| 2014-01-05 07:00 | 6.2 | 5 | 6.1
| 2014-01-05 07:30 | 6.2 | 5 | 6.1
| 2014-01-05 08:00 | 6.2 | 5 | 6.1
| 2014-01-05 08:30 | 6.3 | 5 | 6.1
| 2014-01-05 09:00 | 6.4 | 5 | 6.1
| 2014-01-05 09:30 | 6.4 | 5 | 6.1
| 2014-01-05 10:00 | 6.5 | 5 | 6.1
| 2014-01-05 10:30 | 6.7 | 5 | 6.1
| 2014-01-05 11:00 | 6.5 | 5 | 6.1
| 2014-01-05 11:30 | 5.9 | 5 | 6.1
| 2014-01-05 12:00 | 6.4 | 5 | 6.1
| 2014-01-05 12:30 | 7 | 5 | 6.1
| 2014-01-05 13:00 | 6.9 | 5 | 6.1
| 2014-01-05 13:30 | 7.2 | 5 | 6.1
| 2014-01-05 14:00 | 8 | 5 | 6.1
| 2014-01-05 14:30 | 8.2 | 5 | 6.1
| 2014-01-05 15:00 | 7.9 | 5 | 6.1
| 2014-01-05 15:30 | 8.1 | 5 | 6.1
| 2014-01-05 16:00 | 6.3 | 5.6 | 6.1
| 2014-01-05 16:30 | 5.9 | 5.6 | 6.1
| 2014-01-05 17:00 | 6.1 | 5.6 | 6.1
| 2014-01-05 17:30 | 6.3 | 5.6 | 6.1
| 2014-01-05 18:00 | 6.1 | 5.6 | 6.1
| 2014-01-05 18:30 | 4.6 | 5.6 | 6.1
| 2014-01-05 19:00 | 3.3 | 5.6 | 6.1
| 2014-01-05 19:30 | 3.1 | 5.6 | 6.1
| 2014-01-05 20:00 | 3.1 | 5.6 | 6.1
| 2014-01-05 20:30 | 3.7 | 5 | 6.1
| 2014-01-05 21:00 | 4.2 | 5 | 6.1
| 2014-01-05 21:30 | 3.3 | 5 | 6.1
| 2014-01-05 22:00 | 2.8 | 5 | 6.1
| 2014-01-05 22:30 | 3 | 5 | 6.1
| 2014-01-05 23:00 | 3.4 | 5 | 6.1
| 2014-01-05 23:30 | 3.8 | 5 | 6.1
| 2014-01-06 | 3.7 | 5 | 6.1
| 2014-01-06 00:30 | 3.8 | 4.4 | 6.1
| 2014-01-06 01:00 | 4.1 | 4.4 | 6.1
| 2014-01-06 01:30 | 4.1 | 4.4 | 6.1
| 2014-01-06 02:00 | 3.9 | 4.4 | 6.1
| 2014-01-06 02:30 | 3.8 | 4.4 | 6.1
| 2014-01-06 03:00 | 4.1 | 4.4 | 6.1
| 2014-01-06 03:30 | 4 | 4.4 | 6.1
| 2014-01-06 04:00 | 4.1 | 4.4 | 6.1
| 2014-01-06 04:30 | 4.2 | 3.9 | 6.1
| 2014-01-06 05:00 | 4.3 | 3.9 | 6.1
| 2014-01-06 05:30 | 4.8 | 3.9 | 6.1
| 2014-01-06 06:00 | 5.3 | 3.9 | 6.1
| 2014-01-06 06:30 | 6.2 | 3.9 | 6.1
| 2014-01-06 07:00 | 6.6 | 3.9 | 6.1
| 2014-01-06 07:30 | 6.6 | 3.9 | 6.1
| 2014-01-06 08:00 | 6.6 | 3.9 | 6.1
| 2014-01-06 08:30 | 6.4 | 3.9 | 6.1
| 2014-01-06 09:00 | 6.7 | 3.9 | 6.1
| 2014-01-06 09:30 | 7 | 3.9 | 6.1
| 2014-01-06 10:00 | 7.1 | 3.9 | 6.1
| 2014-01-06 10:30 | 7.4 | 3.9 | 6.1
| 2014-01-06 11:00 | 7.6 | 3.9 | 6.1
| 2014-01-06 11:30 | 7.8 | 3.9 | 6.1
| 2014-01-06 12:00 | 8.1 | 3.9 | 6.1
| 2014-01-06 12:30 | 8.1 | 3.9 | 6.1
| 2014-01-06 13:00 | 8.6 | 4.4 | 6.1
| 2014-01-06 13:30 | 8.9 | 4.4 | 6.1
| 2014-01-06 14:00 | 9.2 | 4.4 | 6.1
| 2014-01-06 14:30 | 9.3 | 4.4 | 6.1
| 2014-01-06 15:00 | 9.5 | 4.4 | 6.1
| 2014-01-06 15:30 | 9.8 | 4.4 | 6.1
| 2014-01-06 16:00 | 9.5 | 4.4 | 6.1
| 2014-01-06 16:30 | 9.1 | 4.4 | 6.1
| 2014-01-06 17:00 | 9.3 | 4.4 | 6.1
| 2014-01-06 17:30 | 9.4 | 5 | 6.1
| 2014-01-06 18:00 | 9.4 | 5 | 6.1
| 2014-01-06 18:30 | 9 | 5 | 6.1
| 2014-01-06 19:00 | 8.1 | 5 | 6.1
| 2014-01-06 19:30 | 7.7 | 5 | 6.1
| 2014-01-06 20:00 | 7.6 | 5 | 6.1
| 2014-01-06 20:30 | 7.6 | 5 | 6.1
| 2014-01-06 21:00 | 7.6 | 5 | 6.1
| 2014-01-06 21:30 | 7.5 | 5 | 6.1
| 2014-01-06 22:00 | 8.1 | 5 | 6.1
| 2014-01-06 22:30 | 8.3 | 5 | 6.1
| 2014-01-06 23:00 | 8.6 | 5 | 6.1
| 2014-01-06 23:30 | 8.4 | 5 | 6.1
| 2014-01-07 | 8.4 | 5 | 6.1
| 2014-01-07 00:30 | 8.7 | 5 | 6.1
| 2014-01-07 01:00 | 9 | 5 | 6.1
| 2014-01-07 01:30 | 9 | 5 | 6.1
| 2014-01-07 02:00 | 8.4 | 5 | 6.1
| 2014-01-07 02:30 | 8.9 | 5.6 | 6.1
| 2014-01-07 03:00 | 9.2 | 5.6 | 6.1
| 2014-01-07 03:30 | 8.9 | 5.6 | 6.1
| 2014-01-07 04:00 | 9.1 | 5.6 | 6.1
| 2014-01-07 04:30 | 9.6 | 5.6 | 6.1
| 2014-01-07 05:00 | 9.7 | 5.6 | 6.1
| 2014-01-07 05:30 | 9.5 | 5.6 | 6.1
| 2014-01-07 06:00 | 8.8 | 5.6 | 6.1
| 2014-01-07 06:30 | 8.3 | 5.6 | 6.1
| 2014-01-07 07:00 | 8.5 | 5.6 | 6.1
| 2014-01-07 07:30 | 8.9 | 5.6 | 6.1
| 2014-01-07 08:00 | 9.1 | 5.6 | 6.1
| 2014-01-07 08:30 | 9 | 5.6 | 6.1
| 2014-01-07 09:00 | 9.7 | 5.6 | 6.1
| 2014-01-07 09:30 | 10.3 | 5.6 | 6.1
| 2014-01-07 10:00 | 10.6 | 5.6 | 6.1
| 2014-01-07 10:30 | 11 | 5.6 | 6.1
| 2014-01-07 11:00 | 11.6 | 5.6 | 6.1
| 2014-01-07 11:30 | 12.2 | 5.6 | 6.1
| 2014-01-07 12:00 | 12.2 | 5.6 | 6.1
| 2014-01-07 12:30 | 11.6 | 5.6 | 6.1
| 2014-01-07 13:00 | 11.8 | 5.6 | 6.1
| 2014-01-07 13:30 | 11.9 | 5.6 | 6.1
| 2014-01-07 14:00 | 11.9 | 5.6 | 6.1
| 2014-01-07 14:30 | 12.2 | 5.6 | 6.1
| 2014-01-07 15:00 | 11.9 | 6.1 | 6.1
| 2014-01-07 15:30 | 12.2 | 6.1 | 6.1
| 2014-01-07 16:00 | 12.1 | 6.1 | 6.1
| 2014-01-07 16:30 | 11.7 | 6.1 | 6.1
| 2014-01-07 17:00 | 11.5 | 6.1 | 6.1
| 2014-01-07 17:30 | 11.3 | 6.1 | 6.1
| 2014-01-07 18:00 | 11.7 | 6.1 | 6.1
| 2014-01-07 18:30 | 10.7 | 6.1 | 6.1
| 2014-01-07 19:00 | 10.2 | 6.1 | 6.1
| 2014-01-07 19:30 | 9.8 | 6.1 | 6.1
| 2014-01-07 20:00 | 9.7 | 6.1 | 6.1
| 2014-01-07 20:30 | 9.7 | 6.1 | 6.1
| 2014-01-07 21:00 | 9.2 | 6.1 | 6.1
| 2014-01-07 21:30 | 9.2 | 6.7 | 6.1
| 2014-01-07 22:00 | 9.7 | 6.7 | 6.1
| 2014-01-07 22:30 | 9.8 | 6.7 | 6.1
| 2014-01-07 23:00 | 9.9 | 6.7 | 6.1
| 2014-01-07 23:30 | 10.2 | 6.7 | 6.1
| 2014-01-08 | 10.3 | 6.7 | 6.1
| 2014-01-08 00:30 | 10.2 | 6.7 | 6.1
| 2014-01-08 01:00 | 10 | 6.7 | 6.1
| 2014-01-08 01:30 | 10.3 | 6.7 | 6.1
| 2014-01-08 02:00 | 10.4 | 6.7 | 6.1
| 2014-01-08 02:30 | 10 | 6.7 | 6.1
| 2014-01-08 03:00 | 10 | 6.7 | 6.1
| 2014-01-08 03:30 | 10.1 | 6.7 | 6.1
| 2014-01-08 04:00 | 10.2 | 6.7 | 6.7
| 2014-01-08 04:30 | 10.2 | 6.7 | 6.7
| 2014-01-08 05:00 | 9.6 | 6.7 | 6.7
| 2014-01-08 05:30 | 9.6 | 6.7 | 6.7
| 2014-01-08 06:00 | 9.5 | 6.7 | 6.7
| 2014-01-08 06:30 | 9.7 | 6.7 | 6.7
| 2014-01-08 07:00 | 9.9 | 6.7 | 6.7
| 2014-01-08 07:30 | 9.8 | 6.7 | 6.7
| 2014-01-08 08:00 | 10.2 | 6.7 | 6.7
| 2014-01-08 08:30 | 10.4 | 6.7 | 6.7
| 2014-01-08 09:00 | 10.8 | 6.7 | 6.7
| 2014-01-08 09:30 | 10.6 | 6.7 | 6.7
| 2014-01-08 10:00 | 10.7 | 6.7 | 6.7
| 2014-01-08 10:30 | 11.1 | 6.7 | 6.7
| 2014-01-08 11:00 | 10.9 | 6.7 | 6.7
| 2014-01-08 11:30 | 12.4 | 6.7 | 6.7
| 2014-01-08 12:00 | 13.2 | 6.7 | 6.7
| 2014-01-08 12:30 | 13.6 | 6.7 | 6.7
| 2014-01-08 13:00 | 13.6 | 6.7 | 6.7
| 2014-01-08 13:30 | 13.8 | 6.7 | 6.7
| 2014-01-08 14:00 | 13.7 | 7.2 | 6.7
| 2014-01-08 14:30 | 13.6 | 7.2 | 6.7
| 2014-01-08 15:00 | 12.9 | 7.2 | 6.7
| 2014-01-08 15:30 | 12.5 | 7.2 | 6.7
| 2014-01-08 16:00 | 11.9 | 7.2 | 6.7
| 2014-01-08 16:30 | 10.8 | 7.8 | 6.7
| 2014-01-08 17:00 | 9.2 | 7.8 | 6.7
| 2014-01-08 17:30 | 9.3 | 7.8 | 6.7
| 2014-01-08 18:00 | 9 | 7.8 | 6.7
| 2014-01-08 18:30 | 9.4 | 7.8 | 6.7
| 2014-01-08 19:00 | 8.9 | 7.8 | 6.7
| 2014-01-08 19:30 | 8.2 | 7.2 | 6.7
| 2014-01-08 20:00 | 8.2 | 7.2 | 6.7
| 2014-01-08 20:30 | 8.1 | 7.2 | 6.7
| 2014-01-08 21:00 | 7.4 | 7.2 | 6.7
| 2014-01-08 21:30 | 6.8 | 7.2 | 6.7
| 2014-01-08 22:00 | 6.7 | 7.2 | 6.7
| 2014-01-08 22:30 | 6.7 | 7.2 | 6.7
| 2014-01-08 23:00 | 6.4 | 7.2 | 6.7
| 2014-01-08 23:30 | 5.9 | 7.2 | 6.7
| 2014-01-09 | 5.6 | 6.7 | 6.7
| 2014-01-09 00:30 | 5.6 | 6.7 | 6.7
| 2014-01-09 01:00 | 5.7 | 6.7 | 6.7
| 2014-01-09 01:30 | 6.2 | 6.7 | 6.7
| 2014-01-09 02:00 | 6.7 | 6.7 | 6.7
| 2014-01-09 02:30 | 6.6 | 6.7 | 6.7
| 2014-01-09 03:00 | 6.5 | 6.7 | 6.7
| 2014-01-09 03:30 | 6.8 | 6.7 | 6.7
| 2014-01-09 04:00 | 6.8 | 6.7 | 6.7
| 2014-01-09 04:30 | 6.7 | 6.7 | 6.7
| 2014-01-09 05:00 | 6.6 | 6.7 | 6.7
| 2014-01-09 05:30 | 6.4 | 6.7 | 6.7
| 2014-01-09 06:00 | 6.8 | 6.7 | 6.7
| 2014-01-09 06:30 | 8.6 | 6.1 | 6.7
| 2014-01-09 07:00 | 9 | 6.1 | 6.7
| 2014-01-09 07:30 | 9 | 6.1 | 6.7
| 2014-01-09 08:00 | 9.2 | 6.1 | 6.7
| 2014-01-09 08:30 | 9 | 6.1 | 6.7
| 2014-01-09 09:00 | 8.8 | 6.1 | 6.7
| 2014-01-09 09:30 | 8.9 | 6.1 | 6.7
| 2014-01-09 10:00 | 9.4 | 6.1 | 6.7
| 2014-01-09 10:30 | 9.6 | 6.1 | 6.7
| 2014-01-09 11:00 | 10.1 | 6.1 | 6.7
| 2014-01-09 11:30 | 10.6 | 6.1 | 6.7
| 2014-01-09 12:00 | 10.7 | 6.7 | 6.7
| 2014-01-09 12:30 | 10.8 | 6.7 | 6.7
| 2014-01-09 13:00 | 11.5 | 6.7 | 6.7
| 2014-01-09 13:30 | 12.1 | 6.7 | 6.7
| 2014-01-09 14:00 | 12.6 | 6.7 | 6.7
| 2014-01-09 14:30 | 12.6 | 6.7 | 6.7
| 2014-01-09 15:00 | 13 | 6.7 | 6.7
| 2014-01-09 15:30 | 12.8 | 6.7 | 6.7
| 2014-01-09 16:00 | 12.7 | 6.7 | 6.7
| 2014-01-09 16:30 | 12.5 | 7.2 | 6.7
| 2014-01-09 17:00 | 12 | 7.2 | 6.7
| 2014-01-09 17:30 | 11.7 | 7.2 | 6.7
| 2014-01-09 18:00 | 10.1 | 7.2 | 6.7
| 2014-01-09 18:30 | 9.7 | 7.2 | 6.7
| 2014-01-09 19:00 | 9.5 | 7.2 | 6.7
| 2014-01-09 19:30 | 9.2 | 7.2 | 6.7
| 2014-01-09 20:00 | 9.2 | 7.2 | 6.7
| 2014-01-09 20:30 | 9.2 | 7.2 | 6.7
| 2014-01-09 21:00 | 9.2 | 7.2 | 6.7
| 2014-01-09 21:30 | 9.4 | 7.2 | 6.7
| 2014-01-09 22:00 | 8.9 | 7.2 | 6.7
| 2014-01-09 22:30 | 9 | 7.2 | 6.7
| 2014-01-09 23:00 | 8.8 | 7.2 | 6.7
| 2014-01-09 23:30 | 7.9 | 7.2 | 6.7
| 2014-01-10 | 7.4 | 7.2 | 6.7
| 2014-01-10 00:30 | 6.8 | 7.2 | 6.7
| 2014-01-10 01:00 | 4.8 | 7.2 | 6.7
| 2014-01-10 01:30 | 5.4 | 7.2 | 6.7
| 2014-01-10 02:00 | 3.8 | 7.2 | 6.7
| 2014-01-10 02:30 | 4.2 | 6.7 | 6.7
| 2014-01-10 03:00 | 4.3 | 6.7 | 6.7
| 2014-01-10 03:30 | 3.9 | 6.7 | 6.7
| 2014-01-10 04:00 | 3.4 | 6.7 | 6.7
| 2014-01-10 04:30 | 2.9 | 6.7 | 6.7
| 2014-01-10 05:00 | 2.5 | 6.7 | 6.7
| 2014-01-10 05:30 | 2.8 | 6.1 | 6.7
| 2014-01-10 06:00 | 2.2 | 6.1 | 6.7
| 2014-01-10 06:30 | 2.1 | 6.1 | 6.7
| 2014-01-10 07:00 | 2.5 | 6.1 | 6.7
| 2014-01-10 07:30 | 1.8 | 6.1 | 6.7
| 2014-01-10 08:00 | 1.9 | 5.6 | 6.7
| 2014-01-10 08:30 | 2.1 | 5.6 | 6.7
| 2014-01-10 09:00 | 2.8 | 5.6 | 6.7
| 2014-01-10 09:30 | 3.8 | 5.6 | 6.7
| 2014-01-10 10:00 | 4.8 | 5.6 | 6.7
| 2014-01-10 10:30 | 6.1 | 5 | 6.7
| 2014-01-10 11:00 | 6.2 | 5 | 6.7
| 2014-01-10 11:30 | 6.7 | 5 | 6.7
| 2014-01-10 12:00 | 6.9 | 5 | 6.7
| 2014-01-10 12:30 | 7.6 | 5 | 6.7
| 2014-01-10 13:00 | 7.5 | 5 | 6.7
| 2014-01-10 13:30 | 8.3 | 5 | 6.7
| 2014-01-10 14:00 | 8.3 | 5 | 6.7
| 2014-01-10 14:30 | 8.7 | 5.6 | 6.7
| 2014-01-10 15:00 | 8.8 | 5.6 | 6.7
| 2014-01-10 15:30 | 8.8 | 5.6 | 6.7
| 2014-01-10 16:00 | 7.8 | 5.6 | 6.7
| 2014-01-10 16:30 | 6.4 | 5.6 | 6.7
| 2014-01-10 17:00 | 4.9 | 5.6 | 6.7
| 2014-01-10 17:30 | 4.5 | 5.6 | 6.7
| 2014-01-10 18:00 | 4.4 | 5.6 | 6.7
| 2014-01-10 18:30 | 3.9 | 5.6 | 6.7
| 2014-01-10 19:00 | 3.4 | 5.6 | 6.7
| 2014-01-10 19:30 | 2.8 | 5.6 | 6.7
| 2014-01-10 20:00 | 2.3 | 5.6 | 7.2
| 2014-01-10 20:30 | 2.4 | 5.6 | 6.7
| 2014-01-10 21:00 | 2.2 | 5.6 | 7.2
| 2014-01-10 21:30 | 1.9 | 5 | 7.2
| 2014-01-10 22:00 | 1.7 | 5 | 7.2
| 2014-01-10 22:30 | 1.4 | 5 | 7.2
| 2014-01-10 23:00 | 1.1 | 5 | 7.2
| 2014-01-10 23:30 | 1.5 | 5 | 7.2
| 2014-01-11 | 1.5 | 5 | 7.2
| 2014-01-11 00:30 | 1.5 | 5 | 7.2
| 2014-01-11 01:00 | 1 | 4.4 | 7.2
| 2014-01-11 01:30 | 0.6 | 4.4 | 7.2
| 2014-01-11 02:00 | 0.3 | 4.4 | 6.7
| 2014-01-11 02:30 | 0 | 4.4 | 7.2
| 2014-01-11 03:00 | -0.6 | 4.4 | 7.2
| 2014-01-11 03:30 | -0.9 | 4.4 | 6.7
| 2014-01-11 04:00 | -1.2 | 4.4 | 6.7
| 2014-01-11 04:30 | -1.4 | 3.9 | 6.7
| 2014-01-11 05:00 | -1.4 | 3.9 | 6.7
| 2014-01-11 05:30 | -1.8 | 3.9 | 6.7
| 2014-01-11 06:00 | -1.8 | 3.9 | 6.7
| 2014-01-11 06:30 | -2.3 | 3.9 | 6.7
| 2014-01-11 07:00 | -1.6 | 3.9 | 6.7
| 2014-01-11 07:30 | -0.5 | 3.9 | 6.7
| 2014-01-11 08:00 | -0.2 | 3.9 | 6.7
| 2014-01-11 08:30 | -0.4 | 3.9 | 6.7
| 2014-01-11 09:00 | 0.2 | 3.9 | 6.7
| 2014-01-11 09:30 | 0.6 | 3.9 | 6.7
| 2014-01-11 10:00 | 0.8 | 3.3 | 6.7
| 2014-01-11 10:30 | 1.5 | 3.3 | 6.7
| 2014-01-11 11:00 | 1.4 | 3.3 | 6.7
| 2014-01-11 11:30 | 1.6 | 3.3 | 6.7
| 2014-01-11 12:00 | 1.9 | 3.3 | 6.7
| 2014-01-11 12:30 | 2.4 | 3.3 | 6.7
| 2014-01-11 13:00 | 2.6 | 3.3 | 6.7
| 2014-01-11 13:30 | 2.9 | 3.3 | 6.7
| 2014-01-11 14:00 | 3.7 | 3.3 | 6.7
| 2014-01-11 14:30 | 4.1 | 3.3 | 6.7
| 2014-01-11 15:00 | 4.3 | 3.3 | 6.7
| 2014-01-11 15:30 | 4.3 | 3.9 | 6.7
| 2014-01-11 16:00 | 4.4 | 3.9 | 6.7
| 2014-01-11 16:30 | 4.1 | 3.9 | 6.7
| 2014-01-11 17:00 | 3.7 | 3.9 | 6.7
| 2014-01-11 17:30 | 4.4 | 3.9 | 6.7
| 2014-01-11 18:00 | 4.7 | 3.9 | 6.7
| 2014-01-11 18:30 | 4.9 | 3.9 | 6.7
| 2014-01-11 19:00 | 5.1 | 3.9 | 6.7
| 2014-01-11 19:30 | 4.2 | 3.9 | 6.7
| 2014-01-11 20:00 | 3.6 | 3.9 | 6.7
| 2014-01-11 20:30 | 3.2 | 3.9 | 6.7
| 2014-01-11 21:00 | 2.8 | 3.9 | 6.7
| 2014-01-11 21:30 | 2.2 | 3.9 | 6.7
| 2014-01-11 22:00 | 1.4 | 3.9 | 6.7
| 2014-01-11 22:30 | 0.9 | 3.9 | 6.7
| 2014-01-11 23:00 | 0.7 | 3.9 | 6.7
| 2014-01-11 23:30 | -0.2 | 3.9 | 6.7
| 2014-01-12 | -0.7 | 3.9 | 6.7
| 2014-01-12 00:30 | -0.7 | 3.9 | 6.7
| 2014-01-12 01:00 | -0.8 | 3.3 | 6.7
| 2014-01-12 01:30 | -1 | 3.3 | 6.7
| 2014-01-12 02:00 | -1 | 3.3 | 6.7
| 2014-01-12 02:30 | -0.8 | 3.3 | 6.7
| 2014-01-12 03:00 | -0.8 | 3.3 | 6.7
| 2014-01-12 03:30 | -1.1 | 3.3 | 6.7
| 2014-01-12 04:00 | -1.5 | 3.3 | 6.7
| 2014-01-12 04:30 | -1.5 | 3.3 | 6.7
| 2014-01-12 05:00 | -1.9 | 3.3 | 6.7
| 2014-01-12 05:30 | -2.1 | 3.3 | 6.7
| 2014-01-12 06:00 | -2.1 | 3.3 | 6.7
| 2014-01-12 06:30 | -2.6 | 3.3 | 6.7
| 2014-01-12 07:00 | -2.7 | 2.8 | 6.7
| 2014-01-12 07:30 | -2.7 | 2.8 | 6.7
| 2014-01-12 08:00 | -2.9 | 2.8 | 6.7
| 2014-01-12 08:30 | -2.6 | 2.8 | 6.7
| 2014-01-12 09:00 | -2.6 | 2.8 | 6.7
| 2014-01-12 09:30 | -2.3 | 2.8 | 6.7
| 2014-01-12 10:00 | -0.8 | 2.8 | 6.7
| 2014-01-12 10:30 | 0.4 | 2.8 | 6.7
| 2014-01-12 11:00 | 1.4 | 2.8 | 6.7
| 2014-01-12 11:30 | 1.7 | 2.8 | 6.7
| 2014-01-12 12:00 | 2.2 | 2.8 | 6.7
| 2014-01-12 12:30 | 2.9 | 2.8 | 6.7
| 2014-01-12 13:00 | 3.8 | 2.8 | 6.7
| 2014-01-12 13:30 | 4.7 | 2.8 | 6.7
| 2014-01-12 14:00 | 5.2 | 2.8 | 6.7
| 2014-01-12 14:30 | 5.4 | 2.8 | 6.7
| 2014-01-12 15:00 | 5.8 | 2.8 | 6.7
| 2014-01-12 15:30 | 5.9 | 2.8 | 6.7
| 2014-01-12 16:00 | 5.6 | 2.8 | 6.7
| 2014-01-12 16:30 | 4.2 | 2.8 | 6.7
| 2014-01-12 17:00 | 2.8 | 2.8 | 6.7
| 2014-01-12 17:30 | 1.8 | 2.8 | 6.7
| 2014-01-12 18:00 | 0.6 | 2.8 | 6.7
| 2014-01-12 18:30 | 0.1 | 2.8 | 6.7
| 2014-01-12 19:00 | -0.6 | 2.8 | 6.7
| 2014-01-12 19:30 | -1 | 2.8 | 6.7
| 2014-01-12 20:00 | -1.4 | 2.8 | 6.7
| 2014-01-12 20:30 | -1.8 | 2.8 | 6.7
| 2014-01-12 21:00 | -1.9 | 2.8 | 6.7
| 2014-01-12 21:30 | -2.2 | 2.8 | 6.7
| 2014-01-12 22:00 | -2.6 | 2.8 | 6.7
| 2014-01-12 22:30 | -3 | 2.8 | 6.7
| 2014-01-12 23:00 | -3.2 | 2.8 | 6.7
| 2014-01-12 23:30 | -3.2 | 2.8 | 6.7
| 2014-01-13 | -3.6 | 2.8 | 6.7
| 2014-01-13 00:30 | -3.6 | 2.8 | 6.7
| 2014-01-13 01:00 | -3.8 | 2.8 | 6.7
| 2014-01-13 01:30 | -2.8 | 2.2 | 6.7
| 2014-01-13 02:00 | -1.1 | 2.2 | 6.7
| 2014-01-13 02:30 | -1.1 | 2.2 | 6.7
| 2014-01-13 03:00 | -1.1 | 2.2 | 6.7
| 2014-01-13 03:30 | -0.1 | 2.2 | 6.7
| 2014-01-13 04:00 | 0.1 | 2.2 | 6.7
| 2014-01-13 04:30 | 0.1 | 2.2 | 6.7
| 2014-01-13 05:00 | 0.3 | 2.2 | 6.7
| 2014-01-13 05:30 | 0.7 | 2.2 | 6.7
| 2014-01-13 06:00 | 1.1 | 2.2 | 6.7
| 2014-01-13 06:30 | 1.3 | 2.2 | 6.7
| 2014-01-13 07:00 | 1.7 | 2.2 | 6.7
| 2014-01-13 07:30 | 2.1 | 2.2 | 6.7
| 2014-01-13 08:00 | 2.5 | 2.2 | 6.1
| 2014-01-13 08:30 | 2.5 | 2.2 | 6.1
| 2014-01-13 09:00 | 2.8 | 2.2 | 6.1
| 2014-01-13 09:30 | 3.1 | 2.2 | 6.1
| 2014-01-13 10:00 | 3.4 | 2.2 | 6.1
| 2014-01-13 10:30 | 3.5 | 2.2 | 6.1
| 2014-01-13 11:00 | 3.7 | 2.2 | 6.1
| 2014-01-13 11:30 | 3.8 | 2.2 | 6.1
| 2014-01-13 12:00 | 3.8 | 2.2 | 6.1
| 2014-01-13 12:30 | 3.8 | 2.2 | 6.1
| 2014-01-13 13:00 | 4.1 | 2.2 | 6.1
| 2014-01-13 13:30 | 4.6 | 2.2 | 6.1
| 2014-01-13 14:00 | 4.7 | 2.2 | 6.1
| 2014-01-13 14:30 | 4.7 | 2.2 | 6.1
| 2014-01-13 15:00 | 4.8 | 2.2 | 6.1
| 2014-01-13 15:30 | 5 | 2.8 | 6.1
| 2014-01-13 16:00 | 4.9 | 2.8 | 6.1
| 2014-01-13 16:30 | 4.8 | 2.8 | 6.1
| 2014-01-13 17:00 | 4.7 | 2.8 | 6.1
| 2014-01-13 17:30 | 4.4 | 2.8 | 6.1
| 2014-01-13 18:00 | 4.3 | 2.8 | 6.1
| 2014-01-13 18:30 | 4.3 | 2.8 | 6.1
| 2014-01-13 19:00 | 4.6 | 2.8 | 6.1
| 2014-01-13 19:30 | 4.4 | 2.8 | 6.1
| 2014-01-13 20:00 | 4.5 | 2.8 | 6.1
| 2014-01-13 20:30 | 4.4 | 2.8 | 6.1
| 2014-01-13 21:00 | 4.3 | 3.3 | 6.1
| 2014-01-13 21:30 | 4.4 | 3.3 | 6.1
| 2014-01-13 22:00 | 4.5 | 3.3 | 6.1
| 2014-01-13 22:30 | 4.5 | 3.3 | 6.1
| 2014-01-13 23:00 | 4.5 | 3.3 | 6.1
| 2014-01-13 23:30 | 4.5 | 3.3 | 6.1
| 2014-01-14 | 4.5 | 3.3 | 6.1
| 2014-01-14 00:30 | 4.6 | 3.3 | 6.1
| 2014-01-14 01:00 | 4.7 | 3.3 | 6.1
| 2014-01-14 01:30 | 4.5 | 3.3 | 6.1
| 2014-01-14 02:00 | 4.3 | 3.3 | 6.1
| 2014-01-14 02:30 | 3.9 | 3.3 | 6.1
| 2014-01-14 03:00 | 3.5 | 3.3 | 6.1
| 2014-01-14 03:30 | 3.8 | 3.3 | 6.1
| 2014-01-14 04:00 | 3.8 | 3.3 | 6.1
| 2014-01-14 04:30 | 3.8 | 3.3 | 6.1
| 2014-01-14 05:00 | 3.9 | 3.3 | 6.1
| 2014-01-14 05:30 | 4.1 | 3.3 | 6.1
| 2014-01-14 06:00 | 3.9 | 3.3 | 6.1
| 2014-01-14 06:30 | 3.8 | 3.3 | 6.1
| 2014-01-14 07:00 | 4 | 3.3 | 6.1
| 2014-01-14 07:30 | 4.1 | 3.3 | 6.1
| 2014-01-14 08:00 | 4.2 | 3.3 | 6.1
| 2014-01-14 08:30 | 3.9 | 3.3 | 6.1
| 2014-01-14 09:00 | 3.9 | 3.3 | 6.1
| 2014-01-14 09:30 | 3.9 | 3.3 | 6.1
| 2014-01-14 10:00 | 4.2 | 3.3 | 6.1
| 2014-01-14 10:30 | 4.3 | 3.3 | 6.1
| 2014-01-14 11:00 | 4.6 | 3.3 | 6.1
| 2014-01-14 11:30 | 5 | 3.3 | 6.1
| 2014-01-14 12:00 | 5.3 | 3.3 | 6.1
| 2014-01-14 12:30 | 5.3 | 3.9 | 6.1
| 2014-01-14 13:00 | 5.6 | 3.9 | 6.1
| 2014-01-14 13:30 | 5.8 | 3.9 | 6.1
| 2014-01-14 14:00 | 5.9 | 3.9 | 6.1
| 2014-01-14 14:30 | 5.8 | 3.9 | 6.1
| 2014-01-14 15:00 | 5.8 | 3.9 | 6.1
| 2014-01-14 15:30 | 5.9 | 3.9 | 6.1
| 2014-01-14 16:00 | 5.8 | 3.9 | 6.1
| 2014-01-14 16:30 | 5.7 | 3.9 | 6.1
| 2014-01-14 17:00 | 5.6 | 4.4 | 6.1
| 2014-01-14 17:30 | 5.4 | 4.4 | 6.1
| 2014-01-14 18:00 | 5.2 | 4.4 | 6.1
| 2014-01-14 18:30 | 5.2 | 4.4 | 6.1
| 2014-01-14 19:00 | 5.2 | 4.4 | 6.1
| 2014-01-14 19:30 | 5.3 | 4.4 | 6.1
| 2014-01-14 20:00 | 5.3 | 4.4 | 6.1
| 2014-01-14 20:30 | 5.1 | 4.4 | 6.1
| 2014-01-14 21:00 | 4.8 | 4.4 | 6.1
| 2014-01-14 21:30 | 4.1 | 4.4 | 6.1
| 2014-01-14 22:00 | 3.2 | 4.4 | 6.1
| 2014-01-14 22:30 | 3.5 | 4.4 | 6.1
| 2014-01-14 23:00 | 3.9 | 4.4 | 6.1
| 2014-01-14 23:30 | 3.6 | 4.4 | 6.1
| 2014-01-15 | 3.6 | 4.4 | 6.1
| 2014-01-15 00:30 | 3.7 | 4.4 | 6.1
| 2014-01-15 01:00 | 3.8 | 4.4 | 6.1
| 2014-01-15 01:30 | 3.8 | 4.4 | 6.1
| 2014-01-15 02:00 | 3.7 | 4.4 | 6.1
| 2014-01-15 02:30 | 3.8 | 4.4 | 6.1
| 2014-01-15 03:00 | 3.9 | 4.4 | 6.1
| 2014-01-15 03:30 | 3.9 | 4.4 | 6.1
| 2014-01-15 04:00 | 3.8 | 4.4 | 6.1
| 2014-01-15 04:30 | 3.8 | 4.4 | 6.1
| 2014-01-15 05:00 | 3.8 | 3.9 | 6.1
| 2014-01-15 05:30 | 4.1 | 3.9 | 6.1
| 2014-01-15 06:00 | 3.9 | 3.9 | 6.1
| 2014-01-15 06:30 | 3.7 | 3.9 | 6.1
| 2014-01-15 07:00 | 3.6 | 3.9 | 6.1
| 2014-01-15 07:30 | 3.2 | 3.9 | 6.1
| 2014-01-15 08:00 | 3 | 3.9 | 6.1
| 2014-01-15 08:30 | 3.1 | 3.9 | 6.1
| 2014-01-15 09:00 | 2.3 | 3.9 | 6.1
| 2014-01-15 09:30 | 2.9 | 3.9 | 6.1
| 2014-01-15 10:00 | 3.5 | 3.9 | 6.1
| 2014-01-15 10:30 | 3.7 | 3.9 | 6.1
| 2014-01-15 11:00 | 3.8 | 3.9 | 6.1
| 2014-01-15 11:30 | 4.5 | 3.9 | 6.1
| 2014-01-15 12:00 | 5.1 | 3.9 | 6.1
| 2014-01-15 12:30 | 5.2 | 3.9 | 6.1
| 2014-01-15 13:00 | 4.8 | 3.9 | 6.1
| 2014-01-15 13:30 | 5.7 | 3.9 | 6.1
| 2014-01-15 14:00 | 5.3 | 3.9 | 6.1
| 2014-01-15 14:30 | 5.1 | 3.9 | 6.1
| 2014-01-15 15:00 | 5.2 | 4.4 | 6.1
| 2014-01-15 15:30 | 5.3 | 4.4 | 6.1
| 2014-01-15 16:00 | 5.1 | 4.4 | 6.1
| 2014-01-15 16:30 | 5.1 | 4.4 | 6.1
| 2014-01-15 17:00 | 4.9 | 4.4 | 6.1
| 2014-01-15 17:30 | 4.6 | 4.4 | 6.1
| 2014-01-15 18:00 | 4.2 | 4.4 | 6.1
| 2014-01-15 18:30 | 4.2 | 4.4 | 6.1
| 2014-01-15 19:00 | 4.6 | 4.4 | 6.1
| 2014-01-15 19:30 | 4.3 | 4.4 | 6.1
| 2014-01-15 20:00 | 4.2 | 4.4 | 6.1
| 2014-01-15 20:30 | 4.6 | 4.4 | 6.1
| 2014-01-15 21:00 | 4.7 | 4.4 | 6.1
| 2014-01-15 21:30 | 4.7 | 4.4 | 6.1
| 2014-01-15 22:00 | 4.9 | 4.4 | 6.1
| 2014-01-15 22:30 | 5.1 | 4.4 | 6.1
| 2014-01-15 23:00 | 5 | 4.4 | 6.1
| 2014-01-15 23:30 | 4.7 | 4.4 | 6.1
| 2014-01-16 | 4.3 | 4.4 | 6.1
| 2014-01-16 00:30 | 4.2 | 4.4 | 6.1
| 2014-01-16 01:00 | 4.1 | 4.4 | 6.1
| 2014-01-16 01:30 | 4.2 | 4.4 | 6.1
| 2014-01-16 02:00 | 4.2 | 4.4 | 6.1
| 2014-01-16 02:30 | 4.2 | 4.4 | 6.1
| 2014-01-16 03:00 | 4.3 | 4.4 | 6.1
| 2014-01-16 03:30 | 4.4 | 4.4 | 6.1
| 2014-01-16 04:00 | 4.4 | 4.4 | 6.1
| 2014-01-16 04:30 | 4.6 | 4.4 | 6.1
| 2014-01-16 05:00 | 4.8 | 4.4 | 6.1
| 2014-01-16 05:30 | 4.8 | 4.4 | 6.1
| 2014-01-16 06:00 | 4.9 | 4.4 | 6.1
| 2014-01-16 06:30 | 5.1 | 4.4 | 6.1
| 2014-01-16 07:00 | 5.1 | 4.4 | 6.1
| 2014-01-16 07:30 | 5 | 4.4 | 6.1
| 2014-01-16 08:00 | 5.4 | 4.4 | 6.1
| 2014-01-16 08:30 | 5.6 | 4.4 | 6.1
| 2014-01-16 09:00 | 5.6 | 4.4 | 6.1
| 2014-01-16 09:30 | 5.7 | 4.4 | 6.1
| 2014-01-16 10:00 | 5.9 | 4.4 | 6.1
| 2014-01-16 10:30 | 6.6 | 4.4 | 6.1
| 2014-01-16 11:00 | 6.8 | 4.4 | 6.1
| 2014-01-16 11:30 | 6.8 | 4.4 | 6.1
| 2014-01-16 12:00 | 6.8 | 4.4 | 6.1
| 2014-01-16 12:30 | 6.7 | 4.4 | 6.1
| 2014-01-16 13:00 | 6.7 | 4.4 | 6.1
| 2014-01-16 13:30 | 6.7 | 4.4 | 6.1
| 2014-01-16 14:00 | 6.9 | 4.4 | 6.1
| 2014-01-16 14:30 | 7.2 | 5 | 6.1
| 2014-01-16 15:00 | 7.6 | 5 | 6.1
| 2014-01-16 15:30 | 7.6 | 5 | 6.1
| 2014-01-16 16:00 | 7.4 | 5 | 6.1
| 2014-01-16 16:30 | 7.3 | 5 | 6.1
| 2014-01-16 17:00 | 7.1 | 5 | 6.1
| 2014-01-16 17:30 | 6.9 | 5 | 6.1
| 2014-01-16 18:00 | 6.8 | 5 | 6.1
| 2014-01-16 18:30 | 7 | 5 | 6.1
| 2014-01-16 19:00 | 7.2 | 5 | 6.1
| 2014-01-16 19:30 | 6.9 | 5 | 6.1
| 2014-01-16 20:00 | 6.9 | 5 | 6.1
| 2014-01-16 20:30 | 7.1 | 5 | 6.1
| 2014-01-16 21:00 | 7.2 | 5 | 6.1
| 2014-01-16 21:30 | 7.3 | 5 | 6.1
| 2014-01-16 22:00 | 7.3 | 5 | 6.1
| 2014-01-16 22:30 | 7.1 | 5 | 6.1
| 2014-01-16 23:00 | 7.2 | 5 | 6.1
| 2014-01-16 23:30 | 7.2 | 5 | 6.1
| 2014-01-17 | 7.2 | 5 | 6.1
| 2014-01-17 00:30 | 7.1 | 5 | 6.1
| 2014-01-17 01:00 | 7.1 | 5 | 6.1
| 2014-01-17 01:30 | 6.9 | 5 | 6.1
| 2014-01-17 02:00 | 6.7 | 5 | 6.1
| 2014-01-17 02:30 | 6.9 | 5 | 6.1
| 2014-01-17 03:00 | 6.9 | 5 | 6.1
| 2014-01-17 03:30 | 6.6 | 5 | 6.1
| 2014-01-17 04:00 | 6.6 | 5 | 6.1
| 2014-01-17 04:30 | 6.6 | 5 | 6.1
| 2014-01-17 05:00 | 6.4 | 5 | 6.1
| 2014-01-17 05:30 | 6.3 | 5 | 6.1
| 2014-01-17 06:00 | 6.1 | 5 | 6.1
| 2014-01-17 06:30 | 6.1 | 5 | 6.1
| 2014-01-17 07:00 | 5.9 | 5 | 6.1
| 2014-01-17 07:30 | 5.7 | 5 | 6.1
| 2014-01-17 08:00 | 5.5 | 5 | 6.1
| 2014-01-17 08:30 | 5.4 | 5 | 6.1
| 2014-01-17 09:00 | 5.4 | 5 | 6.1
| 2014-01-17 09:30 | 5.6 | 5 | 6.1
| 2014-01-17 10:00 | 5.6 | 5 | 6.1
| 2014-01-17 10:30 | 6.2 | 5 | 6.1
| 2014-01-17 11:00 | 6.5 | 5 | 6.1
| 2014-01-17 11:30 | 7.7 | 5 | 6.1
| 2014-01-17 12:00 | 8.6 | 5 | 6.1
| 2014-01-17 12:30 | 8.8 | 5 | 6.1
| 2014-01-17 13:00 | 9.7 | 5 | 6.1
| 2014-01-17 13:30 | 9.9 | 5 | 6.1
| 2014-01-17 14:00 | 10.3 | 5 | 6.1
| 2014-01-17 14:30 | 10.3 | 5 | 6.1
| 2014-01-17 15:00 | 10.3 | 5 | 6.1
| 2014-01-17 15:30 | 10.2 | 5 | 6.1
| 2014-01-17 16:00 | 9.6 | 5 | 6.1
| 2014-01-17 16:30 | 8.8 | 5.6 | 6.1
| 2014-01-17 17:00 | 7.9 | 5.6 | 6.1
| 2014-01-17 17:30 | 6.9 | 5.6 | 6.1
| 2014-01-17 18:00 | 6.3 | 5.6 | 6.1
| 2014-01-17 18:30 | 5.6 | 5.6 | 6.1
| 2014-01-17 19:00 | 4.9 | 5.6 | 6.1
| 2014-01-17 19:30 | 3.8 | 5.6 | 6.1
| 2014-01-17 20:00 | 3.3 | 5.6 | 6.1
| 2014-01-17 20:30 | 2.9 | 5 | 6.1
| 2014-01-17 21:00 | 2.7 | 5 | 6.1
| 2014-01-17 21:30 | 2.2 | 5 | 6.1
| 2014-01-17 22:00 | 2.3 | 5 | 6.1
| 2014-01-17 22:30 | 2.2 | 5 | 6.1
| 2014-01-17 23:00 | 2.6 | 5 | 6.1
| 2014-01-17 23:30 | 1.9 | 5 | 6.1
| 2014-01-18 | 1.3 | 4.4 | 6.1
| 2014-01-18 00:30 | 0.6 | 4.4 | 6.1
| 2014-01-18 01:00 | 0.5 | 4.4 | 6.1
| 2014-01-18 01:30 | 0.2 | 4.4 | 6.1
| 2014-01-18 02:00 | -0.2 | 4.4 | 6.1
| 2014-01-18 02:30 | -0.8 | 4.4 | 6.1
| 2014-01-18 03:00 | -1.3 | 4.4 | 6.1
| 2014-01-18 03:30 | -1.6 | 3.9 | 6.1
| 2014-01-18 04:00 | -1.7 | 3.9 | 6.1
| 2014-01-18 04:30 | -1.6 | 3.9 | 6.1
| 2014-01-18 05:00 | -1.7 | 3.9 | 6.1
| 2014-01-18 05:30 | -1.7 | 3.9 | 6.1
| 2014-01-18 06:00 | -1.7 | 3.9 | 6.1
| 2014-01-18 06:30 | -1.6 | 3.9 | 6.1
| 2014-01-18 07:00 | -1.6 | 3.9 | 6.1
| 2014-01-18 07:30 | -1.9 | 3.9 | 6.1
| 2014-01-18 08:00 | -1.6 | 3.3 | 6.1
| 2014-01-18 08:30 | -1.1 | 3.3 | 6.1
| 2014-01-18 09:00 | -0.2 | 3.3 | 6.1
| 2014-01-18 09:30 | 1.2 | 3.3 | 6.1
| 2014-01-18 10:00 | 2 | 3.3 | 6.1
| 2014-01-18 10:30 | 2.7 | 3.3 | 6.1
| 2014-01-18 11:00 | 2.4 | 3.3 | 6.1
| 2014-01-18 11:30 | 3.7 | 3.3 | 6.1
| 2014-01-18 12:00 | 4.2 | 3.3 | 6.1
| 2014-01-18 12:30 | 5.4 | 3.3 | 6.1
| 2014-01-18 13:00 | 6.8 | 3.3 | 6.1
| 2014-01-18 13:30 | 7.4 | 3.3 | 6.1
| 2014-01-18 14:00 | 6.9 | 3.3 | 6.1
| 2014-01-18 14:30 | 6.5 | 3.3 | 6.1
| 2014-01-18 15:00 | 5.9 | 3.3 | 6.1
| 2014-01-18 15:30 | 5.7 | 3.3 | 6.1
| 2014-01-18 16:00 | 5.9 | 3.9 | 6.1
| 2014-01-18 16:30 | 4.9 | 3.9 | 6.1
| 2014-01-18 17:00 | 4 | 3.9 | 6.1
| 2014-01-18 17:30 | 3.6 | 3.9 | 6.1
| 2014-01-18 18:00 | 3.6 | 3.9 | 6.1
| 2014-01-18 18:30 | 3.8 | 3.9 | 6.1
| 2014-01-18 19:00 | 3.8 | 3.9 | 6.1
| 2014-01-18 19:30 | 3.6 | 3.9 | 6.1
| 2014-01-18 20:00 | 3.4 | 3.9 | 6.1
| 2014-01-18 20:30 | 3 | 3.9 | 6.1
| 2014-01-18 21:00 | 3.1 | 3.9 | 6.1
| 2014-01-18 21:30 | 3.4 | 3.9 | 6.1
| 2014-01-18 22:00 | 3.7 | 3.9 | 6.1
| 2014-01-18 22:30 | 3.7 | 3.9 | 6.1
| 2014-01-18 23:00 | 3 | 3.9 | 6.1
| 2014-01-18 23:30 | 3.3 | 3.3 | 6.1
| 2014-01-19 | 3.5 | 3.3 | 6.1
| 2014-01-19 00:30 | 3.2 | 3.3 | 6.1
| 2014-01-19 01:00 | 2.8 | 3.3 | 6.1
| 2014-01-19 01:30 | 2.9 | 3.3 | 6.1
| 2014-01-19 02:00 | 2.6 | 3.3 | 6.1
| 2014-01-19 02:30 | 2.4 | 3.3 | 6.1
| 2014-01-19 03:00 | 2.2 | 3.3 | 6.1
| 2014-01-19 03:30 | 2 | 3.3 | 6.1
| 2014-01-19 04:00 | 2 | 3.3 | 6.1
| 2014-01-19 04:30 | 2.4 | 3.3 | 6.1
| 2014-01-19 05:00 | 2.7 | 3.3 | 6.1
| 2014-01-19 05:30 | 2.8 | 3.3 | 6.1
| 2014-01-19 06:00 | 3.2 | 3.3 | 6.1
| 2014-01-19 06:30 | 3.3 | 2.8 | 6.1
| 2014-01-19 07:00 | 3.4 | 2.8 | 6.1
| 2014-01-19 07:30 | 3.2 | 2.8 | 6.1
| 2014-01-19 08:00 | 2.8 | 2.8 | 6.1
| 2014-01-19 08:30 | 2.2 | 2.8 | 6.1
| 2014-01-19 09:00 | 1.8 | 2.8 | 6.1
| 2014-01-19 09:30 | 2.3 | 2.8 | 6.1
| 2014-01-19 10:00 | 3.7 | 2.8 | 6.1
| 2014-01-19 10:30 | 4.6 | 2.8 | 6.1
| 2014-01-19 11:00 | 5 | 2.8 | 6.1
| 2014-01-19 11:30 | 5.2 | 2.8 | 6.1
| 2014-01-19 12:00 | 5.7 | 2.8 | 6.1
| 2014-01-19 12:30 | 5.7 | 3.3 | 6.1
| 2014-01-19 13:00 | 5.8 | 3.3 | 6.1
| 2014-01-19 13:30 | 5.9 | 3.3 | 6.1
| 2014-01-19 14:00 | 5.9 | 3.3 | 6.1
| 2014-01-19 14:30 | 6 | 3.3 | 6.1
| 2014-01-19 15:00 | 5.7 | 3.3 | 6.1
| 2014-01-19 15:30 | 5.6 | 3.3 | 6.1
| 2014-01-19 16:00 | 5.4 | 3.9 | 6.1
| 2014-01-19 16:30 | 4.8 | 3.9 | 6.1
| 2014-01-19 17:00 | 4.1 | 3.9 | 6.1
| 2014-01-19 17:30 | 3.3 | 3.9 | 6.1
| 2014-01-19 18:00 | 2.8 | 3.9 | 6.1
| 2014-01-19 18:30 | 2.6 | 3.9 | 6.1
| 2014-01-19 19:00 | 2.3 | 3.9 | 6.1
| 2014-01-19 19:30 | 1.7 | 3.9 | 6.1
| 2014-01-19 20:00 | 1.1 | 3.9 | 6.1
| 2014-01-19 20:30 | 0.6 | 3.9 | 6.1
| 2014-01-19 21:00 | 0.3 | 3.9 | 6.1
| 2014-01-19 21:30 | -0.1 | 3.9 | 6.1
| 2014-01-19 22:00 | -0.1 | 3.3 | 6.1
| 2014-01-19 22:30 | -0.3 | 3.3 | 6.1
| 2014-01-19 23:00 | -0.5 | 3.3 | 6.1
| 2014-01-19 23:30 | -0.9 | 3.3 | 6.1
| 2014-01-20 | -0.9 | 3.3 | 6.1
| 2014-01-20 00:30 | 0.6 | 3.3 | 6.1
| 2014-01-20 01:00 | 1.3 | 3.3 | 6.1
| 2014-01-20 01:30 | 2.1 | 3.3 | 6.1
| 2014-01-20 02:00 | 2.7 | 3.3 | 6.1
| 2014-01-20 02:30 | 2.9 | 3.3 | 6.1
| 2014-01-20 03:00 | 3.1 | 3.3 | 6.1
| 2014-01-20 03:30 | 3.3 | 3.3 | 6.1
| 2014-01-20 04:00 | 3.3 | 3.3 | 6.1
| 2014-01-20 04:30 | 3.3 | 3.3 | 6.1
| 2014-01-20 05:00 | 3.4 | 3.3 | 6.1
| 2014-01-20 05:30 | 3.4 | 3.3 | 6.1
| 2014-01-20 06:00 | 3.4 | 3.3 | 6.1
| 2014-01-20 06:30 | 3.4 | 3.3 | 6.1
| 2014-01-20 07:00 | 3.4 | 3.3 | 6.1
| 2014-01-20 07:30 | 3.4 | 3.3 | 6.1
| 2014-01-20 08:00 | 3.3 | 3.3 | 6.1
| 2014-01-20 08:30 | 3.3 | 3.3 | 6.1
| 2014-01-20 09:00 | 3.3 | 3.3 | 6.1
| 2014-01-20 09:30 | 3.3 | 3.3 | 6.1
| 2014-01-20 10:00 | 3.3 | 3.3 | 6.1
| 2014-01-20 10:30 | 3.3 | 3.3 | 6.1
| 2014-01-20 11:00 | 3.5 | 3.3 | 6.1
| 2014-01-20 11:30 | 3.7 | 3.3 | 6.1
| 2014-01-20 12:00 | 3.8 | 3.3 | 6.1
| 2014-01-20 12:30 | 3.9 | 3.3 | 6.1
| 2014-01-20 13:00 | 4 | 3.3 | 6.1
| 2014-01-20 13:30 | 4.2 | 3.3 | 6.1
| 2014-01-20 14:00 | 4.4 | 3.3 | 6.1
| 2014-01-20 14:30 | 4.6 | 3.3 | 6.1
| 2014-01-20 15:00 | 4.6 | 3.3 | 6.1
| 2014-01-20 15:30 | 4.6 | 3.3 | 6.1
| 2014-01-20 16:00 | 4.3 | 3.9 | 6.1
| 2014-01-20 16:30 | 4.3 | 3.9 | 6.1
| 2014-01-20 17:00 | 4.2 | 3.9 | 6.1
| 2014-01-20 17:30 | 4.2 | 3.9 | 6.1
| 2014-01-20 18:00 | 4.1 | 3.9 | 6.1
| 2014-01-20 18:30 | 3.9 | 3.9 | 6.1
| 2014-01-20 19:00 | 3.8 | 3.9 | 6.1
| 2014-01-20 19:30 | 3.7 | 3.9 | 6.1
| 2014-01-20 20:00 | 3.6 | 3.9 | 6.1
| 2014-01-20 20:30 | 3.6 | 3.9 | 6.1
| 2014-01-20 21:00 | 3.5 | 3.9 | 6.1
| 2014-01-20 21:30 | 3.4 | 3.9 | 6.1
| 2014-01-20 22:00 | 3.4 | 3.9 | 5.6
| 2014-01-20 22:30 | 3.4 | 3.9 | 5.6
| 2014-01-20 23:00 | 3.3 | 3.9 | 5.6
| 2014-01-20 23:30 | 3.3 | 3.9 | 5.6
| 2014-01-21 | 3.3 | 3.9 | 5.6
| 2014-01-21 00:30 | 3.3 | 3.9 | 5.6
| 2014-01-21 01:00 | 3.3 | 3.9 | 5.6
| 2014-01-21 01:30 | 3.3 | 3.9 | 5.6
| 2014-01-21 02:00 | 3.3 | 3.9 | 5.6
| 2014-01-21 02:30 | 3.2 | 3.9 | 5.6
| 2014-01-21 03:00 | 3.2 | 3.9 | 5.6
| 2014-01-21 03:30 | 3.2 | 3.9 | 5.6
| 2014-01-21 04:00 | 3.2 | 3.9 | 5.6
| 2014-01-21 04:30 | 3.1 | 3.9 | 5.6
| 2014-01-21 05:00 | 3.1 | 3.9 | 5.6
| 2014-01-21 05:30 | 3.1 | 3.9 | 5.6
| 2014-01-21 06:00 | 3 | 3.9 | 5.6
| 2014-01-21 06:30 | 3.1 | 3.9 | 5.6
| 2014-01-21 07:00 | 3.1 | 3.9 | 5.6
| 2014-01-21 07:30 | 2.9 | 3.9 | 5.6
| 2014-01-21 08:00 | 2.8 | 3.9 | 5.6
| 2014-01-21 08:30 | 2.8 | 3.9 | 5.6
| 2014-01-21 09:00 | 2.8 | 3.9 | 5.6
| 2014-01-21 09:30 | 2.9 | 3.9 | 5.6
| 2014-01-21 10:00 | 3.1 | 3.9 | 5.6
| 2014-01-21 10:30 | 3.2 | 3.9 | 5.6
| 2014-01-21 11:00 | 3.2 | 3.9 | 5.6
| 2014-01-21 11:30 | 3.3 | 3.9 | 5.6
| 2014-01-21 12:00 | 3.5 | 3.9 | 5.6
| 2014-01-21 12:30 | 3.6 | 3.9 | 5.6
| 2014-01-21 13:00 | 3.7 | 3.9 | 5.6
| 2014-01-21 13:30 | 3.9 | 3.9 | 5.6
| 2014-01-21 14:00 | 3.8 | 3.9 | 5.6
| 2014-01-21 14:30 | 3.8 | 3.9 | 5.6
| 2014-01-21 15:00 | 3.8 | 3.9 | 5.6
| 2014-01-21 15:30 | 3.8 | 3.9 | 5.6
| 2014-01-21 16:00 | 3.8 | 3.9 | 5.6
| 2014-01-21 16:30 | 3.9 | 3.9 | 5.6
| 2014-01-21 17:00 | 3.7 | 3.9 | 5.6
| 2014-01-21 17:30 | 3.4 | 3.9 | 5.6
| 2014-01-21 18:00 | 3.2 | 3.9 | 5.6
| 2014-01-21 18:30 | 3.2 | 3.9 | 5.6
| 2014-01-21 19:00 | 3.2 | 3.9 | 5.6
| 2014-01-21 19:30 | 3.2 | 3.9 | 5.6
| 2014-01-21 20:00 | 3.2 | 3.9 | 5.6
| 2014-01-21 20:30 | 3.2 | 3.9 | 5.6
| 2014-01-21 21:00 | 3.2 | 3.9 | 5.6
| 2014-01-21 21:30 | 3.1 | 3.9 | 5.6
| 2014-01-21 22:00 | 3.2 | 3.9 | 5.6
| 2014-01-21 22:30 | 3.1 | 3.9 | 5.6
| 2014-01-21 23:00 | 3.1 | 3.9 | 5.6
| 2014-01-21 23:30 | 2.9 | 3.9 | 5.6
| 2014-01-22 | 2.9 | 3.9 | 5.6
| 2014-01-22 00:30 | 2.9 | 3.9 | 5.6
| 2014-01-22 01:00 | 2.9 | 3.9 | 5.6
| 2014-01-22 01:30 | 3.1 | 3.9 | 5.6
| 2014-01-22 02:00 | 3.1 | 3.9 | 5.6
| 2014-01-22 02:30 | 3 | 3.9 | 5.6
| 2014-01-22 03:00 | 3 | 3.9 | 5.6
| 2014-01-22 03:30 | 3.1 | 3.9 | 5.6
| 2014-01-22 04:00 | 3.1 | 3.9 | 5.6
| 2014-01-22 04:30 | 3.1 | 3.9 | 5.6
| 2014-01-22 05:00 | 3.1 | 3.9 | 5.6
| 2014-01-22 05:30 | 3.2 | 3.9 | 5.6
| 2014-01-22 06:00 | 3.3 | 3.9 | 5.6
| 2014-01-22 06:30 | 3.3 | 3.9 | 5.6
| 2014-01-22 07:00 | 3.3 | 3.9 | 5.6
| 2014-01-22 07:30 | 3.3 | 3.9 | 5.6
| 2014-01-22 08:00 | 3.3 | 3.9 | 5.6
| 2014-01-22 08:30 | 3.4 | 3.9 | 5.6
| 2014-01-22 09:00 | 3.7 | 3.9 | 5.6
| 2014-01-22 09:30 | 3.8 | 3.9 | 5.6
| 2014-01-22 10:00 | 3.9 | 3.9 | 5.6
| 2014-01-22 10:30 | 4.1 | 3.9 | 5.6
| 2014-01-22 11:00 | 4.1 | 3.9 | 5.6
| 2014-01-22 11:30 | 4.2 | 3.9 | 5.6
| 2014-01-22 12:00 | 4.4 | 3.9 | 5.6
| 2014-01-22 12:30 | 4.6 | 3.9 | 5.6
| 2014-01-22 13:00 | 4.8 | 3.9 | 5.6
| 2014-02-01 00:30 | -2.4 | 2.2 | 5
| 2014-02-01 01:00 | -2.4 | 2.2 | 5
| 2014-02-01 01:30 | -2.8 | 2.2 | 5
| 2014-02-01 02:00 | -2.4 | 2.2 | 5
| 2014-02-01 02:30 | -2.8 | 2.2 | 5
| 2014-02-01 03:00 | -3.1 | 2.2 | 5
| 2014-02-01 03:30 | -3 | 2.2 | 5
| 2014-02-01 04:00 | -3.1 | 2.2 | 5
| 2014-02-01 04:30 | -3.2 | 1.7 | 5
| 2014-02-01 05:00 | -3.5 | 1.7 | 5
| 2014-02-01 05:30 | -2.8 | 1.7 | 5
| 2014-02-01 06:00 | -2.4 | 1.7 | 5
| 2014-02-01 06:30 | -2 | 1.7 | 5
| 2014-02-01 07:00 | -1.8 | 1.7 | 5
| 2014-02-01 07:30 | -1.4 | 1.7 | 5
| 2014-02-01 08:00 | -1.1 | 1.7 | 5
| 2014-02-01 08:30 | -0.7 | 1.7 | 5
| 2014-02-01 09:00 | -0.4 | 1.7 | 5
| 2014-02-01 09:30 | 0.5 | 1.7 | 5
| 2014-02-01 10:00 | 0.9 | 1.7 | 5
| 2014-02-01 10:30 | 1.4 | 1.7 | 5
| 2014-02-01 11:00 | 2 | 1.7 | 5
| 2014-02-01 11:30 | 2.7 | 1.7 | 5
| 2014-02-01 12:00 | 3.3 | 1.7 | 5
| 2014-02-01 12:30 | 4.9 | 1.7 | 5
| 2014-02-01 13:00 | 6 | 1.7 | 5
| 2014-02-01 13:30 | 6.2 | 1.7 | 5
| 2014-02-01 14:00 | 5.5 | 1.7 | 5
| 2014-02-01 14:30 | 6.2 | 1.7 | 5
| 2014-02-01 15:00 | 6.3 | 1.7 | 5
| 2014-02-01 15:30 | 6.1 | 1.7 | 5
| 2014-02-01 16:00 | 6.3 | 1.7 | 5
| 2014-02-01 16:30 | 6.2 | 1.7 | 5
| 2014-02-01 17:00 | 5.4 | 1.7 | 5
| 2014-02-01 17:30 | 4.8 | 2.2 | 5
| 2014-02-01 18:00 | 4.9 | 2.2 | 5
| 2014-02-01 18:30 | 4.4 | 2.2 | 5
| 2014-02-01 19:00 | 4.5 | 2.2 | 5
| 2014-02-01 19:30 | 4.3 | 2.2 | 5
| 2014-02-01 20:00 | 4.5 | 2.2 | 5
| 2014-02-01 20:30 | 4.4 | 2.2 | 5
| 2014-02-01 21:00 | 4.2 | 2.2 | 5
| 2014-02-01 21:30 | 3.9 | 2.2 | 5
| 2014-02-01 22:00 | 4.1 | 2.2 | 5
| 2014-02-01 22:30 | 4.1 | 2.2 | 5
| 2014-02-01 23:00 | 3.9 | 2.2 | 5
| 2014-02-01 23:30 | 3.9 | 2.2 | 5
| 2014-02-02 | 3.9 | 2.2 | 5
| 2014-02-02 00:30 | 3.9 | 2.2 | 5
| 2014-02-02 01:00 | 3.8 | 2.8 | 5
| 2014-02-02 01:30 | 3.8 | 2.8 | 5
| 2014-02-02 02:00 | 3.9 | 2.8 | 5
| 2014-02-02 02:30 | 3.7 | 2.8 | 5
| 2014-02-02 03:00 | 3.7 | 2.8 | 5
| 2014-02-02 03:30 | 3.6 | 2.8 | 5
| 2014-02-02 04:00 | 3.7 | 2.8 | 5
| 2014-02-02 04:30 | 3.7 | 2.8 | 5
| 2014-02-02 05:00 | 3.9 | 2.8 | 5
| 2014-02-02 05:30 | 3.8 | 2.8 | 5
| 2014-02-02 06:00 | 3.7 | 2.8 | 5
| 2014-02-02 06:30 | 3.8 | 2.8 | 5
| 2014-02-02 07:00 | 3.9 | 2.8 | 5
| 2014-02-02 07:30 | 3.7 | 2.8 | 5
| 2014-02-02 08:00 | 3.3 | 2.8 | 5
| 2014-02-02 08:30 | 3.7 | 2.8 | 5
| 2014-02-02 09:00 | 4.1 | 2.8 | 5
| 2014-02-02 09:30 | 4.3 | 2.8 | 5
| 2014-02-02 10:00 | 4.4 | 2.8 | 5
| 2014-02-02 10:30 | 4.7 | 2.8 | 5
| 2014-02-02 11:00 | 5.2 | 2.8 | 5
| 2014-02-02 11:30 | 5.8 | 2.8 | 5
| 2014-02-02 12:00 | 6.3 | 2.8 | 5
| 2014-02-02 12:30 | 6.6 | 2.8 | 5
| 2014-02-02 13:00 | 6.9 | 2.8 | 5
| 2014-02-02 13:30 | 7.1 | 2.8 | 5
| 2014-02-02 14:00 | 7.1 | 3.3 | 5
| 2014-02-02 14:30 | 7.7 | 3.3 | 5
| 2014-02-02 15:00 | 7.5 | 3.3 | 5
| 2014-02-02 15:30 | 7.7 | 3.3 | 5
| 2014-02-02 16:00 | 7.3 | 3.3 | 5
| 2014-02-02 16:30 | 6.7 | 3.9 | 5
| 2014-02-02 17:00 | 6.2 | 3.9 | 5
| 2014-02-02 17:30 | 5.3 | 3.9 | 5
| 2014-02-02 18:00 | 4.6 | 3.9 | 5
| 2014-02-02 18:30 | 3.9 | 3.9 | 5
| 2014-02-02 19:00 | 3.6 | 3.9 | 5
| 2014-02-02 19:30 | 2.9 | 3.9 | 5
| 2014-02-02 20:00 | 2.3 | 3.9 | 5
| 2014-02-02 20:30 | 2.2 | 3.9 | 5
| 2014-02-02 21:00 | 2.3 | 3.9 | 5
| 2014-02-02 21:30 | 2.7 | 3.9 | 5
| 2014-02-02 22:00 | 2.5 | 3.9 | 5
| 2014-02-02 22:30 | 2 | 3.3 | 5
| 2014-02-02 23:00 | 1.3 | 3.3 | 5
| 2014-02-02 23:30 | 1.2 | 3.3 | 5
| 2014-02-03 | 0.5 | 3.3 | 5
| 2014-02-03 00:30 | 0 | 3.3 | 5
| 2014-02-03 01:00 | -0.4 | 3.3 | 5
| 2014-02-03 01:30 | -0.8 | 3.3 | 5
| 2014-02-03 02:00 | -1.1 | 3.3 | 5
| 2014-02-03 02:30 | -1.4 | 3.3 | 5
| 2014-02-03 03:00 | -1.4 | 2.8 | 5
| 2014-02-03 03:30 | -1.6 | 2.8 | 5
| 2014-02-03 04:00 | -1.3 | 2.8 | 5
| 2014-02-03 04:30 | -0.7 | 2.8 | 5
| 2014-02-03 05:00 | -0.4 | 2.8 | 5
| 2014-02-03 05:30 | -0.1 | 2.8 | 5
| 2014-02-03 06:00 | 1.1 | 2.8 | 5
| 2014-02-03 06:30 | 1.4 | 2.8 | 5
| 2014-02-03 07:00 | 1.7 | 2.8 | 5
| 2014-02-03 07:30 | 1.7 | 2.8 | 5
| 2014-02-03 08:00 | 1.8 | 2.8 | 5
| 2014-02-03 08:30 | 1.8 | 2.8 | 5
| 2014-02-03 09:00 | 1.8 | 2.8 | 5
| 2014-02-03 09:30 | 1.6 | 2.2 | 5
| 2014-02-03 10:00 | 2 | 2.2 | 5
| 2014-02-03 10:30 | 2.7 | 2.2 | 5
| 2014-02-03 11:00 | 3.4 | 2.2 | 5
| 2014-02-03 11:30 | 4.4 | 2.2 | 5
| 2014-02-03 12:00 | 5.1 | 2.2 | 5
| 2014-02-03 12:30 | 5.1 | 2.2 | 5
| 2014-02-03 13:00 | 5.3 | 2.8 | 5
| 2014-02-03 13:30 | 5.4 | 2.8 | 5
| 2014-02-03 14:00 | 5.3 | 2.8 | 5
| 2014-02-03 14:30 | 5.3 | 2.8 | 5
| 2014-02-03 15:00 | 5.3 | 2.8 | 5
| 2014-02-03 15:30 | 5.4 | 2.8 | 5
| 2014-02-03 16:00 | 5 | 3.3 | 5
| 2014-02-03 16:30 | 4.8 | 3.3 | 5
| 2014-02-03 17:00 | 4.6 | 3.3 | 5
| 2014-02-03 17:30 | 4.5 | 3.3 | 5
| 2014-02-03 18:00 | 4.4 | 3.3 | 5
| 2014-02-03 18:30 | 4.4 | 3.3 | 5
| 2014-02-03 19:00 | 4.3 | 3.3 | 5
| 2014-02-03 19:30 | 4.2 | 3.3 | 5
| 2014-02-03 20:00 | 4.1 | 3.3 | 5
| 2014-02-03 20:30 | 3.9 | 3.3 | 5
| 2014-02-03 21:00 | 3.8 | 3.3 | 5
| 2014-02-03 21:30 | 3.6 | 3.3 | 5
| 2014-02-03 22:00 | 2.9 | 3.3 | 5
| 2014-02-03 22:30 | 2.4 | 3.3 | 5
| 2014-02-03 23:00 | 1.8 | 3.3 | 5
| 2014-02-03 23:30 | 1.4 | 3.3 | 5
| 2014-02-04 | 1 | 3.3 | 5
| 2014-02-04 00:30 | 0.8 | 3.3 | 5
| 2014-02-04 01:00 | 0.7 | 3.3 | 5
| 2014-02-04 01:30 | 0.6 | 3.3 | 5
| 2014-02-04 02:00 | 0.3 | 3.3 | 5
| 2014-02-04 02:30 | -0.1 | 3.3 | 5
| 2014-02-04 03:00 | -0.5 | 3.3 | 5
| 2014-02-04 03:30 | -0.5 | 2.8 | 5
| 2014-02-04 04:00 | -0.2 | 2.8 | 5
| 2014-02-04 04:30 | -0.4 | 2.8 | 5
| 2014-02-04 05:00 | -0.5 | 2.8 | 5
| 2014-02-04 05:30 | -0.7 | 2.8 | 5
| 2014-02-04 06:00 | -1 | 2.8 | 5
| 2014-02-04 06:30 | -1.1 | 2.8 | 5
| 2014-02-04 07:00 | -0.6 | 2.8 | 5
| 2014-02-04 07:30 | 0.1 | 2.8 | 5
| 2014-02-04 08:00 | 0.7 | 2.8 | 5
| 2014-02-04 08:30 | 0.8 | 2.8 | 5
| 2014-02-04 09:00 | 1.4 | 2.8 | 5
| 2014-02-04 09:30 | 1.4 | 2.8 | 5
| 2014-02-04 10:00 | 1.7 | 2.8 | 5
| 2014-02-04 10:30 | 1.9 | 2.8 | 5
| 2014-02-04 11:00 | 2.8 | 2.2 | 5
| 2014-02-04 11:30 | 3.6 | 2.2 | 5
| 2014-02-04 12:00 | 3.9 | 2.2 | 5
| 2014-02-04 12:30 | 4.2 | 2.8 | 5
| 2014-02-04 13:00 | 4.4 | 2.8 | 5
| 2014-02-04 13:30 | 4.7 | 2.8 | 5
| 2014-02-04 14:00 | 5.3 | 2.8 | 5
| 2014-02-04 14:30 | 6 | 2.8 | 5
| 2014-02-04 15:00 | 6.4 | 2.8 | 5
| 2014-02-04 15:30 | 7.7 | 2.8 | 5
| 2014-02-04 16:00 | 8.1 | 3.3 | 5
| 2014-02-04 16:30 | 7 | 3.3 | 5
| 2014-02-04 17:00 | 5.9 | 3.3 | 5
| 2014-02-04 17:30 | 5 | 3.3 | 5
| 2014-02-04 18:00 | 4.3 | 3.3 | 5
| 2014-02-04 18:30 | 3.4 | 3.3 | 5
| 2014-02-04 19:00 | 3 | 3.3 | 5
| 2014-02-04 19:30 | 2.3 | 3.3 | 5
| 2014-02-04 20:00 | 1.8 | 3.3 | 5
| 2014-02-04 20:30 | 1.4 | 3.3 | 5
| 2014-02-04 21:00 | 1.2 | 3.3 | 5
| 2014-02-04 21:30 | 1.3 | 3.3 | 5
| 2014-02-04 22:00 | 1.8 | 3.3 | 5
| 2014-02-04 22:30 | 2.1 | 3.3 | 5
| 2014-02-04 23:00 | 1.4 | 3.3 | 5
| 2014-02-04 23:30 | 0.9 | 3.3 | 5
| 2014-02-05 | 0.5 | 2.8 | 5
| 2014-02-05 00:30 | 0.3 | 2.8 | 5
| 2014-02-05 01:00 | -0.3 | 2.8 | 5
| 2014-02-05 01:30 | -1 | 2.8 | 5
| 2014-02-05 02:00 | -0.8 | 2.8 | 5
| 2014-02-05 02:30 | 0.4 | 2.8 | 5
| 2014-02-05 03:00 | 0.4 | 2.8 | 5
| 2014-02-05 03:30 | 0.1 | 2.8 | 5
| 2014-02-05 04:00 | 0.1 | 2.8 | 5
| 2014-02-05 04:30 | 0.2 | 2.8 | 5
| 2014-02-05 05:00 | 0.1 | 2.8 | 5
| 2014-02-05 05:30 | 0.1 | 2.2 | 5
| 2014-02-05 06:00 | 0.2 | 2.2 | 5
| 2014-02-05 06:30 | 0.1 | 2.2 | 5
| 2014-02-05 07:00 | -0.3 | 2.2 | 5
| 2014-02-05 07:30 | -0.3 | 2.2 | 5
| 2014-02-05 08:00 | 0 | 2.2 | 5
| 2014-02-05 08:30 | -0.9 | 2.2 | 5
| 2014-02-05 09:00 | -0.6 | 2.2 | 5
| 2014-02-05 09:30 | -0.9 | 2.2 | 5
| 2014-02-05 10:00 | -0.3 | 2.2 | 5
| 2014-02-05 10:30 | 0.1 | 2.2 | 5
| 2014-02-05 11:00 | 0.7 | 2.2 | 5
| 2014-02-05 11:30 | 1.2 | 2.2 | 5
| 2014-02-05 12:00 | 2.1 | 2.2 | 5
| 2014-02-05 12:30 | 2.8 | 2.2 | 5
| 2014-02-05 13:00 | 3.4 | 2.2 | 5
| 2014-02-05 13:30 | 3.7 | 2.2 | 5
| 2014-02-05 14:00 | 3.8 | 2.2 | 5
| 2014-02-05 14:30 | 3.2 | 2.2 | 5
| 2014-02-05 15:00 | 2.6 | 2.2 | 5
| 2014-02-05 15:30 | 2.6 | 2.2 | 5
| 2014-02-05 16:00 | 2.4 | 2.2 | 5
| 2014-02-05 16:30 | 2.8 | 2.2 | 5
| 2014-02-05 17:00 | 3 | 2.2 | 5
| 2014-02-05 17:30 | 2.9 | 2.2 | 5
| 2014-02-05 18:00 | 2.4 | 2.2 | 5
| 2014-02-05 18:30 | 1.8 | 2.2 | 5
| 2014-02-05 19:00 | 1.6 | 2.2 | 5
| 2014-02-05 19:30 | 2.8 | 2.2 | 5
| 2014-02-05 20:00 | 3.3 | 2.2 | 5
| 2014-02-05 20:30 | 3.3 | 2.2 | 5
| 2014-02-05 21:00 | 3.4 | 2.2 | 5
| 2014-02-05 21:30 | 3.7 | 2.2 | 5
| 2014-02-05 22:00 | 3.7 | 2.2 | 5
| 2014-02-05 22:30 | 3.8 | 2.2 | 5
| 2014-02-05 23:00 | 4.4 | 2.2 | 5
| 2014-02-05 23:30 | 4.7 | 2.2 | 5
| 2014-02-06 | 5.2 | 2.2 | 5
| 2014-02-06 00:30 | 5.2 | 2.2 | 5
| 2014-02-06 01:00 | 5.2 | 2.2 | 5
| 2014-02-06 01:30 | 5.2 | 2.2 | 5
| 2014-02-06 02:00 | 5.1 | 2.2 | 5
| 2014-02-06 02:30 | 5.1 | 2.2 | 5
| 2014-02-06 03:00 | 5.3 | 2.2 | 5
| 2014-02-06 03:30 | 5.2 | 2.2 | 5
| 2014-02-06 04:00 | 5.7 | 2.2 | 5
| 2014-02-06 04:30 | 5.4 | 2.2 | 5
| 2014-02-06 05:00 | 5.4 | 2.8 | 5
| 2014-02-06 05:30 | 5.3 | 2.8 | 5
| 2014-02-06 06:00 | 4.8 | 2.8 | 5
| 2014-02-06 06:30 | 5.1 | 2.8 | 5
| 2014-02-06 07:00 | 5.4 | 2.8 | 5
| 2014-02-06 07:30 | 5.6 | 2.8 | 5
| 2014-02-06 08:00 | 5.9 | 2.8 | 5
| 2014-02-06 08:30 | 5.9 | 2.8 | 5
| 2014-02-06 09:00 | 6.3 | 2.8 | 5
| 2014-02-06 09:30 | 6.5 | 2.8 | 5
| 2014-02-06 10:00 | 6.4 | 2.8 | 5
| 2014-02-06 10:30 | 7.1 | 2.8 | 5
| 2014-02-06 11:00 | 7.4 | 2.8 | 5
| 2014-02-06 11:30 | 8.4 | 2.8 | 5
| 2014-02-06 12:00 | 9.4 | 2.8 | 5
| 2014-02-06 12:30 | 9.8 | 2.8 | 5
| 2014-02-06 13:00 | 9.8 | 3.3 | 5
| 2014-02-06 13:30 | 9.8 | 3.3 | 5
| 2014-02-06 14:00 | 10.8 | 3.3 | 5
| 2014-02-06 14:30 | 9.4 | 3.3 | 5
| 2014-02-06 15:00 | 9.8 | 3.3 | 5
| 2014-02-06 15:30 | 9.8 | 3.9 | 5
| 2014-02-06 16:00 | 9 | 3.9 | 5
| 2014-02-06 16:30 | 9 | 3.9 | 5
| 2014-02-06 17:00 | 8.8 | 3.9 | 5
| 2014-02-06 17:30 | 8.4 | 3.9 | 5
| 2014-02-06 18:00 | 8.3 | 3.9 | 5
| 2014-02-06 18:30 | 8.3 | 3.9 | 5
| 2014-02-06 19:00 | 8.7 | 3.9 | 5
| 2014-02-06 19:30 | 8.3 | 4.4 | 5
| 2014-02-06 20:00 | 8.3 | 4.4 | 5
| 2014-02-06 20:30 | 8.5 | 4.4 | 5
| 2014-02-06 21:00 | 8.3 | 4.4 | 5
| 2014-02-06 21:30 | 7.8 | 4.4 | 5
| 2014-02-06 22:00 | 9 | 4.4 | 5
| 2014-02-06 22:30 | 9.7 | 4.4 | 5
| 2014-02-06 23:00 | 9.7 | 4.4 | 5
| 2014-02-06 23:30 | 9.8 | 4.4 | 5
| 2014-02-07 | 9.8 | 4.4 | 5
| 2014-02-07 00:30 | 9.2 | 4.4 | 5
| 2014-02-07 01:00 | 8.8 | 4.4 | 5
| 2014-02-07 01:30 | 8.2 | 4.4 | 5
| 2014-02-07 02:00 | 7.9 | 4.4 | 5
| 2014-02-07 02:30 | 7.4 | 4.4 | 5
| 2014-02-07 03:00 | 5.9 | 4.4 | 5
| 2014-02-07 03:30 | 5.5 | 4.4 | 5
| 2014-02-07 04:00 | 5.8 | 4.4 | 5
| 2014-02-07 04:30 | 5.3 | 3.9 | 5
| 2014-02-07 05:00 | 5.4 | 3.9 | 5
| 2014-02-07 05:30 | 7 | 3.9 | 5
| 2014-02-07 06:00 | 10.2 | 3.9 | 5
| 2014-02-07 06:30 | 10.4 | 3.9 | 5
| 2014-02-07 07:00 | 10.3 | 3.9 | 5
| 2014-02-07 07:30 | 10.5 | 3.9 | 5
| 2014-02-07 08:00 | 10.9 | 3.9 | 5
| 2014-02-07 08:30 | 11.5 | 3.9 | 5
| 2014-02-07 09:00 | 11.5 | 3.9 | 5
| 2014-02-07 09:30 | 11.5 | 3.9 | 5
| 2014-02-07 10:00 | 11.2 | 3.9 | 5
| 2014-02-07 10:30 | 10.8 | 3.9 | 5
| 2014-02-07 11:00 | 10.8 | 4.4 | 5
| 2014-02-07 11:30 | 11.1 | 4.4 | 5
| 2014-02-07 12:00 | 10.7 | 4.4 | 5
| 2014-02-07 12:30 | 9.9 | 4.4 | 5
| 2014-02-07 13:00 | 9.7 | 4.4 | 5
| 2014-02-07 13:30 | 9.9 | 4.4 | 5
| 2014-02-07 14:00 | 10 | 4.4 | 5
| 2014-02-07 14:30 | 10.1 | 4.4 | 5
| 2014-02-07 15:00 | 10.1 | 4.4 | 5
| 2014-02-07 15:30 | 10.1 | 5 | 5
| 2014-02-07 16:00 | 10.2 | 5 | 5
| 2014-02-07 16:30 | 10.3 | 5 | 5
| 2014-02-07 17:00 | 9.8 | 5 | 5
| 2014-02-07 17:30 | 8.9 | 5 | 5
| 2014-02-07 18:00 | 7.9 | 5 | 5
| 2014-02-07 18:30 | 7.4 | 5 | 5
| 2014-02-07 19:00 | 7.1 | 5 | 5
| 2014-02-07 19:30 | 7.6 | 5 | 5
| 2014-02-07 20:00 | 6.8 | 5 | 5
| 2014-02-07 20:30 | 6.3 | 5 | 5
| 2014-02-07 21:00 | 4.9 | 5 | 5
| 2014-02-07 21:30 | 5 | 5 | 5
| 2014-02-07 22:00 | 4.1 | 5 | 5
| 2014-02-07 22:30 | 4.8 | 4.4 | 5
| 2014-02-07 23:00 | 3.2 | 4.4 | 5
| 2014-02-07 23:30 | 3.5 | 4.4 | 5
| 2014-02-08 | 3.9 | 4.4 | 5
| 2014-02-08 00:30 | 4.4 | 4.4 | 5
| 2014-02-08 01:00 | 4.7 | 4.4 | 5
| 2014-02-08 01:30 | 4.3 | 4.4 | 5
| 2014-02-08 02:00 | 4.6 | 4.4 | 5
| 2014-02-08 02:30 | 4.7 | 3.9 | 5
| 2014-02-08 03:00 | 4.9 | 3.9 | 5
| 2014-02-08 03:30 | 4.9 | 3.9 | 5
| 2014-02-08 04:00 | 4.7 | 3.9 | 5
| 2014-02-08 04:30 | 4.8 | 3.9 | 5
| 2014-02-08 05:00 | 5.4 | 3.9 | 5
| 2014-02-08 05:30 | 6.1 | 3.9 | 5
| 2014-02-08 06:00 | 6.6 | 3.9 | 5
| 2014-02-08 06:30 | 6.4 | 3.9 | 5
| 2014-02-08 07:00 | 6.4 | 3.9 | 5
| 2014-02-08 07:30 | 6.7 | 3.9 | 5
| 2014-02-08 08:00 | 7 | 3.9 | 5
| 2014-02-08 08:30 | 7.1 | 3.9 | 5
| 2014-02-08 09:00 | 7.4 | 3.9 | 5
| 2014-02-08 09:30 | 7.6 | 3.9 | 5
| 2014-02-08 10:00 | 7.6 | 3.9 | 5
| 2014-02-08 10:30 | 8 | 3.9 | 5
| 2014-02-08 11:00 | 8.3 | 3.9 | 5
| 2014-02-08 11:30 | 8.6 | 3.9 | 5
| 2014-02-08 12:00 | 9.1 | 3.9 | 5
| 2014-02-08 12:30 | 9.3 | 3.9 | 5
| 2014-02-08 13:00 | 9.6 | 3.9 | 5
| 2014-02-08 13:30 | 9.8 | 3.9 | 5
| 2014-02-08 14:00 | 9.6 | 3.9 | 5
| 2014-02-08 14:30 | 9.4 | 3.9 | 5
| 2014-02-08 15:00 | 8.3 | 3.9 | 5
| 2014-02-08 15:30 | 6.9 | 4.4 | 5
| 2014-02-08 16:00 | 6.4 | 4.4 | 5
| 2014-02-08 16:30 | 6.1 | 4.4 | 5
| 2014-02-08 17:00 | 6.1 | 4.4 | 5
| 2014-02-08 17:30 | 6.2 | 4.4 | 5
| 2014-02-08 18:00 | 6 | 4.4 | 5
| 2014-02-08 18:30 | 6 | 4.4 | 5
| 2014-02-08 19:00 | 6 | 4.4 | 5
| 2014-02-08 19:30 | 6 | 4.4 | 5
| 2014-02-08 20:00 | 6 | 4.4 | 5
| 2014-02-08 20:30 | 6 | 4.4 | 5
| 2014-02-08 21:00 | 6.1 | 4.4 | 5
| 2014-02-08 21:30 | 6.1 | 4.4 | 5
| 2014-02-08 22:00 | 6 | 4.4 | 5
| 2014-02-08 22:30 | 5.8 | 4.4 | 5
| 2014-02-08 23:00 | 5.8 | 4.4 | 5
| 2014-02-08 23:30 | 6.1 | 4.4 | 5
| 2014-02-09 | 5.9 | 4.4 | 5
| 2014-02-09 00:30 | 5.8 | 4.4 | 5
| 2014-02-09 01:00 | 5.8 | 4.4 | 5
| 2014-02-09 01:30 | 5.6 | 4.4 | 5
| 2014-02-09 02:00 | 6.2 | 4.4 | 5
| 2014-02-09 02:30 | 6.2 | 4.4 | 5
| 2014-02-09 03:00 | 5.5 | 4.4 | 5
| 2014-02-09 03:30 | 4.9 | 4.4 | 5
| 2014-02-09 04:00 | 5.6 | 4.4 | 5
| 2014-02-09 04:30 | 5.2 | 4.4 | 5
| 2014-02-09 05:00 | 5.4 | 4.4 | 5
| 2014-02-09 05:30 | 5.4 | 4.4 | 5
| 2014-02-09 06:00 | 5.5 | 4.4 | 5
| 2014-02-09 06:30 | 5.7 | 4.4 | 5
| 2014-02-09 07:00 | 5.7 | 4.4 | 5
| 2014-02-09 07:30 | 5.3 | 4.4 | 5
| 2014-02-09 08:00 | 5.7 | 4.4 | 5
| 2014-02-09 08:30 | 5.7 | 4.4 | 5
| 2014-02-09 09:00 | 5.8 | 4.4 | 5
| 2014-02-09 09:30 | 5.9 | 4.4 | 5
| 2014-02-09 10:00 | 6.7 | 4.4 | 5
| 2014-02-09 10:30 | 7.5 | 4.4 | 5
| 2014-02-09 11:00 | 7 | 4.4 | 5
| 2014-02-09 11:30 | 6.8 | 4.4 | 5
| 2014-02-09 12:00 | 9.1 | 4.4 | 5
| 2014-02-09 12:30 | 7.1 | 4.4 | 5
| 2014-02-09 13:00 | 6 | 4.4 | 5
| 2014-02-09 13:30 | 7.3 | 4.4 | 5
| 2014-02-09 14:00 | 7.2 | 4.4 | 5
| 2014-02-09 14:30 | 7.7 | 4.4 | 5
| 2014-02-09 15:00 | 6.8 | 4.4 | 5
| 2014-02-09 15:30 | 8.1 | 4.4 | 5
| 2014-02-09 16:00 | 7.3 | 4.4 | 5
| 2014-02-09 16:30 | 6.4 | 4.4 | 5
| 2014-02-09 17:00 | 5.4 | 5 | 5
| 2014-02-09 17:30 | 4.6 | 5 | 5
| 2014-02-09 18:00 | 3.4 | 5 | 5
| 2014-02-09 18:30 | 3.1 | 5 | 5
| 2014-02-09 19:00 | 2.7 | 5 | 5
| 2014-02-09 19:30 | 2.1 | 5 | 5
| 2014-02-09 20:00 | 3.3 | 4.4 | 5
| 2014-02-09 20:30 | 3.3 | 4.4 | 5
| 2014-02-09 21:00 | 3.3 | 4.4 | 5
| 2014-02-09 21:30 | 3.1 | 4.4 | 5
| 2014-02-09 22:00 | 2.4 | 4.4 | 5
| 2014-02-09 22:30 | 1.8 | 4.4 | 5
| 2014-02-09 23:00 | 1.5 | 4.4 | 5
| 2014-02-09 23:30 | 2.1 | 4.4 | 5
| 2014-02-10 | 1.9 | 4.4 | 5
| 2014-02-10 00:30 | 1.2 | 3.9 | 5
| 2014-02-10 01:00 | 0.3 | 3.9 | 5
| 2014-02-10 01:30 | -0.4 | 3.9 | 5
| 2014-02-10 02:00 | -0.7 | 3.9 | 5
| 2014-02-10 02:30 | -1.2 | 3.9 | 5
| 2014-02-10 03:00 | -1.9 | 3.9 | 5
| 2014-02-10 03:30 | -1.8 | 3.9 | 5
| 2014-02-10 04:00 | -2.9 | 3.9 | 5
| 2014-02-10 04:30 | -2.4 | 3.3 | 5
| 2014-02-10 05:00 | -1.9 | 3.3 | 5
| 2014-02-10 05:30 | -1.8 | 3.3 | 5
| 2014-02-10 06:00 | -1.1 | 3.3 | 5
| 2014-02-10 06:30 | -0.7 | 3.3 | 5
| 2014-02-10 07:00 | 0.1 | 3.3 | 5
| 2014-02-10 07:30 | 0.9 | 3.3 | 5
| 2014-02-10 08:00 | 1.1 | 3.3 | 5
| 2014-02-10 08:30 | 1.2 | 3.3 | 5
| 2014-02-10 09:00 | 1.9 | 2.8 | 5.6
| 2014-02-10 09:30 | 2.6 | 2.8 | 5.6
| 2014-02-10 10:00 | 3.7 | 2.8 | 5.6
| 2014-02-10 10:30 | 4.2 | 2.8 | 5.6
| 2014-02-10 11:00 | 5.2 | 2.8 | 5.6
| 2014-02-10 11:30 | 5.1 | 2.8 | 5.6
| 2014-02-10 12:00 | 5.2 | 2.8 | 5.6
| 2014-02-10 12:30 | 5.3 | 2.8 | 5.6
| 2014-02-10 13:00 | 5.5 | 2.8 | 5.6
| 2014-02-10 13:30 | 5.6 | 2.8 | 5.6
| 2014-02-10 14:00 | 5.8 | 2.8 | 5.6
| 2014-02-10 14:30 | 6.4 | 2.8 | 5.6
| 2014-02-10 15:00 | 6.4 | 3.3 | 5.6
| 2014-02-10 15:30 | 6.3 | 3.3 | 5.6
| 2014-02-10 16:00 | 6.1 | 3.3 | 5.6
| 2014-02-10 16:30 | 5.1 | 3.3 | 5.6
| 2014-02-10 17:00 | 4.8 | 3.3 | 5.6
| 2014-02-10 17:30 | 4.6 | 3.3 | 5.6
| 2014-02-10 18:00 | 4.4 | 3.3 | 5.6
| 2014-02-10 18:30 | 4.2 | 3.3 | 5.6
| 2014-02-10 19:00 | 3.9 | 3.3 | 5.6
| 2014-02-10 19:30 | 3.7 | 3.3 | 5.6
| 2014-02-10 20:00 | 3.6 | 3.3 | 5.6
| 2014-02-10 20:30 | 3.4 | 3.3 | 5.6
| 2014-02-10 21:00 | 3.5 | 3.3 | 5.6
| 2014-02-10 21:30 | 3.6 | 3.3 | 5.6
| 2014-02-10 22:00 | 3.6 | 3.3 | 5.6
| 2014-02-10 22:30 | 3.7 | 3.3 | 5.6
| 2014-02-10 23:00 | 3.8 | 3.3 | 5.6
| 2014-02-10 23:30 | 3.8 | 3.3 | 5.6
| 2014-02-11 | 3.8 | 3.3 | 5.6
| 2014-02-11 00:30 | 3.9 | 3.9 | 5
| 2014-02-11 01:00 | 3.8 | 3.9 | 5
| 2014-02-11 01:30 | 3.8 | 3.9 | 5
| 2014-02-11 02:00 | 3.7 | 3.9 | 5
| 2014-02-11 02:30 | 3.6 | 3.9 | 5
| 2014-02-11 03:00 | 3.4 | 3.9 | 5
| 2014-02-11 03:30 | 3.8 | 3.9 | 5
| 2014-02-11 04:00 | 3.9 | 3.9 | 5
| 2014-02-11 04:30 | 4.2 | 3.3 | 5
| 2014-02-11 05:00 | 4.2 | 3.3 | 5
| 2014-02-11 05:30 | 4.3 | 3.3 | 5
| 2014-02-11 06:00 | 4.3 | 3.3 | 5
| 2014-02-11 06:30 | 4.2 | 3.3 | 5
| 2014-02-11 07:00 | 4.1 | 3.3 | 5
| 2014-02-11 07:30 | 4.4 | 3.3 | 5
| 2014-02-11 08:00 | 4.5 | 3.3 | 5
| 2014-02-11 08:30 | 4.6 | 3.3 | 5
| 2014-02-11 09:00 | 4.8 | 3.3 | 5
| 2014-02-11 09:30 | 5.2 | 3.3 | 5
| 2014-02-11 10:00 | 5.2 | 3.3 | 5
| 2014-02-11 10:30 | 5.7 | 3.3 | 5
| 2014-02-11 11:00 | 6.8 | 3.3 | 5
| 2014-02-11 11:30 | 6.8 | 3.9 | 5
| 2014-02-11 12:00 | 6.2 | 3.9 | 5
| 2014-02-11 12:30 | 7 | 3.9 | 5
| 2014-02-11 13:00 | 6.8 | 3.9 | 5
| 2014-02-11 13:30 | 8.8 | 3.9 | 5
| 2014-02-11 14:00 | 8.8 | 3.9 | 5
| 2014-02-11 14:30 | 8.2 | 3.9 | 5
| 2014-02-11 15:00 | 8 | 3.9 | 5
| 2014-02-11 15:30 | 8.2 | 4.4 | 5
| 2014-02-11 16:00 | 7.8 | 4.4 | 5
| 2014-02-11 16:30 | 6.7 | 4.4 | 5
| 2014-02-11 17:00 | 6.4 | 4.4 | 5
| 2014-02-11 17:30 | 5.4 | 4.4 | 5
| 2014-02-11 18:00 | 4.7 | 4.4 | 5
| 2014-02-11 18:30 | 4.3 | 4.4 | 5
| 2014-02-11 19:00 | 3.8 | 4.4 | 5
| 2014-02-11 19:30 | 3.5 | 4.4 | 5
| 2014-02-11 20:00 | 2.8 | 4.4 | 5
| 2014-02-11 20:30 | 2.7 | 4.4 | 5
| 2014-02-11 21:00 | 3.6 | 4.4 | 5
| 2014-02-11 21:30 | 4 | 4.4 | 5
| 2014-02-11 22:00 | 3.9 | 4.4 | 5
| 2014-02-11 22:30 | 4.4 | 4.4 | 5
| 2014-02-11 23:00 | 4.6 | 4.4 | 5
| 2014-02-11 23:30 | 4.6 | 3.9 | 5
| 2014-02-12 | 4.6 | 3.9 | 5
| 2014-02-12 00:30 | 4.8 | 3.9 | 5
| 2014-02-12 01:00 | 4.8 | 3.9 | 5
| 2014-02-12 01:30 | 4.6 | 3.9 | 5
| 2014-02-12 02:00 | 4.6 | 3.9 | 5
| 2014-02-12 02:30 | 4.3 | 3.9 | 5
| 2014-02-12 03:00 | 3.7 | 3.9 | 5
| 2014-02-12 03:30 | 3.3 | 3.9 | 5
| 2014-02-12 04:00 | 3.3 | 3.9 | 5
| 2014-02-12 04:30 | 3.5 | 3.9 | 5
| 2014-02-12 05:00 | 3.3 | 3.9 | 5
| 2014-02-12 05:30 | 2.9 | 3.9 | 5
| 2014-02-12 06:00 | 2.7 | 3.9 | 5
| 2014-02-12 06:30 | 3.1 | 3.9 | 5
| 2014-02-12 07:00 | 3.1 | 3.9 | 5
| 2014-02-12 07:30 | 1.9 | 3.9 | 5
| 2014-02-12 08:00 | 2.1 | 3.9 | 5
| 2014-02-12 08:30 | 2.8 | 3.9 | 5
| 2014-02-12 09:00 | 3.7 | 3.3 | 5
| 2014-02-12 09:30 | 3.8 | 3.3 | 5
| 2014-02-12 10:00 | 4.4 | 3.3 | 5
| 2014-02-12 10:30 | 5.3 | 3.3 | 5
| 2014-02-12 11:00 | 5.6 | 3.3 | 5
| 2014-02-12 11:30 | 5.8 | 3.3 | 5
| 2014-02-12 12:00 | 6.7 | 3.3 | 5
| 2014-02-12 12:30 | 6.8 | 3.3 | 5
| 2014-02-12 13:00 | 6.5 | 3.9 | 5
| 2014-02-12 13:30 | 7.2 | 3.9 | 5
| 2014-02-12 14:00 | 7.2 | 3.9 | 5
| 2014-02-12 14:30 | 7.3 | 3.9 | 5
| 2014-02-12 15:00 | 8.4 | 3.9 | 5
| 2014-02-12 15:30 | 7.8 | 3.9 | 5
| 2014-02-12 16:00 | 7.1 | 3.9 | 5
| 2014-02-12 16:30 | 7.3 | 4.4 | 5
| 2014-02-12 17:00 | 6.9 | 4.4 | 5
| 2014-02-12 17:30 | 5.6 | 4.4 | 5
| 2014-02-12 18:00 | 4.6 | 4.4 | 5
| 2014-02-12 18:30 | 4.3 | 4.4 | 5
| 2014-02-12 19:00 | 4.1 | 4.4 | 5
| 2014-02-12 19:30 | 3.9 | 4.4 | 5
| 2014-02-12 20:00 | 3.7 | 4.4 | 5
| 2014-02-12 20:30 | 3.3 | 4.4 | 5
| 2014-02-12 21:00 | 2.9 | 4.4 | 5
| 2014-02-12 21:30 | 3.2 | 3.9 | 5
| 2014-02-12 22:00 | 3.1 | 3.9 | 5
| 2014-02-12 22:30 | 3.2 | 3.9 | 5
| 2014-02-12 23:00 | 3.1 | 3.9 | 5
| 2014-02-12 23:30 | 4.9 | 3.9 | 5
| 2014-02-13 | 6.8 | 3.9 | 5
| 2014-02-13 00:30 | 5.3 | 3.9 | 5
| 2014-02-13 01:00 | 4.9 | 3.9 | 5
| 2014-02-13 01:30 | 5.7 | 3.9 | 5
| 2014-02-13 02:00 | 5.8 | 3.9 | 5
| 2014-02-13 02:30 | 5.9 | 3.9 | 5
| 2014-02-13 03:00 | 5.8 | 3.9 | 5
| 2014-02-13 03:30 | 5.7 | 3.9 | 5
| 2014-02-13 04:00 | 5.6 | 3.9 | 5
| 2014-02-13 04:30 | 5.6 | 3.9 | 5
| 2014-02-13 05:00 | 5.4 | 3.9 | 5
| 2014-02-13 05:30 | 5.2 | 3.9 | 5
| 2014-02-13 06:00 | 5.2 | 3.9 | 5
| 2014-02-13 06:30 | 5.3 | 3.9 | 5
| 2014-02-13 07:00 | 5.4 | 3.9 | 5
| 2014-02-13 07:30 | 5.3 | 3.9 | 5
| 2014-02-13 08:00 | 5.1 | 3.9 | 5
| 2014-02-13 08:30 | 6.3 | 3.9 | 5
| 2014-02-13 09:00 | 6.6 | 3.9 | 5
| 2014-02-13 09:30 | 6.8 | 3.9 | 5
| 2014-02-13 10:00 | 6.9 | 3.9 | 5
| 2014-02-13 10:30 | 6.9 | 3.9 | 5
| 2014-02-13 11:00 | 7.2 | 3.9 | 5
| 2014-02-13 11:30 | 7.5 | 3.9 | 5
| 2014-02-13 12:00 | 7.6 | 3.9 | 5
| 2014-02-13 12:30 | 6.7 | 3.9 | 5
| 2014-02-13 13:00 | 5.8 | 3.9 | 5
| 2014-02-13 13:30 | 5.3 | 3.9 | 5
| 2014-02-13 14:00 | 5.3 | 4.4 | 5
| 2014-02-13 14:30 | 5.1 | 4.4 | 5
| 2014-02-13 15:00 | 5.1 | 4.4 | 5
| 2014-02-13 15:30 | 5.1 | 4.4 | 5
| 2014-02-13 16:00 | 5.2 | 4.4 | 5
| 2014-02-13 16:30 | 5.4 | 4.4 | 5
| 2014-02-13 17:00 | 5.4 | 4.4 | 5
| 2014-02-13 17:30 | 5.2 | 4.4 | 5
| 2014-02-13 18:00 | 5.5 | 4.4 | 5
| 2014-02-13 18:30 | 5.5 | 4.4 | 5
| 2014-02-13 19:00 | 6.1 | 4.4 | 5
| 2014-02-13 19:30 | 6.1 | 4.4 | 5
| 2014-02-13 20:00 | 5.8 | 4.4 | 5
| 2014-02-13 20:30 | 5.7 | 4.4 | 5.6
| 2014-02-13 21:00 | 5.2 | 4.4 | 5
| 2014-02-13 21:30 | 4.9 | 4.4 | 5.6
| 2014-02-13 22:00 | 4.7 | 4.4 | 5.6
| 2014-02-13 22:30 | 4.3 | 4.4 | 5.6
| 2014-02-13 23:00 | 4.2 | 4.4 | 5.6
| 2014-02-13 23:30 | 4.3 | 4.4 | 5.6
| 2014-02-14 | 3.7 | 4.4 | 5.6
| 2014-02-14 00:30 | 4.3 | 4.4 | 5.6
| 2014-02-14 01:00 | 4.2 | 4.4 | 5.6
| 2014-02-14 01:30 | 4.4 | 4.4 | 5.6
| 2014-02-14 02:00 | 4.3 | 4.4 | 5.6
| 2014-02-14 02:30 | 4.5 | 4.4 | 5.6
| 2014-02-14 03:00 | 4.4 | 3.9 | 5.6
| 2014-02-14 03:30 | 4.3 | 3.9 | 5.6
| 2014-02-14 04:00 | 4.3 | 3.9 | 5.6
| 2014-02-14 04:30 | 4.2 | 3.9 | 5.6
| 2014-02-14 05:00 | 4.4 | 3.9 | 5.6
| 2014-02-14 05:30 | 4.1 | 3.9 | 5.6
| 2014-02-14 06:00 | 3.7 | 3.9 | 5.6
| 2014-02-14 06:30 | 4.2 | 3.9 | 5.6
| 2014-02-14 07:00 | 4 | 3.9 | 5.6
| 2014-02-14 07:30 | 4.1 | 3.9 | 5.6
| 2014-02-14 08:00 | 4.1 | 3.9 | 5.6
| 2014-02-14 08:30 | 3.6 | 3.9 | 5.6
| 2014-02-14 09:00 | 4.1 | 3.9 | 5.6
| 2014-02-14 09:30 | 4.8 | 3.9 | 5.6
| 2014-02-14 10:00 | 5.2 | 3.9 | 5.6
| 2014-02-14 10:30 | 6.7 | 3.9 | 5.6
| 2014-02-14 11:00 | 7.3 | 3.9 | 5.6
| 2014-02-14 11:30 | 8.2 | 3.9 | 5.6
| 2014-02-14 12:00 | 9.2 | 3.9 | 5.6
| 2014-02-14 12:30 | 8.8 | 3.9 | 5.6
| 2014-02-14 13:00 | 8.7 | 3.9 | 5.6
| 2014-02-14 13:30 | 8.4 | 3.9 | 5.6
| 2014-02-14 14:00 | 8.4 | 4.4 | 5.6
| 2014-02-14 14:30 | 8.4 | 4.4 | 5.6
| 2014-02-14 15:00 | 8.4 | 4.4 | 5.6
| 2014-02-14 15:30 | 8.6 | 4.4 | 5.6
| 2014-02-14 16:00 | 8.5 | 5 | 5.6
| 2014-02-14 16:30 | 8.4 | 5 | 5.6
| 2014-02-14 17:00 | 8.1 | 5 | 5.6
| 2014-02-14 17:30 | 7.9 | 5 | 5.6
| 2014-02-14 18:00 | 6.8 | 5 | 5.6
| 2014-02-14 18:30 | 5.7 | 5 | 5.6
| 2014-02-14 19:00 | 5.4 | 5 | 5.6
| 2014-02-14 19:30 | 5.4 | 5 | 5.6
| 2014-02-14 20:00 | 5.6 | 5 | 5.6
| 2014-02-14 20:30 | 5.6 | 5 | 5.6
| 2014-02-14 21:00 | 5.6 | 5 | 5.6
| 2014-02-14 21:30 | 5.6 | 5 | 5.6
| 2014-02-14 22:00 | 5.6 | 5 | 5.6
| 2014-02-14 22:30 | 5.6 | 5 | 5.6
| 2014-02-14 23:00 | 5.7 | 5 | 5.6
| 2014-02-14 23:30 | 5.9 | 5 | 5.6
| 2014-02-15 | 5.8 | 5 | 5.6
| 2014-02-15 00:30 | 5.5 | 5 | 5.6
| 2014-02-15 01:00 | 5.4 | 5 | 5.6
| 2014-02-15 01:30 | 5.2 | 5 | 5.6
| 2014-02-15 02:00 | 4.9 | 5 | 5.6
| 2014-02-15 02:30 | 4.7 | 5 | 5.6
| 2014-02-15 03:00 | 4.2 | 5 | 5.6
| 2014-02-15 03:30 | 4.2 | 5 | 5.6
| 2014-02-15 04:00 | 4.4 | 5 | 5.6
| 2014-02-15 04:30 | 4.8 | 4.4 | 5.6
| 2014-02-15 05:00 | 9.7 | 4.4 | 5.6
| 2014-02-15 05:30 | 10.2 | 4.4 | 5.6
| 2014-02-15 06:00 | 10.1 | 4.4 | 5.6
| 2014-02-15 06:30 | 10.3 | 4.4 | 5.6
| 2014-02-15 07:00 | 10.6 | 4.4 | 5.6
| 2014-02-15 07:30 | 10.6 | 4.4 | 5.6
| 2014-02-15 08:00 | 10.5 | 4.4 | 5.6
| 2014-02-15 08:30 | 10.7 | 4.4 | 5.6
| 2014-02-15 09:00 | 10.7 | 4.4 | 5.6
| 2014-02-15 09:30 | 10.7 | 5 | 5.6
| 2014-02-15 10:00 | 10.6 | 5 | 5.6
| 2014-02-15 10:30 | 10.6 | 5 | 5.6
| 2014-02-15 11:00 | 10.5 | 5 | 5.6
| 2014-02-15 11:30 | 10.6 | 5 | 5.6
| 2014-02-15 12:00 | 10.9 | 5 | 5.6
| 2014-02-15 12:30 | 10.3 | 5 | 5.6
| 2014-02-15 13:00 | 10 | 5 | 5.6
| 2014-02-15 13:30 | 9.3 | 5 | 5.6
| 2014-02-15 14:00 | 9 | 5 | 5.6
| 2014-02-15 14:30 | 8.8 | 5.6 | 5.6
| 2014-02-15 15:00 | 8.8 | 5.6 | 5.6
| 2014-02-15 15:30 | 8.5 | 5.6 | 5.6
| 2014-02-15 16:00 | 8.3 | 5.6 | 5.6
| 2014-02-15 16:30 | 8.1 | 5.6 | 5.6
| 2014-02-15 17:00 | 7.9 | 5.6 | 5.6
| 2014-02-15 17:30 | 7.7 | 5.6 | 5.6
| 2014-02-15 18:00 | 7.4 | 5.6 | 5.6
| 2014-02-15 18:30 | 7.3 | 5.6 | 5.6
| 2014-02-15 19:00 | 7.3 | 5.6 | 5.6
| 2014-02-15 19:30 | 7.1 | 5.6 | 5.6
| 2014-02-15 20:00 | 6.9 | 5.6 | 5.6
| 2014-02-15 20:30 | 6.6 | 5.6 | 5.6
| 2014-02-15 21:00 | 6.7 | 5.6 | 5.6
| 2014-02-15 21:30 | 6.7 | 5.6 | 5.6
| 2014-02-15 22:00 | 6.7 | 5.6 | 5.6
| 2014-02-15 22:30 | 6.8 | 5.6 | 5.6
| 2014-02-15 23:00 | 6.8 | 5.6 | 5.6
| 2014-02-15 23:30 | 6.8 | 5.6 | 5.6
| 2014-02-16 | 6.7 | 5.6 | 5.6
| 2014-02-16 00:30 | 6.2 | 5.6 | 5.6
| 2014-02-16 01:00 | 6.3 | 5.6 | 5.6
| 2014-02-16 01:30 | 6.4 | 5.6 | 5.6
| 2014-02-16 02:00 | 6.3 | 5.6 | 5.6
| 2014-02-16 02:30 | 6.1 | 5.6 | 5.6
| 2014-02-16 03:00 | 5.9 | 5.6 | 5.6
| 2014-02-16 03:30 | 5.9 | 5.6 | 5.6
| 2014-02-16 04:00 | 5.7 | 5.6 | 5.6
| 2014-02-16 04:30 | 5.9 | 5.6 | 5.6
| 2014-02-16 05:00 | 6.1 | 5 | 5.6
| 2014-02-16 05:30 | 6.2 | 5 | 5.6
| 2014-02-16 06:00 | 6.2 | 5 | 5.6
| 2014-02-16 06:30 | 6.3 | 5 | 5.6
| 2014-02-16 07:00 | 6.5 | 5 | 5.6
| 2014-02-16 07:30 | 6.6 | 5 | 5.6
| 2014-02-16 08:00 | 5.9 | 5 | 5.6
| 2014-02-16 08:30 | 5.9 | 5 | 5.6
| 2014-02-16 09:00 | 6.1 | 5 | 5.6
| 2014-02-16 09:30 | 6.7 | 5 | 5.6
| 2014-02-16 10:00 | 7.3 | 5 | 5.6
| 2014-02-16 10:30 | 8.2 | 5 | 5.6
| 2014-02-16 11:00 | 9 | 5 | 5.6
| 2014-02-16 11:30 | 8.2 | 5 | 5.6
| 2014-02-16 12:00 | 8.6 | 5 | 5.6
| 2014-02-16 12:30 | 9.8 | 5.6 | 5.6
| 2014-02-16 13:00 | 8.9 | 5.6 | 5.6
| 2014-02-16 13:30 | 9.6 | 5.6 | 5.6
| 2014-02-16 14:00 | 9.4 | 5.6 | 5.6
| 2014-02-16 14:30 | 10.6 | 5.6 | 5.6
| 2014-02-16 15:00 | 11.1 | 5.6 | 5.6
| 2014-02-16 15:30 | 8.1 | 6.1 | 5.6
| 2014-02-16 16:00 | 7.9 | 6.1 | 5.6
| 2014-02-16 16:30 | 7.9 | 6.1 | 5.6
| 2014-02-16 17:00 | 7.7 | 6.1 | 5.6
| 2014-02-16 17:30 | 7.9 | 6.1 | 5.6
| 2014-02-16 18:00 | 7.3 | 6.1 | 5.6
| 2014-02-16 18:30 | 6.2 | 6.1 | 5.6
| 2014-02-16 19:00 | 5.8 | 6.1 | 5.6
| 2014-02-16 19:30 | 6.5 | 6.1 | 5.6
| 2014-02-16 20:00 | 5.9 | 6.1 | 5.6
| 2014-02-16 20:30 | 4.8 | 6.1 | 5.6
| 2014-02-16 21:00 | 4.3 | 6.1 | 5.6
| 2014-02-16 21:30 | 3.8 | 6.1 | 5.6
| 2014-02-16 22:00 | 3.3 | 6.1 | 5.6
| 2014-02-16 22:30 | 2.7 | 6.1 | 5.6
| 2014-02-16 23:00 | 2.4 | 6.1 | 5.6
| 2014-02-16 23:30 | 2.8 | 5.6 | 5.6
| 2014-02-17 | 2.6 | 5.6 | 5.6
| 2014-02-17 00:30 | 2.3 | 5.6 | 5.6
| 2014-02-17 01:00 | 2.1 | 5.6 | 5.6
| 2014-02-17 01:30 | 1.5 | 5.6 | 5.6
| 2014-02-17 02:00 | 1.3 | 5 | 5.6
| 2014-02-17 02:30 | 1.1 | 5 | 5.6
| 2014-02-17 03:00 | 0.8 | 5 | 5.6
| 2014-02-17 03:30 | 0.7 | 5 | 5.6
| 2014-02-17 04:00 | 0.4 | 5 | 5.6
| 2014-02-17 04:30 | 0.5 | 4.4 | 5.6
| 2014-02-17 05:00 | 0.2 | 4.4 | 5.6
| 2014-02-17 05:30 | 0.3 | 4.4 | 5.6
| 2014-02-17 06:00 | 0.2 | 4.4 | 5.6
| 2014-02-17 06:30 | -0.1 | 4.4 | 5.6
| 2014-02-17 07:00 | -0.3 | 4.4 | 5.6
| 2014-02-17 07:30 | -0.1 | 3.9 | 5.6
| 2014-02-17 08:00 | -0.1 | 3.9 | 5.6
| 2014-02-17 08:30 | 0.2 | 3.9 | 5.6
| 2014-02-17 09:00 | 0.7 | 3.9 | 5.6
| 2014-02-17 09:30 | 2.5 | 3.9 | 5.6
| 2014-02-17 10:00 | 2.9 | 3.9 | 5.6
| 2014-02-17 10:30 | 4.3 | 3.9 | 5.6
| 2014-02-17 11:00 | 6.7 | 3.9 | 5.6
| 2014-02-17 11:30 | 6.9 | 3.3 | 5.6
| 2014-02-17 12:00 | 5.8 | 3.3 | 5.6
| 2014-02-17 12:30 | 7 | 3.9 | 5.6
| 2014-02-17 13:00 | 7.6 | 3.9 | 5.6
| 2014-02-17 13:30 | 8.8 | 3.9 | 5.6
| 2014-02-17 14:00 | 10.2 | 4.4 | 5.6
| 2014-02-17 14:30 | 11 | 4.4 | 5.6
| 2014-02-17 15:00 | 11.2 | 4.4 | 5.6
| 2014-02-17 15:30 | 10.5 | 5 | 5.6
| 2014-02-17 16:00 | 10.4 | 5 | 5.6
| 2014-02-17 16:30 | 11.3 | 5.6 | 5.6
| 2014-02-17 17:00 | 10.2 | 5.6 | 5.6
| 2014-02-17 17:30 | 9.2 | 5.6 | 5.6
| 2014-02-17 18:00 | 7.8 | 5.6 | 5.6
| 2014-02-17 18:30 | 7.4 | 6.1 | 5.6
| 2014-02-17 19:00 | 6.7 | 6.1 | 5.6
| 2014-02-17 19:30 | 6.3 | 6.1 | 5.6
| 2014-02-17 20:00 | 5.4 | 6.1 | 5.6
| 2014-02-17 20:30 | 4.3 | 5.6 | 5.6
| 2014-02-17 21:00 | 4.1 | 5.6 | 5.6
| 2014-02-17 21:30 | 3.8 | 5.6 | 5.6
| 2014-02-17 22:00 | 3.7 | 5.6 | 5.6
| 2014-02-17 22:30 | 2.8 | 5.6 | 5.6
| 2014-02-17 23:00 | 1.8 | 5.6 | 5.6
| 2014-02-17 23:30 | 1.2 | 5.6 | 5.6
| 2014-02-18 | 0.9 | 5 | 5.6
| 2014-02-18 00:30 | 1 | 5 | 5.6
| 2014-02-18 01:00 | 0.8 | 5 | 5.6
| 2014-02-18 01:30 | 0.9 | 5 | 5.6
| 2014-02-18 02:00 | 0.3 | 5 | 5.6
| 2014-02-18 02:30 | -0.1 | 5 | 5.6
| 2014-02-18 03:00 | -0.3 | 4.4 | 5.6
| 2014-02-18 03:30 | -0.4 | 4.4 | 5.6
| 2014-02-18 04:00 | -0.8 | 4.4 | 5.6
| 2014-02-18 04:30 | -1.1 | 4.4 | 5.6
| 2014-02-18 05:00 | -1.2 | 4.4 | 5.6
| 2014-02-18 05:30 | -1.6 | 4.4 | 5.6
| 2014-02-18 06:00 | -1.7 | 3.9 | 5.6
| 2014-02-18 06:30 | -1.3 | 3.9 | 5.6
| 2014-02-18 07:00 | -1.1 | 3.9 | 5.6
| 2014-02-18 07:30 | -1.4 | 3.9 | 5.6
| 2014-02-18 08:00 | -1.7 | 3.9 | 5.6
| 2014-02-18 08:30 | -1.6 | 3.9 | 5.6
| 2014-02-18 09:00 | -0.8 | 3.9 | 5.6
| 2014-02-18 09:30 | -0.3 | 3.3 | 5.6
| 2014-02-18 10:00 | 0.8 | 3.3 | 5.6
| 2014-02-18 10:30 | 2.7 | 3.3 | 5.6
| 2014-02-18 11:00 | 4.7 | 3.3 | 5.6
| 2014-02-18 11:30 | 4.5 | 3.3 | 5.6
| 2014-02-18 12:00 | 5.4 | 3.3 | 5.6
| 2014-02-18 12:30 | 6.9 | 3.3 | 5.6
| 2014-02-18 13:00 | 7.4 | 3.3 | 5.6
| 2014-02-18 13:30 | 7.6 | 3.9 | 5.6
| 2014-02-18 14:00 | 8.8 | 3.9 | 5.6
| 2014-02-18 14:30 | 8.9 | 3.9 | 5.6
| 2014-02-18 15:00 | 9.1 | 4.4 | 5.6
| 2014-02-18 15:30 | 9.3 | 4.4 | 5.6
| 2014-02-18 16:00 | 9.1 | 4.4 | 5.6
| 2014-02-18 16:30 | 8.7 | 5 | 5.6
| 2014-02-18 17:00 | 8.3 | 5 | 5.6
| 2014-02-18 17:30 | 7.4 | 5 | 5.6
| 2014-02-18 18:00 | 6.7 | 5 | 5.6
| 2014-02-18 18:30 | 6.3 | 5 | 5.6
| 2014-02-18 19:00 | 6.2 | 5 | 5.6
| 2014-02-18 19:30 | 5.4 | 5 | 5.6
| 2014-02-18 20:00 | 5 | 5 | 5.6
| 2014-02-18 20:30 | 4.8 | 5 | 5.6
| 2014-02-18 21:00 | 4.7 | 5 | 5.6
| 2014-02-18 21:30 | 4.6 | 5 | 5.6
| 2014-02-18 22:00 | 4.4 | 5 | 5.6
| 2014-02-18 22:30 | 4.3 | 5 | 5.6
| 2014-02-18 23:00 | 4.5 | 5 | 5.6
| 2014-02-18 23:30 | 4.7 | 5 | 5.6
| 2014-02-19 | 4.7 | 5 | 5.6
| 2014-02-19 00:30 | 4.9 | 5 | 5.6
| 2014-02-19 01:00 | 5.4 | 5 | 5.6
| 2014-02-19 01:30 | 5.8 | 5 | 5.6
| 2014-02-19 02:00 | 5.6 | 5 | 5.6
| 2014-02-19 02:30 | 5.3 | 5 | 5.6
| 2014-02-19 03:00 | 5.4 | 5 | 5.6
| 2014-02-19 03:30 | 5.6 | 5 | 5.6
| 2014-02-19 04:00 | 5.8 | 5 | 5.6
| 2014-02-19 04:30 | 6 | 5 | 5.6
| 2014-02-19 05:00 | 6.1 | 5 | 5.6
| 2014-02-19 05:30 | 6.1 | 5 | 5.6
| 2014-02-19 06:00 | 5.9 | 5 | 5.6
| 2014-02-19 06:30 | 5.9 | 5 | 5.6
| 2014-02-19 07:00 | 5.7 | 5 | 5.6
| 2014-02-19 07:30 | 6.1 | 5 | 5.6
| 2014-02-19 08:00 | 6.2 | 5 | 5.6
| 2014-02-19 08:30 | 6.4 | 5 | 5.6
| 2014-02-19 09:00 | 6.4 | 5 | 5.6
| 2014-02-19 09:30 | 6.6 | 5 | 5.6
| 2014-02-19 10:00 | 6.9 | 5 | 5.6
| 2014-02-19 10:30 | 8.2 | 5 | 5.6
| 2014-02-19 11:00 | 8.8 | 5 | 5.6
| 2014-02-19 11:30 | 10.4 | 5 | 5.6
| 2014-02-19 12:00 | 10.7 | 5 | 5.6
| 2014-02-19 12:30 | 11.2 | 5 | 5.6
| 2014-02-19 13:00 | 11.7 | 5 | 5.6
| 2014-02-19 13:30 | 10.8 | 5.6 | 5.6
| 2014-02-19 14:00 | 10.8 | 5.6 | 5.6
| 2014-02-19 14:30 | 10.5 | 5.6 | 5.6
| 2014-02-19 15:00 | 9.9 | 5.6 | 5.6
| 2014-02-19 15:30 | 10.9 | 6.1 | 5.6
| 2014-02-19 16:00 | 11.2 | 6.1 | 5.6
| 2014-02-19 16:30 | 10.8 | 6.1 | 5.6
| 2014-02-19 17:00 | 9.6 | 6.1 | 5.6
| 2014-02-19 17:30 | 9.1 | 6.1 | 5.6
| 2014-02-19 18:00 | 8.7 | 6.1 | 5.6
| 2014-02-19 18:30 | 8 | 6.1 | 5.6
| 2014-02-19 19:00 | 7.4 | 6.1 | 5.6
| 2014-02-19 19:30 | 7.4 | 6.1 | 5.6
| 2014-02-19 20:00 | 7.3 | 6.1 | 5.6
| 2014-02-19 20:30 | 7.1 | 6.1 | 5.6
| 2014-02-19 21:00 | 7.1 | 6.1 | 5.6
| 2014-02-19 21:30 | 6.3 | 6.1 | 5.6
| 2014-02-19 22:00 | 6.2 | 6.1 | 5.6
| 2014-02-19 22:30 | 6.4 | 6.1 | 5.6
| 2014-02-19 23:00 | 5.6 | 6.1 | 5.6
| 2014-02-19 23:30 | 4.8 | 6.1 | 5.6
| 2014-02-20 | 4.3 | 6.1 | 5.6
| 2014-02-20 00:30 | 4.1 | 6.1 | 5.6
| 2014-02-20 01:00 | 3.7 | 6.1 | 5.6
| 2014-02-20 01:30 | 3.4 | 6.1 | 5.6
| 2014-02-20 02:00 | 3.2 | 5.6 | 5.6
| 2014-02-20 02:30 | 3.4 | 5.6 | 5.6
| 2014-02-20 03:00 | 3.9 | 5.6 | 5.6
| 2014-02-20 03:30 | 4.9 | 5.6 | 5.6
| 2014-02-20 04:00 | 5.1 | 5.6 | 5.6
| 2014-02-20 04:30 | 5.1 | 5.6 | 5.6
| 2014-02-20 05:00 | 5.4 | 5.6 | 5.6
| 2014-02-20 05:30 | 5.7 | 5 | 5.6
| 2014-02-20 06:00 | 5.8 | 5 | 5.6
| 2014-02-20 06:30 | 5.9 | 5 | 5.6
| 2014-02-20 07:00 | 6.1 | 5 | 5.6
| 2014-02-20 07:30 | 6.1 | 5 | 5.6
| 2014-02-20 08:00 | 6.4 | 5 | 5.6
| 2014-02-20 08:30 | 6.6 | 5 | 5.6
| 2014-02-20 09:00 | 6.9 | 5 | 5.6
| 2014-02-20 09:30 | 7.3 | 5 | 5.6
| 2014-02-20 10:00 | 7.8 | 5 | 5.6
| 2014-02-20 10:30 | 8.6 | 5 | 5.6
| 2014-02-20 11:00 | 9.7 | 5 | 5.6
| 2014-02-20 11:30 | 10.2 | 5 | 5.6
| 2014-02-20 12:00 | 9.8 | 5.6 | 5.6
| 2014-02-20 12:30 | 10.2 | 5.6 | 5.6
| 2014-02-20 13:00 | 10.9 | 5.6 | 5.6
| 2014-02-20 13:30 | 12.6 | 5.6 | 5.6
| 2014-02-20 14:00 | 12.6 | 6.1 | 5.6
| 2014-02-20 14:30 | 13.1 | 6.1 | 5.6
| 2014-02-20 15:00 | 13.1 | 6.1 | 5.6
| 2014-02-20 15:30 | 12.2 | 6.1 | 5.6
| 2014-02-20 16:00 | 12.8 | 6.7 | 5.6
| 2014-02-20 16:30 | 11.6 | 6.7 | 5.6
| 2014-02-20 17:00 | 11.3 | 6.7 | 5.6
| 2014-02-20 17:30 | 10.8 | 7.2 | 5.6
| 2014-02-20 18:00 | 10.4 | 7.2 | 5.6
| 2014-02-20 18:30 | 10 | 7.2 | 5.6
| 2014-02-20 19:00 | 9.9 | 7.2 | 5.6
| 2014-02-20 19:30 | 9.6 | 7.2 | 5.6
| 2014-02-20 20:00 | 9.8 | 7.2 | 5.6
| 2014-02-20 20:30 | 9.9 | 7.2 | 6.1
| 2014-02-20 21:00 | 10 | 7.2 | 6.1
| 2014-02-20 21:30 | 9.8 | 7.2 | 6.1
| 2014-02-20 22:00 | 9.7 | 7.2 | 6.1
| 2014-02-20 22:30 | 9.6 | 7.2 | 6.1
| 2014-02-20 23:00 | 8.9 | 6.7 | 6.1
| 2014-02-20 23:30 | 9.1 | 6.7 | 6.1
| 2014-02-21 | 9.2 | 6.7 | 6.1
| 2014-02-21 00:30 | 9.3 | 6.7 | 6.1
| 2014-02-21 01:00 | 7.9 | 6.7 | 6.1
| 2014-02-21 01:30 | 8.3 | 6.7 | 6.1
| 2014-02-21 02:00 | 8.5 | 6.7 | 6.1
| 2014-02-21 02:30 | 8.1 | 6.7 | 6.1
| 2014-02-21 03:00 | 8.1 | 6.7 | 6.1
| 2014-02-21 03:30 | 8.2 | 6.7 | 6.1
| 2014-02-21 04:00 | 8.2 | 6.7 | 6.1
| 2014-02-21 04:30 | 8.3 | 6.7 | 6.1
| 2014-02-21 05:00 | 8.3 | 6.7 | 6.1
| 2014-02-21 05:30 | 8.4 | 6.7 | 6.1
| 2014-02-21 06:00 | 7.9 | 6.7 | 6.1
| 2014-02-21 06:30 | 7.8 | 6.7 | 6.1
| 2014-02-21 07:00 | 7.3 | 6.7 | 6.1
| 2014-02-21 07:30 | 7.4 | 6.7 | 6.1
| 2014-02-21 08:00 | 7.2 | 6.7 | 6.1
| 2014-02-21 08:30 | 7.7 | 6.7 | 6.1
| 2014-02-21 09:00 | 8.3 | 6.7 | 6.1
| 2014-02-21 09:30 | 8.2 | 6.7 | 6.1
| 2014-02-21 10:00 | 7.7 | 6.7 | 6.1
| 2014-02-21 10:30 | 7.7 | 6.7 | 6.1
| 2014-02-21 11:00 | 8.4 | 6.7 | 6.1
| 2014-02-21 11:30 | 8.8 | 6.7 | 6.1
| 2014-02-21 12:00 | 9.3 | 6.7 | 6.1
| 2014-02-21 12:30 | 9.6 | 6.7 | 6.1
| 2014-02-21 13:00 | 9.8 | 6.7 | 6.1
| 2014-02-21 13:30 | 10.1 | 6.7 | 6.1
| 2014-02-21 14:00 | 11.1 | 6.7 | 6.1
| 2014-02-21 14:30 | 10.1 | 6.7 | 6.1
| 2014-02-21 15:00 | 11.2 | 6.7 | 6.1
| 2014-02-21 15:30 | 11 | 7.2 | 6.1
| 2014-02-21 16:00 | 10.2 | 7.2 | 6.1
| 2014-02-21 16:30 | 9.9 | 7.2 | 6.1
| 2014-02-21 17:00 | 9.2 | 7.2 | 6.1
| 2014-02-21 17:30 | 8.7 | 7.2 | 6.1
| 2014-02-21 18:00 | 7.7 | 7.2 | 6.1
| 2014-02-21 18:30 | 6.7 | 7.2 | 6.1
| 2014-02-21 19:00 | 6.1 | 7.2 | 6.1
| 2014-02-21 19:30 | 6.3 | 7.2 | 6.1
| 2014-02-21 20:00 | 5.7 | 7.2 | 6.1
| 2014-02-21 20:30 | 5.2 | 7.2 | 6.1
| 2014-02-21 21:00 | 5.3 | 7.2 | 6.1
| 2014-02-21 21:30 | 5.4 | 6.7 | 6.1
| 2014-02-21 22:00 | 5.2 | 6.7 | 6.1
| 2014-02-21 22:30 | 4.9 | 6.7 | 6.1
| 2014-02-21 23:00 | 4.1 | 6.7 | 6.1
| 2014-02-21 23:30 | 4.5 | 6.7 | 6.1
| 2014-02-22 | 4.4 | 6.7 | 6.1
| 2014-02-22 00:30 | 3.9 | 6.7 | 6.1
| 2014-02-22 01:00 | 3.7 | 6.1 | 6.1
| 2014-02-22 01:30 | 3.2 | 6.1 | 6.1
| 2014-02-22 02:00 | 2.4 | 6.1 | 6.1
| 2014-02-22 02:30 | 1.9 | 6.1 | 6.1
| 2014-02-22 03:00 | 1.6 | 6.1 | 6.1
| 2014-02-22 03:30 | 2 | 6.1 | 6.1
| 2014-02-22 04:00 | 2.5 | 5.6 | 6.1
| 2014-02-22 04:30 | 3.4 | 5.6 | 6.1
| 2014-02-22 05:00 | 3.7 | 5.6 | 6.1
| 2014-02-22 05:30 | 3.4 | 5.6 | 6.1
| 2014-02-22 06:00 | 3.4 | 5.6 | 6.1
| 2014-02-22 06:30 | 3.3 | 5 | 6.1
| 2014-02-22 07:00 | 3 | 5 | 6.1
| 2014-02-22 07:30 | 2.8 | 5 | 6.1
| 2014-02-22 08:00 | 3.4 | 5 | 6.1
| 2014-02-22 08:30 | 3.5 | 5 | 6.1
| 2014-02-22 09:00 | 4.6 | 5 | 6.1
| 2014-02-22 09:30 | 4.9 | 5 | 6.1
| 2014-02-22 10:00 | 5 | 5 | 6.1
| 2014-02-22 10:30 | 6.1 | 5 | 6.1
| 2014-02-22 11:00 | 7.5 | 5 | 6.1
| 2014-02-22 11:30 | 7.6 | 5 | 6.1
| 2014-02-22 12:00 | 7.6 | 5 | 6.1
| 2014-02-22 12:30 | 9.3 | 5 | 6.1
| 2014-02-22 13:00 | 9 | 5 | 6.1
| 2014-02-22 13:30 | 8.6 | 5 | 6.1
| 2014-02-22 14:00 | 8.6 | 5.6 | 6.1
| 2014-02-22 14:30 | 8.7 | 5.6 | 6.1
| 2014-02-22 15:00 | 7.9 | 5.6 | 6.1
| 2014-02-22 15:30 | 6.9 | 5.6 | 6.1
| 2014-02-22 16:00 | 6.8 | 6.1 | 6.1
| 2014-02-22 16:30 | 6.4 | 6.1 | 6.1
| 2014-02-22 17:00 | 6.2 | 6.1 | 6.1
| 2014-02-22 17:30 | 6.1 | 6.1 | 6.1
| 2014-02-22 18:00 | 5.7 | 6.1 | 6.1
| 2014-02-22 18:30 | 5.4 | 6.1 | 6.1
| 2014-02-22 19:00 | 5.2 | 6.1 | 6.1
| 2014-02-22 19:30 | 4.9 | 6.1 | 6.1
| 2014-02-22 20:00 | 4.8 | 6.1 | 6.1
| 2014-02-22 20:30 | 4.7 | 6.1 | 6.1
| 2014-02-22 21:00 | 4.8 | 6.1 | 6.1
| 2014-02-22 21:30 | 4.2 | 6.1 | 6.1
| 2014-02-22 22:00 | 3.5 | 6.1 | 6.1
| 2014-02-22 22:30 | 3.6 | 6.1 | 6.1
| 2014-02-22 23:00 | 4.2 | 6.1 | 6.1
| 2014-02-22 23:30 | 4.6 | 6.1 | 6.1
| 2014-02-23 | 4.6 | 5.6 | 6.1
| 2014-02-23 00:30 | 4.5 | 5.6 | 6.1
| 2014-02-23 01:00 | 4.3 | 5.6 | 6.1
| 2014-02-23 01:30 | 4.4 | 5.6 | 6.1
| 2014-02-23 02:00 | 4.5 | 5.6 | 6.1
| 2014-02-23 02:30 | 4.6 | 5.6 | 6.1
| 2014-02-23 03:00 | 4.5 | 5.6 | 6.1
| 2014-02-23 03:30 | 4.5 | 5.6 | 6.1
| 2014-02-23 04:00 | 4.4 | 5.6 | 6.1
| 2014-02-23 04:30 | 4.3 | 5.6 | 6.1
| 2014-02-23 05:00 | 4.3 | 5.6 | 6.1
| 2014-02-23 05:30 | 4.4 | 5.6 | 6.1
| 2014-02-23 06:00 | 4.4 | 5.6 | 6.1
| 2014-02-23 06:30 | 4.4 | 5.6 | 6.1
| 2014-02-23 07:00 | 4.3 | 5.6 | 6.1
| 2014-02-23 07:30 | 4.4 | 5.6 | 6.1
| 2014-02-23 08:00 | 4.5 | 5.6 | 6.1
| 2014-02-23 08:30 | 4.8 | 5.6 | 6.1
| 2014-02-23 09:00 | 5.4 | 5.6 | 6.1
| 2014-02-23 09:30 | 6.2 | 5.6 | 6.1
| 2014-02-23 10:00 | 7 | 5.6 | 6.1
| 2014-02-23 10:30 | 8.3 | 5.6 | 6.1
| 2014-02-23 11:00 | 9.1 | 5.6 | 6.1
| 2014-02-23 11:30 | 9.2 | 5.6 | 6.1
| 2014-02-23 12:00 | 10.2 | 5.6 | 6.1
| 2014-02-23 12:30 | 10.1 | 5.6 | 6.1
| 2014-02-23 13:00 | 9.8 | 5.6 | 6.1
| 2014-02-23 13:30 | 9.7 | 6.1 | 6.1
| 2014-02-23 14:00 | 10 | 6.1 | 6.1
| 2014-02-23 14:30 | 11.2 | 6.1 | 6.1
| 2014-02-23 15:00 | 10.2 | 6.1 | 6.1
| 2014-02-23 15:30 | 10.1 | 6.7 | 6.1
| 2014-02-23 16:00 | 10.2 | 6.7 | 6.1
| 2014-02-23 16:30 | 9.9 | 6.7 | 6.1
| 2014-02-23 17:00 | 9.3 | 6.7 | 6.1
| 2014-02-23 17:30 | 8.7 | 7.2 | 6.1
| 2014-02-23 18:00 | 8.1 | 7.2 | 6.1
| 2014-02-23 18:30 | 7.3 | 7.2 | 6.1
| 2014-02-23 19:00 | 6.3 | 7.2 | 6.1
| 2014-02-23 19:30 | 5.3 | 7.2 | 6.1
| 2014-02-23 20:00 | 4.7 | 7.2 | 6.1
| 2014-02-23 20:30 | 4 | 6.7 | 6.1
| 2014-02-23 21:00 | 3.1 | 6.7 | 6.1
| 2014-02-23 21:30 | 2.6 | 6.7 | 6.1
| 2014-02-23 22:00 | 2.5 | 6.7 | 6.1
| 2014-02-23 22:30 | 2.4 | 6.7 | 6.1
| 2014-02-23 23:00 | 2.1 | 6.7 | 6.1
| 2014-02-23 23:30 | 1.8 | 6.1 | 6.1
| 2014-02-24 | 1.9 | 6.1 | 6.1
| 2014-02-24 00:30 | 1.9 | 6.1 | 6.1
| 2014-02-24 01:00 | 1.6 | 6.1 | 6.1
| 2014-02-24 01:30 | 1.2 | 5.6 | 6.1
| 2014-02-24 02:00 | 0.8 | 5.6 | 6.1
| 2014-02-24 02:30 | 1.2 | 5.6 | 6.1
| 2014-02-24 03:00 | 1.3 | 5.6 | 6.1
| 2014-02-24 03:30 | 0.9 | 5.6 | 6.1
| 2014-02-24 04:00 | 0.6 | 5 | 6.1
| 2014-02-24 04:30 | 0 | 5 | 6.1
| 2014-02-24 05:00 | -0.9 | 5 | 6.1
| 2014-02-24 05:30 | -1.1 | 5 | 6.1
| 2014-02-24 06:00 | -1.4 | 5 | 6.1
| 2014-02-24 06:30 | -1.6 | 4.4 | 6.1
| 2014-02-24 07:00 | -2.4 | 4.4 | 6.1
| 2014-02-24 07:30 | -2.4 | 4.4 | 6.1
| 2014-02-24 08:00 | -2.2 | 4.4 | 6.1
| 2014-02-24 08:30 | -0.7 | 4.4 | 6.1
| 2014-02-24 09:00 | 0.8 | 4.4 | 6.1
| 2014-02-24 09:30 | 2.4 | 3.9 | 6.1
| 2014-02-24 10:00 | 5 | 3.9 | 6.1
| 2014-02-24 10:30 | 6.5 | 3.9 | 6.1
| 2014-02-24 11:00 | 7.8 | 3.9 | 6.1
| 2014-02-24 11:30 | 9.1 | 3.9 | 6.1
| 2014-02-24 12:00 | 10.1 | 3.9 | 6.1
| 2014-02-24 12:30 | 10.7 | 3.9 | 6.1
| 2014-02-24 13:00 | 11 | 4.4 | 6.1
| 2014-02-24 13:30 | 11.2 | 4.4 | 6.1
| 2014-02-24 14:00 | 12.8 | 4.4 | 6.1
| 2014-02-24 14:30 | 13.8 | 5 | 6.1
| 2014-02-24 15:00 | 14.3 | 5 | 6.1
| 2014-02-24 15:30 | 14.9 | 5.6 | 6.1
| 2014-02-24 16:00 | 14.8 | 5.6 | 6.1
| 2014-02-24 16:30 | 14.4 | 6.1 | 6.1
| 2014-02-24 17:00 | 12.8 | 6.1 | 6.1
| 2014-02-24 17:30 | 11.4 | 6.1 | 6.1
| 2014-02-24 18:00 | 9.7 | 6.7 | 6.1
| 2014-02-24 18:30 | 9.1 | 6.7 | 6.1
| 2014-02-24 19:00 | 7.9 | 6.7 | 6.1
| 2014-02-24 19:30 | 7 | 6.7 | 6.1
| 2014-02-24 20:00 | 6.3 | 6.7 | 6.1
| 2014-02-24 20:30 | 4.9 | 6.7 | 6.1
| 2014-02-24 21:00 | 4.2 | 6.7 | 6.1
| 2014-02-24 21:30 | 4 | 6.7 | 6.1
| 2014-02-24 22:00 | 3.5 | 6.1 | 6.1
| 2014-02-24 22:30 | 2.8 | 6.1 | 6.1
| 2014-02-24 23:00 | 2.1 | 6.1 | 6.1
| 2014-02-24 23:30 | 2 | 6.1 | 6.1
| 2014-02-25 | 1.5 | 6.1 | 6.1
| 2014-02-25 00:30 | 1.1 | 5.6 | 6.1
| 2014-02-25 01:00 | 0.8 | 5.6 | 6.1
| 2014-02-25 01:30 | 0.8 | 5.6 | 6.1
| 2014-02-25 02:00 | 0.5 | 5.6 | 6.1
| 2014-02-25 02:30 | 0.8 | 5.6 | 6.1
| 2014-02-25 03:00 | 0.4 | 5 | 6.1
| 2014-02-25 03:30 | 0.6 | 5 | 6.1
| 2014-02-25 04:00 | 0.2 | 5 | 6.1
| 2014-02-25 04:30 | 0.6 | 5 | 6.1
| 2014-02-25 05:00 | 0.7 | 5 | 6.1
| 2014-02-25 05:30 | 0.9 | 5 | 6.1
| 2014-02-25 06:00 | 1.4 | 4.4 | 6.1
| 2014-02-25 06:30 | 2.5 | 4.4 | 6.1
| 2014-02-25 07:00 | 3.9 | 4.4 | 6.1
| 2014-02-25 07:30 | 5.6 | 4.4 | 6.1
| 2014-02-25 08:00 | 7.1 | 4.4 | 6.1
| 2014-02-25 08:30 | 7.7 | 4.4 | 6.1
| 2014-02-25 09:00 | 7.9 | 4.4 | 6.1
| 2014-02-25 09:30 | 8.7 | 4.4 | 6.1
| 2014-02-25 10:00 | 9.8 | 4.4 | 6.1
| 2014-02-25 10:30 | 10 | 4.4 | 6.1
| 2014-02-25 11:00 | 10.8 | 4.4 | 6.1
| 2014-02-25 11:30 | 11.1 | 4.4 | 6.1
| 2014-02-25 12:00 | 12 | 4.4 | 6.1
| 2014-02-25 12:30 | 12.9 | 4.4 | 6.1
| 2014-02-25 13:00 | 13.4 | 4.4 | 6.1
| 2014-02-25 13:30 | 13.8 | 5 | 6.1
| 2014-02-25 14:00 | 13.1 | 5 | 6.1
| 2014-02-25 14:30 | 12.6 | 5 | 6.1
| 2014-02-25 15:00 | 12 | 5.6 | 6.1
| 2014-02-25 15:30 | 11.6 | 5.6 | 6.1
| 2014-02-25 16:00 | 11.6 | 6.1 | 6.1
| 2014-02-25 16:30 | 11.5 | 6.1 | 6.1
| 2014-02-25 17:00 | 11.2 | 6.1 | 6.1
| 2014-02-25 17:30 | 10.8 | 6.1 | 6.1
| 2014-02-25 18:00 | 10.3 | 6.1 | 6.1
| 2014-02-25 18:30 | 9.9 | 6.1 | 6.1
| 2014-02-25 19:00 | 9.3 | 6.1 | 6.1
| 2014-02-25 19:30 | 9.1 | 6.1 | 6.1
| 2014-02-25 20:00 | 9.4 | 6.7 | 6.1
| 2014-02-25 20:30 | 9.6 | 6.7 | 6.1
| 2014-02-25 21:00 | 9.8 | 6.7 | 6.1
| 2014-02-25 21:30 | 9.6 | 6.7 | 6.1
| 2014-02-25 22:00 | 9.3 | 6.1 | 6.1
| 2014-02-25 22:30 | 9.3 | 6.1 | 6.1
| 2014-02-25 23:00 | 9.1 | 6.1 | 6.1
| 2014-02-25 23:30 | 8.3 | 6.1 | 6.1
| 2014-02-26 | 8.2 | 6.1 | 6.1
| 2014-02-26 00:30 | 7.7 | 6.1 | 6.1
| 2014-02-26 01:00 | 7.6 | 6.1 | 6.1
| 2014-02-26 01:30 | 7.7 | 6.1 | 6.1
| 2014-02-26 02:00 | 7.2 | 6.1 | 6.1
| 2014-02-26 02:30 | 6.9 | 6.1 | 6.1
| 2014-02-26 03:00 | 6.4 | 6.1 | 6.1
| 2014-02-26 03:30 | 6.1 | 6.1 | 6.1
| 2014-02-26 04:00 | 5.7 | 6.1 | 6.1
| 2014-02-26 04:30 | 5.7 | 6.1 | 6.1
| 2014-02-26 05:00 | 5.7 | 6.1 | 6.1
| 2014-02-26 05:30 | 5.4 | 6.1 | 6.1
| 2014-02-26 06:00 | 6.3 | 6.1 | 6.1
| 2014-02-26 06:30 | 6.4 | 6.1 | 6.1
| 2014-02-26 07:00 | 6.3 | 5.6 | 6.1
| 2014-02-26 07:30 | 6.6 | 5.6 | 6.1
| 2014-02-26 08:00 | 6.8 | 5.6 | 6.1
| 2014-02-26 08:30 | 6.8 | 5.6 | 6.1
| 2014-02-26 09:00 | 7.2 | 5.6 | 6.1
| 2014-02-26 09:30 | 7.7 | 5.6 | 6.1
| 2014-02-26 10:00 | 8.3 | 5.6 | 6.1
| 2014-02-26 10:30 | 9.4 | 5.6 | 6.1
| 2014-02-26 11:00 | 10 | 5.6 | 6.1
| 2014-02-26 11:30 | 10.8 | 5.6 | 6.1
| 2014-02-26 12:00 | 11.1 | 6.1 | 6.1
| 2014-02-26 12:30 | 10.7 | 6.1 | 6.1
| 2014-02-26 13:00 | 10.6 | 6.1 | 6.1
| 2014-02-26 13:30 | 10.9 | 6.1 | 6.1
| 2014-02-26 14:00 | 10.7 | 6.1 | 6.1
| 2014-02-26 14:30 | 10.7 | 6.7 | 6.1
| 2014-02-26 15:00 | 10.6 | 6.7 | 6.1
| 2014-02-26 15:30 | 10.2 | 6.7 | 6.1
| 2014-02-26 16:00 | 9.9 | 6.7 | 6.1
| 2014-02-26 16:30 | 10 | 6.7 | 6.1
| 2014-02-26 17:00 | 9.6 | 6.7 | 6.1
| 2014-02-26 17:30 | 8.6 | 7.2 | 6.1
| 2014-02-26 18:00 | 7.8 | 7.2 | 6.1
| 2014-02-26 18:30 | 7.5 | 7.2 | 6.1
| 2014-02-26 19:00 | 7.4 | 7.2 | 6.1
| 2014-02-26 19:30 | 7.5 | 7.2 | 6.1
| 2014-02-26 20:00 | 7.4 | 7.2 | 6.1
| 2014-02-26 20:30 | 7.3 | 7.2 | 6.1
| 2014-02-26 21:00 | 7.1 | 7.2 | 6.1
| 2014-02-26 21:30 | 7 | 7.2 | 6.1
| 2014-02-26 22:00 | 6.9 | 7.2 | 6.1
| 2014-02-26 22:30 | 6.8 | 7.2 | 6.1
| 2014-02-26 23:00 | 6.4 | 6.7 | 6.1
| 2014-02-26 23:30 | 6.1 | 6.7 | 6.1
| 2014-02-27 | 5.8 | 6.7 | 6.1
| 2014-02-27 00:30 | 5.8 | 6.7 | 6.1
| 2014-02-27 01:00 | 5.5 | 6.7 | 6.1
| 2014-02-27 01:30 | 5.2 | 6.7 | 6.1
| 2014-02-27 02:00 | 4.9 | 6.7 | 6.1
| 2014-02-27 02:30 | 4.6 | 6.7 | 6.1
| 2014-02-27 03:00 | 4.4 | 6.7 | 6.1
| 2014-02-27 03:30 | 5.2 | 6.7 | 6.1
| 2014-02-27 04:00 | 5.5 | 6.7 | 6.1
| 2014-02-27 04:30 | 5.4 | 6.7 | 6.1
| 2014-02-27 05:00 | 5.3 | 6.1 | 6.1
| 2014-02-27 05:30 | 4.8 | 6.1 | 6.1
| 2014-02-27 06:00 | 4.1 | 6.1 | 6.1
| 2014-02-27 06:30 | 3.8 | 6.1 | 6.1
| 2014-02-27 07:00 | 4.7 | 6.1 | 6.1
| 2014-02-27 07:30 | 5.1 | 6.1 | 6.1
| 2014-02-27 08:00 | 5.2 | 6.1 | 6.1
| 2014-02-27 08:30 | 5.3 | 6.1 | 6.1
| 2014-02-27 09:00 | 5.4 | 6.1 | 6.1
| 2014-02-27 09:30 | 5.5 | 6.1 | 6.1
| 2014-02-27 10:00 | 6.6 | 6.1 | 6.1
| 2014-02-27 10:30 | 6.9 | 6.1 | 6.1
| 2014-02-27 11:00 | 7.2 | 6.1 | 6.1
| 2014-02-27 11:30 | 8.5 | 6.1 | 6.1
| 2014-02-27 12:00 | 8.8 | 6.1 | 6.1
| 2014-02-27 12:30 | 9.4 | 6.1 | 6.1
| 2014-02-27 13:00 | 9.9 | 6.1 | 6.1
| 2014-02-27 13:30 | 9.4 | 6.1 | 6.1
| 2014-02-27 14:00 | 9.4 | 6.7 | 6.1
| 2014-02-27 14:30 | 9.2 | 6.7 | 6.1
| 2014-02-27 15:00 | 9.6 | 6.7 | 6.1
| 2014-02-27 15:30 | 9.7 | 7.2 | 6.1
| 2014-02-27 16:00 | 10.5 | 7.2 | 6.7
| 2014-02-27 16:30 | 8.9 | 7.2 | 6.7
| 2014-02-27 17:00 | 8.6 | 7.2 | 6.7
| 2014-02-27 17:30 | 8.1 | 7.2 | 6.7
| 2014-02-27 18:00 | 7.6 | 7.2 | 6.7
| 2014-02-27 18:30 | 7.2 | 7.2 | 6.7
| 2014-02-27 19:00 | 7.1 | 7.2 | 6.7
| 2014-02-27 19:30 | 7 | 7.2 | 6.7
| 2014-02-27 20:00 | 7.4 | 7.2 | 6.7
| 2014-02-27 20:30 | 6.9 | 7.2 | 6.7
| 2014-02-27 21:00 | 5.4 | 7.2 | 6.7
| 2014-02-27 21:30 | 5.1 | 7.2 | 6.7
| 2014-02-27 22:00 | 4.9 | 7.2 | 6.7
| 2014-02-27 22:30 | 4.8 | 7.2 | 6.7
| 2014-02-27 23:00 | 4.7 | 7.2 | 6.7
| 2014-02-27 23:30 | 4.6 | 6.7 | 6.7
| 2014-02-28 | 4.6 | 6.7 | 6.7
| 2014-02-28 00:30 | 4.6 | 6.7 | 6.7
| 2014-02-28 01:00 | 4.4 | 6.7 | 6.7
| 2014-02-28 01:30 | 4.2 | 6.7 | 6.7
| 2014-02-28 02:00 | 4.2 | 6.7 | 6.7
| 2014-02-28 02:30 | 4 | 6.7 | 6.7
| 2014-02-28 03:00 | 4.1 | 6.7 | 6.7
| 2014-02-28 03:30 | 4.2 | 6.7 | 6.7
| 2014-02-28 04:00 | 4.2 | 6.7 | 6.7
| 2014-02-28 04:30 | 4.2 | 6.1 | 6.7
| 2014-02-28 05:00 | 4.2 | 6.1 | 6.7
| 2014-02-28 05:30 | 3.3 | 6.1 | 6.7
| 2014-02-28 06:00 | 3.7 | 6.1 | 6.7
| 2014-02-28 06:30 | 4.2 | 6.1 | 6.7
| 2014-02-28 07:00 | 3.9 | 6.1 | 6.7
| 2014-02-28 07:30 | 4.3 | 6.1 | 6.7
| 2014-02-28 08:00 | 4.6 | 6.1 | 6.7
| 2014-02-28 08:30 | 4.8 | 6.1 | 6.7
| 2014-02-28 09:00 | 4.9 | 6.1 | 6.7
| 2014-02-28 09:30 | 5.9 | 6.1 | 6.7
| 2014-02-28 10:00 | 6.1 | 6.1 | 6.7
| 2014-02-28 10:30 | 6.4 | 6.1 | 6.7
| 2014-02-28 11:00 | 6.6 | 6.1 | 6.7
| 2014-02-28 11:30 | 6.4 | 6.1 | 6.7
| 2014-02-28 12:00 | 7.7 | 6.1 | 6.7
| 2014-02-28 12:30 | 8.6 | 6.1 | 6.7
| 2014-02-28 13:00 | 8.4 | 6.1 | 6.7
| 2014-02-28 13:30 | 9.3 | 6.1 | 6.7
| 2014-02-28 14:00 | 10.4 | 6.1 | 6.7
| 2014-02-28 14:30 | 10.6 | 6.7 | 6.7
| 2014-02-28 15:00 | 11.2 | 6.7 | 6.7
| 2014-02-28 15:30 | 10.4 | 7.2 | 6.7
| 2014-02-28 16:00 | 10.2 | 7.2 | 6.7
| 2014-02-28 16:30 | 10.1 | 7.2 | 6.7
| 2014-02-28 17:00 | 10.2 | 7.8 | 6.7
| 2014-02-28 17:30 | 9.3 | 7.8 | 6.7
| 2014-02-28 18:00 | 8.9 | 7.8 | 6.7
| 2014-02-28 18:30 | 8.6 | 7.8 | 6.7
| 2014-02-28 19:00 | 8.4 | 7.8 | 6.7
| 2014-02-28 19:30 | 8.4 | 7.8 | 6.7
| 2014-02-28 20:00 | 8.4 | 7.8 | 6.7
| 2014-02-28 20:30 | 8 | 7.8 | 6.7
| 2014-02-28 21:00 | 7.6 | 7.8 | 6.7
| 2014-02-28 21:30 | 7.2 | 7.8 | 6.7
| 2014-02-28 22:00 | 6.9 | 7.8 | 6.7
| 2014-02-28 22:30 | 7.1 | 7.8 | 6.7
| 2014-02-28 23:00 | 6.9 | 7.8 | 6.7
| 2014-02-28 23:30 | 7.1 | 7.2 | 6.7
| 2014-03-01 | 6.7 | 7.2 | 6.7
| 2014-03-01 00:30 | 6.2 | 7.2 | 6.7
| 2014-03-01 01:00 | 5.4 | 7.2 | 6.7
| 2014-03-01 01:30 | 4.1 | 7.2 | 6.7
| 2014-03-01 02:00 | 3.8 | 7.2 | 6.7
| 2014-03-01 02:30 | 3.6 | 7.2 | 6.7
| 2014-03-01 03:00 | 3.3 | 7.2 | 6.7
| 2014-03-01 03:30 | 2.9 | 6.7 | 6.7
| 2014-03-01 04:00 | 2.3 | 6.7 | 6.7
| 2014-03-01 04:30 | 2.6 | 6.7 | 6.7
| 2014-03-01 05:00 | 2.8 | 6.7 | 6.7
| 2014-03-01 05:30 | 2.4 | 6.7 | 6.7
| 2014-03-01 06:00 | 2.3 | 6.7 | 6.7
| 2014-03-01 06:30 | 2.5 | 6.1 | 6.7
| 2014-03-01 07:00 | 2.5 | 6.1 | 6.7
| 2014-03-01 07:30 | 2.6 | 6.1 | 6.7
| 2014-03-01 08:00 | 3.4 | 6.1 | 6.7
| 2014-03-01 08:30 | 4.3 | 6.1 | 6.7
| 2014-03-01 09:00 | 4.6 | 6.1 | 6.7
| 2014-03-01 09:30 | 5.4 | 6.1 | 6.7
| 2014-03-01 10:00 | 6.5 | 6.1 | 6.7
| 2014-03-01 10:30 | 6.9 | 6.1 | 6.7
| 2014-03-01 11:00 | 7.6 | 6.1 | 6.7
| 2014-03-01 11:30 | 7.5 | 6.1 | 6.7
| 2014-03-01 12:00 | 7.7 | 6.1 | 6.7
| 2014-03-01 12:30 | 7.9 | 6.1 | 6.7
| 2014-03-01 13:00 | 7.9 | 6.7 | 6.7
| 2014-03-01 13:30 | 8.1 | 6.7 | 6.7
| 2014-03-01 14:00 | 8.3 | 6.7 | 6.7
| 2014-03-01 14:30 | 8.4 | 6.7 | 6.7
| 2014-03-01 15:00 | 8.4 | 6.7 | 6.7
| 2014-03-01 15:30 | 8.6 | 7.2 | 6.7
| 2014-03-01 16:00 | 8.6 | 7.2 | 6.7
| 2014-03-01 16:30 | 8.5 | 7.2 | 6.7
| 2014-03-01 17:00 | 8.2 | 7.2 | 6.7
| 2014-03-01 17:30 | 7.8 | 7.2 | 6.7
| 2014-03-01 18:00 | 7.3 | 7.2 | 6.7
| 2014-03-01 18:30 | 6.8 | 7.2 | 6.7
| 2014-03-01 19:00 | 6.4 | 7.2 | 6.7
| 2014-03-01 19:30 | 6.3 | 7.2 | 6.7
| 2014-03-01 20:00 | 6.1 | 7.2 | 6.7
| 2014-03-01 20:30 | 5.9 | 7.2 | 6.7
| 2014-03-01 21:00 | 6 | 7.2 | 6.7
| 2014-03-01 21:30 | 5.8 | 7.2 | 6.7
| 2014-03-01 22:00 | 5.7 | 7.2 | 6.7
| 2014-03-01 22:30 | 5.4 | 7.2 | 6.7
| 2014-03-01 23:00 | 5 | 7.2 | 6.7
| 2014-03-01 23:30 | 4.6 | 7.2 | 6.7
| 2014-03-02 | 4.2 | 6.7 | 6.7
| 2014-03-02 00:30 | 3.3 | 6.7 | 6.7
| 2014-03-02 01:00 | 2.4 | 6.7 | 6.7
| 2014-03-02 01:30 | 1.4 | 6.7 | 6.7
| 2014-03-02 02:00 | 1.1 | 6.7 | 6.7
| 2014-03-02 02:30 | 0.8 | 6.7 | 6.7
| 2014-03-02 03:00 | 1 | 6.7 | 6.7
| 2014-03-02 03:30 | 1.7 | 6.1 | 6.7
| 2014-03-02 04:00 | 1.8 | 6.1 | 6.7
| 2014-03-02 04:30 | 2.1 | 6.1 | 6.7
| 2014-03-02 05:00 | 1.8 | 6.1 | 6.7
| 2014-03-02 05:30 | 1.9 | 6.1 | 6.7
| 2014-03-02 06:00 | 2 | 6.1 | 6.7
| 2014-03-02 06:30 | 1.7 | 6.1 | 6.7
| 2014-03-02 07:00 | 1.6 | 5.6 | 6.7
| 2014-03-02 07:30 | 1.6 | 5.6 | 6.7
| 2014-03-02 08:00 | 1.4 | 5.6 | 6.7
| 2014-03-02 08:30 | 1.2 | 5.6 | 6.7
| 2014-03-02 09:00 | 1.7 | 5.6 | 6.7
| 2014-03-02 09:30 | 2.9 | 5.6 | 6.7
| 2014-03-02 10:00 | 4.2 | 5.6 | 6.7
| 2014-03-02 10:30 | 4.6 | 5.6 | 6.7
| 2014-03-02 11:00 | 6.4 | 5.6 | 6.7
| 2014-03-02 11:30 | 6.7 | 5.6 | 6.7
| 2014-03-02 12:00 | 7 | 5.6 | 6.7
| 2014-03-02 12:30 | 7 | 5.6 | 6.7
| 2014-03-02 13:00 | 7.8 | 5.6 | 6.7
| 2014-03-02 13:30 | 7.8 | 5.6 | 6.7
| 2014-03-02 14:00 | 7.7 | 6.1 | 6.7
| 2014-03-02 14:30 | 8.1 | 6.1 | 6.7
| 2014-03-02 15:00 | 8.8 | 6.1 | 6.7
| 2014-03-02 15:30 | 9.6 | 6.1 | 6.7
| 2014-03-02 16:00 | 9.2 | 6.7 | 6.7
| 2014-03-02 16:30 | 9.3 | 6.7 | 6.7
| 2014-03-02 17:00 | 8.7 | 6.7 | 6.7
| 2014-03-02 17:30 | 7.5 | 7.2 | 6.7
| 2014-03-02 18:00 | 6 | 7.2 | 6.7
| 2014-03-02 18:30 | 5.3 | 7.2 | 6.7
| 2014-03-02 19:00 | 4.2 | 7.2 | 6.7
| 2014-03-02 19:30 | 3.8 | 7.2 | 6.7
| 2014-03-02 20:00 | 3.3 | 7.2 | 6.7
| 2014-03-02 20:30 | 3.2 | 7.2 | 6.7
| 2014-03-02 21:00 | 3.3 | 7.2 | 6.7
| 2014-03-02 21:30 | 3.4 | 6.7 | 6.7
| 2014-03-02 22:00 | 3.2 | 6.7 | 6.7
| 2014-03-02 22:30 | 2.7 | 6.7 | 6.7
| 2014-03-02 23:00 | 2.5 | 6.7 | 6.7
| 2014-03-02 23:30 | 2.8 | 6.7 | 6.7
| 2014-03-03 | 1.9 | 6.1 | 6.7
| 2014-03-03 00:30 | 1.4 | 6.1 | 6.7
| 2014-03-03 01:00 | 0.9 | 6.1 | 6.7
| 2014-03-03 01:30 | 0.6 | 6.1 | 6.7
| 2014-03-03 02:00 | 0.9 | 6.1 | 6.7
| 2014-03-03 02:30 | 1.4 | 5.6 | 6.7
| 2014-03-03 03:00 | 1.8 | 5.6 | 6.7
| 2014-03-03 03:30 | 1 | 5.6 | 6.7
| 2014-03-03 04:00 | 0.8 | 5.6 | 6.7
| 2014-03-03 04:30 | 1.2 | 5.6 | 6.7
| 2014-03-03 05:00 | 1.7 | 5 | 6.7
| 2014-03-03 05:30 | 1.8 | 5 | 6.7
| 2014-03-03 06:00 | 1.3 | 5 | 6.7
| 2014-03-03 06:30 | 0.5 | 5 | 6.7
| 2014-03-03 07:00 | 0.6 | 5 | 6.7
| 2014-03-03 07:30 | 0.1 | 5 | 6.7
| 2014-03-03 08:00 | 0.6 | 4.4 | 6.7
| 2014-03-03 08:30 | 1.2 | 4.4 | 6.7
| 2014-03-03 09:00 | 2.3 | 4.4 | 6.7
| 2014-03-03 09:30 | 3.2 | 4.4 | 6.7
| 2014-03-03 10:00 | 4.1 | 4.4 | 6.7
| 2014-03-03 10:30 | 5.1 | 4.4 | 6.7
| 2014-03-03 11:00 | 6.6 | 4.4 | 6.7
| 2014-03-03 11:30 | 7.3 | 4.4 | 6.7
| 2014-03-03 12:00 | 7.2 | 4.4 | 6.7
| 2014-03-03 12:30 | 7.3 | 4.4 | 6.7
| 2014-03-03 13:00 | 7.4 | 5 | 6.7
| 2014-03-03 13:30 | 7.6 | 5 | 6.7
| 2014-03-03 14:00 | 7.7 | 5 | 6.7
| 2014-03-03 14:30 | 8.8 | 5 | 6.7
| 2014-03-03 15:00 | 9 | 5 | 6.7
| 2014-03-03 15:30 | 8.7 | 5.6 | 6.7
| 2014-03-03 16:00 | 9.3 | 5.6 | 6.7
| 2014-03-03 16:30 | 9.2 | 5.6 | 6.7
| 2014-03-03 17:00 | 8.9 | 5.6 | 6.7
| 2014-03-03 17:30 | 8.3 | 5.6 | 6.7
| 2014-03-03 18:00 | 6.9 | 5.6 | 6.7
| 2014-03-03 18:30 | 6 | 6.1 | 6.7
| 2014-03-03 19:00 | 5.8 | 6.1 | 6.7
| 2014-03-03 19:30 | 5.5 | 6.1 | 6.7
| 2014-03-03 20:00 | 5.1 | 6.1 | 6.7
| 2014-03-03 20:30 | 4.8 | 6.1 | 6.7
| 2014-03-03 21:00 | 4.4 | 6.1 | 6.7
| 2014-03-03 21:30 | 4.1 | 5.6 | 6.7
| 2014-03-03 22:00 | 3.9 | 5.6 | 6.7
| 2014-03-03 22:30 | 3 | 5.6 | 6.7
| 2014-03-03 23:00 | 2.1 | 5.6 | 6.7
| 2014-03-03 23:30 | 1.7 | 5.6 | 6.7
| 2014-03-04 | 1.2 | 5.6 | 6.7
| 2014-03-04 00:30 | 0.8 | 5.6 | 6.7
| 2014-03-04 01:00 | 0.3 | 5 | 6.7
| 2014-03-04 01:30 | -0.3 | 5 | 6.7
| 2014-03-04 02:00 | -0.2 | 5 | 6.7
| 2014-03-04 02:30 | -0.3 | 5 | 6.7
| 2014-03-04 03:00 | -0.5 | 5 | 6.7
| 2014-03-04 03:30 | -0.8 | 5 | 6.7
| 2014-03-04 04:00 | -0.8 | 4.4 | 6.7
| 2014-03-04 04:30 | 0.2 | 4.4 | 6.7
| 2014-03-04 05:00 | 0.5 | 4.4 | 6.7
| 2014-03-04 05:30 | 0.6 | 4.4 | 6.7
| 2014-03-04 06:00 | 0.9 | 4.4 | 6.7
| 2014-03-04 06:30 | 1.2 | 4.4 | 6.7
| 2014-03-04 07:00 | 1.4 | 4.4 | 6.7
| 2014-03-04 07:30 | 1.6 | 4.4 | 6.7
| 2014-03-04 08:00 | 2 | 3.9 | 6.7
| 2014-03-04 08:30 | 2.7 | 3.9 | 6.7
| 2014-03-04 09:00 | 3.8 | 3.9 | 6.7
| 2014-03-04 09:30 | 4.8 | 3.9 | 6.7
| 2014-03-04 10:00 | 6.2 | 3.9 | 6.7
| 2014-03-04 10:30 | 7.7 | 3.9 | 6.7
| 2014-03-04 11:00 | 8.8 | 3.9 | 6.7
| 2014-03-04 11:30 | 9.4 | 3.9 | 6.7
| 2014-03-04 12:00 | 10.6 | 4.4 | 6.7
| 2014-03-04 12:30 | 10.6 | 4.4 | 6.7
| 2014-03-04 13:00 | 10.9 | 4.4 | 6.7
| 2014-03-04 13:30 | 11.6 | 5 | 6.7
| 2014-03-04 14:00 | 12.1 | 5 | 6.7
| 2014-03-04 14:30 | 12.4 | 5.6 | 6.7
| 2014-03-04 15:00 | 12.6 | 5.6 | 6.7
| 2014-03-04 15:30 | 12.6 | 6.1 | 6.7
| 2014-03-04 16:00 | 12.5 | 6.1 | 6.7
| 2014-03-04 16:30 | 12.5 | 6.7 | 6.7
| 2014-03-04 17:00 | 11.8 | 6.7 | 6.7
| 2014-03-04 17:30 | 11 | 6.7 | 6.7
| 2014-03-04 18:00 | 9.9 | 7.2 | 6.7
| 2014-03-04 18:30 | 8.8 | 7.2 | 6.7
| 2014-03-04 19:00 | 7.6 | 7.2 | 6.7
| 2014-03-04 19:30 | 6.9 | 7.2 | 6.7
| 2014-03-04 20:00 | 6.4 | 7.2 | 6.7
| 2014-03-04 20:30 | 5.4 | 7.2 | 6.7
| 2014-03-04 21:00 | 4.8 | 7.2 | 6.7
| 2014-03-04 21:30 | 4.4 | 7.2 | 6.7
| 2014-03-04 22:00 | 4.1 | 7.2 | 6.7
| 2014-03-04 22:30 | 4.3 | 6.7 | 6.7
| 2014-03-04 23:00 | 4.2 | 6.7 | 6.7
| 2014-03-04 23:30 | 3.5 | 6.7 | 6.7
| 2014-03-05 | 3.1 | 6.7 | 6.7
| 2014-03-05 00:30 | 2.4 | 6.7 | 6.7
| 2014-03-05 01:00 | 2.1 | 6.1 | 6.7
| 2014-03-05 01:30 | 1.7 | 6.1 | 6.7
| 2014-03-05 02:00 | 1.7 | 6.1 | 6.7
| 2014-03-05 02:30 | 1.9 | 6.1 | 6.7
| 2014-03-05 03:00 | 2.6 | 6.1 | 6.7
| 2014-03-05 03:30 | 2.9 | 6.1 | 6.7
| 2014-03-05 04:00 | 2.8 | 5.6 | 6.7
| 2014-03-05 04:30 | 2.7 | 5.6 | 6.7
| 2014-03-05 05:00 | 2.7 | 5.6 | 6.7
| 2014-03-05 05:30 | 2.6 | 5.6 | 6.7
| 2014-03-05 06:00 | 2.3 | 5.6 | 6.7
| 2014-03-05 06:30 | 2 | 5.6 | 6.7
| 2014-03-05 07:00 | 1.8 | 5.6 | 6.7
| 2014-03-05 07:30 | 1.7 | 5.6 | 6.7
| 2014-03-05 08:00 | 1.9 | 5 | 6.7
| 2014-03-05 08:30 | 2.8 | 5 | 6.7
| 2014-03-05 09:00 | 3.8 | 5 | 6.7
| 2014-03-05 09:30 | 5 | 5 | 6.7
| 2014-03-05 10:00 | 6.3 | 5 | 6.7
| 2014-03-05 10:30 | 7.4 | 5 | 6.7
| 2014-03-05 11:00 | 8.3 | 5 | 6.7
| 2014-03-05 11:30 | 8.4 | 5 | 6.7
| 2014-03-05 12:00 | 9.8 | 5 | 6.7
| 2014-03-05 12:30 | 10.3 | 5.6 | 6.7
| 2014-03-05 13:00 | 10.8 | 5.6 | 6.7
| 2014-03-05 13:30 | 11.2 | 5.6 | 6.7
| 2014-03-05 14:00 | 11.4 | 6.1 | 6.7
| 2014-03-05 14:30 | 11.7 | 6.1 | 6.7
| 2014-03-05 15:00 | 11.4 | 6.1 | 6.7
| 2014-03-05 15:30 | 11.6 | 6.7 | 6.7
| 2014-03-05 16:00 | 11.9 | 6.7 | 6.7
| 2014-03-05 16:30 | 12 | 7.2 | 6.7
| 2014-03-05 17:00 | 11.6 | 7.2 | 6.7
| 2014-03-05 17:30 | 11 | 7.8 | 6.7
| 2014-03-05 18:00 | 10.7 | 7.8 | 6.7
| 2014-03-05 18:30 | 9.7 | 7.8 | 6.7
| 2014-03-05 19:00 | 8.6 | 7.8 | 6.7
| 2014-03-05 19:30 | 7.3 | 7.8 | 6.7
| 2014-03-05 20:00 | 6.4 | 7.8 | 6.7
| 2014-03-05 20:30 | 5.5 | 7.8 | 6.7
| 2014-03-05 21:00 | 5.1 | 7.8 | 6.7
| 2014-03-05 21:30 | 4.2 | 7.8 | 6.7
| 2014-03-05 22:00 | 3.3 | 7.8 | 6.7
| 2014-03-05 22:30 | 2.8 | 7.8 | 6.7
| 2014-03-05 23:00 | 2.5 | 7.2 | 6.7
| 2014-03-05 23:30 | 1.9 | 7.2 | 6.7
| 2014-03-06 | 0.9 | 7.2 | 6.7
| 2014-03-06 00:30 | 3.4 | 7.2 | 6.7
| 2014-03-06 01:00 | 3.1 | 6.7 | 6.7
| 2014-03-06 01:30 | 2.9 | 6.7 | 6.7
| 2014-03-06 02:00 | 4.4 | 6.7 | 6.7
| 2014-03-06 02:30 | 3.9 | 6.7 | 6.7
| 2014-03-06 03:00 | 3.6 | 6.1 | 6.7
| 2014-03-06 03:30 | 3.6 | 6.1 | 6.7
| 2014-03-06 04:00 | 3.7 | 6.1 | 6.7
| 2014-03-06 04:30 | 3.9 | 6.1 | 6.7
| 2014-03-06 05:00 | 3.6 | 5.6 | 6.7
| 2014-03-06 05:30 | 3.6 | 5.6 | 6.7
| 2014-03-06 06:00 | 3.3 | 5.6 | 6.7
| 2014-03-06 06:30 | 3 | 5.6 | 6.7
| 2014-03-06 07:00 | 2.8 | 5.6 | 6.7
| 2014-03-06 07:30 | 2.8 | 5 | 6.7
| 2014-03-06 08:00 | 3.2 | 5 | 6.7
| 2014-03-06 08:30 | 3.9 | 5 | 6.7
| 2014-03-06 09:00 | 4.9 | 5 | 6.7
| 2014-03-06 09:30 | 5.6 | 5 | 6.7
| 2014-03-06 10:00 | 6.5 | 5 | 6.7
| 2014-03-06 10:30 | 7.9 | 5 | 6.7
| 2014-03-06 11:00 | 8.9 | 5 | 6.7
| 2014-03-06 11:30 | 10 | 5 | 6.7
| 2014-03-06 12:00 | 10.8 | 5 | 6.7
| 2014-03-06 12:30 | 11.8 | 5 | 6.7
| 2014-03-06 13:00 | 12.1 | 5 | 6.7
| 2014-03-06 13:30 | 12.1 | 5.6 | 6.7
| 2014-03-06 14:00 | 11.8 | 5.6 | 6.7
| 2014-03-06 14:30 | 12.3 | 6.1 | 6.7
| 2014-03-06 15:00 | 13.2 | 6.1 | 6.7
| 2014-03-06 15:30 | 13.1 | 6.7 | 6.7
| 2014-03-06 16:00 | 13.7 | 6.7 | 6.7
| 2014-03-06 16:30 | 13.2 | 6.7 | 6.7
| 2014-03-06 17:00 | 12.6 | 7.2 | 6.7
| 2014-03-06 17:30 | 11.8 | 7.2 | 6.7
| 2014-03-06 18:00 | 10.9 | 7.8 | 6.7
| 2014-03-06 18:30 | 9.4 | 7.8 | 6.7
| 2014-03-06 19:00 | 8.2 | 7.8 | 6.7
| 2014-03-06 19:30 | 7.6 | 7.8 | 6.7
| 2014-03-06 20:00 | 7.1 | 7.8 | 6.7
| 2014-03-06 20:30 | 6.3 | 7.8 | 6.7
| 2014-03-06 21:00 | 5.6 | 7.8 | 6.7
| 2014-03-06 21:30 | 5.2 | 7.2 | 6.7
| 2014-03-06 22:00 | 4.9 | 7.2 | 6.7
| 2014-03-06 22:30 | 4.1 | 7.2 | 6.7
| 2014-03-06 23:00 | 3.3 | 7.2 | 6.7
| 2014-03-06 23:30 | 2.5 | 7.2 | 6.7
| 2014-03-07 | 1.8 | 6.7 | 6.7
| 2014-03-07 00:30 | 1.4 | 6.7 | 6.7
| 2014-03-07 01:00 | 1.2 | 6.7 | 6.7
| 2014-03-07 01:30 | 1.7 | 6.7 | 6.7
| 2014-03-07 02:00 | 3.1 | 6.1 | 6.7
| 2014-03-07 02:30 | 0.4 | 6.1 | 6.7
| 2014-03-07 03:00 | 0 | 6.1 | 6.7
| 2014-03-07 03:30 | -0.2 | 6.1 | 6.7
| 2014-03-07 04:00 | -0.8 | 6.1 | 6.7
| 2014-03-07 04:30 | -1.1 | 5.6 | 6.7
| 2014-03-07 05:00 | -1.3 | 5.6 | 6.7
| 2014-03-07 05:30 | -1.9 | 5.6 | 6.7
| 2014-03-07 06:00 | -2 | 5.6 | 6.7
| 2014-03-07 06:30 | -2.2 | 5 | 6.7
| 2014-03-07 07:00 | -2.2 | 5 | 6.7
| 2014-03-07 07:30 | -2.1 | 5 | 6.7
| 2014-03-07 08:00 | -1.7 | 5 | 6.7
| 2014-03-07 08:30 | -0.2 | 5 | 6.7
| 2014-03-07 09:00 | 1.2 | 5 | 6.7
| 2014-03-07 09:30 | 3.2 | 4.4 | 6.7
| 2014-03-07 10:00 | 5.2 | 4.4 | 6.7
| 2014-03-07 10:30 | 7.3 | 4.4 | 6.7
| 2014-03-07 11:00 | 8.7 | 4.4 | 6.7
| 2014-03-07 11:30 | 9.7 | 4.4 | 6.7
| 2014-03-07 12:00 | 10.4 | 4.4 | 6.7
| 2014-03-07 12:30 | 10.9 | 5 | 6.7
| 2014-03-07 13:00 | 11.6 | 5 | 6.7
| 2014-03-07 13:30 | 12.4 | 5 | 6.7
| 2014-03-07 14:00 | 13 | 5.6 | 6.7
| 2014-03-07 14:30 | 13.4 | 5.6 | 6.7
| 2014-03-07 15:00 | 14 | 6.1 | 6.7
| 2014-03-07 15:30 | 14.2 | 6.1 | 6.7
| 2014-03-07 16:00 | 14.9 | 6.7 | 6.7
| 2014-03-07 16:30 | 14.6 | 6.7 | 6.7
| 2014-03-07 17:00 | 13.7 | 7.2 | 6.7
| 2014-03-07 17:30 | 12.7 | 7.2 | 6.7
| 2014-03-07 18:00 | 11.7 | 7.8 | 6.7
| 2014-03-07 18:30 | 10.7 | 7.8 | 6.7
| 2014-03-07 19:00 | 9.6 | 7.8 | 6.7
| 2014-03-07 19:30 | 8.9 | 7.8 | 6.7
| 2014-03-07 20:00 | 8.3 | 7.8 | 6.7
| 2014-03-07 20:30 | 7.6 | 7.8 | 6.7
| 2014-03-07 21:00 | 7.4 | 7.8 | 6.7
| 2014-03-07 21:30 | 6.4 | 7.8 | 6.7
| 2014-03-07 22:00 | 6.2 | 7.8 | 6.7
| 2014-03-07 22:30 | 6.3 | 7.8 | 6.7
| 2014-03-07 23:00 | 5.7 | 7.8 | 6.7
| 2014-03-07 23:30 | 5 | 7.2 | 6.7
| 2014-03-08 | 3.9 | 7.2 | 6.7
| 2014-03-08 00:30 | 2.8 | 7.2 | 6.7
| 2014-03-08 01:00 | 2.7 | 7.2 | 6.7
| 2014-03-08 01:30 | 2.3 | 7.2 | 6.7
| 2014-03-08 02:00 | 1.9 | 6.7 | 6.7
| 2014-03-08 02:30 | 1.9 | 6.7 | 6.7
| 2014-03-08 03:00 | 1 | 6.7 | 6.7
| 2014-03-08 03:30 | 0.6 | 6.7 | 6.7
| 2014-03-08 04:00 | 0.2 | 6.7 | 6.7
| 2014-03-08 04:30 | 0.2 | 6.1 | 6.7
| 2014-03-08 05:00 | -0.2 | 6.1 | 6.7
| 2014-03-08 05:30 | -0.3 | 6.1 | 6.7
| 2014-03-08 06:00 | -0.4 | 6.1 | 6.7
| 2014-03-08 06:30 | -0.4 | 6.1 | 6.7
| 2014-03-08 07:00 | -0.3 | 5.6 | 6.7
| 2014-03-08 07:30 | 1.4 | 5.6 | 6.7
| 2014-03-08 08:00 | 1.9 | 5.6 | 6.7
| 2014-03-08 08:30 | 4.2 | 5.6 | 6.7
| 2014-03-08 09:00 | 5.9 | 5.6 | 6.7
| 2014-03-08 09:30 | 7.6 | 5 | 6.7
| 2014-03-08 10:00 | 9 | 5 | 6.7
| 2014-03-08 10:30 | 10.4 | 5 | 6.7
| 2014-03-08 11:00 | 13.6 | 5 | 6.7
| 2014-03-08 11:30 | 14.8 | 5 | 6.7
| 2014-03-08 12:00 | 15.8 | 5.6 | 6.7
| 2014-03-08 12:30 | 15.9 | 5.6 | 6.7
| 2014-03-08 13:00 | 16.4 | 5.6 | 6.7
| 2014-03-08 13:30 | 16.6 | 6.1 | 6.7
| 2014-03-08 14:00 | 16.4 | 6.1 | 6.7
| 2014-03-08 14:30 | 17.4 | 6.7 | 6.7
| 2014-03-08 15:00 | 17.7 | 6.7 | 6.7
| 2014-03-08 15:30 | 17.7 | 7.2 | 6.7
| 2014-03-08 16:00 | 17.6 | 7.8 | 6.7
| 2014-03-08 16:30 | 17.2 | 7.8 | 6.7
| 2014-03-08 17:00 | 16.7 | 8.3 | 6.7
| 2014-03-08 17:30 | 15.4 | 8.3 | 6.7
| 2014-03-08 18:00 | 14.1 | 8.3 | 6.7
| 2014-03-08 18:30 | 12.5 | 8.9 | 6.7
| 2014-03-08 19:00 | 11.2 | 8.9 | 6.7
| 2014-03-08 19:30 | 10.3 | 8.9 | 6.7
| 2014-03-08 20:00 | 9.6 | 8.9 | 6.7
| 2014-03-08 20:30 | 8.7 | 8.9 | 6.7
| 2014-03-08 21:00 | 8.4 | 8.3 | 6.7
| 2014-03-08 21:30 | 6.5 | 8.3 | 6.7
| 2014-03-08 22:00 | 5.9 | 8.3 | 6.7
| 2014-03-08 22:30 | 5.2 | 8.3 | 6.7
| 2014-03-08 23:00 | 4.1 | 8.3 | 6.7
| 2014-03-08 23:30 | 3.5 | 8.3 | 6.7
| 2014-03-09 | 3.2 | 7.8 | 6.7
| 2014-03-09 00:30 | 2.7 | 7.8 | 6.7
| 2014-03-09 01:00 | 2.8 | 7.8 | 6.7
| 2014-03-09 01:30 | 3.6 | 7.8 | 6.7
| 2014-03-09 02:00 | 4.3 | 7.2 | 6.7
| 2014-03-09 02:30 | 3.4 | 7.2 | 6.7
| 2014-03-09 03:00 | 2.7 | 7.2 | 6.7
| 2014-03-09 03:30 | 2.7 | 6.7 | 6.7
| 2014-03-09 04:00 | 2.5 | 6.7 | 6.7
| 2014-03-09 04:30 | 1.7 | 6.7 | 6.7
| 2014-03-09 05:00 | 0.8 | 6.7 | 6.7
| 2014-03-09 05:30 | 0.5 | 6.7 | 6.7
| 2014-03-09 06:00 | -0.3 | 6.1 | 6.7
| 2014-03-09 06:30 | -0.6 | 6.1 | 6.7
| 2014-03-09 07:00 | -0.7 | 6.1 | 6.7
| 2014-03-09 07:30 | -1.1 | 6.1 | 6.7
| 2014-03-09 08:00 | -0.1 | 5.6 | 6.7
| 2014-03-09 08:30 | 2.1 | 5.6 | 6.7
| 2014-03-09 09:00 | 4.9 | 5.6 | 6.7
| 2014-03-09 09:30 | 8.3 | 5.6 | 6.7
| 2014-03-09 10:00 | 11.1 | 5.6 | 6.7
| 2014-03-09 10:30 | 12.7 | 5.6 | 6.7
| 2014-03-09 11:00 | 13.3 | 5.6 | 6.7
| 2014-03-09 11:30 | 14.1 | 5.6 | 6.7
| 2014-03-09 12:00 | 14.8 | 5.6 | 6.7
| 2014-03-09 12:30 | 15.9 | 5.6 | 6.7
| 2014-03-09 13:00 | 17.3 | 6.1 | 6.7
| 2014-03-09 13:30 | 18.4 | 6.1 | 6.7
| 2014-03-09 14:00 | 19.6 | 6.7 | 6.7
| 2014-03-09 14:30 | 20.3 | 6.7 | 6.7
| 2014-03-09 15:00 | 20.5 | 7.2 | 6.7
| 2014-03-09 15:30 | 21.1 | 7.8 | 6.7
| 2014-03-09 16:00 | 20.7 | 7.8 | 6.7
| 2014-03-09 16:30 | 20.4 | 8.3 | 6.7
| 2014-03-09 17:00 | 19.4 | 8.3 | 6.7
| 2014-03-09 17:30 | 18.2 | 8.9 | 6.7
| 2014-03-09 18:00 | 16.8 | 8.9 | 6.7
| 2014-03-09 18:30 | 14.9 | 8.9 | 6.7
| 2014-03-09 19:00 | 13.5 | 9.4 | 6.7
| 2014-03-09 19:30 | 12.4 | 9.4 | 6.7
| 2014-03-09 20:00 | 11.7 | 9.4 | 6.7
| 2014-03-09 20:30 | 10.8 | 9.4 | 6.7
| 2014-03-09 21:00 | 10.2 | 8.9 | 6.7
| 2014-03-09 21:30 | 8.6 | 8.9 | 6.7
| 2014-03-09 22:00 | 6.6 | 8.9 | 6.7
| 2014-03-09 22:30 | 6.3 | 8.9 | 6.7
| 2014-03-09 23:00 | 6.3 | 8.9 | 6.7
| 2014-03-09 23:30 | 5.6 | 8.3 | 6.7
| 2014-03-10 | 4.6 | 8.3 | 6.7
| 2014-03-10 00:30 | 5.1 | 8.3 | 6.7
| 2014-03-10 01:00 | 5.8 | 8.3 | 6.7
| 2014-03-10 01:30 | 6.7 | 8.3 | 6.7
| 2014-03-10 02:00 | 6.6 | 7.8 | 6.7
| 2014-03-10 02:30 | 6.1 | 7.8 | 6.7
| 2014-03-10 03:00 | 4.8 | 7.8 | 6.7
| 2014-03-10 03:30 | 4.6 | 7.8 | 6.7
| 2014-03-10 04:00 | 4.6 | 7.2 | 6.7
| 2014-03-10 04:30 | 4.7 | 7.2 | 6.7
| 2014-03-10 05:00 | 3.8 | 7.2 | 6.7
| 2014-03-10 05:30 | 2.9 | 7.2 | 6.7
| 2014-03-10 06:00 | 3.5 | 6.7 | 6.7
| 2014-03-10 06:30 | 4.1 | 6.7 | 6.7
| 2014-03-10 07:00 | 4.5 | 6.7 | 6.7
| 2014-03-10 07:30 | 5.3 | 6.7 | 6.7
| 2014-03-10 08:00 | 6.4 | 6.7 | 6.7
| 2014-03-10 08:30 | 7.7 | 6.1 | 6.7
| 2014-03-10 09:00 | 9.3 | 6.1 | 6.7
| 2014-03-10 09:30 | 10.7 | 6.1 | 6.7
| 2014-03-10 10:00 | 11.8 | 6.1 | 6.7
| 2014-03-10 10:30 | 13.1 | 6.1 | 6.7
| 2014-03-10 11:00 | 13.2 | 6.1 | 6.7
| 2014-03-10 11:30 | 13.4 | 6.1 | 6.7
| 2014-03-10 12:00 | 14.2 | 6.1 | 6.7
| 2014-03-10 12:30 | 14.7 | 6.1 | 6.7
| 2014-03-10 13:00 | 15 | 6.7 | 6.7
| 2014-03-10 13:30 | 16.6 | 6.7 | 6.7
| 2014-03-10 14:00 | 16.8 | 7.2 | 6.7
| 2014-03-10 14:30 | 16.9 | 7.2 | 6.7
| 2014-03-10 15:00 | 17.3 | 7.8 | 7.2
| 2014-03-10 15:30 | 17.5 | 8.3 | 7.2
| 2014-03-10 16:00 | 17.9 | 8.3 | 7.2
| 2014-03-10 16:30 | 17.6 | 8.9 | 7.2
| 2014-03-10 17:00 | 17.2 | 8.9 | 7.2
| 2014-03-10 17:30 | 16.6 | 9.4 | 7.2
| 2014-03-10 18:00 | 15.8 | 9.4 | 7.2
| 2014-03-10 18:30 | 13.7 | 9.4 | 7.2
| 2014-03-10 19:00 | 12.1 | 9.4 | 7.2
| 2014-03-10 19:30 | 10.1 | 9.4 | 7.2
| 2014-03-10 20:00 | 8.9 | 9.4 | 7.2
| 2014-03-10 20:30 | 8.4 | 9.4 | 7.2
| 2014-03-10 21:00 | 7.4 | 9.4 | 7.2
| 2014-03-10 21:30 | 7 | 9.4 | 7.2
| 2014-03-10 22:00 | 6.1 | 9.4 | 7.2
| 2014-03-10 22:30 | 5.6 | 9.4 | 7.2
| 2014-03-10 23:00 | 4.3 | 8.9 | 7.2
| 2014-03-10 23:30 | 4.1 | 8.9 | 7.2
| 2014-03-11 | 4.3 | 8.9 | 7.2
| 2014-03-11 00:30 | 4.2 | 8.9 | 7.2
| 2014-03-11 01:00 | 4 | 8.3 | 7.2
| 2014-03-11 01:30 | 4.9 | 8.3 | 7.2
| 2014-03-11 02:00 | 5.3 | 8.3 | 7.2
| 2014-03-11 02:30 | 6.1 | 8.3 | 7.2
| 2014-03-11 03:00 | 6.6 | 7.8 | 7.2
| 2014-03-11 03:30 | 6.4 | 7.8 | 7.2
| 2014-03-11 04:00 | 5.2 | 7.8 | 7.2
| 2014-03-11 04:30 | 4.8 | 7.8 | 7.2
| 2014-03-11 05:00 | 4.5 | 7.8 | 7.2
| 2014-03-11 05:30 | 4.2 | 7.2 | 7.2
| 2014-03-11 06:00 | 3.9 | 7.2 | 7.2
| 2014-03-11 06:30 | 3.7 | 7.2 | 7.2
| 2014-03-11 07:00 | 3.4 | 7.2 | 7.2
| 2014-03-11 07:30 | 2.9 | 6.7 | 7.2
| 2014-03-11 08:00 | 5.2 | 6.7 | 7.2
| 2014-03-11 08:30 | 6.8 | 6.7 | 7.2
| 2014-03-11 09:00 | 8.3 | 6.7 | 7.2
| 2014-03-11 09:30 | 9.8 | 6.7 | 7.2
| 2014-03-11 10:00 | 11.1 | 6.7 | 7.2
| 2014-03-11 10:30 | 12.6 | 6.7 | 7.2
| 2014-03-11 11:00 | 13.6 | 6.7 | 7.2
| 2014-03-11 11:30 | 15.1 | 6.7 | 7.2
| 2014-03-11 12:00 | 16.5 | 6.7 | 7.2
| 2014-03-11 12:30 | 18.2 | 6.7 | 7.2
| 2014-03-11 13:00 | 18.9 | 6.7 | 7.2
| 2014-03-11 13:30 | 19 | 7.2 | 7.2
| 2014-03-11 14:00 | 20 | 7.8 | 7.2
| 2014-03-11 14:30 | 20.3 | 7.8 | 7.2
| 2014-03-11 15:00 | 20.6 | 8.3 | 7.2
| 2014-03-11 15:30 | 20.6 | 8.3 | 7.2
| 2014-03-11 16:00 | 20.6 | 8.9 | 7.2
| 2014-03-11 16:30 | 20.1 | 8.9 | 7.2
| 2014-03-11 17:00 | 19.4 | 9.4 | 7.2
| 2014-03-11 17:30 | 18.2 | 9.4 | 7.2
| 2014-03-11 18:00 | 17.3 | 10 | 7.2
| 2014-03-11 18:30 | 15.8 | 10 | 7.2
| 2014-03-11 19:00 | 14.4 | 10 | 7.2
| 2014-03-11 19:30 | 14.1 | 10 | 7.2
| 2014-03-11 20:00 | 13.3 | 10 | 7.2
| 2014-03-11 20:30 | 12.7 | 10 | 7.2
| 2014-03-11 21:00 | 12 | 10 | 7.2
| 2014-03-11 21:30 | 11.2 | 10 | 7.2
| 2014-03-11 22:00 | 10.7 | 10 | 7.2
| 2014-03-11 22:30 | 10.2 | 10 | 7.2
| 2014-03-11 23:00 | 9.7 | 9.4 | 7.2
| 2014-03-11 23:30 | 9.2 | 9.4 | 7.2
| 2014-03-12 | 8.6 | 9.4 | 7.2
| 2014-03-12 00:30 | 8.3 | 9.4 | 7.2
| 2014-03-12 01:00 | 7.7 | 9.4 | 7.2
| 2014-03-12 01:30 | 7.4 | 8.9 | 7.2
| 2014-03-12 02:00 | 7.1 | 8.9 | 7.2
| 2014-03-12 02:30 | 6.3 | 8.9 | 7.2
| 2014-03-12 03:00 | 5.7 | 8.9 | 7.2
| 2014-03-12 03:30 | 5.2 | 8.3 | 7.2
| 2014-03-12 04:00 | 4.8 | 8.3 | 7.2
| 2014-03-12 04:30 | 4 | 8.3 | 7.2
| 2014-03-12 05:00 | 3.2 | 8.3 | 7.2
| 2014-03-12 05:30 | 2.3 | 8.3 | 7.2
| 2014-03-12 06:00 | 2.1 | 7.8 | 7.2
| 2014-03-12 06:30 | 1.9 | 7.8 | 7.2
| 2014-03-12 07:00 | 2.4 | 7.8 | 7.2
| 2014-03-12 07:30 | 3.4 | 7.8 | 7.2
| 2014-03-12 08:00 | 4.8 | 7.2 | 7.2
| 2014-03-12 08:30 | 6.6 | 7.2 | 7.2
| 2014-03-12 09:00 | 8.2 | 7.2 | 7.2
| 2014-03-12 09:30 | 10.1 | 7.2 | 7.2
| 2014-03-12 10:00 | 11.7 | 7.2 | 7.2
| 2014-03-12 10:30 | 13.4 | 6.7 | 7.2
| 2014-03-12 11:00 | 14.6 | 6.7 | 7.2
| 2014-03-12 11:30 | 15.7 | 7.2 | 7.2
| 2014-03-12 12:00 | 15.3 | 7.2 | 7.2
| 2014-03-12 12:30 | 16.6 | 7.2 | 7.2
| 2014-03-12 13:00 | 17.2 | 7.2 | 7.2
| 2014-03-12 13:30 | 18.1 | 7.8 | 7.2
| 2014-03-12 14:00 | 19.1 | 7.8 | 7.2
| 2014-03-12 14:30 | 19 | 8.3 | 7.2
| 2014-03-12 15:00 | 19.3 | 8.9 | 7.2
| 2014-03-12 15:30 | 19.8 | 8.9 | 7.2
| 2014-03-12 16:00 | 19.6 | 9.4 | 7.2
| 2014-03-12 16:30 | 19.7 | 9.4 | 7.2
| 2014-03-12 17:00 | 18.8 | 10 | 7.2
| 2014-03-12 17:30 | 17.8 | 10 | 7.2
| 2014-03-12 18:00 | 16.8 | 10.6 | 7.2
| 2014-03-12 18:30 | 14.7 | 10.6 | 7.2
| 2014-03-12 19:00 | 12.8 | 10.6 | 7.2
| 2014-03-12 19:30 | 11.4 | 10.6 | 7.2
| 2014-03-12 20:00 | 10.2 | 10.6 | 7.2
| 2014-03-12 20:30 | 9.7 | 10.6 | 7.2
| 2014-03-12 21:00 | 8.8 | 10.6 | 7.2
| 2014-03-12 21:30 | 7.8 | 10.6 | 7.2
| 2014-03-12 22:00 | 7.1 | 10 | 7.2
| 2014-03-12 22:30 | 7 | 10 | 7.2
| 2014-03-12 23:00 | 6.1 | 10 | 7.2
| 2014-03-12 23:30 | 6.4 | 10 | 7.2
| 2014-03-13 | 6.9 | 9.4 | 7.2
| 2014-03-13 00:30 | 7.1 | 9.4 | 7.2
| 2014-03-13 01:00 | 6.7 | 9.4 | 7.2
| 2014-03-13 01:30 | 5.6 | 9.4 | 7.2
| 2014-03-13 02:00 | 5.2 | 9.4 | 7.2
| 2014-03-13 02:30 | 5.1 | 8.9 | 7.2
| 2014-03-13 03:00 | 4.4 | 8.9 | 7.2
| 2014-03-13 03:30 | 4.2 | 8.9 | 7.2
| 2014-03-13 04:00 | 4.1 | 8.9 | 7.2
| 2014-03-13 04:30 | 3.7 | 8.3 | 7.2
| 2014-03-13 05:00 | 3.1 | 8.3 | 7.2
| 2014-03-13 05:30 | 2.1 | 8.3 | 7.8
| 2014-03-13 06:00 | 1.6 | 8.3 | 7.8
| 2014-03-13 06:30 | 1.3 | 7.8 | 7.8
| 2014-03-13 07:00 | 1.4 | 7.8 | 7.8
| 2014-03-13 07:30 | 1.1 | 7.8 | 7.8
| 2014-03-13 08:00 | 2.1 | 7.8 | 7.8
| 2014-03-13 08:30 | 4.1 | 7.8 | 7.8
| 2014-03-13 09:00 | 6.4 | 7.2 | 7.8
| 2014-03-13 09:30 | 7.9 | 7.2 | 7.8
| 2014-03-13 10:00 | 9 | 7.2 | 7.8
| 2014-03-13 10:30 | 10.4 | 7.2 | 7.8
| 2014-03-13 11:00 | 11.9 | 7.2 | 7.8
| 2014-03-13 11:30 | 13.1 | 7.2 | 7.8
| 2014-03-13 12:00 | 14 | 7.2 | 7.8
| 2014-03-13 12:30 | 15.3 | 7.2 | 7.8
| 2014-03-13 13:00 | 16.3 | 7.8 | 7.8
| 2014-03-13 13:30 | 17.3 | 7.8 | 7.8
| 2014-03-13 14:00 | 18.5 | 8.3 | 7.8
| 2014-03-13 14:30 | 19 | 8.3 | 7.8
| 2014-03-13 15:00 | 19.7 | 8.9 | 7.8
| 2014-03-13 15:30 | 19.7 | 8.9 | 7.8
| 2014-03-13 16:00 | 19.9 | 9.4 | 7.8
| 2014-03-13 16:30 | 19.9 | 9.4 | 7.8
| 2014-03-13 17:00 | 19.4 | 10 | 7.8
| 2014-03-13 17:30 | 17.5 | 10 | 7.8
| 2014-03-13 18:00 | 16.2 | 10.6 | 7.8
| 2014-03-13 18:30 | 14.6 | 10.6 | 7.8
| 2014-03-13 19:00 | 13.4 | 10.6 | 7.8
| 2014-03-13 19:30 | 12.1 | 10.6 | 7.8
| 2014-03-13 20:00 | 10.8 | 10.6 | 7.8
| 2014-03-13 20:30 | 9.6 | 10.6 | 7.8
| 2014-03-13 21:00 | 8.5 | 10.6 | 7.8
| 2014-03-13 21:30 | 7.7 | 10.6 | 7.8
| 2014-03-13 22:00 | 6.7 | 10.6 | 7.8
| 2014-03-13 22:30 | 6.6 | 10.6 | 7.8
| 2014-03-13 23:00 | 6.3 | 10 | 7.8
| 2014-03-13 23:30 | 5.8 | 10 | 7.8
| 2014-03-14 | 5.4 | 10 | 7.8
| 2014-03-14 00:30 | 4.8 | 10 | 7.8
| 2014-03-14 01:00 | 4.2 | 9.4 | 7.8
| 2014-03-14 01:30 | 3.7 | 9.4 | 7.8
| 2014-03-14 02:00 | 3.2 | 9.4 | 7.8
| 2014-03-14 02:30 | 3 | 9.4 | 7.8
| 2014-03-14 03:00 | 2.6 | 8.9 | 7.8
| 2014-03-14 03:30 | 2.1 | 8.9 | 7.8
| 2014-03-14 04:00 | 2.2 | 8.9 | 7.8
| 2014-03-14 04:30 | 1.9 | 8.9 | 7.8
| 2014-03-14 05:00 | 1.2 | 8.3 | 7.8
| 2014-03-14 05:30 | 0.8 | 8.3 | 7.8
| 2014-03-14 06:00 | 0.5 | 8.3 | 7.8
| 2014-03-14 06:30 | 0.4 | 8.3 | 7.8
| 2014-03-14 07:00 | 0.3 | 7.8 | 7.8
| 2014-03-14 07:30 | 1.1 | 7.8 | 7.8
| 2014-03-14 08:00 | 2.9 | 7.8 | 7.8
| 2014-03-14 08:30 | 5.6 | 7.8 | 7.8
| 2014-03-14 09:00 | 7.7 | 7.8 | 7.8
| 2014-03-14 09:30 | 8.9 | 7.2 | 7.8
| 2014-03-14 10:00 | 10.4 | 7.2 | 7.8
| 2014-03-14 10:30 | 11.5 | 7.2 | 7.8
| 2014-03-14 11:00 | 12.3 | 7.2 | 7.8
| 2014-03-14 11:30 | 13.6 | 7.2 | 7.8
| 2014-03-14 12:00 | 15 | 7.2 | 7.8
| 2014-03-14 12:30 | 16.1 | 7.8 | 7.8
| 2014-03-14 13:00 | 16.7 | 7.8 | 7.8
| 2014-03-14 13:30 | 17.2 | 7.8 | 7.8
| 2014-03-14 14:00 | 17.9 | 8.3 | 7.8
| 2014-03-14 14:30 | 17.9 | 8.9 | 7.8
| 2014-03-14 15:00 | 18.4 | 8.9 | 7.8
| 2014-03-14 15:30 | 18.6 | 9.4 | 7.8
| 2014-03-14 16:00 | 18.7 | 9.4 | 7.8
| 2014-03-14 16:30 | 18.5 | 10 | 7.8
| 2014-03-14 17:00 | 18.2 | 10 | 7.8
| 2014-03-14 17:30 | 16.8 | 10.6 | 7.8
| 2014-03-14 18:00 | 15.2 | 10.6 | 7.8
| 2014-03-14 18:30 | 13.7 | 10.6 | 7.8
| 2014-03-14 19:00 | 12.3 | 10.6 | 7.8
| 2014-03-14 19:30 | 11 | 10.6 | 7.8
| 2014-03-14 20:00 | 9.8 | 10.6 | 7.8
| 2014-03-14 20:30 | 9 | 10.6 | 7.8
| 2014-03-14 21:00 | 8.2 | 10.6 | 7.8
| 2014-03-14 21:30 | 7.3 | 10.6 | 7.8
| 2014-03-14 22:00 | 7.4 | 10.6 | 7.8
| 2014-03-14 22:30 | 8.1 | 10.6 | 7.8
| 2014-03-14 23:00 | 7.4 | 10 | 7.8
| 2014-03-14 23:30 | 6.5 | 10 | 7.8
| 2014-03-15 | 5.9 | 10 | 7.8
| 2014-03-15 00:30 | 5.6 | 10 | 7.8
| 2014-03-15 01:00 | 5.1 | 9.4 | 7.8
| 2014-03-15 01:30 | 5.4 | 9.4 | 7.8
| 2014-03-15 02:00 | 5.6 | 9.4 | 7.8
| 2014-03-15 02:30 | 5.4 | 9.4 | 7.8
| 2014-03-15 03:00 | 6.3 | 9.4 | 7.8
| 2014-03-15 03:30 | 6.8 | 8.9 | 7.8
| 2014-03-15 04:00 | 7.5 | 8.9 | 7.8
| 2014-03-15 04:30 | 7.8 | 8.9 | 7.8
| 2014-03-15 05:00 | 7.4 | 8.9 | 7.8
| 2014-03-15 05:30 | 6.5 | 8.9 | 7.8
| 2014-03-15 06:00 | 5.8 | 8.3 | 7.8
| 2014-03-15 06:30 | 5.7 | 8.3 | 7.8
| 2014-03-15 07:00 | 5.5 | 8.3 | 7.8
| 2014-03-15 07:30 | 8.1 | 8.3 | 7.8
| 2014-03-15 08:00 | 9.4 | 8.3 | 7.8
| 2014-03-15 08:30 | 9.4 | 8.3 | 7.8
| 2014-03-15 09:00 | 9.4 | 8.3 | 7.8
| 2014-03-15 09:30 | 9.6 | 8.3 | 7.8
| 2014-03-15 10:00 | 9.6 | 8.3 | 7.8
| 2014-03-15 10:30 | 9.1 | 8.3 | 7.8
| 2014-03-15 11:00 | 9 | 8.3 | 7.8
| 2014-03-15 11:30 | 8.6 | 8.3 | 7.8
| 2014-03-15 12:00 | 8.9 | 8.3 | 7.8
| 2014-03-15 12:30 | 8.6 | 8.3 | 7.8
| 2014-03-15 13:00 | 8.8 | 8.3 | 7.8
| 2014-03-15 13:30 | 9.4 | 8.3 | 7.8
| 2014-03-15 14:00 | 9.8 | 8.3 | 7.8
| 2014-03-15 14:30 | 10.3 | 8.3 | 7.8
| 2014-03-15 15:00 | 10 | 8.3 | 7.8
| 2014-03-15 15:30 | 10.2 | 8.3 | 7.8
| 2014-03-15 16:00 | 9.7 | 8.3 | 7.8
| 2014-03-15 16:30 | 9.4 | 8.3 | 7.8
| 2014-03-15 17:00 | 9.5 | 8.9 | 7.8
| 2014-03-15 17:30 | 9.6 | 8.9 | 7.8
| 2014-03-15 18:00 | 9.1 | 8.9 | 7.8
| 2014-03-15 18:30 | 8.7 | 8.9 | 7.8
| 2014-03-15 19:00 | 8.8 | 8.9 | 7.8
| 2014-03-15 19:30 | 8.9 | 8.9 | 7.8
| 2014-03-15 20:00 | 8.9 | 8.9 | 7.8
| 2014-03-15 20:30 | 8.5 | 8.9 | 7.8
| 2014-03-15 21:00 | 8.7 | 8.9 | 7.8
| 2014-03-15 21:30 | 8.6 | 8.9 | 7.8
| 2014-03-15 22:00 | 8.6 | 8.9 | 7.8
| 2014-03-15 22:30 | 8.5 | 8.3 | 7.8
| 2014-03-15 23:00 | 8.5 | 8.3 | 7.8
| 2014-03-15 23:30 | 8.6 | 8.3 | 7.8
| 2014-03-16 | 8.6 | 8.3 | 7.8
| 2014-03-16 00:30 | 8.6 | 8.3 | 7.8
| 2014-03-16 01:00 | 8.4 | 8.3 | 7.8
| 2014-03-16 01:30 | 8.5 | 8.3 | 7.8
| 2014-03-16 02:00 | 8.8 | 8.3 | 7.8
| 2014-03-16 02:30 | 8.9 | 8.3 | 7.8
| 2014-03-16 03:00 | 9.1 | 8.3 | 7.8
| 2014-03-16 03:30 | 9.6 | 8.3 | 7.8
| 2014-03-16 04:00 | 9.7 | 8.3 | 7.8
| 2014-03-16 04:30 | 9.7 | 8.3 | 7.8
| 2014-03-16 05:00 | 9.6 | 8.3 | 7.8
| 2014-03-16 05:30 | 9.1 | 8.3 | 7.8
| 2014-03-16 06:00 | 9.1 | 8.3 | 7.8
| 2014-03-16 06:30 | 9.2 | 8.3 | 7.8
| 2014-03-16 07:00 | 9.2 | 8.3 | 7.8
| 2014-03-16 07:30 | 9.4 | 8.3 | 7.8
| 2014-03-16 08:00 | 9.6 | 8.3 | 7.8
| 2014-03-16 08:30 | 9.6 | 8.3 | 7.8
| 2014-03-16 09:00 | 9.6 | 8.3 | 7.8
| 2014-03-16 09:30 | 9.7 | 8.3 | 7.8
| 2014-03-16 10:00 | 10 | 8.3 | 7.8
| 2014-03-16 10:30 | 10.5 | 8.3 | 7.8
| 2014-03-16 11:00 | 11.3 | 8.3 | 7.8
| 2014-03-16 11:30 | 11.8 | 8.3 | 7.8
| 2014-03-16 12:00 | 11.9 | 8.3 | 7.8
| 2014-03-16 12:30 | 12.6 | 8.3 | 7.8
| 2014-03-16 13:00 | 13.2 | 8.3 | 7.8
| 2014-03-16 13:30 | 13.8 | 8.3 | 7.8
| 2014-03-16 14:00 | 14.6 | 8.3 | 7.8
| 2014-03-16 14:30 | 15.5 | 8.9 | 7.8
| 2014-03-16 15:00 | 16.6 | 8.9 | 7.8
| 2014-03-16 15:30 | 15.8 | 8.9 | 7.8
| 2014-03-16 16:00 | 15.1 | 8.9 | 7.8
| 2014-03-16 16:30 | 14.7 | 9.4 | 7.8
| 2014-03-16 17:00 | 13.8 | 9.4 | 7.8
| 2014-03-16 17:30 | 13.1 | 9.4 | 7.8
| 2014-03-16 18:00 | 12.4 | 10 | 7.8
| 2014-03-16 18:30 | 11.5 | 10 | 7.8
| 2014-03-16 19:00 | 10.1 | 10 | 7.8
| 2014-03-16 19:30 | 8.8 | 10 | 7.8
| 2014-03-16 20:00 | 8.2 | 10 | 7.8
| 2014-03-16 20:30 | 7.6 | 10 | 7.8
| 2014-03-16 21:00 | 7.3 | 10 | 7.8
| 2014-03-16 21:30 | 7.1 | 10 | 7.8
| 2014-03-16 22:00 | 6.8 | 10 | 7.8
| 2014-03-16 22:30 | 6.6 | 9.4 | 7.8
| 2014-03-16 23:00 | 6.6 | 9.4 | 7.8
| 2014-03-16 23:30 | 8.1 | 9.4 | 7.8
| 2014-03-17 | 8.1 | 9.4 | 7.8
| 2014-03-17 00:30 | 7.5 | 9.4 | 7.8
| 2014-03-17 01:00 | 6.8 | 9.4 | 7.8
| 2014-03-17 01:30 | 7.2 | 8.9 | 7.8
| 2014-03-17 02:00 | 6.6 | 8.9 | 7.8
| 2014-03-17 02:30 | 6.6 | 8.9 | 7.8
| 2014-03-17 03:00 | 6.9 | 8.9 | 7.8
| 2014-03-17 03:30 | 6.8 | 8.9 | 7.8
| 2014-03-17 04:00 | 6.6 | 8.9 | 7.8
| 2014-03-17 04:30 | 5.9 | 8.3 | 7.8
| 2014-03-17 05:00 | 5.1 | 8.3 | 7.8
| 2014-03-17 05:30 | 5.8 | 8.3 | 8.3
| 2014-03-17 06:00 | 6.1 | 8.3 | 8.3
| 2014-03-17 06:30 | 5.9 | 8.3 | 8.3
| 2014-03-17 07:00 | 6.8 | 8.3 | 8.3
| 2014-03-17 07:30 | 7.5 | 7.8 | 8.3
| 2014-03-17 08:00 | 8.1 | 7.8 | 8.3
| 2014-03-17 08:30 | 8.6 | 7.8 | 8.3
| 2014-03-17 09:00 | 9.2 | 7.8 | 8.3
| 2014-03-17 09:30 | 9.8 | 7.8 | 8.3
| 2014-03-17 10:00 | 10.6 | 7.8 | 8.3
| 2014-03-17 10:30 | 11.1 | 7.8 | 8.3
| 2014-03-17 11:00 | 12.4 | 7.8 | 8.3
| 2014-03-17 11:30 | 13.1 | 7.8 | 8.3
| 2014-03-17 12:00 | 13.3 | 7.8 | 8.3
| 2014-03-17 12:30 | 13.4 | 8.3 | 8.3
| 2014-03-17 13:00 | 13.8 | 8.3 | 8.3
| 2014-03-17 13:30 | 14.2 | 8.3 | 8.3
| 2014-03-17 14:00 | 14.9 | 8.3 | 8.3
| 2014-03-17 14:30 | 14.9 | 8.9 | 8.3
| 2014-03-17 15:00 | 15.6 | 8.9 | 8.3
| 2014-03-17 15:30 | 15.5 | 8.9 | 8.3
| 2014-03-17 16:00 | 15.7 | 9.4 | 8.3
| 2014-03-17 16:30 | 15.5 | 9.4 | 8.3
| 2014-03-17 17:00 | 15.7 | 9.4 | 8.3
| 2014-03-17 17:30 | 15.2 | 10 | 8.3
| 2014-03-17 18:00 | 14.7 | 10 | 8.3
| 2014-03-17 18:30 | 13.7 | 10 | 8.3
| 2014-03-17 19:00 | 12.7 | 10 | 8.3
| 2014-03-17 19:30 | 12.4 | 10 | 8.3
| 2014-03-17 20:00 | 11.5 | 10 | 8.3
| 2014-03-17 20:30 | 10.8 | 10 | 8.3
| 2014-03-17 21:00 | 9.9 | 10 | 8.3
| 2014-03-17 21:30 | 9.4 | 10 | 8.3
| 2014-03-17 22:00 | 9.3 | 10 | 8.3
| 2014-03-17 22:30 | 8.8 | 10 | 8.3
| 2014-03-17 23:00 | 8.1 | 10 | 8.3
| 2014-03-17 23:30 | 7.8 | 10 | 8.3
| 2014-03-18 | 7.6 | 10 | 8.3
| 2014-03-18 00:30 | 7.6 | 10 | 8.3
| 2014-03-18 01:00 | 7.3 | 9.4 | 8.3
| 2014-03-18 01:30 | 7.1 | 9.4 | 8.3
| 2014-03-18 02:00 | 6.8 | 9.4 | 8.3
| 2014-03-18 02:30 | 6.8 | 9.4 | 8.3
| 2014-03-18 03:00 | 6.6 | 9.4 | 8.3
| 2014-03-18 03:30 | 6.7 | 9.4 | 8.3
| 2014-03-18 04:00 | 6.6 | 9.4 | 8.3
| 2014-03-18 04:30 | 6.3 | 9.4 | 8.3
| 2014-03-18 05:00 | 5.6 | 8.9 | 8.3
| 2014-03-18 05:30 | 5.1 | 8.9 | 8.3
| 2014-03-18 06:00 | 4.8 | 8.9 | 8.3
| 2014-03-18 06:30 | 5 | 8.9 | 8.3
| 2014-03-18 07:00 | 4.6 | 8.9 | 8.3
| 2014-03-18 07:30 | 6.2 | 8.9 | 8.3
| 2014-03-18 08:00 | 6.4 | 8.9 | 8.3
| 2014-03-18 08:30 | 7 | 8.9 | 8.3
| 2014-03-18 09:00 | 7.7 | 8.3 | 8.3
| 2014-03-18 09:30 | 8.3 | 8.3 | 8.3
| 2014-03-18 10:00 | 9.2 | 8.3 | 8.3
| 2014-03-18 10:30 | 9.4 | 8.3 | 8.3
| 2014-03-18 11:00 | 9.9 | 8.3 | 8.3
| 2014-03-18 11:30 | 11 | 8.9 | 8.3
| 2014-03-18 12:00 | 11.4 | 8.9 | 8.3
| 2014-03-18 12:30 | 12.7 | 8.9 | 8.3
| 2014-03-18 13:00 | 12.5 | 8.9 | 8.3
| 2014-03-18 13:30 | 12.7 | 8.9 | 8.3
| 2014-03-18 14:00 | 12.2 | 9.4 | 8.3
| 2014-03-18 14:30 | 11.1 | 9.4 | 8.3
| 2014-03-18 15:00 | 10.1 | 9.4 | 8.3
| 2014-03-18 15:30 | 10.7 | 9.4 | 8.3
| 2014-03-18 16:00 | 10.9 | 9.4 | 8.3
| 2014-03-18 16:30 | 11.3 | 10 | 8.3
| 2014-03-18 17:00 | 11.1 | 10 | 8.3
| 2014-03-18 17:30 | 10.9 | 10 | 8.3
| 2014-03-18 18:00 | 10.7 | 10 | 8.3
| 2014-03-18 18:30 | 9.8 | 10 | 8.3
| 2014-03-18 19:00 | 9.7 | 10 | 8.3
| 2014-03-18 19:30 | 9.2 | 10 | 8.3
| 2014-03-18 20:00 | 10.3 | 10 | 8.3
| 2014-03-18 20:30 | 10 | 10 | 8.3
| 2014-03-18 21:00 | 10.1 | 10 | 8.3
| 2014-03-18 21:30 | 9.4 | 10 | 8.3
| 2014-03-18 22:00 | 9.2 | 9.4 | 8.3
| 2014-03-18 22:30 | 9.6 | 9.4 | 8.3
| 2014-03-18 23:00 | 9.6 | 9.4 | 8.3
| 2014-03-18 23:30 | 9 | 9.4 | 8.3
| 2014-03-19 | 9.1 | 9.4 | 8.3
| 2014-03-19 00:30 | 8.8 | 9.4 | 8.3
| 2014-03-19 01:00 | 8.8 | 9.4 | 8.3
| 2014-03-19 01:30 | 8.9 | 9.4 | 8.3
| 2014-03-19 02:00 | 8.6 | 9.4 | 8.3
| 2014-03-19 02:30 | 8.7 | 8.9 | 8.3
| 2014-03-19 03:00 | 8.8 | 8.9 | 8.3
| 2014-03-19 03:30 | 9.7 | 8.9 | 8.3
| 2014-03-19 04:00 | 9.6 | 8.9 | 8.3
| 2014-03-19 04:30 | 9.4 | 8.9 | 8.3
| 2014-03-19 05:00 | 9.2 | 8.9 | 8.3
| 2014-03-19 05:30 | 8.8 | 8.9 | 8.3
| 2014-03-19 06:00 | 9 | 8.9 | 8.3
| 2014-03-19 06:30 | 9 | 8.9 | 8.3
| 2014-03-19 07:00 | 8.9 | 8.9 | 8.3
| 2014-03-19 07:30 | 9 | 8.9 | 8.3
| 2014-03-19 08:00 | 9.4 | 8.3 | 8.3
| 2014-03-19 08:30 | 9.5 | 8.3 | 8.3
| 2014-03-19 09:00 | 9.9 | 8.3 | 8.3
| 2014-03-19 09:30 | 10.6 | 8.3 | 8.3
| 2014-03-19 10:00 | 11.1 | 8.3 | 8.3
| 2014-03-19 10:30 | 11.3 | 8.3 | 8.3
| 2014-03-19 11:00 | 12.1 | 8.3 | 8.3
| 2014-03-19 11:30 | 13.3 | 8.3 | 8.3
| 2014-03-19 12:00 | 12.9 | 8.9 | 8.3
| 2014-03-19 12:30 | 13.9 | 8.9 | 8.3
| 2014-03-19 13:00 | 14.7 | 8.9 | 8.3
| 2014-03-19 13:30 | 15 | 8.9 | 8.3
| 2014-03-19 14:00 | 15.4 | 8.9 | 8.3
| 2014-03-19 14:30 | 15.6 | 9.4 | 8.3
| 2014-03-19 15:00 | 16.4 | 9.4 | 8.3
| 2014-03-19 15:30 | 16.3 | 9.4 | 8.3
| 2014-03-19 16:00 | 16 | 10 | 8.3
| 2014-03-19 16:30 | 15.4 | 10 | 8.3
| 2014-03-19 17:00 | 15.1 | 10.6 | 8.3
| 2014-03-19 17:30 | 14.2 | 10.6 | 8.3
| 2014-03-19 18:00 | 13.3 | 10.6 | 8.3
| 2014-03-19 18:30 | 12.7 | 10.6 | 8.3
| 2014-03-19 19:00 | 11.6 | 10.6 | 8.3
| 2014-03-19 19:30 | 11.3 | 10.6 | 8.3
| 2014-03-19 20:00 | 10.6 | 10.6 | 8.3
| 2014-03-19 20:30 | 9.3 | 10.6 | 8.3
| 2014-03-19 21:00 | 9.2 | 10.6 | 8.3
| 2014-03-19 21:30 | 9.3 | 10.6 | 8.3
| 2014-03-19 22:00 | 9.3 | 10.6 | 8.3
| 2014-03-19 22:30 | 9.2 | 10.6 | 8.3
| 2014-03-19 23:00 | 8.9 | 10.6 | 8.3
| 2014-03-19 23:30 | 8.8 | 10 | 8.3
| 2014-03-20 | 8.2 | 10 | 8.3
| 2014-03-20 00:30 | 6.9 | 10 | 8.3
| 2014-03-20 01:00 | 6.4 | 10 | 8.3
| 2014-03-20 01:30 | 6.4 | 10 | 8.3
| 2014-03-20 02:00 | 6.1 | 9.4 | 8.3
| 2014-03-20 02:30 | 5.7 | 9.4 | 8.3
| 2014-03-20 03:00 | 5.2 | 9.4 | 8.3
| 2014-03-20 03:30 | 4.8 | 9.4 | 8.3
| 2014-03-20 04:00 | 4.2 | 8.9 | 8.3
| 2014-03-20 04:30 | 4 | 8.9 | 8.3
| 2014-03-20 05:00 | 3.9 | 8.9 | 8.3
| 2014-03-20 05:30 | 3.3 | 8.9 | 8.3
| 2014-03-20 06:00 | 2.8 | 8.9 | 8.3
| 2014-03-20 06:30 | 2.7 | 8.3 | 8.3
| 2014-03-20 07:00 | 3 | 8.3 | 8.3
| 2014-03-20 07:30 | 3.2 | 8.3 | 8.3
| 2014-03-20 08:00 | 5.2 | 8.3 | 8.3
| 2014-03-20 08:30 | 6.9 | 8.3 | 8.3
| 2014-03-20 09:00 | 8.8 | 7.8 | 8.3
| 2014-03-20 09:30 | 10.8 | 7.8 | 8.3
| 2014-03-20 10:00 | 11.9 | 7.8 | 8.3
| 2014-03-20 10:30 | 13.5 | 7.8 | 8.3
| 2014-03-20 11:00 | 14.9 | 7.8 | 8.3
| 2014-03-20 11:30 | 16.4 | 7.8 | 8.3
| 2014-03-20 12:00 | 16.8 | 7.8 | 8.3
| 2014-03-20 12:30 | 18.5 | 8.3 | 8.3
| 2014-03-20 13:00 | 19.5 | 8.3 | 8.3
| 2014-03-20 13:30 | 20.8 | 8.9 | 8.3
| 2014-03-20 14:00 | 21.5 | 8.9 | 8.3
| 2014-03-20 14:30 | 22.3 | 9.4 | 8.3
| 2014-03-20 15:00 | 22.3 | 10 | 8.3
| 2014-03-20 15:30 | 22.1 | 10.6 | 8.3
| 2014-03-20 16:00 | 22.1 | 10.6 | 8.3
| 2014-03-20 16:30 | 22.1 | 11.1 | 8.3
| 2014-03-20 17:00 | 21.8 | 11.1 | 8.3
| 2014-03-20 17:30 | 20.8 | 11.7 | 8.3
| 2014-03-20 18:00 | 19.8 | 11.7 | 8.3
| 2014-03-20 18:30 | 18.3 | 12.2 | 8.3
| 2014-03-20 19:00 | 17.2 | 12.2 | 8.3
| 2014-03-20 19:30 | 16.3 | 12.2 | 8.3
| 2014-03-20 20:00 | 15.8 | 12.2 | 8.3
| 2014-03-20 20:30 | 15.8 | 12.2 | 8.3
| 2014-03-20 21:00 | 15.2 | 12.2 | 8.3
| 2014-03-20 21:30 | 14.1 | 12.2 | 8.3
| 2014-03-20 22:00 | 13.9 | 12.2 | 8.3
| 2014-03-20 22:30 | 14.8 | 11.7 | 8.3
| 2014-03-20 23:00 | 15 | 11.7 | 8.3
| 2014-03-20 23:30 | 14.9 | 11.7 | 8.3
| 2014-03-21 | 15.4 | 11.7 | 8.3
| 2014-03-21 00:30 | 15.2 | 11.7 | 8.3
| 2014-03-21 01:00 | 14.6 | 11.7 | 8.3
| 2014-03-21 01:30 | 14.1 | 11.7 | 8.3
| 2014-03-21 02:00 | 13.9 | 11.1 | 8.3
| 2014-03-21 02:30 | 13.3 | 11.1 | 8.3
| 2014-03-21 03:00 | 12.9 | 11.1 | 8.3
| 2014-03-21 03:30 | 12.7 | 11.1 | 8.3
| 2014-03-21 04:00 | 12.4 | 11.1 | 8.3
| 2014-03-21 04:30 | 12.2 | 11.1 | 8.3
| 2014-03-21 05:00 | 12.1 | 11.1 | 8.3
| 2014-03-21 05:30 | 12.1 | 10.6 | 8.3
| 2014-03-21 06:00 | 12 | 10.6 | 8.3
| 2014-03-21 06:30 | 12.1 | 10.6 | 8.3
| 2014-03-21 07:00 | 12.2 | 10.6 | 8.3
| 2014-03-21 07:30 | 13.2 | 10.6 | 8.3
| 2014-03-21 08:00 | 14.3 | 10.6 | 8.3
| 2014-03-21 08:30 | 15 | 10.6 | 8.3
| 2014-03-21 09:00 | 15.8 | 10.6 | 8.3
| 2014-03-21 09:30 | 17.7 | 10.6 | 8.3
| 2014-03-21 10:00 | 18.3 | 10.6 | 8.3
| 2014-03-21 10:30 | 19.4 | 10.6 | 8.3
| 2014-03-21 11:00 | 19.1 | 10.6 | 8.3
| 2014-03-21 11:30 | 19.8 | 10.6 | 8.3
| 2014-03-21 12:00 | 20.4 | 10.6 | 8.3
| 2014-03-21 12:30 | 20.5 | 11.1 | 8.3
| 2014-03-21 13:00 | 19.1 | 11.1 | 8.3
| 2014-03-21 13:30 | 18.6 | 11.7 | 8.3
| 2014-03-21 14:00 | 18 | 11.7 | 8.3
| 2014-03-21 14:30 | 17.7 | 11.7 | 8.3
| 2014-03-21 15:00 | 16.8 | 12.2 | 8.3
| 2014-03-21 15:30 | 16.2 | 12.2 | 8.3
| 2014-03-21 16:00 | 15.6 | 12.2 | 8.9
| 2014-03-21 16:30 | 15.3 | 12.2 | 8.9
| 2014-03-21 17:00 | 14.9 | 12.2 | 8.9
| 2014-03-21 17:30 | 14.7 | 12.2 | 8.9
| 2014-03-21 18:00 | 14.4 | 12.8 | 8.9
| 2014-03-21 18:30 | 12.4 | 12.8 | 8.9
| 2014-03-21 19:00 | 11.8 | 12.8 | 8.9
| 2014-03-21 19:30 | 10.8 | 12.2 | 8.9
| 2014-03-21 20:00 | 10.8 | 12.2 | 8.9
| 2014-03-21 20:30 | 10.5 | 12.2 | 8.9
| 2014-03-21 21:00 | 10.1 | 12.2 | 8.9
| 2014-03-21 21:30 | 9.6 | 12.2 | 8.9
| 2014-03-21 22:00 | 9.3 | 12.2 | 8.9
| 2014-03-21 22:30 | 9.1 | 12.2 | 8.9
| 2014-03-21 23:00 | 8.9 | 12.2 | 8.9
| 2014-03-21 23:30 | 8.9 | 11.7 | 8.9
| 2014-03-22 | 8.9 | 11.7 | 8.9
| 2014-03-22 00:30 | 10.1 | 11.7 | 8.9
| 2014-03-22 01:00 | 9.9 | 11.7 | 8.9
| 2014-03-22 01:30 | 9.7 | 11.7 | 8.9
| 2014-03-22 02:00 | 9.6 | 11.7 | 8.9
| 2014-03-22 02:30 | 9.6 | 11.7 | 8.9
| 2014-03-22 03:00 | 9.5 | 11.7 | 8.9
| 2014-03-22 03:30 | 9.7 | 11.1 | 8.9
| 2014-03-22 04:00 | 10.2 | 11.1 | 8.9
| 2014-03-22 04:30 | 10.7 | 11.1 | 8.9
| 2014-03-22 05:00 | 10.7 | 11.1 | 8.9
| 2014-03-22 05:30 | 10.6 | 11.1 | 8.9
| 2014-03-22 06:00 | 10.7 | 11.1 | 8.9
| 2014-03-22 06:30 | 10.3 | 11.1 | 8.9
| 2014-03-22 07:00 | 9.7 | 11.1 | 8.9
| 2014-03-22 07:30 | 9.5 | 11.1 | 8.9
| 2014-03-22 08:00 | 9.3 | 10.6 | 8.9
| 2014-03-22 08:30 | 9.3 | 10.6 | 8.9
| 2014-03-22 09:00 | 9.4 | 10.6 | 8.9
| 2014-03-22 09:30 | 9.7 | 10.6 | 8.9
| 2014-03-22 10:00 | 9.8 | 10.6 | 8.9
| 2014-03-22 10:30 | 10.1 | 10.6 | 8.9
| 2014-03-22 11:00 | 9.8 | 10.6 | 8.9
| 2014-03-22 11:30 | 9.3 | 10.6 | 8.9
| 2014-03-22 12:00 | 9.8 | 10.6 | 8.9
| 2014-03-22 12:30 | 9.9 | 10.6 | 8.9
| 2014-03-22 13:00 | 10.3 | 10.6 | 8.9
| 2014-03-22 13:30 | 10.7 | 10.6 | 8.9
| 2014-03-22 14:00 | 10.8 | 10.6 | 8.9
| 2014-03-22 14:30 | 10.8 | 10.6 | 8.9
| 2014-03-22 15:00 | 11 | 10.6 | 8.9
| 2014-03-22 15:30 | 11.2 | 10.6 | 8.9
| 2014-03-22 16:00 | 11.2 | 10.6 | 8.9
| 2014-03-22 16:30 | 11.3 | 11.1 | 8.9
| 2014-03-22 17:00 | 11.2 | 11.1 | 8.9
| 2014-03-22 17:30 | 11.1 | 11.1 | 8.9
| 2014-03-22 18:00 | 11 | 11.1 | 8.9
| 2014-03-22 18:30 | 11.2 | 11.1 | 8.9
| 2014-03-22 19:00 | 8.2 | 11.1 | 8.9
| 2014-03-22 19:30 | 7.4 | 11.1 | 8.9
| 2014-03-22 20:00 | 7.2 | 10.6 | 8.9
| 2014-03-22 20:30 | 7.2 | 10.6 | 8.9
| 2014-03-22 21:00 | 7.3 | 10.6 | 8.9
| 2014-03-22 21:30 | 7 | 10.6 | 8.9
| 2014-03-22 22:00 | 6.9 | 10.6 | 8.9
| 2014-03-22 22:30 | 6.8 | 10.6 | 8.9
| 2014-03-22 23:00 | 6.6 | 10.6 | 8.9
| 2014-03-22 23:30 | 6.6 | 10 | 8.9
| 2014-03-23 | 6.9 | 10 | 8.9
| 2014-03-23 00:30 | 6.7 | 10 | 8.9
| 2014-03-23 01:00 | 6.3 | 10 | 8.9
| 2014-03-23 01:30 | 6.2 | 9.4 | 8.9
| 2014-03-23 02:00 | 6.2 | 9.4 | 8.9
| 2014-03-23 02:30 | 6.2 | 9.4 | 8.9
| 2014-03-23 03:00 | 6.3 | 9.4 | 8.9
| 2014-03-23 03:30 | 6.6 | 9.4 | 8.9
| 2014-03-23 04:00 | 6.7 | 8.9 | 8.9
| 2014-03-23 04:30 | 6.7 | 8.9 | 8.9
| 2014-03-23 05:00 | 6.2 | 8.9 | 8.9
| 2014-03-23 05:30 | 5.9 | 8.9 | 8.9
| 2014-03-23 06:00 | 5.8 | 8.9 | 8.9
| 2014-03-23 06:30 | 5.7 | 8.3 | 8.9
| 2014-03-23 07:00 | 5.6 | 8.3 | 8.9
| 2014-03-23 07:30 | 5.4 | 8.3 | 8.9
| 2014-03-23 08:00 | 5.8 | 8.3 | 8.9
| 2014-03-23 08:30 | 6.1 | 8.3 | 8.9
| 2014-03-23 09:00 | 6.4 | 8.3 | 8.9
| 2014-03-23 09:30 | 6.9 | 8.3 | 8.9
| 2014-03-23 10:00 | 7.2 | 8.3 | 8.9
| 2014-03-23 10:30 | 7.6 | 8.3 | 8.9
| 2014-03-23 11:00 | 7.7 | 8.3 | 8.9
| 2014-03-23 11:30 | 7.9 | 8.3 | 8.9
| 2014-03-23 12:00 | 8.2 | 8.3 | 8.9
| 2014-03-23 12:30 | 8.5 | 8.3 | 8.9
| 2014-03-23 13:00 | 8.7 | 8.3 | 8.9
| 2014-03-23 13:30 | 9.2 | 8.3 | 8.9
| 2014-03-23 14:00 | 9.3 | 8.9 | 8.9
| 2014-03-23 14:30 | 9.8 | 8.9 | 8.9
| 2014-03-23 15:00 | 9.9 | 8.9 | 8.9
| 2014-03-23 15:30 | 10.1 | 8.9 | 8.9
| 2014-03-23 16:00 | 9.9 | 9.4 | 8.9
| 2014-03-23 16:30 | 9.5 | 9.4 | 8.9
| 2014-03-23 17:00 | 9.3 | 9.4 | 8.9
| 2014-03-23 17:30 | 9.3 | 9.4 | 8.9
| 2014-03-23 18:00 | 9.2 | 9.4 | 8.9
| 2014-03-23 18:30 | 8.9 | 9.4 | 8.9
| 2014-03-23 19:00 | 8.3 | 9.4 | 8.9
| 2014-03-23 19:30 | 7.4 | 9.4 | 8.9
| 2014-03-23 20:00 | 7.1 | 9.4 | 8.9
| 2014-03-23 20:30 | 7.3 | 9.4 | 8.9
| 2014-03-23 21:00 | 6.7 | 9.4 | 8.9
| 2014-03-23 21:30 | 6 | 8.9 | 8.9
| 2014-03-23 22:00 | 5 | 8.9 | 8.9
| 2014-03-23 22:30 | 4.8 | 8.9 | 8.9
| 2014-03-23 23:00 | 4.6 | 8.9 | 8.9
| 2014-03-23 23:30 | 4 | 8.9 | 8.9
| 2014-03-24 | 3.2 | 8.3 | 8.9
| 2014-03-24 00:30 | 3.7 | 8.3 | 8.9
| 2014-03-24 01:00 | 3 | 8.3 | 8.9
| 2014-03-24 01:30 | 3.6 | 8.3 | 8.9
| 2014-03-24 02:00 | 3.5 | 7.8 | 8.9
| 2014-03-24 02:30 | 3.1 | 7.8 | 8.9
| 2014-03-24 03:00 | 2.7 | 7.8 | 8.9
| 2014-03-24 03:30 | 2.3 | 7.8 | 8.9
| 2014-03-24 04:00 | 2.4 | 7.8 | 8.9
| 2014-03-24 04:30 | 2.2 | 7.8 | 8.9
| 2014-03-24 05:00 | 2.1 | 7.2 | 8.9
| 2014-03-24 05:30 | 2.1 | 7.2 | 8.9
| 2014-03-24 06:00 | 1.9 | 7.2 | 8.9
| 2014-03-24 06:30 | 2.1 | 7.2 | 8.9
| 2014-03-24 07:00 | 2.3 | 6.7 | 8.9
| 2014-03-24 07:30 | 3.3 | 6.7 | 8.9
| 2014-03-24 08:00 | 4.1 | 6.7 | 8.9
| 2014-03-24 08:30 | 4.7 | 6.7 | 8.9
| 2014-03-24 09:00 | 5.1 | 6.7 | 8.9
| 2014-03-24 09:30 | 5.6 | 6.7 | 8.9
| 2014-03-24 10:00 | 5.9 | 6.7 | 8.9
| 2014-03-24 10:30 | 6.3 | 6.7 | 8.9
| 2014-03-24 11:00 | 6.6 | 6.7 | 8.9
| 2014-03-24 11:30 | 7.1 | 6.7 | 8.9
| 2014-03-24 12:00 | 7.8 | 6.7 | 8.9
| 2014-03-24 12:30 | 8.5 | 7.2 | 8.9
| 2014-03-24 13:00 | 7.1 | 7.2 | 8.9
| 2014-03-24 13:30 | 6.9 | 7.8 | 8.9
| 2014-03-24 14:00 | 6.3 | 7.8 | 8.9
| 2014-03-24 14:30 | 6.9 | 8.3 | 8.9
| 2014-03-24 15:00 | 7.8 | 8.3 | 8.9
| 2014-03-24 15:30 | 8.4 | 8.3 | 8.9
| 2014-03-24 16:00 | 8.2 | 8.3 | 8.9
| 2014-03-24 16:30 | 9.2 | 8.9 | 8.9
| 2014-03-24 17:00 | 9.1 | 8.9 | 8.9
| 2014-03-24 17:30 | 8.2 | 8.9 | 8.9
| 2014-03-24 18:00 | 7.8 | 8.9 | 8.9
| 2014-03-24 18:30 | 6.9 | 8.9 | 8.9
| 2014-03-24 19:00 | 6 | 8.9 | 8.9
| 2014-03-24 19:30 | 5.8 | 8.9 | 8.9
| 2014-03-24 20:00 | 4.9 | 8.9 | 8.9
| 2014-03-24 20:30 | 4.8 | 8.9 | 8.9
| 2014-03-24 21:00 | 4.4 | 8.9 | 8.9
| 2014-03-24 21:30 | 3.7 | 8.9 | 8.9
| 2014-03-24 22:00 | 3.4 | 8.3 | 8.9
| 2014-03-24 22:30 | 3.1 | 8.3 | 8.9
| 2014-03-24 23:00 | 2.9 | 8.3 | 8.9
| 2014-03-24 23:30 | 3 | 8.3 | 8.9
| 2014-03-25 | 2.9 | 7.8 | 8.9
| 2014-03-25 00:30 | 2.9 | 7.8 | 8.9
| 2014-03-25 01:00 | 2.6 | 7.8 | 8.9
| 2014-03-25 01:30 | 2.2 | 7.8 | 8.9
| 2014-03-25 02:00 | 2.2 | 7.2 | 8.9
| 2014-03-25 02:30 | 1 | 7.2 | 8.9
| 2014-03-25 03:00 | 0.6 | 7.2 | 8.9
| 2014-03-25 03:30 | 0.8 | 7.2 | 8.9
| 2014-03-25 04:00 | 0.6 | 6.7 | 8.9
| 2014-03-25 04:30 | 1.7 | 6.7 | 8.9
| 2014-03-25 05:00 | 0.9 | 6.7 | 8.9
| 2014-03-25 05:30 | 0.2 | 6.7 | 8.9
| 2014-03-25 06:00 | 0.1 | 6.1 | 8.9
| 2014-03-25 06:30 | -0.7 | 6.1 | 8.9
| 2014-03-25 07:00 | -0.3 | 6.1 | 8.9
| 2014-03-25 07:30 | 0.6 | 6.1 | 8.9
| 2014-03-25 08:00 | 1.3 | 5.6 | 8.9
| 2014-03-25 08:30 | 2.8 | 5.6 | 8.9
| 2014-03-25 09:00 | 2.9 | 5.6 | 8.9
| 2014-03-25 09:30 | 3.1 | 5.6 | 8.9
| 2014-03-25 10:00 | 3.9 | 5.6 | 8.9
| 2014-03-25 10:30 | 5.1 | 5.6 | 8.9
| 2014-03-25 11:00 | 5.7 | 5.6 | 8.9
| 2014-03-25 11:30 | 6.9 | 5.6 | 8.9
| 2014-03-25 12:00 | 7.7 | 6.1 | 8.9
| 2014-03-25 12:30 | 8.2 | 6.1 | 8.9
| 2014-03-25 13:00 | 8.1 | 6.7 | 8.9
| 2014-03-25 13:30 | 8.3 | 6.7 | 8.9
| 2014-03-25 14:00 | 8.5 | 7.2 | 8.9
| 2014-03-25 14:30 | 9.4 | 7.2 | 8.9
| 2014-03-25 15:00 | 7.6 | 7.8 | 8.9
| 2014-03-25 15:30 | 4.8 | 7.8 | 8.9
| 2014-03-25 16:00 | 4.4 | 7.8 | 8.9
| 2014-03-25 16:30 | 5.4 | 7.8 | 8.9
| 2014-03-25 17:00 | 7.1 | 7.8 | 8.9
| 2014-03-25 17:30 | 7.1 | 7.8 | 8.9
| 2014-03-25 18:00 | 6.7 | 7.8 | 8.9
| 2014-03-25 18:30 | 5.8 | 7.8 | 8.9
| 2014-03-25 19:00 | 4.3 | 7.8 | 8.9
| 2014-03-25 19:30 | 3.3 | 7.8 | 8.9
| 2014-03-25 20:00 | 2.7 | 7.8 | 8.9
| 2014-03-25 20:30 | 1.9 | 7.8 | 8.9
| 2014-03-25 21:00 | 1.8 | 7.8 | 8.9
| 2014-03-25 21:30 | 1.4 | 7.8 | 8.9
| 2014-03-25 22:00 | 1.3 | 7.8 | 8.9
| 2014-03-25 22:30 | 0.8 | 7.2 | 8.9
| 2014-03-25 23:00 | 0.1 | 7.2 | 8.9
| 2014-03-25 23:30 | -0.1 | 7.2 | 8.9
| 2014-03-26 | -0.4 | 6.7 | 8.9
| 2014-03-26 00:30 | -0.3 | 6.7 | 8.9
| 2014-03-26 01:00 | -0.2 | 6.7 | 8.9
| 2014-03-26 01:30 | -0.3 | 6.7 | 8.9
| 2014-03-26 02:00 | -0.7 | 6.1 | 8.9
| 2014-03-26 02:30 | -0.3 | 6.1 | 8.9
| 2014-03-26 03:00 | 0 | 6.1 | 8.3
| 2014-03-26 03:30 | -0.6 | 6.1 | 8.3
| 2014-03-26 04:00 | -0.6 | 6.1 | 8.3
| 2014-03-26 04:30 | -0.6 | 5.6 | 8.3
| 2014-03-26 05:00 | -0.8 | 5.6 | 8.3
| 2014-03-26 05:30 | -0.8 | 5.6 | 8.3
| 2014-03-26 06:00 | -0.8 | 5.6 | 8.3
| 2014-03-26 06:30 | -1.2 | 5.6 | 8.3
| 2014-03-26 07:00 | -0.7 | 5 | 8.3
| 2014-03-26 07:30 | 0.2 | 5 | 8.3
| 2014-03-26 08:00 | 1.3 | 5 | 8.3
| 2014-03-26 08:30 | 2.6 | 5 | 8.3
| 2014-03-26 09:00 | 3.8 | 5 | 8.3
| 2014-03-26 09:30 | 5.2 | 5 | 8.3
| 2014-03-26 10:00 | 6.8 | 5 | 8.3
| 2014-03-26 10:30 | 8.2 | 5 | 8.3
| 2014-03-26 11:00 | 8.8 | 5 | 8.3
| 2014-03-26 11:30 | 10.4 | 5 | 8.3
| 2014-03-26 12:00 | 10.9 | 5 | 8.3
| 2014-03-26 12:30 | 10.8 | 5.6 | 8.3
| 2014-03-26 13:00 | 11.7 | 5.6 | 8.3
| 2014-03-26 13:30 | 12.7 | 6.1 | 8.3
| 2014-03-26 14:00 | 12.1 | 6.7 | 8.3
| 2014-03-26 14:30 | 11.8 | 6.7 | 8.3
| 2014-03-26 15:00 | 11.5 | 7.2 | 8.3
| 2014-03-26 15:30 | 11.7 | 7.8 | 8.3
| 2014-03-26 16:00 | 11.1 | 7.8 | 8.3
| 2014-03-26 16:30 | 12.5 | 7.8 | 8.3
| 2014-03-26 17:00 | 11 | 8.3 | 8.3
| 2014-03-26 17:30 | 11.4 | 8.3 | 8.3
| 2014-03-26 18:00 | 11 | 8.3 | 8.3
| 2014-03-26 18:30 | 10.5 | 8.3 | 8.3
| 2014-03-26 19:00 | 9.8 | 8.9 | 8.3
| 2014-03-26 19:30 | 9.3 | 8.9 | 8.3
| 2014-03-26 20:00 | 9.2 | 8.9 | 8.3
| 2014-03-26 20:30 | 9.2 | 8.9 | 8.3
| 2014-03-26 21:00 | 8.7 | 8.3 | 8.3
| 2014-03-26 21:30 | 8.3 | 8.3 | 8.3
| 2014-03-26 22:00 | 8.4 | 8.3 | 8.3
| 2014-03-26 22:30 | 8.2 | 8.3 | 8.3
| 2014-03-26 23:00 | 7.9 | 8.3 | 8.3
| 2014-03-26 23:30 | 7.7 | 8.3 | 8.3
| 2014-03-27 | 6.6 | 8.3 | 8.3
| 2014-03-27 00:30 | 5.9 | 8.3 | 8.3
| 2014-03-27 01:00 | 5.4 | 8.3 | 8.3
| 2014-03-27 01:30 | 5.1 | 7.8 | 8.3
| 2014-03-27 02:00 | 5.3 | 7.8 | 8.3
| 2014-03-27 02:30 | 4.7 | 7.8 | 8.3
| 2014-03-27 03:00 | 4.1 | 7.8 | 8.3
| 2014-03-27 03:30 | 3.7 | 7.8 | 8.3
| 2014-03-27 04:00 | 3.3 | 7.2 | 8.3
| 2014-03-27 04:30 | 2.5 | 7.2 | 8.3
| 2014-03-27 05:00 | 1.6 | 7.2 | 8.3
| 2014-03-27 05:30 | 0.9 | 7.2 | 8.3
| 2014-03-27 06:00 | 1.1 | 6.7 | 8.3
| 2014-03-27 06:30 | 1 | 6.7 | 8.3
| 2014-03-27 07:00 | 1.5 | 6.7 | 8.3
| 2014-03-27 07:30 | 3.5 | 6.7 | 8.3
| 2014-03-27 08:00 | 5.2 | 6.1 | 8.3
| 2014-03-27 08:30 | 7.2 | 6.1 | 8.3
| 2014-03-27 09:00 | 8.7 | 6.1 | 8.3
| 2014-03-27 09:30 | 9.7 | 6.1 | 8.3
| 2014-03-27 10:00 | 10.7 | 6.1 | 8.3
| 2014-03-27 10:30 | 12.1 | 6.1 | 8.3
| 2014-03-27 11:00 | 13.1 | 6.1 | 8.3
| 2014-03-27 11:30 | 13.9 | 6.1 | 8.3
| 2014-03-27 12:00 | 14.7 | 6.7 | 8.3
| 2014-03-27 12:30 | 15.2 | 6.7 | 8.3
| 2014-03-27 13:00 | 15.8 | 7.2 | 8.3
| 2014-03-27 13:30 | 16 | 7.2 | 8.3
| 2014-03-27 14:00 | 16.4 | 7.8 | 8.3
| 2014-03-27 14:30 | 17 | 8.3 | 8.3
| 2014-03-27 15:00 | 17.3 | 8.3 | 8.3
| 2014-03-27 15:30 | 17.3 | 8.9 | 8.3
| 2014-03-27 16:00 | 16.3 | 9.4 | 8.3
| 2014-03-27 16:30 | 16.6 | 9.4 | 8.3
| 2014-03-27 17:00 | 16.2 | 10 | 8.3
| 2014-03-27 17:30 | 15.1 | 10 | 8.3
| 2014-03-27 18:00 | 14.3 | 10 | 8.3
| 2014-03-27 18:30 | 13.3 | 10.6 | 8.3
| 2014-03-27 19:00 | 11.7 | 10.6 | 8.3
| 2014-03-27 19:30 | 10.2 | 10.6 | 8.3
| 2014-03-27 20:00 | 8.9 | 10.6 | 8.3
| 2014-03-27 20:30 | 8.1 | 10.6 | 8.3
| 2014-03-27 21:00 | 8.4 | 10 | 8.3
| 2014-03-27 21:30 | 8.7 | 10 | 8.3
| 2014-03-27 22:00 | 8.6 | 10 | 8.3
| 2014-03-27 22:30 | 8.2 | 10 | 8.3
| 2014-03-27 23:00 | 7.8 | 9.4 | 8.3
| 2014-03-27 23:30 | 7.6 | 9.4 | 8.3
| 2014-03-28 | 6.9 | 9.4 | 8.3
| 2014-03-28 00:30 | 8.4 | 9.4 | 8.3
| 2014-03-28 01:00 | 8.5 | 9.4 | 8.3
| 2014-03-28 01:30 | 8.5 | 8.9 | 8.3
| 2014-03-28 02:00 | 8.6 | 8.9 | 8.3
| 2014-03-28 02:30 | 8.7 | 8.9 | 8.3
| 2014-03-28 03:00 | 8.4 | 8.9 | 8.3
| 2014-03-28 03:30 | 8.4 | 8.3 | 8.3
| 2014-03-28 04:00 | 7.6 | 8.3 | 8.3
| 2014-03-28 04:30 | 7 | 8.3 | 8.3
| 2014-03-28 05:00 | 6.6 | 8.3 | 8.3
| 2014-03-28 05:30 | 6.9 | 8.3 | 8.3
| 2014-03-28 06:00 | 6.8 | 7.8 | 8.3
| 2014-03-28 06:30 | 6.6 | 7.8 | 8.3
| 2014-03-28 07:00 | 7 | 7.8 | 8.3
| 2014-03-28 07:30 | 8 | 7.8 | 8.3
| 2014-03-28 08:00 | 9 | 7.8 | 8.3
| 2014-03-28 08:30 | 9.8 | 7.2 | 8.3
| 2014-03-28 09:00 | 11.6 | 7.2 | 8.3
| 2014-03-28 09:30 | 12.5 | 7.2 | 8.3
| 2014-03-28 10:00 | 13.5 | 7.2 | 8.3
| 2014-03-28 10:30 | 14.3 | 7.2 | 8.3
| 2014-03-28 11:00 | 15.1 | 7.2 | 8.3
| 2014-03-28 11:30 | 15.9 | 7.8 | 8.3
| 2014-03-28 12:00 | 18.8 | 7.8 | 8.3
| 2014-03-28 12:30 | 18.8 | 7.8 | 8.3
| 2014-03-28 13:00 | 19.1 | 8.3 | 8.3
| 2014-03-28 13:30 | 19.9 | 8.9 | 8.3
| 2014-03-28 14:00 | 19.4 | 8.9 | 8.3
| 2014-03-28 14:30 | 19.4 | 9.4 | 8.3
| 2014-03-28 15:00 | 19.8 | 10 | 8.3
| 2014-03-28 15:30 | 19.7 | 10 | 8.3
| 2014-03-28 16:00 | 19.4 | 10.6 | 8.3
| 2014-03-28 16:30 | 19.3 | 11.1 | 8.3
| 2014-03-28 17:00 | 18.6 | 11.1 | 8.3
| 2014-03-28 17:30 | 18.1 | 11.7 | 8.3
| 2014-03-28 18:00 | 16.8 | 11.7 | 8.3
| 2014-03-28 18:30 | 15.6 | 11.7 | 8.3
| 2014-03-28 19:00 | 14.3 | 12.2 | 8.3
| 2014-03-28 19:30 | 13.9 | 12.2 | 8.3
| 2014-03-28 20:00 | 13.1 | 12.2 | 8.3
| 2014-03-28 20:30 | 12 | 12.2 | 8.3
| 2014-03-28 21:00 | 11.3 | 11.7 | 8.3
| 2014-03-28 21:30 | 11.2 | 11.7 | 8.3
| 2014-03-28 22:00 | 11 | 11.7 | 8.3
| 2014-03-28 22:30 | 10.5 | 11.7 | 8.3
| 2014-03-28 23:00 | 9.9 | 11.7 | 8.3
| 2014-03-28 23:30 | 9.7 | 11.1 | 8.3
| 2014-03-29 | 9.1 | 11.1 | 8.3
| 2014-03-29 00:30 | 8.8 | 11.1 | 8.3
| 2014-03-29 01:00 | 7.8 | 11.1 | 8.3
| 2014-03-29 01:30 | 7.2 | 10.6 | 8.3
| 2014-03-29 02:00 | 6.4 | 10.6 | 8.3
| 2014-03-29 02:30 | 6.2 | 10.6 | 8.3
| 2014-03-29 03:00 | 5.4 | 10.6 | 8.3
| 2014-03-29 03:30 | 5.1 | 10 | 8.3
| 2014-03-29 04:00 | 5.1 | 10 | 8.3
| 2014-03-29 04:30 | 4.8 | 10 | 8.3
| 2014-03-29 05:00 | 4.8 | 9.4 | 8.3
| 2014-03-29 05:30 | 4.7 | 9.4 | 8.3
| 2014-03-29 06:00 | 4.2 | 9.4 | 8.3
| 2014-03-29 06:30 | 4.2 | 9.4 | 8.3
| 2014-03-29 07:00 | 4.3 | 8.9 | 8.3
| 2014-03-29 07:30 | 5.6 | 8.9 | 8.3
| 2014-03-29 08:00 | 8.4 | 8.9 | 8.3
| 2014-03-29 08:30 | 10.7 | 8.9 | 8.3
| 2014-03-29 09:00 | 11.8 | 8.9 | 8.3
| 2014-03-29 09:30 | 13.1 | 8.3 | 8.3
| 2014-03-29 10:00 | 14.6 | 8.3 | 8.3
| 2014-03-29 10:30 | 16 | 8.3 | 8.3
| 2014-03-29 11:00 | 17.3 | 8.3 | 8.3
| 2014-03-29 11:30 | 18.2 | 8.9 | 8.3
| 2014-03-29 12:00 | 18.8 | 8.9 | 8.3
| 2014-03-29 12:30 | 19.9 | 8.9 | 8.3
| 2014-03-29 13:00 | 20.6 | 9.4 | 8.3
| 2014-03-29 13:30 | 20.9 | 10 | 8.3
| 2014-03-29 14:00 | 21.1 | 10 | 8.3
| 2014-03-29 14:30 | 20.9 | 10.6 | 8.3
| 2014-03-29 15:00 | 21.9 | 11.1 | 8.3
| 2014-03-29 15:30 | 21.7 | 11.7 | 8.3
| 2014-03-29 16:00 | 21.6 | 11.7 | 8.3
| 2014-03-29 16:30 | 20.6 | 12.2 | 8.3
| 2014-03-29 17:00 | 20.3 | 12.8 | 8.3
| 2014-03-29 17:30 | 20.4 | 12.8 | 8.3
| 2014-03-29 18:00 | 18.9 | 12.8 | 8.3
| 2014-03-29 18:30 | 17.7 | 13.3 | 8.3
| 2014-03-29 19:00 | 16.4 | 13.3 | 8.3
| 2014-03-29 19:30 | 14.8 | 13.3 | 8.3
| 2014-03-29 20:00 | 14.1 | 13.3 | 8.3
| 2014-03-29 20:30 | 13.2 | 13.3 | 8.3
| 2014-03-29 21:00 | 12.1 | 13.3 | 8.3
| 2014-03-29 21:30 | 10.7 | 13.3 | 8.3
| 2014-03-29 22:00 | 9.4 | 12.8 | 8.3
| 2014-03-29 22:30 | 8.6 | 12.8 | 8.3
| 2014-03-29 23:00 | 8.4 | 12.8 | 8.3
| 2014-03-29 23:30 | 8.9 | 12.8 | 8.3
| 2014-03-30 | 8.8 | 12.2 | 8.3
| 2014-03-30 00:30 | 8.8 | 12.2 | 8.3
| 2014-03-30 01:00 | 7.6 | 12.2 | 8.3
| 2014-03-30 01:30 | 7 | 11.7 | 8.9
| 2014-03-30 03:00 | 6.4 | 11.7 | 8.9
| 2014-03-30 03:30 | 5.8 | 11.7 | 8.9
| 2014-03-30 04:00 | 5.8 | 11.7 | 8.9
| 2014-03-30 04:30 | 6.7 | 11.1 | 8.9
| 2014-03-30 05:00 | 5.9 | 11.1 | 8.9
| 2014-03-30 05:30 | 4.7 | 11.1 | 8.9
| 2014-03-30 06:00 | 5.6 | 10.6 | 8.9
| 2014-03-30 06:30 | 5.7 | 10.6 | 8.9
| 2014-03-30 07:00 | 5.7 | 10.6 | 8.9
| 2014-03-30 07:30 | 5.4 | 10.6 | 8.9
| 2014-03-30 08:00 | 5.6 | 10 | 8.9
| 2014-03-30 08:30 | 6.9 | 10 | 8.9
| 2014-03-30 09:00 | 8.6 | 10 | 8.9
| 2014-03-30 09:30 | 10.6 | 10 | 8.9
| 2014-03-30 10:00 | 12.4 | 9.4 | 8.9
| 2014-03-30 10:30 | 14.4 | 9.4 | 8.9
| 2014-03-30 11:00 | 15.3 | 9.4 | 8.9
| 2014-03-30 11:30 | 16.4 | 9.4 | 8.9
| 2014-03-30 12:00 | 17.1 | 9.4 | 8.9
| 2014-03-30 12:30 | 17.8 | 10 | 8.9
| 2014-03-30 13:00 | 18.6 | 10 | 8.9
| 2014-03-30 13:30 | 19.2 | 10 | 8.9
| 2014-03-30 14:00 | 19.8 | 10.6 | 8.9
| 2014-03-30 14:30 | 20.5 | 11.1 | 8.9
| 2014-03-30 15:00 | 20.9 | 11.1 | 8.9
| 2014-03-30 15:30 | 21.3 | 11.7 | 8.9
| 2014-03-30 16:00 | 21.4 | 11.7 | 8.9
| 2014-03-30 16:30 | 21.7 | 12.2 | 8.9
| 2014-03-30 17:00 | 21.5 | 12.8 | 8.9
| 2014-03-30 17:30 | 21 | 12.8 | 8.9
| 2014-03-30 18:00 | 20.4 | 13.3 | 8.9
| 2014-03-30 18:30 | 19.8 | 13.3 | 8.9
| 2014-03-30 19:00 | 19.1 | 13.9 | 8.9
| 2014-03-30 19:30 | 17.8 | 13.9 | 8.9
| 2014-03-30 20:00 | 16.6 | 13.9 | 8.9
| 2014-03-30 20:30 | 14.9 | 13.9 | 8.9
| 2014-03-30 21:00 | 13.2 | 13.9 | 8.9
| 2014-03-30 21:30 | 12.2 | 13.9 | 8.9
| 2014-03-30 22:00 | 11.6 | 13.9 | 8.9
| 2014-03-30 22:30 | 10.7 | 13.9 | 8.9
| 2014-03-30 23:00 | 9.7 | 13.3 | 8.9
| 2014-03-30 23:30 | 9.1 | 13.3 | 8.9
| 2014-03-31 | 8.9 | 13.3 | 8.9
| 2014-03-31 00:30 | 8.8 | 13.3 | 8.9
| 2014-03-31 01:00 | 8.2 | 12.8 | 8.9
| 2014-03-31 01:30 | 7.8 | 12.8 | 8.9
| 2014-03-31 02:00 | 7.7 | 12.8 | 8.9
| 2014-03-31 02:30 | 7.2 | 12.8 | 8.9
| 2014-03-31 03:00 | 6.7 | 12.2 | 8.9
| 2014-03-31 03:30 | 6.3 | 12.2 | 8.9
| 2014-03-31 04:00 | 6 | 12.2 | 8.9
| 2014-03-31 04:30 | 5.9 | 12.2 | 8.9
| 2014-03-31 05:00 | 5.6 | 11.7 | 8.9
| 2014-03-31 05:30 | 5.7 | 11.7 | 8.9
| 2014-03-31 06:00 | 5.8 | 11.7 | 8.9
| 2014-03-31 06:30 | 5.6 | 11.7 | 8.9
| 2014-03-31 07:00 | 5.2 | 11.1 | 8.9
| 2014-03-31 07:30 | 5.1 | 11.1 | 8.9
| 2014-03-31 08:00 | 5.4 | 11.1 | 8.9
| 2014-03-31 08:30 | 6.1 | 11.1 | 8.9
| 2014-03-31 09:00 | 7.2 | 11.1 | 8.9
| 2014-03-31 09:30 | 8.8 | 10.6 | 8.9
| 2014-03-31 10:00 | 9.7 | 10.6 | 8.9
| 2014-03-31 10:30 | 10.8 | 10.6 | 8.9
| 2014-03-31 11:00 | 11.7 | 10.6 | 8.9
| 2014-03-31 11:30 | 12.7 | 10.6 | 8.9
| 2014-03-31 12:00 | 13.2 | 10.6 | 8.9
| 2014-03-31 12:30 | 14 | 10.6 | 8.9
| 2014-03-31 13:00 | 15.3 | 10.6 | 8.9
| 2014-03-31 13:30 | 17.8 | 11.1 | 9.4
| 2014-03-31 14:00 | 18.8 | 11.1 | 9.4
| 2014-03-31 14:30 | 19.1 | 11.1 | 9.4
| 2014-03-31 15:00 | 20.2 | 11.7 | 9.4
| 2014-03-31 15:30 | 20.3 | 11.7 | 9.4
| 2014-03-31 16:00 | 21.3 | 12.2 | 9.4
| 2014-03-31 16:30 | 21.4 | 12.2 | 9.4
| 2014-03-31 17:00 | 21.7 | 12.8 | 9.4
| 2014-03-31 17:30 | 21.6 | 12.8 | 9.4
| 2014-03-31 18:00 | 21.2 | 13.3 | 9.4
| 2014-03-31 18:30 | 20.9 | 13.3 | 9.4
| 2014-03-31 19:00 | 19.9 | 13.9 | 9.4
| 2014-03-31 19:30 | 18.3 | 13.9 | 9.4
| 2014-03-31 20:00 | 16.2 | 13.9 | 9.4
| 2014-03-31 20:30 | 14.4 | 13.9 | 9.4
| 2014-03-31 21:00 | 13 | 13.9 | 9.4
| 2014-03-31 21:30 | 12.3 | 13.9 | 9.4
| 2014-03-31 22:00 | 11.2 | 13.9 | 9.4
| 2014-03-31 22:30 | 10.2 | 13.9 | 9.4
| 2014-03-31 23:00 | 9.6 | 13.9 | 9.4
| 2014-03-31 23:30 | 9.1 | 13.9 | 9.4
| 2014-04-01 | 9.3 | 13.3 | 9.4
| 2014-04-01 00:30 | 9.2 | 13.3 | 9.4
| 2014-04-01 01:00 | 8.9 | 13.3 | 9.4
| 2014-04-01 01:30 | 8.3 | 13.3 | 9.4
| 2014-04-01 02:00 | 7.6 | 12.8 | 9.4
| 2014-04-01 02:30 | 6.7 | 12.8 | 9.4
| 2014-04-01 03:00 | 6.6 | 12.8 | 9.4
| 2014-04-01 03:30 | 6.6 | 12.8 | 9.4
| 2014-04-01 04:00 | 6.6 | 12.2 | 9.4
| 2014-04-01 04:30 | 5.9 | 12.2 | 9.4
| 2014-04-01 05:00 | 5.7 | 12.2 | 9.4
| 2014-04-01 05:30 | 6 | 12.2 | 9.4
| 2014-04-01 06:00 | 5.9 | 11.7 | 9.4
| 2014-04-01 06:30 | 6 | 11.7 | 9.4
| 2014-04-01 07:00 | 5.3 | 11.7 | 9.4
| 2014-04-01 07:30 | 5.2 | 11.7 | 9.4
| 2014-04-01 08:00 | 5.2 | 11.7 | 9.4
| 2014-04-01 08:30 | 5.3 | 11.1 | 9.4
| 2014-04-01 09:00 | 7.3 | 11.1 | 9.4
| 2014-04-01 09:30 | 9.4 | 11.1 | 9.4
| 2014-04-01 10:00 | 11.5 | 11.1 | 9.4
| 2014-04-01 10:30 | 13 | 11.1 | 9.4
| 2014-04-01 11:00 | 14.5 | 11.1 | 9.4
| 2014-04-01 11:30 | 15.7 | 11.1 | 9.4
| 2014-04-01 12:00 | 17.2 | 11.1 | 9.4
| 2014-04-01 12:30 | 18.3 | 11.1 | 9.4
| 2014-04-01 13:00 | 19.4 | 11.1 | 9.4
| 2014-04-01 13:30 | 20.3 | 11.7 | 9.4
| 2014-04-01 14:00 | 20.7 | 11.7 | 9.4
| 2014-04-01 14:30 | 21.8 | 12.2 | 9.4
| 2014-04-01 15:00 | 22.2 | 12.2 | 9.4
| 2014-04-01 15:30 | 22.3 | 12.8 | 9.4
| 2014-04-01 16:00 | 22.1 | 13.3 | 9.4
| 2014-04-01 16:30 | 22.2 | 13.3 | 9.4
| 2014-04-01 17:00 | 22.1 | 13.9 | 9.4
| 2014-04-01 17:30 | 21.7 | 13.9 | 9.4
| 2014-04-01 18:00 | 21.4 | 14.4 | 9.4
| 2014-04-01 18:30 | 20.9 | 14.4 | 9.4
| 2014-04-01 19:00 | 20.1 | 14.4 | 9.4
| 2014-04-01 19:30 | 18.9 | 15 | 9.4
| 2014-04-01 20:00 | 17.7 | 15 | 9.4
| 2014-04-01 20:30 | 16.2 | 15 | 9.4
| 2014-04-01 21:00 | 15.6 | 15 | 9.4
| 2014-04-01 21:30 | 14.4 | 15 | 9.4
| 2014-04-01 22:00 | 13.1 | 15 | 9.4
| 2014-04-01 22:30 | 12.4 | 15 | 9.4
| 2014-04-01 23:00 | 11.6 | 14.4 | 9.4
| 2014-04-01 23:30 | 10.7 | 14.4 | 9.4
| 2014-04-02 | 10.4 | 14.4 | 9.4
| 2014-04-02 00:30 | 10.2 | 14.4 | 9.4
| 2014-04-02 01:00 | 10.1 | 13.9 | 9.4
| 2014-04-02 01:30 | 9.7 | 13.9 | 9.4
| 2014-04-02 02:00 | 9 | 13.9 | 9.4
| 2014-04-02 02:30 | 8.4 | 13.9 | 9.4
| 2014-04-02 03:00 | 8.2 | 13.9 | 9.4
| 2014-04-02 03:30 | 8.1 | 13.3 | 9.4
| 2014-04-02 04:00 | 7.6 | 13.3 | 9.4
| 2014-04-02 04:30 | 7.1 | 13.3 | 9.4
| 2014-04-02 05:00 | 6.2 | 13.3 | 9.4
| 2014-04-02 05:30 | 6.2 | 12.8 | 9.4
| 2014-04-02 06:00 | 5.7 | 12.8 | 9.4
| 2014-04-02 06:30 | 5.8 | 12.8 | 10
| 2014-04-02 07:00 | 4.7 | 12.8 | 10
| 2014-04-02 07:30 | 5.8 | 12.2 | 10
| 2014-04-02 08:00 | 6.8 | 12.2 | 10
| 2014-04-02 08:30 | 8.6 | 12.2 | 10
| 2014-04-02 09:00 | 10.6 | 12.2 | 10
| 2014-04-02 09:30 | 13 | 11.7 | 10
| 2014-04-02 10:00 | 14.7 | 11.7 | 10
| 2014-04-02 10:30 | 15.9 | 11.7 | 10
| 2014-04-02 11:00 | 16.7 | 11.7 | 10
| 2014-04-02 11:30 | 17.8 | 11.7 | 10
| 2014-04-02 12:00 | 18.6 | 11.7 | 10
| 2014-04-02 12:30 | 18.9 | 11.7 | 10
| 2014-04-02 13:00 | 19.9 | 12.2 | 10
| 2014-04-02 13:30 | 20.6 | 12.2 | 10
| 2014-04-02 14:00 | 20.8 | 12.8 | 10
| 2014-04-02 14:30 | 21.5 | 12.8 | 10
| 2014-04-02 15:00 | 22.8 | 13.3 | 10
| 2014-04-02 15:30 | 23.8 | 13.3 | 10
| 2014-04-02 16:00 | 23.8 | 13.9 | 10
| 2014-04-02 16:30 | 23.2 | 14.4 | 10
| 2014-04-02 17:00 | 23.7 | 14.4 | 10
| 2014-04-02 17:30 | 23.5 | 15 | 10
| 2014-04-02 18:00 | 23.1 | 15.6 | 10
| 2014-04-02 18:30 | 22.4 | 15.6 | 10
| 2014-04-02 19:00 | 21.2 | 15.6 | 10
| 2014-04-02 19:30 | 19.5 | 16.1 | 10
| 2014-04-02 20:00 | 18.2 | 16.1 | 10
| 2014-04-02 20:30 | 16.8 | 16.1 | 10
| 2014-04-02 21:00 | 15.8 | 16.1 | 10
| 2014-04-02 21:30 | 15.1 | 16.1 | 10
| 2014-04-02 22:00 | 14.4 | 16.1 | 10
| 2014-04-02 22:30 | 13.9 | 16.1 | 10
| 2014-04-02 23:00 | 13.4 | 15.6 | 10
| 2014-04-02 23:30 | 12.7 | 15.6 | 10
| 2014-04-03 | 11.9 | 15.6 | 10
| 2014-04-03 00:30 | 11.3 | 15.6 | 10
| 2014-04-03 01:00 | 10.5 | 15 | 10
| 2014-04-03 01:30 | 9.9 | 15 | 10
| 2014-04-03 02:00 | 9.2 | 15 | 10
| 2014-04-03 02:30 | 9 | 15 | 10
| 2014-04-03 03:00 | 8.9 | 14.4 | 10
| 2014-04-03 03:30 | 8.8 | 14.4 | 10
| 2014-04-03 04:00 | 8.5 | 14.4 | 10
| 2014-04-03 04:30 | 8.3 | 14.4 | 10
| 2014-04-03 05:00 | 7.9 | 13.9 | 10
| 2014-04-03 05:30 | 7.6 | 13.9 | 10
| 2014-04-03 06:00 | 7.3 | 13.9 | 10
| 2014-04-03 06:30 | 6.9 | 13.9 | 10
| 2014-04-03 07:00 | 6.2 | 13.3 | 10
| 2014-04-03 07:30 | 7 | 13.3 | 10
| 2014-04-03 08:00 | 7.7 | 13.3 | 10
| 2014-04-03 08:30 | 9.4 | 13.3 | 10
| 2014-04-03 09:00 | 10.7 | 12.8 | 10
| 2014-04-03 09:30 | 12.4 | 12.8 | 10
| 2014-04-03 10:00 | 13.7 | 12.8 | 10
| 2014-04-03 10:30 | 14.4 | 12.8 | 10
| 2014-04-03 11:00 | 16.6 | 12.8 | 10
| 2014-04-03 11:30 | 18.7 | 12.8 | 10
| 2014-04-03 12:00 | 19.2 | 12.8 | 10
| 2014-04-03 12:30 | 19.9 | 12.8 | 10.6
| 2014-04-03 13:00 | 20.3 | 13.3 | 10.6
| 2014-04-03 13:30 | 20.8 | 13.3 | 10.6
| 2014-04-03 14:00 | 21.2 | 13.3 | 10.6
| 2014-04-03 14:30 | 22.4 | 13.3 | 10.6
| 2014-04-03 15:00 | 22.7 | 13.9 | 10.6
| 2014-04-03 15:30 | 23.4 | 13.9 | 10.6
| 2014-04-03 16:00 | 23.4 | 13.9 | 10.6
| 2014-04-03 16:30 | 23.4 | 14.4 | 10.6
| 2014-04-03 17:00 | 22.6 | 14.4 | 10.6
| 2014-04-03 17:30 | 21.8 | 14.4 | 10.6
| 2014-04-03 18:00 | 21.7 | 15 | 10.6
| 2014-04-03 18:30 | 21.5 | 15 | 10.6
| 2014-04-03 19:00 | 21.3 | 15 | 10.6
| 2014-04-03 19:30 | 20.6 | 15 | 10.6
| 2014-04-03 20:00 | 18.7 | 15 | 10.6
| 2014-04-03 20:30 | 18.1 | 15 | 10.6
| 2014-04-03 21:00 | 16.9 | 15 | 10.6
| 2014-04-03 21:30 | 16.6 | 15 | 10.6
| 2014-04-03 22:00 | 18.3 | 15 | 10.6
| 2014-04-03 22:30 | 17.1 | 15 | 10.6
| 2014-04-03 23:00 | 16.5 | 15 | 10.6
| 2014-04-03 23:30 | 15.6 | 15 | 10.6
| 2014-04-04 | 15.4 | 15 | 10.6
| 2014-04-04 00:30 | 15.4 | 15 | 10.6
| 2014-04-04 01:00 | 15 | 15 | 10.6
| 2014-04-04 01:30 | 14.8 | 15 | 10.6
| 2014-04-04 02:00 | 15 | 15 | 10.6
| 2014-04-04 02:30 | 14.2 | 14.4 | 10.6
| 2014-04-04 03:00 | 13.9 | 14.4 | 10.6
| 2014-04-04 03:30 | 13.3 | 14.4 | 10.6
| 2014-04-04 04:00 | 12.4 | 14.4 | 10.6
| 2014-04-04 04:30 | 12.1 | 14.4 | 10.6
| 2014-04-04 05:00 | 12.9 | 14.4 | 10.6
| 2014-04-04 05:30 | 12.8 | 13.9 | 10.6
| 2014-04-04 06:00 | 12.7 | 13.9 | 10.6
| 2014-04-04 06:30 | 12.2 | 13.9 | 10.6
| 2014-04-04 07:00 | 11.2 | 13.9 | 10.6
| 2014-04-04 07:30 | 11.1 | 13.9 | 10.6
| 2014-04-04 08:00 | 11.9 | 13.9 | 10.6
| 2014-04-04 08:30 | 12.7 | 13.9 | 10.6
| 2014-04-04 09:00 | 13.4 | 13.3 | 10.6
| 2014-04-04 09:30 | 14.7 | 13.3 | 10.6
| 2014-04-04 10:00 | 16 | 13.3 | 10.6
| 2014-04-04 10:30 | 17.1 | 13.3 | 10.6
| 2014-04-04 11:00 | 18.4 | 13.3 | 10.6
| 2014-04-04 11:30 | 19.5 | 13.3 | 10.6
| 2014-04-04 12:00 | 19.5 | 13.3 | 10.6
| 2014-04-04 12:30 | 19.8 | 13.3 | 10.6
| 2014-04-04 13:00 | 21.3 | 13.9 | 10.6
| 2014-04-04 13:30 | 21.8 | 13.9 | 10.6
| 2014-04-04 14:00 | 22.3 | 13.9 | 10.6
| 2014-04-04 14:30 | 22.4 | 14.4 | 10.6
| 2014-04-04 15:00 | 22.3 | 14.4 | 10.6
| 2014-04-04 15:30 | 22.9 | 14.4 | 10.6
| 2014-04-04 16:00 | 23.7 | 15 | 10.6
| 2014-04-04 16:30 | 23.8 | 15 | 10.6
| 2014-04-04 17:00 | 23.7 | 15.6 | 10.6
| 2014-04-04 17:30 | 23.1 | 15.6 | 10.6
| 2014-04-04 18:00 | 22.4 | 15.6 | 10.6
| 2014-04-04 18:30 | 21.8 | 16.1 | 10.6
| 2014-04-04 19:00 | 21.1 | 16.1 | 10.6
| 2014-04-04 19:30 | 19.9 | 16.1 | 10.6
| 2014-04-04 20:00 | 17.2 | 16.1 | 10.6
| 2014-04-04 20:30 | 15.7 | 16.1 | 10.6
| 2014-04-04 21:00 | 15.4 | 16.1 | 10.6
| 2014-04-04 21:30 | 15.2 | 16.1 | 10.6
| 2014-04-04 22:00 | 14.1 | 16.1 | 10.6
| 2014-04-04 22:30 | 14.1 | 16.1 | 10.6
| 2014-04-04 23:00 | 13.9 | 16.1 | 10.6
| 2014-04-04 23:30 | 13.6 | 16.1 | 10.6
| 2014-04-05 | 13.4 | 16.1 | 10.6
| 2014-04-05 00:30 | 13.4 | 16.1 | 10.6
| 2014-04-05 01:00 | 13.2 | 15.6 | 10.6
| 2014-04-05 01:30 | 12.9 | 15.6 | 10.6
| 2014-04-05 02:00 | 12.5 | 15.6 | 10.6
| 2014-04-05 02:30 | 12.3 | 15.6 | 11.1
| 2014-04-05 03:00 | 12.4 | 15.6 | 11.1
| 2014-04-05 03:30 | 11.7 | 15 | 11.1
| 2014-04-05 04:00 | 11.9 | 15 | 11.1
| 2014-04-05 04:30 | 11.4 | 15 | 11.1
| 2014-04-05 05:00 | 10.7 | 15 | 11.1
| 2014-04-05 05:30 | 10 | 15 | 11.1
| 2014-04-05 06:00 | 9.7 | 14.4 | 11.1
| 2014-04-05 06:30 | 9.7 | 14.4 | 11.1
| 2014-04-05 07:00 | 9.9 | 14.4 | 11.1
| 2014-04-05 07:30 | 10 | 14.4 | 11.1
| 2014-04-05 08:00 | 10.1 | 13.9 | 11.1
| 2014-04-05 08:30 | 10.7 | 13.9 | 11.1
| 2014-04-05 09:00 | 11.3 | 13.9 | 11.1
| 2014-04-05 09:30 | 11.8 | 13.9 | 11.1
| 2014-04-05 10:00 | 12.2 | 13.9 | 11.1
| 2014-04-05 10:30 | 12.3 | 13.9 | 11.1
| 2014-04-05 11:00 | 12.7 | 13.9 | 11.1
| 2014-04-05 11:30 | 13 | 13.9 | 11.1
| 2014-04-05 12:00 | 13.1 | 13.9 | 11.1
| 2014-04-05 12:30 | 13.5 | 13.9 | 11.1
| 2014-04-05 13:00 | 14.6 | 13.9 | 11.1
| 2014-04-05 13:30 | 15.4 | 13.9 | 11.1
| 2014-04-05 14:00 | 15.5 | 13.9 | 11.1
| 2014-04-05 14:30 | 15.8 | 13.9 | 11.1
| 2014-04-05 15:00 | 15.3 | 13.9 | 11.1
| 2014-04-05 15:30 | 15.7 | 14.4 | 11.1
| 2014-04-05 16:00 | 16.2 | 14.4 | 11.1
| 2014-04-05 16:30 | 16 | 14.4 | 11.1
| 2014-04-05 17:00 | 15.8 | 14.4 | 11.1
| 2014-04-05 17:30 | 15.4 | 14.4 | 11.1
| 2014-04-05 18:00 | 15.3 | 14.4 | 11.1
| 2014-04-05 18:30 | 15.1 | 15 | 11.1
| 2014-04-05 19:00 | 14.8 | 15 | 11.1
| 2014-04-05 19:30 | 14.6 | 15 | 11.1
| 2014-04-05 20:00 | 14.4 | 15 | 11.1
| 2014-04-05 20:30 | 14.1 | 15 | 11.1
| 2014-04-05 21:00 | 13.7 | 14.4 | 11.1
| 2014-04-05 21:30 | 13.6 | 14.4 | 11.1
| 2014-04-05 22:00 | 13.7 | 14.4 | 11.1
| 2014-04-05 22:30 | 13.4 | 14.4 | 11.1
| 2014-04-05 23:00 | 12.9 | 14.4 | 11.1
| 2014-04-05 23:30 | 12.6 | 14.4 | 11.1
| 2014-04-06 | 12.3 | 14.4 | 11.1
| 2014-04-06 00:30 | 12.2 | 14.4 | 11.1
| 2014-04-06 01:00 | 11.8 | 13.9 | 11.1
| 2014-04-06 01:30 | 11.3 | 13.9 | 11.1
| 2014-04-06 02:00 | 11.1 | 13.9 | 11.1
| 2014-04-06 02:30 | 11 | 13.9 | 11.1
| 2014-04-06 03:00 | 10.4 | 13.9 | 11.1
| 2014-04-06 03:30 | 9.7 | 13.9 | 11.1
| 2014-04-06 04:00 | 9.2 | 13.9 | 11.1
| 2014-04-06 04:30 | 8.8 | 13.9 | 11.1
| 2014-04-06 05:00 | 8.6 | 13.3 | 11.1
| 2014-04-06 05:30 | 8.2 | 13.3 | 11.1
| 2014-04-06 06:00 | 8.1 | 13.3 | 11.1
| 2014-04-06 06:30 | 7.8 | 13.3 | 11.1
| 2014-04-06 07:00 | 7.1 | 13.3 | 11.1
| 2014-04-06 07:30 | 7.8 | 12.8 | 11.1
| 2014-04-06 08:00 | 8.7 | 12.8 | 11.1
| 2014-04-06 08:30 | 8.9 | 12.8 | 11.1
| 2014-04-06 09:00 | 9.9 | 12.8 | 11.1
| 2014-04-06 09:30 | 10.7 | 12.8 | 11.1
| 2014-04-06 10:00 | 12 | 12.8 | 11.1
| 2014-04-06 10:30 | 14 | 12.8 | 11.1
| 2014-04-06 11:00 | 15.2 | 12.8 | 11.1
| 2014-04-06 11:30 | 16.3 | 12.8 | 11.1
| 2014-04-06 12:00 | 17.2 | 12.8 | 11.1
| 2014-04-06 12:30 | 17.9 | 12.8 | 11.1
| 2014-04-06 13:00 | 18.8 | 12.8 | 11.1
| 2014-04-06 13:30 | 19.4 | 13.3 | 11.1
| 2014-04-06 14:00 | 18.6 | 13.3 | 11.1
| 2014-04-06 14:30 | 18.9 | 13.9 | 11.1
| 2014-04-06 15:00 | 20.2 | 13.9 | 11.1
| 2014-04-06 15:30 | 20.3 | 13.9 | 11.1
| 2014-04-06 16:00 | 20.6 | 14.4 | 11.1
| 2014-04-06 16:30 | 21.1 | 14.4 | 11.1
| 2014-04-06 17:00 | 20.7 | 15 | 11.1
| 2014-04-06 17:30 | 20.9 | 15 | 11.1
| 2014-04-06 18:00 | 20.1 | 15.6 | 11.1
| 2014-04-06 18:30 | 19.5 | 15.6 | 11.1
| 2014-04-06 19:00 | 18.9 | 15.6 | 11.1
| 2014-04-06 19:30 | 18.1 | 16.1 | 11.1
| 2014-04-06 20:00 | 17.3 | 16.1 | 11.1
| 2014-04-06 20:30 | 16.5 | 16.1 | 11.1
| 2014-04-06 21:00 | 15.3 | 16.1 | 11.1
| 2014-04-06 21:30 | 14.3 | 16.1 | 11.1
| 2014-04-06 22:00 | 15.4 | 16.1 | 11.1
| 2014-04-06 22:30 | 15.7 | 16.1 | 11.1
| 2014-04-06 23:00 | 14.1 | 15.6 | 11.1
| 2014-04-06 23:30 | 13.1 | 15.6 | 11.1
| 2014-04-07 | 12.1 | 15.6 | 11.1
| 2014-04-07 00:30 | 11.2 | 15.6 | 11.1
| 2014-04-07 01:00 | 10.8 | 15.6 | 11.1
| 2014-04-07 01:30 | 10.6 | 15 | 11.1
| 2014-04-07 02:00 | 10.4 | 15 | 11.1
| 2014-04-07 02:30 | 10.1 | 15 | 11.1
| 2014-04-07 03:00 | 9.9 | 15 | 11.1
| 2014-04-07 03:30 | 9.3 | 14.4 | 11.1
| 2014-04-07 04:00 | 8.7 | 14.4 | 11.1
| 2014-04-07 04:30 | 8.6 | 14.4 | 11.1
| 2014-04-07 05:00 | 8.7 | 14.4 | 11.1
| 2014-04-07 05:30 | 8.9 | 13.9 | 11.1
| 2014-04-07 06:00 | 9 | 13.9 | 11.1
| 2014-04-07 06:30 | 8.7 | 13.9 | 11.1
| 2014-04-07 07:00 | 8.9 | 13.9 | 11.1
| 2014-04-07 07:30 | 9.8 | 13.3 | 11.1
| 2014-04-07 08:00 | 10.3 | 13.3 | 11.1
| 2014-04-07 08:30 | 10.8 | 13.3 | 11.1
| 2014-04-07 09:00 | 11.6 | 13.3 | 11.1
| 2014-04-07 09:30 | 13.6 | 13.3 | 11.7
| 2014-04-07 10:00 | 16 | 13.3 | 11.7
| 2014-04-07 10:30 | 17 | 13.3 | 11.7
| 2014-04-07 11:00 | 18.4 | 13.3 | 11.7
| 2014-04-07 11:30 | 19.1 | 13.3 | 11.7
| 2014-04-07 12:00 | 19.8 | 13.3 | 11.7
| 2014-04-07 12:30 | 20.2 | 13.3 | 11.7
| 2014-04-07 13:00 | 20.8 | 13.9 | 11.7
| 2014-04-07 13:30 | 21.3 | 13.9 | 11.7
| 2014-04-07 14:00 | 21.2 | 14.4 | 11.7
| 2014-04-07 14:30 | 20.8 | 14.4 | 11.7
| 2014-04-07 15:00 | 21.1 | 15 | 11.7
| 2014-04-07 15:30 | 21.5 | 15 | 11.7
| 2014-04-07 16:00 | 21.7 | 15.6 | 11.7
| 2014-04-07 16:30 | 21.9 | 15.6 | 11.7
| 2014-04-07 17:00 | 21.9 | 16.1 | 11.7
| 2014-04-07 17:30 | 21.3 | 16.1 | 11.7
| 2014-04-07 18:00 | 21.3 | 16.1 | 11.7
| 2014-04-07 18:30 | 21.9 | 16.7 | 11.7
| 2014-04-07 19:00 | 21.2 | 16.7 | 11.7
| 2014-04-07 19:30 | 19.6 | 16.7 | 11.7
| 2014-04-07 20:00 | 18.4 | 16.7 | 11.7
| 2014-04-07 20:30 | 17 | 16.7 | 11.7
| 2014-04-07 21:00 | 16.2 | 16.7 | 11.7
| 2014-04-07 21:30 | 15.4 | 16.7 | 11.7
| 2014-04-07 22:00 | 15.6 | 16.7 | 11.7
| 2014-04-07 22:30 | 15.3 | 16.7 | 11.7
| 2014-04-07 23:00 | 15.2 | 16.7 | 11.7
| 2014-04-07 23:30 | 16.3 | 16.7 | 11.7
| 2014-04-08 | 16.8 | 16.1 | 11.7
| 2014-04-08 00:30 | 16.9 | 16.1 | 11.7
| 2014-04-08 01:00 | 17 | 16.1 | 11.7
| 2014-04-08 01:30 | 16.8 | 16.1 | 11.7
| 2014-04-08 02:00 | 15.6 | 16.1 | 11.7
| 2014-04-08 02:30 | 15.7 | 15.6 | 11.7
| 2014-04-08 03:00 | 14.9 | 15.6 | 11.7
| 2014-04-08 03:30 | 13.7 | 15.6 | 11.7
| 2014-04-08 04:00 | 13.2 | 15.6 | 11.7
| 2014-04-08 04:30 | 13.7 | 15.6 | 11.7
| 2014-04-08 05:00 | 13.8 | 15.6 | 11.7
| 2014-04-08 05:30 | 13.9 | 15 | 11.7
| 2014-04-08 06:00 | 13.3 | 15 | 11.7
| 2014-04-08 06:30 | 12.8 | 15 | 11.7
| 2014-04-08 07:00 | 13.1 | 15 | 11.7
| 2014-04-08 07:30 | 13.4 | 15 | 11.7
| 2014-04-08 08:00 | 14 | 15 | 11.7
| 2014-04-08 08:30 | 13.7 | 14.4 | 11.7
| 2014-04-08 09:00 | 13.6 | 14.4 | 11.7
| 2014-04-08 09:30 | 13.4 | 14.4 | 11.7
| 2014-04-08 10:00 | 13.1 | 14.4 | 11.7
| 2014-04-08 10:30 | 13.1 | 14.4 | 11.7
| 2014-04-08 11:00 | 12.8 | 13.9 | 11.7
| 2014-04-08 11:30 | 13.8 | 13.9 | 11.7
| 2014-04-08 12:00 | 13.2 | 13.9 | 11.7
| 2014-04-08 12:30 | 14.3 | 13.9 | 11.7
| 2014-04-08 13:00 | 13.7 | 13.9 | 11.7
| 2014-04-08 13:30 | 14.7 | 13.9 | 11.7
| 2014-04-08 14:00 | 15.4 | 13.9 | 11.7
| 2014-04-08 14:30 | 13.3 | 13.9 | 11.7
| 2014-04-08 15:00 | 13.6 | 14.4 | 11.7
| 2014-04-08 15:30 | 14.4 | 14.4 | 11.7
| 2014-04-08 16:00 | 14.1 | 14.4 | 11.7
| 2014-04-08 16:30 | 13.2 | 14.4 | 11.7
| 2014-04-08 17:00 | 13.6 | 14.4 | 11.7
| 2014-04-08 17:30 | 13.2 | 14.4 | 11.7
| 2014-04-08 18:00 | 13.1 | 14.4 | 11.7
| 2014-04-08 18:30 | 12.8 | 14.4 | 11.7
| 2014-04-08 19:00 | 12.1 | 14.4 | 11.7
| 2014-04-08 19:30 | 11.6 | 14.4 | 11.7
| 2014-04-08 20:00 | 10.9 | 14.4 | 11.7
| 2014-04-08 20:30 | 10.2 | 14.4 | 11.7
| 2014-04-08 21:00 | 10.2 | 14.4 | 11.7
| 2014-04-08 21:30 | 9.9 | 14.4 | 11.7
| 2014-04-08 22:00 | 9.8 | 13.9 | 11.7
| 2014-04-08 22:30 | 9.1 | 13.9 | 11.7
| 2014-04-08 23:00 | 9.3 | 13.9 | 11.7
| 2014-04-08 23:30 | 9.1 | 13.9 | 11.7
| 2014-04-09 | 8.7 | 13.9 | 11.7
| 2014-04-09 00:30 | 7.7 | 13.3 | 11.7
| 2014-04-09 01:00 | 7.6 | 13.3 | 11.7
| 2014-04-09 01:30 | 7.6 | 13.3 | 11.7
| 2014-04-09 02:00 | 7 | 13.3 | 11.7
| 2014-04-09 02:30 | 6.6 | 13.3 | 11.7
| 2014-04-09 03:00 | 6.1 | 12.8 | 11.7
| 2014-04-09 03:30 | 5.2 | 12.8 | 11.7
| 2014-04-09 04:00 | 5.2 | 12.8 | 11.7
| 2014-04-09 04:30 | 4.9 | 12.8 | 11.7
| 2014-04-09 05:00 | 4.1 | 12.2 | 11.7
| 2014-04-09 05:30 | 3.4 | 12.2 | 11.7
| 2014-04-09 06:00 | 3.2 | 12.2 | 11.7
| 2014-04-09 06:30 | 2.8 | 12.2 | 11.7
| 2014-04-09 07:00 | 2.7 | 11.7 | 11.7
| 2014-04-09 07:30 | 2.6 | 11.7 | 11.7
| 2014-04-09 08:00 | 3.4 | 11.7 | 11.7
| 2014-04-09 08:30 | 5.8 | 11.7 | 11.7
| 2014-04-09 09:00 | 7.3 | 11.7 | 11.7
| 2014-04-09 09:30 | 8.4 | 11.1 | 11.7
| 2014-04-09 10:00 | 9.4 | 11.1 | 11.7
| 2014-04-09 10:30 | 10.3 | 11.1 | 11.7
| 2014-04-09 11:00 | 11.4 | 11.1 | 11.7
| 2014-04-09 11:30 | 12.4 | 11.1 | 11.7
| 2014-04-09 12:00 | 12.5 | 11.1 | 11.7
| 2014-04-09 12:30 | 13.4 | 11.1 | 11.7
| 2014-04-09 13:00 | 13 | 11.1 | 11.7
| 2014-04-09 13:30 | 14.3 | 11.7 | 11.7
| 2014-04-09 14:00 | 14 | 11.7 | 11.7
| 2014-04-09 14:30 | 14.1 | 11.7 | 11.7
| 2014-04-09 15:00 | 14.2 | 12.2 | 11.7
| 2014-04-09 15:30 | 13.6 | 12.2 | 11.7
| 2014-04-09 16:00 | 14.2 | 12.8 | 11.7
| 2014-04-09 16:30 | 14.3 | 12.8 | 11.7
| 2014-04-09 17:00 | 14.4 | 13.3 | 11.7
| 2014-04-09 17:30 | 14.2 | 13.3 | 11.7
| 2014-04-09 18:00 | 13.9 | 13.3 | 11.7
| 2014-04-09 18:30 | 13.8 | 13.3 | 11.7
| 2014-04-09 19:00 | 14.1 | 13.9 | 11.7
| 2014-04-09 19:30 | 13.6 | 13.9 | 11.7
| 2014-04-09 20:00 | 13.1 | 13.9 | 11.7
| 2014-04-09 20:30 | 11.7 | 13.9 | 11.7
| 2014-04-09 21:00 | 10.9 | 13.9 | 11.7
| 2014-04-09 21:30 | 10.4 | 13.9 | 11.7
| 2014-04-09 22:00 | 10.3 | 13.9 | 11.7
| 2014-04-09 22:30 | 10.1 | 13.3 | 11.7
| 2014-04-09 23:00 | 9.9 | 13.3 | 11.7
| 2014-04-09 23:30 | 9.8 | 13.3 | 11.7
| 2014-04-10 | 9.6 | 13.3 | 11.7
| 2014-04-10 00:30 | 10.7 | 13.3 | 11.7
| 2014-04-10 01:00 | 10.2 | 13.3 | 11.7
| 2014-04-10 01:30 | 10.6 | 13.3 | 11.7
| 2014-04-10 02:00 | 10.8 | 13.3 | 11.7
| 2014-04-10 02:30 | 10.5 | 12.8 | 11.7
| 2014-04-10 03:00 | 10.3 | 12.8 | 11.7
| 2014-04-10 03:30 | 10.3 | 12.8 | 11.7
| 2014-04-10 04:00 | 10.2 | 12.8 | 11.7
| 2014-04-10 04:30 | 10.4 | 12.8 | 11.7
| 2014-04-10 05:00 | 10.1 | 12.8 | 11.7
| 2014-04-10 05:30 | 10.5 | 12.8 | 11.7
| 2014-04-10 06:00 | 11.1 | 12.8 | 11.7
| 2014-04-10 06:30 | 9.9 | 12.2 | 11.7
| 2014-04-10 07:00 | 10.2 | 12.2 | 11.7
| 2014-04-10 07:30 | 9.7 | 12.2 | 11.7
| 2014-04-10 08:00 | 10 | 12.2 | 11.7
| 2014-04-10 08:30 | 10.4 | 12.2 | 11.7
| 2014-04-10 09:00 | 10.7 | 12.2 | 11.7
| 2014-04-10 09:30 | 11 | 12.2 | 11.7
| 2014-04-10 10:00 | 11.3 | 12.2 | 11.7
| 2014-04-10 10:30 | 11.9 | 12.2 | 11.7
| 2014-04-10 11:00 | 12.7 | 12.2 | 11.7
| 2014-04-10 11:30 | 12.8 | 12.2 | 11.7
| 2014-04-10 12:00 | 13.8 | 12.2 | 11.7
| 2014-04-10 12:30 | 14.7 | 12.2 | 11.7
| 2014-04-10 13:00 | 14.3 | 12.2 | 11.7
| 2014-04-10 13:30 | 14.9 | 12.8 | 11.7
| 2014-04-10 14:00 | 15.6 | 12.8 | 11.7
| 2014-04-10 14:30 | 15.6 | 12.8 | 11.7
| 2014-04-10 15:00 | 16.1 | 13.3 | 11.7
| 2014-04-10 15:30 | 16.2 | 13.3 | 11.7
| 2014-04-10 16:00 | 16.3 | 13.9 | 11.7
| 2014-04-10 16:30 | 16.4 | 13.9 | 11.7
| 2014-04-10 17:00 | 16.6 | 14.4 | 11.7
| 2014-04-10 17:30 | 16.7 | 14.4 | 11.7
| 2014-04-10 18:00 | 16.7 | 15 | 11.7
| 2014-04-10 18:30 | 16.3 | 15 | 11.7
| 2014-04-10 19:00 | 16.2 | 15 | 11.7
| 2014-04-10 19:30 | 16 | 15 | 11.7
| 2014-04-10 20:00 | 15.7 | 15 | 11.7
| 2014-04-10 20:30 | 15.2 | 15 | 11.7
| 2014-04-10 21:00 | 14.6 | 15 | 11.7
| 2014-04-10 21:30 | 13.9 | 15 | 11.7
| 2014-04-10 22:00 | 13.6 | 15 | 11.7
| 2014-04-10 22:30 | 13.3 | 15 | 11.7
| 2014-04-10 23:00 | 13 | 15 | 11.7
| 2014-04-10 23:30 | 12.5 | 15 | 11.7
| 2014-04-11 | 12.2 | 15 | 11.7
| 2014-04-11 00:30 | 11.9 | 15 | 11.7
| 2014-04-11 01:00 | 11.5 | 14.4 | 11.7
| 2014-04-11 01:30 | 11.3 | 14.4 | 11.7
| 2014-04-11 02:00 | 11.2 | 14.4 | 11.7
| 2014-04-11 02:30 | 10.1 | 13.9 | 11.7
| 2014-04-11 03:00 | 10.2 | 13.9 | 11.7
| 2014-04-11 03:30 | 8.4 | 13.9 | 11.7
| 2014-04-11 04:00 | 8.6 | 13.9 | 11.7
| 2014-04-11 04:30 | 9 | 13.3 | 11.7
| 2014-04-11 05:00 | 9.6 | 13.3 | 11.7
| 2014-04-11 05:30 | 10.2 | 13.3 | 11.7
| 2014-04-11 06:00 | 10.1 | 13.3 | 11.7
| 2014-04-11 06:30 | 9.7 | 13.3 | 11.7
| 2014-04-11 07:00 | 9.2 | 13.3 | 11.7
| 2014-04-11 07:30 | 9.3 | 12.8 | 11.7
| 2014-04-11 08:00 | 10 | 12.8 | 11.7
| 2014-04-11 08:30 | 11.7 | 12.8 | 11.7
| 2014-04-11 09:00 | 13.3 | 12.8 | 11.7
| 2014-04-11 09:30 | 14.1 | 12.8 | 11.7
| 2014-04-11 10:00 | 15 | 12.8 | 11.7
| 2014-04-11 10:30 | 15.8 | 12.8 | 11.7
| 2014-04-11 11:00 | 16.6 | 12.2 | 11.7
| 2014-04-11 11:30 | 17.3 | 12.2 | 11.7
| 2014-04-11 12:00 | 17.7 | 12.8 | 11.7
| 2014-04-11 12:30 | 17.6 | 12.8 | 11.7
| 2014-04-11 13:00 | 18.1 | 12.8 | 11.7
| 2014-04-11 13:30 | 18.2 | 13.3 | 11.7
| 2014-04-11 14:00 | 18.6 | 13.3 | 11.7
| 2014-04-11 14:30 | 18.4 | 13.3 | 11.7
| 2014-04-11 15:00 | 18.7 | 13.9 | 11.7
| 2014-04-11 15:30 | 19.4 | 13.9 | 11.7
| 2014-04-11 16:00 | 19.4 | 14.4 | 11.7
| 2014-04-11 16:30 | 19.2 | 14.4 | 11.7
| 2014-04-11 17:00 | 19.4 | 15 | 11.7
| 2014-04-11 17:30 | 19.4 | 15 | 11.7
| 2014-04-11 18:00 | 21.2 | 15.6 | 11.7
| 2014-04-11 18:30 | 20.6 | 15.6 | 11.7
| 2014-04-11 19:00 | 19.3 | 15.6 | 11.7
| 2014-04-11 19:30 | 18.3 | 16.1 | 11.7
| 2014-04-11 20:00 | 17.3 | 16.1 | 11.7
| 2014-04-11 20:30 | 16.2 | 16.1 | 11.7
| 2014-04-11 21:00 | 15.8 | 16.1 | 11.7
| 2014-04-11 21:30 | 15.1 | 16.1 | 11.7
| 2014-04-11 22:00 | 14.6 | 16.1 | 11.7
| 2014-04-11 22:30 | 15.1 | 16.1 | 11.7
| 2014-04-11 23:00 | 14.8 | 16.1 | 11.7
| 2014-04-11 23:30 | 14.4 | 16.1 | 11.7
| 2014-04-12 | 13.5 | 15.6 | 11.7
| 2014-04-12 00:30 | 12.3 | 15.6 | 11.7
| 2014-04-12 01:00 | 11.7 | 15.6 | 11.7
| 2014-04-12 01:30 | 11.2 | 15.6 | 11.7
| 2014-04-12 02:00 | 10.7 | 15.6 | 11.7
| 2014-04-12 02:30 | 10.6 | 15 | 11.7
| 2014-04-12 03:00 | 10.4 | 15 | 11.7
| 2014-04-12 03:30 | 10.4 | 15 | 11.7
| 2014-04-12 04:00 | 10.1 | 15 | 11.7
| 2014-04-12 04:30 | 9.8 | 15 | 11.7
| 2014-04-12 05:00 | 9.7 | 14.4 | 11.7
| 2014-04-12 05:30 | 9.6 | 14.4 | 11.7
| 2014-04-12 06:00 | 9.2 | 14.4 | 11.7
| 2014-04-12 06:30 | 8.7 | 14.4 | 11.7
| 2014-04-12 07:00 | 8.2 | 13.9 | 11.7
| 2014-04-12 07:30 | 8.8 | 13.9 | 11.7
| 2014-04-12 08:00 | 9.2 | 13.9 | 11.7
| 2014-04-12 08:30 | 10.3 | 13.9 | 11.7
| 2014-04-12 09:00 | 11.2 | 13.9 | 11.7
| 2014-04-12 09:30 | 11.9 | 13.3 | 11.7
| 2014-04-12 10:00 | 12.9 | 13.3 | 11.7
| 2014-04-12 10:30 | 14.7 | 13.3 | 11.7
| 2014-04-12 11:00 | 14.6 | 13.3 | 11.7
| 2014-04-12 11:30 | 15.6 | 13.3 | 11.7
| 2014-04-12 12:00 | 16.2 | 13.3 | 11.7
| 2014-04-12 12:30 | 16.8 | 13.3 | 11.7
| 2014-04-12 13:00 | 17.4 | 13.9 | 11.7
| 2014-04-12 13:30 | 18.4 | 13.9 | 11.7
| 2014-04-12 14:00 | 19.6 | 13.9 | 11.7
| 2014-04-12 14:30 | 19.9 | 14.4 | 11.7
| 2014-04-12 15:00 | 19.9 | 15 | 11.7
| 2014-04-12 15:30 | 20.1 | 15 | 11.7
| 2014-04-12 16:00 | 20.4 | 15.6 | 11.7
| 2014-04-12 16:30 | 20.3 | 16.1 | 11.7
| 2014-04-12 17:00 | 20.8 | 16.1 | 11.7
| 2014-04-12 17:30 | 20.1 | 16.7 | 11.7
| 2014-04-12 18:00 | 19.6 | 16.7 | 11.7
| 2014-04-12 18:30 | 18.6 | 17.2 | 11.7
| 2014-04-12 19:00 | 18 | 17.2 | 11.7
| 2014-04-12 19:30 | 17.6 | 17.2 | 11.7
| 2014-04-12 20:00 | 16.9 | 17.2 | 11.7
| 2014-04-12 20:30 | 16.3 | 17.8 | 11.7
| 2014-04-12 21:00 | 15.8 | 17.8 | 11.7
| 2014-04-12 21:30 | 15.2 | 17.2 | 11.7
| 2014-04-12 22:00 | 14.7 | 17.2 | 11.7
| 2014-04-12 22:30 | 14.3 | 17.2 | 11.7
| 2014-04-12 23:00 | 13.9 | 17.2 | 11.7
| 2014-04-12 23:30 | 13.5 | 17.2 | 11.7
| 2014-04-13 | 13.2 | 17.2 | 12.2
| 2014-04-13 00:30 | 13 | 16.7 | 12.2
| 2014-04-13 01:00 | 12.8 | 16.7 | 12.2
| 2014-04-13 01:30 | 12.6 | 16.7 | 12.2
| 2014-04-13 02:00 | 12.5 | 16.7 | 12.2
| 2014-04-13 02:30 | 11.8 | 16.1 | 12.2
| 2014-04-13 03:00 | 12 | 16.1 | 12.2
| 2014-04-13 03:30 | 11.2 | 16.1 | 12.2
| 2014-04-13 04:00 | 10.7 | 16.1 | 12.2
| 2014-04-13 04:30 | 10.9 | 16.1 | 12.2
| 2014-04-13 05:00 | 8.7 | 15.6 | 12.2
| 2014-04-13 05:30 | 7.2 | 15.6 | 12.2
| 2014-04-13 06:00 | 6.6 | 15.6 | 12.2
| 2014-04-13 06:30 | 6.1 | 15.6 | 12.2
| 2014-04-13 07:00 | 5.7 | 15 | 12.2
| 2014-04-13 07:30 | 5.8 | 15 | 12.2
| 2014-04-13 08:00 | 6.6 | 15 | 12.2
| 2014-04-13 08:30 | 8.2 | 15 | 12.2
| 2014-04-13 09:00 | 10.3 | 14.4 | 12.2
| 2014-04-13 09:30 | 11.8 | 14.4 | 12.2
| 2014-04-13 10:00 | 12.4 | 14.4 | 12.2
| 2014-04-13 10:30 | 12.8 | 14.4 | 12.2
| 2014-04-13 11:00 | 13.5 | 14.4 | 12.2
| 2014-04-13 11:30 | 14.4 | 14.4 | 12.2
| 2014-04-13 12:00 | 15.3 | 14.4 | 12.2
| 2014-04-13 12:30 | 16.2 | 14.4 | 12.2
| 2014-04-13 13:00 | 16.4 | 14.4 | 12.2
| 2014-04-13 13:30 | 16.4 | 14.4 | 12.2
| 2014-04-13 14:00 | 17.3 | 15 | 12.2
| 2014-04-13 14:30 | 17.4 | 15 | 12.2
| 2014-04-13 15:00 | 17.4 | 15.6 | 12.2
| 2014-04-13 15:30 | 17.1 | 15.6 | 12.2
| 2014-04-13 16:00 | 17.4 | 16.1 | 12.2
| 2014-04-13 16:30 | 16.6 | 16.7 | 12.2
| 2014-04-13 17:00 | 16.4 | 16.7 | 12.2
| 2014-04-13 17:30 | 16.3 | 16.7 | 12.2
| 2014-04-13 18:00 | 16.1 | 17.2 | 12.2
| 2014-04-13 18:30 | 15.8 | 17.2 | 12.2
| 2014-04-13 19:00 | 15.3 | 17.2 | 12.2
| 2014-04-13 19:30 | 14.7 | 17.2 | 12.2
| 2014-04-13 20:00 | 13.8 | 17.2 | 12.2
| 2014-04-13 20:30 | 13 | 17.2 | 12.2
| 2014-04-13 21:00 | 11.4 | 17.2 | 12.2
| 2014-04-13 21:30 | 10 | 17.2 | 12.2
| 2014-04-13 22:00 | 9.1 | 17.2 | 12.2
| 2014-04-13 22:30 | 8.3 | 17.2 | 12.2
| 2014-04-13 23:00 | 7.3 | 16.7 | 12.2
| 2014-04-13 23:30 | 6.7 | 16.7 | 12.2
| 2014-04-14 | 6.4 | 16.7 | 12.2
| 2014-04-14 00:30 | 6.1 | 16.1 | 12.2
| 2014-04-14 01:00 | 6.1 | 16.1 | 12.2
| 2014-04-14 01:30 | 5.6 | 16.1 | 12.2
| 2014-04-14 02:00 | 5.3 | 15.6 | 12.2
| 2014-04-14 02:30 | 5.2 | 15.6 | 12.2
| 2014-04-14 03:00 | 5.6 | 15.6 | 12.2
| 2014-04-14 03:30 | 6.9 | 15 | 12.2
| 2014-04-14 04:00 | 6.8 | 15 | 12.2
| 2014-04-14 04:30 | 6.1 | 15 | 12.2
| 2014-04-14 05:00 | 5.4 | 15 | 12.2
| 2014-04-14 05:30 | 4.9 | 14.4 | 12.2
| 2014-04-14 06:00 | 5.1 | 14.4 | 12.2
| 2014-04-14 06:30 | 6.9 | 14.4 | 12.2
| 2014-04-14 07:00 | 7.9 | 14.4 | 12.2
| 2014-04-14 07:30 | 8.7 | 13.9 | 12.2
| 2014-04-14 08:00 | 9.3 | 13.9 | 12.2
| 2014-04-14 08:30 | 9.4 | 13.9 | 12.2
| 2014-04-14 09:00 | 10 | 13.9 | 12.2
| 2014-04-14 09:30 | 10.6 | 13.9 | 12.2
| 2014-04-14 10:00 | 11.2 | 13.3 | 12.2
| 2014-04-14 10:30 | 11.9 | 13.3 | 12.2
| 2014-04-14 11:00 | 12.7 | 13.3 | 12.2
| 2014-04-14 11:30 | 11.2 | 13.3 | 12.2
| 2014-04-14 12:00 | 8.8 | 13.3 | 12.2
| 2014-04-14 12:30 | 11.6 | 13.9 | 12.2
| 2014-04-14 13:00 | 13.6 | 13.9 | 12.2
| 2014-04-14 13:30 | 10.2 | 13.9 | 12.2
| 2014-04-14 14:00 | 12.7 | 13.9 | 12.2
| 2014-04-14 14:30 | 14.1 | 13.9 | 12.2
| 2014-04-14 15:00 | 14.3 | 13.9 | 12.2
| 2014-04-14 15:30 | 14.4 | 14.4 | 12.2
| 2014-04-14 16:00 | 14.1 | 14.4 | 12.2
| 2014-04-14 16:30 | 14.3 | 14.4 | 12.8
| 2014-04-14 17:00 | 14 | 15 | 12.8
| 2014-04-14 17:30 | 12.1 | 15 | 12.8
| 2014-04-14 18:00 | 12.7 | 15 | 12.8
| 2014-04-14 18:30 | 11.8 | 15.6 | 12.8
| 2014-04-14 19:00 | 11.5 | 15.6 | 12.8
| 2014-04-14 19:30 | 11 | 15.6 | 12.8
| 2014-04-14 20:00 | 10.7 | 15.6 | 12.8
| 2014-04-14 20:30 | 10.2 | 15.6 | 12.8
| 2014-04-14 21:00 | 9.4 | 15.6 | 12.8
| 2014-04-14 21:30 | 8.9 | 15.6 | 12.8
| 2014-04-14 22:00 | 8.6 | 15 | 12.8
| 2014-04-14 22:30 | 7.6 | 15 | 12.8
| 2014-04-14 23:00 | 7.2 | 15 | 12.8
| 2014-04-14 23:30 | 6.9 | 15 | 12.8
| 2014-04-15 | 6.1 | 15 | 12.8
| 2014-04-15 00:30 | 5.6 | 14.4 | 12.8
| 2014-04-15 01:00 | 4.4 | 14.4 | 12.8
| 2014-04-15 01:30 | 3.8 | 14.4 | 12.8
| 2014-04-15 02:00 | 3.2 | 14.4 | 12.8
| 2014-04-15 02:30 | 3.2 | 13.9 | 12.8
| 2014-04-15 03:00 | 2.6 | 13.9 | 12.8
| 2014-04-15 03:30 | 4.3 | 13.9 | 12.8
| 2014-04-15 04:00 | 4.3 | 13.9 | 12.8
| 2014-04-15 04:30 | 4.1 | 13.3 | 12.8
| 2014-04-15 05:00 | 4.1 | 13.3 | 12.8
| 2014-04-15 05:30 | 4.3 | 13.3 | 12.8
| 2014-04-15 06:00 | 4.4 | 12.8 | 12.8
| 2014-04-15 06:30 | 4.7 | 12.8 | 12.8
| 2014-04-15 07:00 | 4.8 | 12.8 | 12.8
| 2014-04-15 07:30 | 5 | 12.8 | 12.8
| 2014-04-15 08:00 | 5.3 | 12.8 | 12.8
| 2014-04-15 08:30 | 5.7 | 12.2 | 12.8
| 2014-04-15 09:00 | 5.9 | 12.2 | 12.8
| 2014-04-15 09:30 | 6.3 | 12.2 | 12.8
| 2014-04-15 10:00 | 6.9 | 12.2 | 12.8
| 2014-04-15 10:30 | 7.1 | 12.2 | 12.8
| 2014-04-15 11:00 | 7.5 | 12.2 | 12.8
| 2014-04-15 11:30 | 7.9 | 12.2 | 12.8
| 2014-04-15 12:00 | 8.2 | 12.2 | 12.8
| 2014-04-15 12:30 | 7.8 | 12.2 | 12.8
| 2014-04-15 13:00 | 8 | 12.2 | 12.8
| 2014-04-15 13:30 | 8.6 | 12.2 | 12.8
| 2014-04-15 14:00 | 8.7 | 12.8 | 12.8
| 2014-04-15 14:30 | 8.9 | 12.8 | 12.8
| 2014-04-15 15:00 | 9.7 | 12.8 | 12.8
| 2014-04-15 15:30 | 9.7 | 12.8 | 12.8
| 2014-04-15 16:00 | 9.6 | 12.8 | 12.8
| 2014-04-15 16:30 | 9.9 | 12.8 | 12.8
| 2014-04-15 17:00 | 9.3 | 13.3 | 12.8
| 2014-04-15 17:30 | 9.6 | 13.3 | 12.8
| 2014-04-15 18:00 | 9.3 | 13.3 | 12.8
| 2014-04-15 18:30 | 9.2 | 13.3 | 12.8
| 2014-04-15 19:00 | 9.1 | 13.3 | 12.8
| 2014-04-15 19:30 | 9.1 | 13.3 | 12.8
| 2014-04-15 20:00 | 8.7 | 13.3 | 12.8
| 2014-04-15 20:30 | 8.3 | 13.3 | 12.8
| 2014-04-15 21:00 | 7.9 | 13.3 | 12.8
| 2014-04-15 21:30 | 7.8 | 13.3 | 12.8
| 2014-04-15 22:00 | 7.6 | 13.3 | 12.8
| 2014-04-15 22:30 | 7.2 | 13.3 | 12.8
| 2014-04-15 23:00 | 6.8 | 13.3 | 12.8
| 2014-04-15 23:30 | 6.2 | 13.3 | 12.8
| 2014-04-16 | 5.3 | 12.8 | 12.8
| 2014-04-16 00:30 | 4.1 | 12.8 | 12.8
| 2014-04-16 01:00 | 3.1 | 12.8 | 12.8
| 2014-04-16 01:30 | 2.3 | 12.8 | 12.8
| 2014-04-16 02:00 | 1.6 | 12.8 | 12.8
| 2014-04-16 02:30 | 1.2 | 12.8 | 12.8
| 2014-04-16 03:00 | 0.7 | 12.2 | 12.2
| 2014-04-16 03:30 | 0.4 | 12.2 | 12.2
| 2014-04-16 04:00 | -0.3 | 12.2 | 12.2
| 2014-04-16 04:30 | -0.2 | 11.7 | 12.2
| 2014-04-16 05:00 | 0.1 | 11.7 | 12.2
| 2014-04-16 05:30 | 0.4 | 11.7 | 12.2
| 2014-04-16 06:00 | 0.3 | 11.7 | 12.2
| 2014-04-16 06:30 | 0.3 | 11.1 | 12.2
| 2014-04-16 07:00 | 0.2 | 11.1 | 12.2
| 2014-04-16 07:30 | 0.7 | 11.1 | 12.2
| 2014-04-16 08:00 | 2.7 | 11.1 | 12.2
| 2014-04-16 08:30 | 4 | 10.6 | 12.2
| 2014-04-16 09:00 | 5.3 | 10.6 | 12.2
| 2014-04-16 09:30 | 7.1 | 10.6 | 12.2
| 2014-04-16 10:00 | 8.1 | 10.6 | 12.2
| 2014-04-16 10:30 | 9.8 | 10.6 | 12.2
| 2014-04-16 11:00 | 10.7 | 10.6 | 12.2
| 2014-04-16 11:30 | 11.8 | 10.6 | 12.2
| 2014-04-16 12:00 | 12.9 | 10.6 | 12.2
| 2014-04-16 12:30 | 12.4 | 10.6 | 12.2
| 2014-04-16 13:00 | 11.7 | 10.6 | 12.2
| 2014-04-16 13:30 | 12.3 | 11.1 | 12.2
| 2014-04-16 14:00 | 13.7 | 11.1 | 12.2
| 2014-04-16 14:30 | 13.2 | 11.7 | 12.2
| 2014-04-16 15:00 | 13.7 | 11.7 | 12.2
| 2014-04-16 15:30 | 15.7 | 12.2 | 12.2
| 2014-04-16 16:00 | 15.8 | 12.2 | 12.2
| 2014-04-16 16:30 | 13.7 | 12.8 | 12.2
| 2014-04-16 17:00 | 14.8 | 13.3 | 12.2
| 2014-04-16 17:30 | 14.4 | 13.3 | 12.2
| 2014-04-16 18:00 | 16 | 13.3 | 12.2
| 2014-04-16 18:30 | 14.8 | 13.9 | 12.2
| 2014-04-16 19:00 | 14.3 | 13.9 | 12.2
| 2014-04-16 19:30 | 13.8 | 13.9 | 12.2
| 2014-04-16 20:00 | 12.6 | 13.9 | 12.2
| 2014-04-16 20:30 | 10.9 | 14.4 | 12.2
| 2014-04-16 21:00 | 9.4 | 14.4 | 12.2
| 2014-04-16 21:30 | 8.2 | 14.4 | 12.2
| 2014-04-16 22:00 | 7.4 | 13.9 | 12.2
| 2014-04-16 22:30 | 6.6 | 13.9 | 12.2
| 2014-04-16 23:00 | 5.9 | 13.9 | 12.2
| 2014-04-16 23:30 | 5.6 | 13.9 | 12.2
| 2014-04-17 | 5.2 | 13.9 | 12.2
| 2014-04-17 00:30 | 4.9 | 13.3 | 12.2
| 2014-04-17 01:00 | 4.8 | 13.3 | 12.2
| 2014-04-17 01:30 | 4.8 | 13.3 | 12.2
| 2014-04-17 02:00 | 5 | 13.3 | 12.2
| 2014-04-17 02:30 | 4.8 | 12.8 | 12.2
| 2014-04-17 03:00 | 4.2 | 12.8 | 12.2
| 2014-04-17 03:30 | 3.5 | 12.8 | 12.2
| 2014-04-17 04:00 | 3.4 | 12.8 | 12.2
| 2014-04-17 04:30 | 1.6 | 12.2 | 12.2
| 2014-04-17 05:00 | 1.2 | 12.2 | 12.2
| 2014-04-17 05:30 | 1.3 | 12.2 | 12.2
| 2014-04-17 06:00 | 1.1 | 11.7 | 12.2
| 2014-04-17 06:30 | 1.1 | 11.7 | 12.2
| 2014-04-17 07:00 | 1 | 11.7 | 12.2
| 2014-04-17 07:30 | 1.3 | 11.7 | 12.2
| 2014-04-17 08:00 | 2.9 | 11.1 | 12.2
| 2014-04-17 08:30 | 5.6 | 11.1 | 12.2
| 2014-04-17 09:00 | 7.8 | 11.1 | 12.2
| 2014-04-17 09:30 | 9.6 | 11.1 | 12.2
| 2014-04-17 10:00 | 10.3 | 10.6 | 12.2
| 2014-04-17 10:30 | 11.3 | 10.6 | 12.2
| 2014-04-17 11:00 | 12.5 | 10.6 | 12.2
| 2014-04-17 11:30 | 13.2 | 10.6 | 12.2
| 2014-04-17 12:00 | 14.1 | 10.6 | 12.2
| 2014-04-17 12:30 | 14.1 | 11.1 | 12.2
| 2014-04-17 13:00 | 14.8 | 11.1 | 12.2
| 2014-04-17 13:30 | 15.5 | 11.1 | 12.2
| 2014-04-17 14:00 | 16.3 | 11.7 | 12.2
| 2014-04-17 14:30 | 16.7 | 11.7 | 12.2
| 2014-04-17 15:00 | 16.7 | 12.2 | 12.2
| 2014-04-17 15:30 | 16.6 | 12.8 | 12.2
| 2014-04-17 16:00 | 17.8 | 13.3 | 12.2
| 2014-04-17 16:30 | 17.7 | 13.3 | 12.2
| 2014-04-17 17:00 | 18 | 13.9 | 12.2
| 2014-04-17 17:30 | 17.8 | 14.4 | 12.2
| 2014-04-17 18:00 | 17.5 | 14.4 | 12.2
| 2014-04-17 18:30 | 17.2 | 15 | 12.2
| 2014-04-17 19:00 | 16.7 | 15 | 12.2
| 2014-04-17 19:30 | 15 | 15 | 12.2
| 2014-04-17 20:00 | 13.3 | 15.6 | 12.2
| 2014-04-17 20:30 | 11.8 | 15.6 | 12.2
| 2014-04-17 21:00 | 10.3 | 15.6 | 12.2
| 2014-04-17 21:30 | 9.3 | 15.6 | 12.2
| 2014-04-17 22:00 | 8.7 | 15.6 | 12.2
| 2014-04-17 22:30 | 8.3 | 15 | 12.2
| 2014-04-17 23:00 | 7.8 | 15 | 12.2
| 2014-04-17 23:30 | 7.7 | 15 | 12.2
| 2014-04-18 | 8.1 | 15 | 12.2
| 2014-04-18 00:30 | 8.9 | 15 | 12.2
| 2014-04-18 01:00 | 9.7 | 14.4 | 12.2
| 2014-04-18 01:30 | 10.6 | 14.4 | 12.2
| 2014-04-18 02:00 | 10.8 | 14.4 | 12.2
| 2014-04-18 02:30 | 10.7 | 14.4 | 12.2
| 2014-04-18 03:00 | 10.3 | 13.9 | 12.2
| 2014-04-18 03:30 | 9.4 | 13.9 | 12.2
| 2014-04-18 04:00 | 9.7 | 13.9 | 12.2
| 2014-04-18 04:30 | 8.6 | 13.9 | 12.2
| 2014-04-18 05:00 | 7.9 | 13.9 | 12.2
| 2014-04-18 05:30 | 9.2 | 13.9 | 12.2
| 2014-04-18 06:00 | 9.2 | 13.3 | 12.2
| 2014-04-18 06:30 | 9.6 | 13.3 | 12.2
| 2014-04-18 07:00 | 8.5 | 13.3 | 12.2
| 2014-04-18 07:30 | 7.8 | 13.3 | 12.2
| 2014-04-18 08:00 | 7.8 | 13.3 | 12.2
| 2014-04-18 08:30 | 8.2 | 13.3 | 12.2
| 2014-04-18 09:00 | 8.4 | 13.3 | 12.2
| 2014-04-18 09:30 | 9.2 | 12.8 | 12.2
| 2014-04-18 10:00 | 9.7 | 12.8 | 12.2
| 2014-04-18 10:30 | 9.6 | 12.8 | 12.2
| 2014-04-18 11:00 | 10.8 | 12.8 | 12.2
| 2014-04-18 11:30 | 11 | 12.8 | 12.2
| 2014-04-18 12:00 | 12.6 | 12.8 | 12.2
| 2014-04-18 12:30 | 10.6 | 12.8 | 12.2
| 2014-04-18 13:00 | 11.2 | 12.8 | 12.2
| 2014-04-18 13:30 | 12.2 | 13.3 | 12.2
| 2014-04-18 14:00 | 12.2 | 13.3 | 12.2
| 2014-04-18 14:30 | 12.7 | 13.3 | 12.2
| 2014-04-18 15:00 | 10.6 | 13.3 | 12.2
| 2014-04-18 15:30 | 11.4 | 13.3 | 12.2
| 2014-04-18 16:00 | 13.8 | 13.9 | 12.2
| 2014-04-18 16:30 | 12.9 | 13.9 | 12.2
| 2014-04-18 17:00 | 13.6 | 13.9 | 12.2
| 2014-04-18 17:30 | 13.2 | 13.9 | 12.2
| 2014-04-18 18:00 | 14.3 | 13.9 | 12.2
| 2014-04-18 18:30 | 12.9 | 14.4 | 12.2
| 2014-04-18 19:00 | 12.8 | 14.4 | 12.2
| 2014-04-18 19:30 | 12.1 | 14.4 | 12.2
| 2014-04-18 20:00 | 11.9 | 14.4 | 12.2
| 2014-04-18 20:30 | 10.6 | 14.4 | 12.2
| 2014-04-18 21:00 | 9.1 | 14.4 | 12.2
| 2014-04-18 21:30 | 7.3 | 14.4 | 12.2
| 2014-04-18 22:00 | 5.9 | 14.4 | 12.2
| 2014-04-18 22:30 | 5.4 | 14.4 | 12.2
| 2014-04-18 23:00 | 4.8 | 14.4 | 12.2
| 2014-04-18 23:30 | 4.9 | 13.9 | 12.2
| 2014-04-19 | 5.3 | 13.9 | 12.2
| 2014-04-19 00:30 | 4.8 | 13.9 | 12.2
| 2014-04-19 01:00 | 3.9 | 13.9 | 12.2
| 2014-04-19 01:30 | 2.9 | 13.3 | 12.2
| 2014-04-19 02:00 | 2.4 | 13.3 | 12.2
| 2014-04-19 02:30 | 2.2 | 13.3 | 12.2
| 2014-04-19 03:00 | 2.4 | 13.3 | 12.2
| 2014-04-19 03:30 | 3 | 12.8 | 12.2
| 2014-04-19 04:00 | 3.7 | 12.8 | 12.2
| 2014-04-19 04:30 | 3.9 | 12.8 | 12.2
| 2014-04-19 05:00 | 3.8 | 12.8 | 12.2
| 2014-04-19 05:30 | 3.8 | 12.2 | 12.2
| 2014-04-19 06:00 | 3.8 | 12.2 | 12.2
| 2014-04-19 06:30 | 4 | 12.2 | 12.2
| 2014-04-19 07:00 | 4.1 | 12.2 | 12.2
| 2014-04-19 07:30 | 4.7 | 11.7 | 12.2
| 2014-04-19 08:00 | 5 | 11.7 | 12.2
| 2014-04-19 08:30 | 6 | 11.7 | 12.2
| 2014-04-19 09:00 | 6.8 | 11.7 | 12.2
| 2014-04-19 09:30 | 7 | 11.7 | 12.2
| 2014-04-19 10:00 | 7.5 | 11.7 | 12.2
| 2014-04-19 10:30 | 9.8 | 11.7 | 12.2
| 2014-04-19 11:00 | 10.7 | 11.7 | 12.2
| 2014-04-19 11:30 | 11.2 | 11.7 | 12.2
| 2014-04-19 12:00 | 12.7 | 11.7 | 12.2
| 2014-04-19 12:30 | 13.7 | 11.7 | 12.2
| 2014-04-19 13:00 | 14.5 | 11.7 | 12.2
| 2014-04-19 13:30 | 15.9 | 12.2 | 12.2
| 2014-04-19 14:00 | 16.4 | 12.2 | 12.2
| 2014-04-19 14:30 | 17.9 | 12.8 | 12.2
| 2014-04-19 15:00 | 18.9 | 13.3 | 12.2
| 2014-04-19 15:30 | 19.2 | 13.3 | 12.2
| 2014-04-19 16:00 | 20.2 | 13.9 | 12.2
| 2014-04-19 16:30 | 19.4 | 14.4 | 12.2
| 2014-04-19 17:00 | 17.9 | 14.4 | 12.2
| 2014-04-19 17:30 | 18.3 | 15 | 12.2
| 2014-04-19 18:00 | 18.4 | 15 | 12.2
| 2014-04-19 18:30 | 18.3 | 15.6 | 12.2
| 2014-04-19 19:00 | 18.8 | 15.6 | 12.2
| 2014-04-19 19:30 | 17.6 | 16.1 | 12.2
| 2014-04-19 20:00 | 16.3 | 16.1 | 12.2
| 2014-04-19 20:30 | 15.2 | 16.1 | 12.2
| 2014-04-19 21:00 | 14.1 | 16.1 | 12.2
| 2014-04-19 21:30 | 13.4 | 16.1 | 12.2
| 2014-04-19 22:00 | 13.2 | 16.1 | 12.2
| 2014-04-19 22:30 | 12.6 | 16.1 | 12.2
| 2014-04-19 23:00 | 12.1 | 16.1 | 12.2
| 2014-04-19 23:30 | 11.7 | 15.6 | 12.2
| 2014-04-20 | 11.4 | 15.6 | 12.2
| 2014-04-20 00:30 | 11.6 | 15.6 | 12.2
| 2014-04-20 01:00 | 11.2 | 15.6 | 12.2
| 2014-04-20 01:30 | 10.4 | 15 | 12.2
| 2014-04-20 02:00 | 10 | 15 | 12.2
| 2014-04-20 02:30 | 10.7 | 15 | 12.2
| 2014-04-20 03:00 | 11 | 15 | 12.2
| 2014-04-20 03:30 | 10.6 | 15 | 12.2
| 2014-04-20 04:00 | 9.8 | 14.4 | 12.2
| 2014-04-20 04:30 | 8.9 | 14.4 | 12.2
| 2014-04-20 05:00 | 8.9 | 14.4 | 12.2
| 2014-04-20 05:30 | 7.9 | 14.4 | 12.2
| 2014-04-20 06:00 | 8.6 | 13.9 | 12.2
| 2014-04-20 06:30 | 8.5 | 13.9 | 12.2
| 2014-04-20 07:00 | 8.4 | 13.9 | 12.2
| 2014-04-20 07:30 | 8 | 13.9 | 12.2
| 2014-04-20 08:00 | 8.6 | 13.9 | 12.2
| 2014-04-20 08:30 | 10.9 | 13.3 | 12.2
| 2014-04-20 09:00 | 13.3 | 13.3 | 12.2
| 2014-04-20 09:30 | 15.2 | 13.3 | 12.2
| 2014-04-20 10:00 | 16.6 | 13.3 | 12.2
| 2014-04-20 10:30 | 17.8 | 13.3 | 12.2
| 2014-04-20 11:00 | 18.8 | 13.3 | 12.2
| 2014-04-20 11:30 | 19.2 | 13.3 | 12.2
| 2014-04-20 12:00 | 20.8 | 13.3 | 12.2
| 2014-04-20 12:30 | 21.2 | 13.3 | 12.2
| 2014-04-20 13:00 | 21.4 | 13.9 | 12.2
| 2014-04-20 13:30 | 22.1 | 13.9 | 12.2
| 2014-04-20 14:00 | 21.1 | 14.4 | 12.2
| 2014-04-20 14:30 | 20.7 | 14.4 | 12.2
| 2014-04-20 15:00 | 22.3 | 15 | 12.2
| 2014-04-20 15:30 | 23.3 | 15 | 12.2
| 2014-04-20 16:00 | 22.2 | 15.6 | 12.2
| 2014-04-20 16:30 | 22.5 | 16.1 | 12.2
| 2014-04-20 17:00 | 21.9 | 16.1 | 12.2
| 2014-04-20 17:30 | 20.8 | 16.7 | 12.2
| 2014-04-20 18:00 | 21.9 | 16.7 | 12.2
| 2014-04-20 18:30 | 22.6 | 17.2 | 12.2
| 2014-04-20 19:00 | 20.9 | 17.2 | 12.2
| 2014-04-20 19:30 | 19.2 | 17.2 | 12.2
| 2014-04-20 20:00 | 17.9 | 17.8 | 12.2
| 2014-04-20 20:30 | 16.7 | 17.8 | 12.2
| 2014-04-20 21:00 | 15.3 | 17.8 | 12.2
| 2014-04-20 21:30 | 14.5 | 17.8 | 12.2
| 2014-04-20 22:00 | 14 | 17.8 | 12.2
| 2014-04-20 22:30 | 13.8 | 17.8 | 12.2
| 2014-04-20 23:00 | 13.4 | 17.2 | 12.2
| 2014-04-20 23:30 | 13.1 | 17.2 | 12.2
| 2014-04-21 | 12.3 | 17.2 | 12.2
| 2014-04-21 00:30 | 11.3 | 17.2 | 12.2
| 2014-04-21 01:00 | 10.4 | 16.7 | 12.2
| 2014-04-21 01:30 | 9.6 | 16.7 | 12.2
| 2014-04-21 02:00 | 9.2 | 16.7 | 12.2
| 2014-04-21 02:30 | 8.6 | 16.7 | 12.2
| 2014-04-21 03:00 | 8.1 | 16.1 | 12.2
| 2014-04-21 03:30 | 7.8 | 16.1 | 12.2
| 2014-04-21 04:00 | 7.5 | 16.1 | 12.2
| 2014-04-21 04:30 | 7.8 | 15.6 | 12.2
| 2014-04-21 05:00 | 7.2 | 15.6 | 12.2
| 2014-04-21 05:30 | 6.3 | 15.6 | 12.2
| 2014-04-21 06:00 | 5.7 | 15 | 12.2
| 2014-04-21 06:30 | 5.4 | 15 | 12.2
| 2014-04-21 07:00 | 5.6 | 15 | 12.2
| 2014-04-21 07:30 | 6.1 | 15 | 12.2
| 2014-04-21 08:00 | 8.2 | 14.4 | 12.2
| 2014-04-21 08:30 | 9.4 | 14.4 | 12.2
| 2014-04-21 09:00 | 11.4 | 14.4 | 12.2
| 2014-04-21 09:30 | 13.4 | 14.4 | 12.2
| 2014-04-21 10:00 | 15.3 | 13.9 | 12.2
| 2014-04-21 10:30 | 16.3 | 13.9 | 12.2
| 2014-04-21 11:00 | 17.1 | 13.9 | 12.2
| 2014-04-21 11:30 | 18 | 13.9 | 12.2
| 2014-04-21 12:00 | 18.3 | 13.9 | 12.2
| 2014-04-21 12:30 | 19.8 | 13.9 | 12.2
| 2014-04-21 13:00 | 19.9 | 14.4 | 12.2
| 2014-04-21 13:30 | 19.3 | 14.4 | 12.2
| 2014-04-21 14:00 | 20.6 | 15 | 12.2
| 2014-04-21 14:30 | 19.4 | 15 | 12.2
| 2014-04-21 15:00 | 21.1 | 15.6 | 12.2
| 2014-04-21 15:30 | 21.9 | 16.1 | 12.2
| 2014-04-21 16:00 | 20.8 | 16.1 | 12.2
| 2014-04-21 16:30 | 20.9 | 16.7 | 12.2
| 2014-04-21 17:00 | 19.9 | 16.7 | 12.2
| 2014-04-21 17:30 | 19.1 | 17.2 | 12.2
| 2014-04-21 18:00 | 18.9 | 17.2 | 12.2
| 2014-04-21 18:30 | 17.1 | 17.8 | 12.2
| 2014-04-21 19:00 | 16.1 | 17.8 | 12.2
| 2014-04-21 19:30 | 15.4 | 17.8 | 12.8
| 2014-04-21 20:00 | 14.5 | 17.8 | 12.8
| 2014-04-21 20:30 | 14.1 | 17.8 | 12.8
| 2014-04-21 21:00 | 13.7 | 17.8 | 12.8
| 2014-04-21 21:30 | 13.3 | 17.8 | 12.8
| 2014-04-21 22:00 | 12.8 | 17.8 | 12.8
| 2014-04-21 22:30 | 11.9 | 17.8 | 12.8
| 2014-04-21 23:00 | 11.7 | 17.2 | 12.8
| 2014-04-21 23:30 | 11.5 | 17.2 | 12.8
| 2014-04-22 | 11.3 | 17.2 | 12.8
| 2014-04-22 00:30 | 11.1 | 17.2 | 12.8
| 2014-04-22 01:00 | 11 | 17.2 | 12.8
| 2014-04-22 01:30 | 10.9 | 16.7 | 12.8
| 2014-04-22 02:00 | 10.9 | 16.7 | 12.8
| 2014-04-22 02:30 | 10.8 | 16.7 | 12.8
| 2014-04-22 03:00 | 10.9 | 16.7 | 12.8
| 2014-04-22 03:30 | 11.1 | 16.1 | 12.8
| 2014-04-22 04:00 | 10.9 | 16.1 | 12.8
| 2014-04-22 04:30 | 10.8 | 16.1 | 12.8
| 2014-04-22 05:00 | 10.7 | 16.1 | 12.8
| 2014-04-22 05:30 | 11 | 16.1 | 12.8
| 2014-04-22 06:00 | 11.2 | 16.1 | 12.8
| 2014-04-22 06:30 | 11.2 | 15.6 | 12.8
| 2014-04-22 07:00 | 11.1 | 15.6 | 12.8
| 2014-04-22 07:30 | 10.9 | 15.6 | 12.8
| 2014-04-22 08:00 | 11.1 | 15.6 | 12.8
| 2014-04-22 08:30 | 11.4 | 15.6 | 12.8
| 2014-04-22 09:00 | 11.9 | 15 | 12.8
| 2014-04-22 09:30 | 12.2 | 15 | 12.8
| 2014-04-22 10:00 | 12.5 | 15 | 12.8
| 2014-04-22 10:30 | 12.9 | 15 | 12.8
| 2014-04-22 11:00 | 13.4 | 15 | 12.8
| 2014-04-22 11:30 | 13.6 | 15 | 12.8
| 2014-04-22 12:00 | 13.9 | 15 | 12.8
| 2014-04-22 12:30 | 14.6 | 15 | 12.8
| 2014-04-22 13:00 | 15.2 | 15 | 12.8
| 2014-04-22 13:30 | 16.3 | 15 | 12.8
| 2014-04-22 14:00 | 16.2 | 15 | 12.8
| 2014-04-22 14:30 | 17.4 | 15 | 12.8
| 2014-04-22 15:00 | 18.6 | 15.6 | 12.8
| 2014-04-22 15:30 | 19.1 | 15.6 | 12.8
| 2014-04-22 16:00 | 18.7 | 15.6 | 12.8
| 2014-04-22 16:30 | 20.2 | 16.1 | 12.8
| 2014-04-22 17:00 | 18.3 | 16.1 | 12.8
| 2014-04-22 17:30 | 17.8 | 16.1 | 12.8
| 2014-04-22 18:00 | 18.8 | 16.7 | 12.8
| 2014-04-22 18:30 | 19.1 | 16.7 | 12.8
| 2014-04-22 19:00 | 17.9 | 17.2 | 12.8
| 2014-04-22 19:30 | 17.9 | 17.2 | 12.8
| 2014-04-22 20:00 | 17.1 | 17.2 | 12.8
| 2014-04-22 20:30 | 15.4 | 17.2 | 12.8
| 2014-04-22 21:00 | 13.7 | 17.2 | 12.8
| 2014-04-22 21:30 | 12.5 | 17.2 | 12.8
| 2014-04-22 22:00 | 11.6 | 17.2 | 12.8
| 2014-04-22 22:30 | 11.1 | 17.2 | 12.8
| 2014-04-22 23:00 | 10.5 | 17.2 | 12.8
| 2014-04-22 23:30 | 9.6 | 16.7 | 12.8
| 2014-04-23 | 9.6 | 16.7 | 12.8
| 2014-04-23 00:30 | 9.4 | 16.7 | 12.8
| 2014-04-23 01:00 | 9 | 16.7 | 12.8
| 2014-04-23 01:30 | 8.9 | 16.1 | 12.8
| 2014-04-23 02:00 | 8.9 | 16.1 | 12.8
| 2014-04-23 02:30 | 8.6 | 16.1 | 12.8
| 2014-04-23 03:00 | 8.5 | 16.1 | 12.8
| 2014-04-23 03:30 | 8.6 | 15.6 | 12.8
| 2014-04-23 04:00 | 7.9 | 15.6 | 12.8
| 2014-04-23 04:30 | 7.3 | 15.6 | 12.8
| 2014-04-23 05:00 | 7.4 | 15.6 | 12.8
| 2014-04-23 05:30 | 7.4 | 15.6 | 12.8
| 2014-04-23 06:00 | 7.1 | 15 | 12.8
| 2014-04-23 06:30 | 6.7 | 15 | 12.8
| 2014-04-23 07:00 | 6.8 | 15 | 12.8
| 2014-04-23 07:30 | 6.8 | 15 | 12.8
| 2014-04-23 08:00 | 8.1 | 15 | 12.8
| 2014-04-23 08:30 | 9.8 | 14.4 | 12.8
| 2014-04-23 09:00 | 11.2 | 14.4 | 12.8
| 2014-04-23 09:30 | 13.8 | 14.4 | 12.8
| 2014-04-23 10:00 | 15.4 | 14.4 | 12.8
| 2014-04-23 10:30 | 16.9 | 14.4 | 12.8
| 2014-04-23 11:00 | 17.8 | 14.4 | 12.8
| 2014-04-23 11:30 | 19.2 | 14.4 | 12.8
| 2014-04-23 12:00 | 20.2 | 14.4 | 12.8
| 2014-04-23 12:30 | 21.3 | 14.4 | 12.8
| 2014-04-23 13:00 | 20.9 | 14.4 | 12.8
| 2014-04-23 13:30 | 20.7 | 15 | 12.8
| 2014-04-23 14:00 | 20.9 | 15 | 12.8
| 2014-04-23 14:30 | 22.6 | 15.6 | 12.8
| 2014-04-23 15:00 | 22 | 15.6 | 12.8
| 2014-04-23 15:30 | 22.9 | 16.1 | 12.8
| 2014-04-23 16:00 | 23.7 | 16.1 | 12.8
| 2014-04-23 16:30 | 23.3 | 16.7 | 12.8
| 2014-04-23 17:00 | 22.1 | 16.7 | 12.8
| 2014-04-23 17:30 | 20.3 | 17.2 | 12.8
| 2014-04-23 18:00 | 22.9 | 17.2 | 12.8
| 2014-04-23 18:30 | 23.1 | 17.8 | 12.8
| 2014-04-23 19:00 | 22.9 | 17.8 | 12.8
| 2014-04-23 19:30 | 22.4 | 17.8 | 12.8
| 2014-04-23 20:00 | 20.9 | 17.8 | 12.8
| 2014-04-23 20:30 | 18.6 | 18.3 | 12.8
| 2014-04-23 21:00 | 17.3 | 18.3 | 12.8
| 2014-04-23 21:30 | 16.1 | 18.3 | 12.8
| 2014-04-23 22:00 | 15.1 | 18.3 | 12.8
| 2014-04-23 22:30 | 14.3 | 17.8 | 12.8
| 2014-04-23 23:00 | 13.5 | 17.8 | 12.8
| 2014-04-23 23:30 | 13.6 | 17.8 | 12.8
| 2014-04-24 | 14 | 17.8 | 12.8
| 2014-04-24 00:30 | 13.8 | 17.8 | 12.8
| 2014-04-24 01:00 | 13.7 | 17.2 | 12.8
| 2014-04-24 01:30 | 13.2 | 17.2 | 12.8
| 2014-04-24 02:00 | 12.6 | 17.2 | 12.8
| 2014-04-24 02:30 | 11.9 | 17.2 | 12.8
| 2014-04-24 03:00 | 12.1 | 16.7 | 12.8
| 2014-04-24 03:30 | 11.5 | 16.7 | 12.8
| 2014-04-24 04:00 | 11.7 | 16.7 | 12.8
| 2014-04-24 04:30 | 11.7 | 16.7 | 12.8
| 2014-04-24 05:00 | 11.5 | 16.7 | 13.3
| 2014-04-24 05:30 | 11.2 | 16.1 | 13.3
| 2014-04-24 06:00 | 10.6 | 16.1 | 13.3
| 2014-04-24 06:30 | 10.2 | 16.1 | 13.3
| 2014-04-24 07:00 | 9.9 | 16.1 | 13.3
| 2014-04-24 07:30 | 9.9 | 16.1 | 13.3
| 2014-04-24 08:00 | 10.7 | 16.1 | 13.3
| 2014-04-24 08:30 | 12.3 | 15.6 | 13.3
| 2014-04-24 09:00 | 13.4 | 15.6 | 13.3
| 2014-04-24 09:30 | 15.2 | 15.6 | 13.3
| 2014-04-24 10:00 | 17.1 | 15.6 | 13.3
| 2014-04-24 10:30 | 18.7 | 15.6 | 13.3
| 2014-04-24 11:00 | 19.6 | 15.6 | 13.3
| 2014-04-24 11:30 | 21.1 | 15.6 | 13.3
| 2014-04-24 12:00 | 22.7 | 15.6 | 13.3
| 2014-04-24 12:30 | 23.5 | 15.6 | 13.3
| 2014-04-24 13:00 | 24.9 | 15.6 | 13.3
| 2014-04-24 13:30 | 25.3 | 16.1 | 13.3
| 2014-04-24 14:00 | 25.2 | 16.1 | 13.3
| 2014-04-24 14:30 | 25.1 | 16.7 | 13.3
| 2014-04-24 15:00 | 25.1 | 17.2 | 13.3
| 2014-04-24 15:30 | 24 | 17.2 | 13.3
| 2014-04-24 16:00 | 26.4 | 17.8 | 13.3
| 2014-04-24 16:30 | 24.9 | 18.3 | 13.3
| 2014-04-24 17:00 | 24.6 | 18.3 | 13.3
| 2014-04-24 17:30 | 25.9 | 18.3 | 13.3
| 2014-04-24 18:00 | 26.2 | 18.9 | 13.3
| 2014-04-24 18:30 | 25.8 | 18.9 | 13.3
| 2014-04-24 19:00 | 24.8 | 18.9 | 13.3
| 2014-04-24 19:30 | 23.1 | 19.4 | 13.3
| 2014-04-24 20:00 | 20.8 | 19.4 | 13.3
| 2014-04-24 20:30 | 18.9 | 19.4 | 13.3
| 2014-04-24 21:00 | 17.4 | 19.4 | 13.3
| 2014-04-24 21:30 | 16.4 | 19.4 | 13.3
| 2014-04-24 22:00 | 15.4 | 19.4 | 13.3
| 2014-04-24 22:30 | 15.1 | 19.4 | 13.3
| 2014-04-24 23:00 | 15.5 | 18.9 | 13.3
| 2014-04-24 23:30 | 15.4 | 18.9 | 13.3
| 2014-04-25 | 15.3 | 18.9 | 13.3
| 2014-04-25 00:30 | 15.2 | 18.9 | 13.3
| 2014-04-25 01:00 | 15.7 | 18.3 | 13.3
| 2014-04-25 01:30 | 15.2 | 18.3 | 13.3
| 2014-04-25 02:00 | 14.7 | 18.3 | 13.3
| 2014-04-25 02:30 | 13.9 | 18.3 | 13.3
| 2014-04-25 03:00 | 12.8 | 18.3 | 13.3
| 2014-04-25 03:30 | 12.9 | 17.8 | 13.3
| 2014-04-25 04:00 | 12.1 | 17.8 | 13.3
| 2014-04-25 04:30 | 11.8 | 17.8 | 13.3
| 2014-04-25 05:00 | 11.4 | 17.8 | 13.3
| 2014-04-25 05:30 | 11.1 | 17.2 | 13.3
| 2014-04-25 06:00 | 11.1 | 17.2 | 13.3
| 2014-04-25 06:30 | 10.9 | 17.2 | 13.3
| 2014-04-25 07:00 | 11.2 | 17.2 | 13.3
| 2014-04-25 07:30 | 11.7 | 16.7 | 13.3
| 2014-04-25 08:00 | 12.9 | 16.7 | 13.3
| 2014-04-25 08:30 | 14.3 | 16.7 | 13.3
| 2014-04-25 09:00 | 15.9 | 16.7 | 13.3
| 2014-04-25 09:30 | 17.4 | 16.1 | 13.3
| 2014-04-25 10:00 | 18.9 | 16.1 | 13.3
| 2014-04-25 10:30 | 20.3 | 16.1 | 13.3
| 2014-04-25 11:00 | 21.6 | 16.1 | 13.3
| 2014-04-25 11:30 | 22.4 | 16.1 | 13.3
| 2014-04-25 12:00 | 23.1 | 16.1 | 13.3
| 2014-04-25 12:30 | 24.3 | 16.1 | 13.3
| 2014-04-25 13:00 | 24.3 | 16.7 | 13.3
| 2014-04-25 13:30 | 25 | 16.7 | 13.3
| 2014-04-25 14:00 | 26.3 | 17.2 | 13.3
| 2014-04-25 14:30 | 26.9 | 17.2 | 13.3
| 2014-04-25 15:00 | 26.7 | 17.8 | 13.3
| 2014-04-25 15:30 | 26.8 | 18.3 | 13.3
| 2014-04-25 16:00 | 25.3 | 18.3 | 13.3
| 2014-04-25 16:30 | 25.6 | 18.9 | 13.3
| 2014-04-25 17:00 | 25.3 | 19.4 | 13.3
| 2014-04-25 17:30 | 24.6 | 19.4 | 13.3
| 2014-04-25 18:00 | 24.5 | 20 | 13.3
| 2014-04-25 18:30 | 24.3 | 20 | 13.3
| 2014-04-25 19:00 | 23.9 | 20 | 13.3
| 2014-04-25 19:30 | 22.3 | 20.6 | 13.3
| 2014-04-25 20:00 | 21.4 | 20.6 | 13.3
| 2014-04-25 20:30 | 19.9 | 20.6 | 13.3
| 2014-04-25 21:00 | 18.8 | 20.6 | 13.3
| 2014-04-25 21:30 | 18.1 | 20.6 | 13.3
| 2014-04-25 22:00 | 17.1 | 20.6 | 13.3
| 2014-04-25 22:30 | 16.6 | 20 | 13.3
| 2014-04-25 23:00 | 16.1 | 20 | 13.3
| 2014-04-25 23:30 | 17.2 | 20 | 13.3
| 2014-04-26 | 17.2 | 20 | 13.3
| 2014-04-26 00:30 | 16.3 | 20 | 13.3
| 2014-04-26 01:00 | 15.2 | 19.4 | 13.3
| 2014-04-26 01:30 | 14.7 | 19.4 | 13.3
| 2014-04-26 02:00 | 14.2 | 19.4 | 13.3
| 2014-04-26 02:30 | 14.1 | 19.4 | 13.3
| 2014-04-26 03:00 | 13.7 | 19.4 | 13.3
| 2014-04-26 03:30 | 13.4 | 18.9 | 13.9
| 2014-04-26 04:00 | 13.2 | 18.9 | 13.9
| 2014-04-26 04:30 | 12.9 | 18.9 | 13.9
| 2014-04-26 05:00 | 12.7 | 18.9 | 13.9
| 2014-04-26 05:30 | 12.3 | 18.3 | 13.9
| 2014-04-26 06:00 | 11.8 | 18.3 | 13.9
| 2014-04-26 06:30 | 11.9 | 18.3 | 13.9
| 2014-04-26 07:00 | 12.3 | 18.3 | 13.9
| 2014-04-26 07:30 | 12.6 | 18.3 | 13.9
| 2014-04-26 08:00 | 12.8 | 17.8 | 13.9
| 2014-04-26 08:30 | 13.1 | 17.8 | 13.9
| 2014-04-26 09:00 | 13.6 | 17.8 | 13.9
| 2014-04-26 09:30 | 14 | 17.8 | 13.9
| 2014-04-26 10:00 | 14.4 | 17.8 | 13.9
| 2014-04-26 10:30 | 15.2 | 17.2 | 13.9
| 2014-04-26 11:00 | 16.2 | 17.2 | 13.9
| 2014-04-26 11:30 | 16.6 | 17.2 | 13.9
| 2014-04-26 12:00 | 16.8 | 17.2 | 13.9
| 2014-04-26 12:30 | 17.6 | 17.8 | 13.9
| 2014-04-26 13:00 | 18.4 | 17.8 | 13.9
| 2014-04-26 13:30 | 19.2 | 17.8 | 13.9
| 2014-04-26 14:00 | 19.8 | 17.8 | 13.9
| 2014-04-26 14:30 | 20 | 18.3 | 13.9
| 2014-04-26 15:00 | 19.8 | 18.3 | 13.9
| 2014-04-26 15:30 | 20.9 | 18.3 | 13.9
| 2014-04-26 16:00 | 21.8 | 18.9 | 13.9
| 2014-04-26 16:30 | 21.5 | 18.9 | 13.9
| 2014-04-26 17:00 | 20.9 | 19.4 | 13.9
| 2014-04-26 17:30 | 20.8 | 19.4 | 13.9
| 2014-04-26 18:00 | 20.7 | 20 | 13.9
| 2014-04-26 18:30 | 19.8 | 20 | 13.9
| 2014-04-26 19:00 | 19.1 | 20 | 13.9
| 2014-04-26 19:30 | 18.7 | 20 | 13.9
| 2014-04-26 20:00 | 18.2 | 20.6 | 13.9
| 2014-04-26 20:30 | 17.8 | 20.6 | 13.9
| 2014-04-26 21:00 | 17.4 | 20 | 13.9
| 2014-04-26 21:30 | 16.9 | 20 | 13.9
| 2014-04-26 22:00 | 16.3 | 20 | 13.9
| 2014-04-26 22:30 | 15.6 | 20 | 13.9
| 2014-04-26 23:00 | 15.2 | 20 | 13.9
| 2014-04-26 23:30 | 14.8 | 20 | 13.9
| 2014-04-27 | 14.6 | 19.4 | 13.9
| 2014-04-27 00:30 | 14.4 | 19.4 | 13.9
| 2014-04-27 01:00 | 14.4 | 19.4 | 13.9
| 2014-04-27 01:30 | 14.2 | 19.4 | 13.9
| 2014-04-27 02:00 | 13.1 | 18.9 | 13.9
| 2014-04-27 02:30 | 12.1 | 18.9 | 13.9
| 2014-04-27 03:00 | 11.6 | 18.9 | 13.9
| 2014-04-27 03:30 | 11.6 | 18.9 | 13.9
| 2014-04-27 04:00 | 11.5 | 18.3 | 13.9
| 2014-04-27 04:30 | 11.5 | 18.3 | 13.9
| 2014-04-27 05:00 | 11.5 | 17.8 | 13.9
| 2014-04-27 05:30 | 11.5 | 17.8 | 13.9
| 2014-04-27 06:00 | 11.4 | 17.2 | 13.9
| 2014-04-27 06:30 | 11.4 | 17.2 | 13.9
| 2014-04-27 07:00 | 11.3 | 17.2 | 13.9
| 2014-04-27 07:30 | 11.2 | 17.2 | 13.9
| 2014-04-27 08:00 | 11.3 | 16.7 | 13.9
| 2014-04-27 08:30 | 11.6 | 16.7 | 13.9
| 2014-04-27 09:00 | 11.8 | 16.7 | 13.9
| 2014-04-27 09:30 | 11.8 | 16.7 | 13.9
| 2014-04-27 10:00 | 12 | 16.7 | 13.9
| 2014-04-27 10:30 | 12.8 | 16.7 | 13.9
| 2014-04-27 11:00 | 13.3 | 16.7 | 13.9
| 2014-04-27 11:30 | 13.3 | 16.7 | 13.9
| 2014-04-27 12:00 | 13.6 | 16.7 | 13.9
| 2014-04-27 12:30 | 13.8 | 16.7 | 13.9
| 2014-04-27 13:00 | 13.9 | 16.7 | 13.9
| 2014-04-27 13:30 | 14.5 | 16.7 | 13.9
| 2014-04-27 14:00 | 14.5 | 16.7 | 13.9
| 2014-04-27 14:30 | 14.8 | 16.7 | 14.4
| 2014-04-27 15:00 | 15.3 | 16.7 | 14.4
| 2014-04-27 15:30 | 15.2 | 16.7 | 14.4
| 2014-04-27 16:00 | 15.4 | 16.7 | 14.4
| 2014-04-27 16:30 | 15.7 | 16.7 | 14.4
| 2014-04-27 17:00 | 15.6 | 17.2 | 14.4
| 2014-04-27 17:30 | 16.1 | 17.2 | 14.4
| 2014-04-27 18:00 | 15.8 | 17.2 | 14.4
| 2014-04-27 18:30 | 15.3 | 17.2 | 14.4
| 2014-04-27 19:00 | 15.3 | 17.2 | 14.4
| 2014-04-27 19:30 | 15.3 | 17.2 | 14.4
| 2014-04-27 20:00 | 14.7 | 17.2 | 14.4
| 2014-04-27 20:30 | 13.3 | 17.2 | 14.4
| 2014-04-27 21:00 | 12.1 | 17.2 | 14.4
| 2014-04-27 21:30 | 11.3 | 17.2 | 14.4
| 2014-04-27 22:00 | 10.7 | 17.2 | 14.4
| 2014-04-27 22:30 | 10 | 16.7 | 14.4
| 2014-04-27 23:00 | 9.7 | 16.7 | 14.4
| 2014-04-27 23:30 | 9.5 | 16.7 | 14.4
| 2014-04-28 | 9.4 | 16.7 | 14.4
| 2014-04-28 00:30 | 9.5 | 16.1 | 14.4
| 2014-04-28 01:00 | 9.6 | 16.1 | 14.4
| 2014-04-28 01:30 | 9.6 | 16.1 | 14.4
| 2014-04-28 02:00 | 9.6 | 16.1 | 14.4
| 2014-04-28 02:30 | 9.6 | 16.1 | 14.4
| 2014-04-28 03:00 | 9.7 | 15.6 | 14.4
| 2014-04-28 03:30 | 9.7 | 15.6 | 14.4
| 2014-04-28 04:00 | 9.7 | 15.6 | 14.4
| 2014-04-28 04:30 | 9.7 | 15.6 | 14.4
| 2014-04-28 05:00 | 9.6 | 15.6 | 14.4
| 2014-04-28 05:30 | 9.4 | 15 | 14.4
| 2014-04-28 06:00 | 9.6 | 15 | 14.4
| 2014-04-28 06:30 | 9.6 | 15 | 14.4
| 2014-04-28 07:00 | 9.8 | 15 | 14.4
| 2014-04-28 07:30 | 10.2 | 15 | 14.4
| 2014-04-28 08:00 | 10.8 | 15 | 14.4
| 2014-04-28 08:30 | 11.4 | 15 | 14.4
| 2014-04-28 09:00 | 12 | 15 | 14.4
| 2014-04-28 09:30 | 12.6 | 15 | 14.4
| 2014-04-28 10:00 | 13 | 15 | 14.4
| 2014-04-28 10:30 | 13.4 | 15 | 14.4
| 2014-04-28 11:00 | 13.7 | 15 | 14.4
| 2014-04-28 11:30 | 14.4 | 15 | 14.4
| 2014-04-28 12:00 | 14.7 | 15 | 14.4
| 2014-04-28 12:30 | 15.1 | 15 | 14.4
| 2014-04-28 13:00 | 15.4 | 15 | 14.4
| 2014-04-28 13:30 | 15.7 | 15 | 14.4
| 2014-04-28 14:00 | 15.8 | 15.6 | 14.4
| 2014-04-28 14:30 | 15.8 | 15.6 | 14.4
| 2014-04-28 15:00 | 15.7 | 15.6 | 14.4
| 2014-04-28 15:30 | 15.9 | 16.1 | 14.4
| 2014-04-28 16:00 | 15.8 | 16.1 | 14.4
| 2014-04-28 16:30 | 15.5 | 16.1 | 14.4
| 2014-04-28 17:00 | 15.6 | 16.1 | 14.4
| 2014-04-28 17:30 | 15.6 | 16.1 | 14.4
| 2014-04-28 18:00 | 15.4 | 16.1 | 14.4
| 2014-04-28 18:30 | 15.3 | 16.1 | 14.4
| 2014-04-28 19:00 | 15 | 16.1 | 14.4
| 2014-04-28 19:30 | 14.7 | 16.1 | 14.4
| 2014-04-28 20:00 | 14.4 | 16.1 | 14.4
| 2014-04-28 20:30 | 14.2 | 16.1 | 14.4
| 2014-04-28 21:00 | 14 | 16.1 | 14.4
| 2014-04-28 21:30 | 13.8 | 16.1 | 14.4
| 2014-04-28 22:00 | 13.6 | 16.1 | 14.4
| 2014-04-28 22:30 | 13.4 | 16.1 | 14.4
| 2014-04-28 23:00 | 13.3 | 16.1 | 14.4
| 2014-04-28 23:30 | 13.3 | 16.1 | 14.4
| 2014-04-29 | 13.2 | 16.1 | 14.4
| 2014-04-29 00:30 | 13.2 | 16.1 | 14.4
| 2014-04-29 01:00 | 13.1 | 15.6 | 14.4
| 2014-04-29 01:30 | 13 | 15.6 | 14.4
| 2014-04-29 02:00 | 12.7 | 15.6 | 14.4
| 2014-04-29 02:30 | 12.6 | 15.6 | 14.4
| 2014-04-29 03:00 | 12.5 | 15.6 | 14.4
| 2014-04-29 03:30 | 12.4 | 15.6 | 14.4
| 2014-04-29 04:00 | 12.4 | 15.6 | 14.4
| 2014-04-29 04:30 | 12.3 | 15.6 | 14.4
| 2014-04-29 05:00 | 12.2 | 15.6 | 14.4
| 2014-04-29 05:30 | 12.1 | 15.6 | 14.4
| 2014-04-29 06:00 | 11.8 | 15 | 14.4
| 2014-04-29 06:30 | 11.7 | 15 | 14.4
| 2014-04-29 07:00 | 11.7 | 15 | 14.4
| 2014-04-29 07:30 | 12.1 | 15 | 14.4
| 2014-04-29 08:00 | 12.7 | 15 | 14.4
| 2014-04-29 08:30 | 12.8 | 15 | 13.9
| 2014-04-29 09:00 | 12.9 | 15 | 13.9
| 2014-04-29 09:30 | 13.3 | 15 | 13.9
| 2014-04-29 10:00 | 13.6 | 15 | 13.9
| 2014-04-29 10:30 | 13.7 | 15 | 13.9
| 2014-04-29 11:00 | 13.8 | 15 | 13.9
| 2014-04-29 11:30 | 14.1 | 15 | 13.9
| 2014-04-29 12:00 | 15.3 | 15 | 13.9
| 2014-04-29 12:30 | 15.9 | 15 | 13.9
| 2014-04-29 13:00 | 16.6 | 15 | 13.9
| 2014-04-29 13:30 | 17.3 | 15 | 13.9
| 2014-04-29 14:00 | 17.2 | 15.6 | 13.9
| 2014-04-29 14:30 | 17.4 | 15.6 | 13.9
| 2014-04-29 15:00 | 17.8 | 15.6 | 13.9
| 2014-04-29 15:30 | 17.4 | 15.6 | 13.9
| 2014-04-29 16:00 | 17.9 | 16.1 | 13.9
| 2014-04-29 16:30 | 17.2 | 16.1 | 13.9
| 2014-04-29 17:00 | 16.7 | 16.1 | 13.9
| 2014-04-29 17:30 | 17.5 | 16.1 | 13.9
| 2014-04-29 18:00 | 17.8 | 16.7 | 13.9
| 2014-04-29 18:30 | 17.6 | 16.7 | 13.9
| 2014-04-29 19:00 | 16.1 | 16.7 | 13.9
| 2014-04-29 19:30 | 14.3 | 16.7 | 13.9
| 2014-04-29 20:00 | 14.1 | 16.7 | 13.9
| 2014-04-29 20:30 | 13.7 | 16.7 | 13.9
| 2014-04-29 21:00 | 13.3 | 16.7 | 13.9
| 2014-04-29 21:30 | 13.1 | 16.7 | 13.9
| 2014-04-29 22:00 | 13.1 | 16.7 | 13.9
| 2014-04-29 22:30 | 12.9 | 16.7 | 13.9
| 2014-04-29 23:00 | 12.7 | 16.7 | 13.9
| 2014-04-29 23:30 | 12.2 | 16.1 | 13.9
| 2014-04-30 | 11.7 | 16.1 | 13.9
| 2014-04-30 00:30 | 11.1 | 16.1 | 13.9
| 2014-04-30 01:00 | 10.6 | 16.1 | 13.9
| 2014-04-30 01:30 | 10.1 | 16.1 | 13.9
| 2014-04-30 02:00 | 9.6 | 16.1 | 13.9
| 2014-04-30 02:30 | 9.1 | 15.6 | 13.9
| 2014-04-30 03:00 | 8.6 | 15.6 | 13.9
| 2014-04-30 03:30 | 8.4 | 15.6 | 13.9
| 2014-04-30 04:00 | 8.2 | 15.6 | 13.9
| 2014-04-30 04:30 | 8.7 | 15 | 13.9
| 2014-04-30 05:00 | 9.2 | 15 | 13.9
| 2014-04-30 05:30 | 9.8 | 15 | 13.9
| 2014-04-30 06:00 | 10.3 | 15 | 13.9
| 2014-04-30 06:30 | 10.7 | 15 | 13.9
| 2014-04-30 07:00 | 11.1 | 15 | 13.9
| 2014-04-30 07:30 | 11.5 | 14.4 | 13.9
| 2014-04-30 08:00 | 11.8 | 14.4 | 13.9
| 2014-04-30 08:30 | 11.9 | 14.4 | 13.9
| 2014-04-30 09:00 | 12.2 | 14.4 | 13.9
| 2014-04-30 09:30 | 12.8 | 14.4 | 13.9
| 2014-04-30 10:00 | 13.5 | 14.4 | 13.9
| 2014-04-30 10:30 | 13.8 | 14.4 | 13.9
| 2014-04-30 11:00 | 14.2 | 14.4 | 13.9
| 2014-04-30 11:30 | 14.4 | 14.4 | 13.9
| 2014-04-30 12:00 | 14.7 | 14.4 | 13.9
| 2014-04-30 12:30 | 14.9 | 15 | 13.9
| 2014-04-30 13:00 | 16.1 | 15 | 13.9
| 2014-04-30 13:30 | 17.3 | 15 | 13.9
| 2014-04-30 14:00 | 17.8 | 15 | 13.9
| 2014-04-30 14:30 | 18.3 | 15.6 | 13.9
| 2014-04-30 15:00 | 19.1 | 15.6 | 13.9
| 2014-04-30 15:30 | 20.1 | 16.1 | 13.9
| 2014-04-30 16:00 | 19.2 | 16.1 | 13.9
| 2014-04-30 16:30 | 18.6 | 16.7 | 13.9
| 2014-04-30 17:00 | 18.7 | 16.7 | 13.9
| 2014-04-30 17:30 | 18.8 | 16.7 | 13.9
| 2014-04-30 18:00 | 18.6 | 17.2 | 13.9
| 2014-04-30 18:30 | 18.7 | 17.2 | 13.9
| 2014-04-30 19:00 | 18.7 | 17.2 | 13.9
| 2014-04-30 19:30 | 18.7 | 17.2 | 13.9
| 2014-04-30 20:00 | 17.7 | 17.8 | 13.9
| 2014-04-30 20:30 | 16.1 | 17.8 | 13.9
| 2014-04-30 21:00 | 15 | 17.2 | 13.9
| 2014-04-30 21:30 | 14.4 | 17.2 | 13.9
| 2014-04-30 22:00 | 13.8 | 17.2 | 13.9
| 2014-04-30 22:30 | 13.9 | 17.2 | 13.9
| 2014-04-30 23:00 | 14.6 | 17.2 | 13.9
| 2014-04-30 23:30 | 13.4 | 17.2 | 13.9
| 2014-05-01 | 12.7 | 17.2 | 13.9
| 2014-05-01 00:30 | 12.1 | 16.7 | 13.9
| 2014-05-01 01:00 | 11.8 | 16.7 | 13.9
| 2014-05-01 01:30 | 11.8 | 16.7 | 13.9
| 2014-05-01 02:00 | 11.9 | 16.7 | 13.9
| 2014-05-01 02:30 | 11.8 | 16.1 | 13.9
| 2014-05-01 03:00 | 11.6 | 16.1 | 13.9
| 2014-05-01 03:30 | 11.6 | 16.1 | 13.9
| 2014-05-01 04:00 | 11.5 | 16.1 | 13.9
| 2014-05-01 04:30 | 11.7 | 16.1 | 13.9
| 2014-05-01 05:00 | 11.7 | 15.6 | 13.9
| 2014-05-01 05:30 | 11.9 | 15.6 | 13.9
| 2014-05-01 06:00 | 12.1 | 15.6 | 13.9
| 2014-05-01 06:30 | 12.2 | 15.6 | 13.9
| 2014-05-01 07:00 | 12.2 | 15.6 | 13.9
| 2014-05-01 07:30 | 12.4 | 15.6 | 13.9
| 2014-05-01 08:00 | 12.7 | 15.6 | 13.9
| 2014-05-01 08:30 | 12.8 | 15 | 13.9
| 2014-05-01 09:00 | 13 | 15 | 13.9
| 2014-05-01 09:30 | 12.7 | 15 | 13.9
| 2014-05-01 10:00 | 12.8 | 15 | 13.9
| 2014-05-01 10:30 | 13 | 15 | 13.9
| 2014-05-01 11:00 | 13.4 | 15 | 13.9
| 2014-05-01 11:30 | 13.6 | 15 | 13.9
| 2014-05-01 12:00 | 14.1 | 15 | 13.9
| 2014-05-01 12:30 | 14.6 | 15 | 13.9
| 2014-05-01 13:00 | 15.1 | 15 | 13.9
| 2014-05-01 13:30 | 15.6 | 15 | 13.9
| 2014-05-01 14:00 | 16.6 | 15.6 | 13.9
| 2014-05-01 14:30 | 17.3 | 15.6 | 13.9
| 2014-05-01 15:00 | 17.2 | 15.6 | 13.9
| 2014-05-01 15:30 | 16.4 | 16.1 | 13.9
| 2014-05-01 16:00 | 16 | 16.1 | 13.9
| 2014-05-01 16:30 | 16 | 16.1 | 13.9
| 2014-05-01 17:00 | 15.7 | 16.7 | 13.9
| 2014-05-01 17:30 | 15.3 | 16.7 | 13.9
| 2014-05-01 18:00 | 15 | 16.7 | 13.9
| 2014-05-01 18:30 | 14.8 | 16.7 | 13.9
| 2014-05-01 19:00 | 14.4 | 16.7 | 13.9
| 2014-05-01 19:30 | 13.7 | 16.7 | 13.9
| 2014-05-01 20:00 | 13.2 | 16.7 | 13.9
| 2014-05-01 20:30 | 12.7 | 16.7 | 13.9
| 2014-05-01 21:00 | 12.2 | 16.7 | 13.9
| 2014-05-01 21:30 | 11.9 | 16.7 | 13.9
| 2014-05-01 22:00 | 11.7 | 16.7 | 13.9
| 2014-05-01 22:30 | 11.6 | 16.7 | 13.9
| 2014-05-01 23:00 | 11.3 | 16.1 | 13.9
| 2014-05-01 23:30 | 11.3 | 16.1 | 13.9
| 2014-05-02 | 11.5 | 16.1 | 13.9
| 2014-05-02 00:30 | 11.5 | 16.1 | 13.9
| 2014-05-02 01:00 | 11.5 | 16.1 | 13.9
| 2014-05-02 01:30 | 11.4 | 16.1 | 13.9
| 2014-05-02 02:00 | 11.4 | 15.6 | 13.9
| 2014-05-02 02:30 | 11.3 | 15.6 | 13.9
| 2014-05-02 03:00 | 11.5 | 15.6 | 13.9
| 2014-05-02 03:30 | 11.2 | 15.6 | 13.9
| 2014-05-02 04:00 | 11.2 | 15.6 | 13.9
| 2014-05-02 04:30 | 10.8 | 15.6 | 13.9
| 2014-05-02 05:00 | 10.6 | 15 | 13.9
| 2014-05-02 05:30 | 10.5 | 15 | 13.9
| 2014-05-02 06:00 | 10.6 | 15 | 13.9
| 2014-05-02 06:30 | 10.7 | 15 | 13.9
| 2014-05-02 07:00 | 10.9 | 15 | 13.9
| 2014-05-02 07:30 | 11.1 | 15 | 13.9
| 2014-05-02 08:00 | 11.3 | 15 | 13.9
| 2014-05-02 08:30 | 11.8 | 15 | 13.9
| 2014-05-02 09:00 | 12.3 | 15 | 13.9
| 2014-05-02 09:30 | 12.9 | 15 | 13.9
| 2014-05-02 10:00 | 13.8 | 15 | 13.9
| 2014-05-02 10:30 | 14.3 | 15 | 13.9
| 2014-05-02 11:00 | 15.2 | 15 | 13.9
| 2014-05-02 11:30 | 15.5 | 15 | 13.9
| 2014-05-02 12:00 | 15.6 | 15 | 13.9
| 2014-05-02 12:30 | 16.3 | 15 | 13.9
| 2014-05-02 13:00 | 17.4 | 15 | 13.9
| 2014-05-02 13:30 | 17.2 | 15.6 | 13.9
| 2014-05-02 14:00 | 17.3 | 15.6 | 13.9
| 2014-05-02 14:30 | 17.2 | 15.6 | 13.9
| 2014-05-02 15:00 | 17.6 | 16.1 | 13.9
| 2014-05-02 15:30 | 17.9 | 16.1 | 13.9
| 2014-05-02 16:00 | 14.7 | 16.1 | 13.9
| 2014-05-02 16:30 | 14.1 | 16.7 | 13.9
| 2014-05-02 17:00 | 14.6 | 16.7 | 13.9
| 2014-05-02 17:30 | 15.4 | 16.7 | 13.9
| 2014-05-02 18:00 | 15.2 | 16.7 | 13.9
| 2014-05-02 18:30 | 14.3 | 16.7 | 13.9
| 2014-05-02 19:00 | 14 | 16.7 | 13.9
| 2014-05-02 19:30 | 13.1 | 16.7 | 13.9
| 2014-05-02 20:00 | 11.8 | 16.7 | 13.9
| 2014-05-02 20:30 | 11.4 | 16.7 | 13.9
| 2014-05-02 21:00 | 11.1 | 16.7 | 13.9
| 2014-05-02 21:30 | 10.8 | 16.7 | 13.9
| 2014-05-02 22:00 | 10.2 | 16.7 | 13.9
| 2014-05-02 22:30 | 10.1 | 16.1 | 13.9
| 2014-05-02 23:00 | 10 | 16.1 | 13.9
| 2014-05-02 23:30 | 9.6 | 16.1 | 13.9
| 2014-05-03 | 9 | 16.1 | 13.9
| 2014-05-03 00:30 | 8.7 | 16.1 | 13.9
| 2014-05-03 01:00 | 8.6 | 15.6 | 13.9
| 2014-05-03 01:30 | 8.4 | 15.6 | 13.9
| 2014-05-03 02:00 | 8.3 | 15.6 | 13.9
| 2014-05-03 02:30 | 8.1 | 15.6 | 13.9
| 2014-05-03 03:00 | 7.8 | 15 | 13.9
| 2014-05-03 03:30 | 7.8 | 15 | 13.9
| 2014-05-03 04:00 | 7.6 | 15 | 13.9
| 2014-05-03 04:30 | 7.2 | 15 | 13.9
| 2014-05-03 05:00 | 7.1 | 15 | 13.9
| 2014-05-03 05:30 | 6.9 | 14.4 | 13.9
| 2014-05-03 06:00 | 6.7 | 14.4 | 13.9
| 2014-05-03 06:30 | 6.5 | 14.4 | 13.9
| 2014-05-03 07:00 | 6.5 | 14.4 | 13.9
| 2014-05-03 07:30 | 6.8 | 13.9 | 13.9
| 2014-05-03 08:00 | 7.4 | 13.9 | 13.9
| 2014-05-03 08:30 | 8.1 | 13.9 | 13.9
| 2014-05-03 09:00 | 8.4 | 13.9 | 13.9
| 2014-05-03 09:30 | 8.3 | 13.9 | 13.9
| 2014-05-03 10:00 | 9.5 | 13.9 | 13.9
| 2014-05-03 10:30 | 9.4 | 13.9 | 13.9
| 2014-05-03 11:00 | 10.9 | 13.9 | 13.9
| 2014-05-03 11:30 | 10.1 | 13.9 | 13.9
| 2014-05-03 12:00 | 10.4 | 13.9 | 13.9
| 2014-05-03 12:30 | 9.7 | 13.9 | 13.9
| 2014-05-03 13:00 | 10.1 | 13.9 | 13.9
| 2014-05-03 13:30 | 10.7 | 13.9 | 13.9
| 2014-05-03 14:00 | 12.5 | 13.9 | 13.9
| 2014-05-03 14:30 | 12.4 | 14.4 | 13.9
| 2014-05-03 15:00 | 11.9 | 14.4 | 13.9
| 2014-05-03 15:30 | 12.8 | 14.4 | 13.9
| 2014-05-03 16:00 | 11.9 | 14.4 | 13.9
| 2014-05-03 16:30 | 11.7 | 15 | 13.9
| 2014-05-03 17:00 | 11.5 | 15 | 13.9
| 2014-05-03 17:30 | 11.9 | 15 | 13.9
| 2014-05-03 18:00 | 11.9 | 15 | 13.9
| 2014-05-03 18:30 | 12.2 | 15 | 13.9
| 2014-05-03 19:00 | 13.3 | 15 | 13.9
| 2014-05-03 19:30 | 13.9 | 15 | 13.9
| 2014-05-03 20:00 | 13.3 | 15 | 13.9
| 2014-05-03 20:30 | 11.7 | 15 | 13.9
| 2014-05-03 21:00 | 9.7 | 15 | 13.9
| 2014-05-03 21:30 | 7.9 | 15 | 13.9
| 2014-05-03 22:00 | 6.6 | 15 | 13.9
| 2014-05-03 22:30 | 5.4 | 15 | 13.9
| 2014-05-03 23:00 | 4.8 | 15 | 13.9
| 2014-05-03 23:30 | 4.4 | 14.4 | 13.9
| 2014-05-04 | 4.1 | 14.4 | 13.9
| 2014-05-04 00:30 | 3.7 | 14.4 | 13.9
| 2014-05-04 01:00 | 3.2 | 13.9 | 13.9
| 2014-05-04 01:30 | 2.8 | 13.9 | 13.9
| 2014-05-04 02:00 | 2.4 | 13.9 | 13.9
| 2014-05-04 02:30 | 2 | 13.9 | 13.9
| 2014-05-04 03:00 | 1.8 | 13.3 | 13.9
| 2014-05-04 03:30 | 1.4 | 13.3 | 13.9
| 2014-05-04 04:00 | 1.1 | 13.3 | 13.9
| 2014-05-04 04:30 | 0.5 | 12.8 | 13.9
| 2014-05-04 05:00 | 0.1 | 12.8 | 13.9
| 2014-05-04 05:30 | 0.1 | 12.8 | 13.9
| 2014-05-04 06:00 | -0.1 | 12.2 | 13.9
| 2014-05-04 06:30 | 0.5 | 12.2 | 13.9
| 2014-05-04 07:00 | 1.9 | 12.2 | 13.9
| 2014-05-04 07:30 | 3.4 | 11.7 | 13.9
| 2014-05-04 08:00 | 4.8 | 11.7 | 13.9
| 2014-05-04 08:30 | 6.4 | 11.7 | 13.9
| 2014-05-04 09:00 | 7.7 | 11.7 | 13.9
| 2014-05-04 09:30 | 8.9 | 11.7 | 13.9
| 2014-05-04 10:00 | 10.3 | 11.1 | 13.9
| 2014-05-04 10:30 | 11.5 | 11.1 | 13.9
| 2014-05-04 11:00 | 12.4 | 11.1 | 13.9
| 2014-05-04 11:30 | 13.2 | 11.1 | 13.9
| 2014-05-04 12:00 | 13.4 | 11.7 | 13.9
| 2014-05-04 12:30 | 14.6 | 11.7 | 13.9
| 2014-05-04 13:00 | 14.8 | 12.2 | 13.9
| 2014-05-04 13:30 | 14.3 | 12.2 | 13.9
| 2014-05-04 14:00 | 15.2 | 12.8 | 13.9
| 2014-05-04 14:30 | 15.2 | 13.3 | 13.9
| 2014-05-04 15:00 | 15.7 | 13.3 | 13.9
| 2014-05-04 15:30 | 16.1 | 13.9 | 13.9
| 2014-05-04 16:00 | 16.7 | 14.4 | 13.9
| 2014-05-04 16:30 | 16.6 | 14.4 | 13.9
| 2014-05-04 17:00 | 17.2 | 15 | 13.9
| 2014-05-04 17:30 | 16.8 | 15.6 | 13.9
| 2014-05-04 18:00 | 16.7 | 15.6 | 13.9
| 2014-05-04 18:30 | 16.4 | 16.1 | 13.9
| 2014-05-04 19:00 | 16.7 | 16.1 | 13.9
| 2014-05-04 19:30 | 15.8 | 16.1 | 13.9
| 2014-05-04 20:00 | 15.7 | 16.7 | 13.9
| 2014-05-04 20:30 | 13.9 | 16.7 | 13.9
| 2014-05-04 21:00 | 11.7 | 16.7 | 13.9
| 2014-05-04 21:30 | 10.2 | 16.7 | 13.9
| 2014-05-04 22:00 | 9.2 | 16.1 | 13.9
| 2014-05-04 22:30 | 8.3 | 16.1 | 13.9
| 2014-05-04 23:00 | 7.4 | 16.1 | 13.9
| 2014-05-04 23:30 | 7.1 | 16.1 | 13.9
| 2014-05-05 | 6.5 | 16.1 | 13.9
| 2014-05-05 00:30 | 6.6 | 15.6 | 13.9
| 2014-05-05 01:00 | 6.6 | 15.6 | 13.9
| 2014-05-05 01:30 | 6.9 | 15.6 | 13.9
| 2014-05-05 02:00 | 7.3 | 15 | 13.9
| 2014-05-05 02:30 | 7.3 | 15 | 13.9
| 2014-05-05 03:00 | 6.9 | 15 | 13.9
| 2014-05-05 03:30 | 7 | 14.4 | 13.9
| 2014-05-05 04:00 | 6.9 | 14.4 | 13.9
| 2014-05-05 04:30 | 6.4 | 14.4 | 13.9
| 2014-05-05 05:00 | 5.9 | 13.9 | 13.9
| 2014-05-05 05:30 | 5.4 | 13.9 | 13.9
| 2014-05-05 06:00 | 5.2 | 13.9 | 13.9
| 2014-05-05 06:30 | 5.1 | 13.9 | 13.9
| 2014-05-05 07:00 | 5.5 | 13.3 | 13.9
| 2014-05-05 07:30 | 6.2 | 13.3 | 13.9
| 2014-05-05 08:00 | 7.1 | 13.3 | 13.9
| 2014-05-05 08:30 | 8.3 | 13.3 | 13.9
| 2014-05-05 09:00 | 9.4 | 13.3 | 13.9
| 2014-05-05 09:30 | 10.8 | 12.8 | 13.9
| 2014-05-05 10:00 | 12.2 | 12.8 | 13.9
| 2014-05-05 10:30 | 13.9 | 12.8 | 13.9
| 2014-05-05 11:00 | 14.8 | 12.8 | 13.9
| 2014-05-05 11:30 | 15.9 | 12.8 | 13.9
| 2014-05-05 12:00 | 16.7 | 12.8 | 13.9
| 2014-05-05 12:30 | 17.3 | 13.3 | 13.9
| 2014-05-05 13:00 | 17.6 | 13.3 | 13.9
| 2014-05-05 13:30 | 17.8 | 13.9 | 13.9
| 2014-05-05 14:00 | 18 | 13.9 | 13.9
| 2014-05-05 14:30 | 18.4 | 14.4 | 13.9
| 2014-05-05 15:00 | 19.3 | 15 | 13.9
| 2014-05-05 15:30 | 19.8 | 15 | 13.9
| 2014-05-05 16:00 | 19.8 | 15.6 | 13.9
| 2014-05-05 16:30 | 20.3 | 16.1 | 13.9
| 2014-05-05 17:00 | 20.1 | 16.1 | 13.9
| 2014-05-05 17:30 | 20.2 | 16.7 | 13.9
| 2014-05-05 18:00 | 20.5 | 17.2 | 13.9
| 2014-05-05 18:30 | 20 | 17.2 | 13.9
| 2014-05-05 19:00 | 19.9 | 17.8 | 13.9
| 2014-05-05 19:30 | 19.6 | 17.8 | 13.9
| 2014-05-05 20:00 | 18.3 | 17.8 | 13.9
| 2014-05-05 20:30 | 16.3 | 17.8 | 13.9
| 2014-05-05 21:00 | 14.2 | 18.3 | 13.9
| 2014-05-05 21:30 | 12.8 | 17.8 | 13.9
| 2014-05-05 22:00 | 11.9 | 17.8 | 13.9
| 2014-05-05 22:30 | 11.3 | 17.8 | 13.9
| 2014-05-05 23:00 | 10.6 | 17.8 | 13.9
| 2014-05-05 23:30 | 10.2 | 17.8 | 13.9
| 2014-05-06 | 9.4 | 17.2 | 13.9
| 2014-05-06 00:30 | 9.1 | 17.2 | 13.9
| 2014-05-06 01:00 | 9.3 | 17.2 | 13.9
| 2014-05-06 01:30 | 9.3 | 16.7 | 13.9
| 2014-05-06 02:00 | 8.3 | 16.7 | 13.9
| 2014-05-06 02:30 | 7.6 | 16.7 | 13.9
| 2014-05-06 03:00 | 6.8 | 16.1 | 13.9
| 2014-05-06 03:30 | 6.2 | 16.1 | 13.9
| 2014-05-06 04:00 | 5.9 | 16.1 | 13.9
| 2014-05-06 04:30 | 5.9 | 15.6 | 13.9
| 2014-05-06 05:00 | 5.5 | 15.6 | 13.9
| 2014-05-06 05:30 | 5.1 | 15.6 | 13.9
| 2014-05-06 06:00 | 4.8 | 15 | 13.9
| 2014-05-06 06:30 | 4.9 | 15 | 13.9
| 2014-05-06 07:00 | 6.3 | 15 | 13.9
| 2014-05-06 07:30 | 7.3 | 15 | 13.9
| 2014-05-06 08:00 | 8.7 | 14.4 | 13.9
| 2014-05-06 08:30 | 10.8 | 14.4 | 13.9
| 2014-05-06 09:00 | 13.3 | 14.4 | 13.9
| 2014-05-06 09:30 | 14.3 | 14.4 | 13.9
| 2014-05-06 10:00 | 16.6 | 13.9 | 13.9
| 2014-05-06 10:30 | 17.4 | 13.9 | 13.9
| 2014-05-06 11:00 | 18.2 | 13.9 | 13.9
| 2014-05-06 11:30 | 19.5 | 14.4 | 13.9
| 2014-05-06 12:00 | 19.4 | 14.4 | 13.9
| 2014-05-06 12:30 | 19.8 | 14.4 | 13.9
| 2014-05-06 13:00 | 19.6 | 15 | 13.9
| 2014-05-06 13:30 | 20.8 | 15 | 13.9
| 2014-05-06 14:00 | 20.2 | 15 | 13.9
| 2014-05-06 14:30 | 19.9 | 15.6 | 13.9
| 2014-05-06 15:00 | 19.2 | 15.6 | 13.9
| 2014-05-06 15:30 | 18.7 | 15.6 | 13.9
| 2014-05-06 16:00 | 18.3 | 16.1 | 13.9
| 2014-05-06 16:30 | 19.2 | 16.1 | 13.9
| 2014-05-06 17:00 | 20.2 | 16.1 | 13.9
| 2014-05-06 17:30 | 19.8 | 16.1 | 13.9
| 2014-05-06 18:00 | 21.1 | 16.7 | 13.9
| 2014-05-06 18:30 | 19.4 | 16.7 | 13.9
| 2014-05-06 19:00 | 19 | 16.7 | 13.9
| 2014-05-06 19:30 | 18.7 | 16.7 | 13.9
| 2014-05-06 20:00 | 18.3 | 16.7 | 13.9
| 2014-05-06 20:30 | 17.8 | 16.7 | 13.9
| 2014-05-06 21:00 | 17.3 | 16.7 | 13.9
| 2014-05-06 21:30 | 16.2 | 16.7 | 13.9
| 2014-05-06 22:00 | 16 | 16.7 | 13.9
| 2014-05-06 22:30 | 16.7 | 16.7 | 13.9
| 2014-05-06 23:00 | 16.3 | 16.7 | 13.9
| 2014-05-06 23:30 | 16 | 16.7 | 13.9
| 2014-05-07 | 16.2 | 16.7 | 13.9
| 2014-05-07 00:30 | 15.9 | 16.7 | 13.9
| 2014-05-07 01:00 | 15.9 | 16.1 | 13.9
| 2014-05-07 01:30 | 16.3 | 16.1 | 13.9
| 2014-05-07 02:00 | 16.3 | 16.1 | 13.9
| 2014-05-07 02:30 | 16 | 16.1 | 13.9
| 2014-05-07 03:00 | 16 | 16.1 | 13.9
| 2014-05-07 03:30 | 16 | 16.1 | 13.9
| 2014-05-07 04:00 | 14.4 | 16.1 | 13.9
| 2014-05-07 04:30 | 12.3 | 16.1 | 13.9
| 2014-05-07 05:00 | 11.7 | 16.1 | 13.9
| 2014-05-07 05:30 | 11.3 | 15.6 | 13.9
| 2014-05-07 06:00 | 11.2 | 15.6 | 13.9
| 2014-05-07 06:30 | 11.1 | 15.6 | 13.9
| 2014-05-07 07:00 | 11.4 | 15.6 | 13.9
| 2014-05-07 07:30 | 11.9 | 15.6 | 13.9
| 2014-05-07 08:00 | 12.8 | 15.6 | 13.9
| 2014-05-07 08:30 | 13.8 | 15.6 | 13.9
| 2014-05-07 09:00 | 13.8 | 15 | 13.9
| 2014-05-07 09:30 | 14.4 | 15 | 13.9
| 2014-05-07 10:00 | 14.9 | 15 | 13.9
| 2014-05-07 10:30 | 15.4 | 15 | 13.9
| 2014-05-07 11:00 | 15.9 | 15 | 13.9
| 2014-05-07 11:30 | 16.4 | 15 | 13.9
| 2014-05-07 12:00 | 16.3 | 15.6 | 13.9
| 2014-05-07 12:30 | 17.1 | 15.6 | 13.9
| 2014-05-07 13:00 | 15.5 | 15.6 | 13.9
| 2014-05-07 13:30 | 17.1 | 15.6 | 13.9
| 2014-05-07 14:00 | 16.9 | 15.6 | 13.9
| 2014-05-07 14:30 | 17.7 | 16.1 | 13.9
| 2014-05-07 15:00 | 16.8 | 16.1 | 13.9
| 2014-05-07 15:30 | 12.7 | 16.1 | 13.9
| 2014-05-07 16:00 | 14 | 16.1 | 13.9
| 2014-05-07 16:30 | 14.8 | 16.1 | 13.9
| 2014-05-07 17:00 | 15 | 16.1 | 13.9
| 2014-05-07 17:30 | 16.2 | 16.7 | 13.9
| 2014-05-07 18:00 | 16.8 | 16.7 | 13.9
| 2014-05-07 18:30 | 16.2 | 16.7 | 13.9
| 2014-05-07 19:00 | 16.1 | 16.7 | 13.9
| 2014-05-07 19:30 | 15.1 | 16.7 | 13.9
| 2014-05-07 20:00 | 14.4 | 16.7 | 13.9
| 2014-05-07 20:30 | 13.1 | 16.7 | 13.9
| 2014-05-07 21:00 | 13.2 | 16.7 | 13.9
| 2014-05-07 21:30 | 12.6 | 16.7 | 13.9
| 2014-05-07 22:00 | 12.2 | 16.1 | 13.9
| 2014-05-07 22:30 | 12.5 | 16.1 | 13.9
| 2014-05-07 23:00 | 12.1 | 16.1 | 13.9
| 2014-05-07 23:30 | 11.9 | 16.1 | 13.9
| 2014-05-08 | 11.6 | 16.1 | 13.9
| 2014-05-08 00:30 | 11.4 | 15.6 | 13.9
| 2014-05-08 01:00 | 11.5 | 15.6 | 13.9
| 2014-05-08 01:30 | 11.6 | 15.6 | 13.9
| 2014-05-08 02:00 | 11.4 | 15.6 | 13.9
| 2014-05-08 02:30 | 11.3 | 15 | 13.9
| 2014-05-08 03:00 | 10.9 | 15 | 13.9
| 2014-05-08 03:30 | 10.2 | 15 | 13.9
| 2014-05-08 04:00 | 9.9 | 15 | 13.9
| 2014-05-08 04:30 | 9.3 | 15 | 13.9
| 2014-05-08 05:00 | 9.2 | 15 | 13.9
| 2014-05-08 05:30 | 8.8 | 14.4 | 13.9
| 2014-05-08 06:00 | 9.4 | 14.4 | 13.9
| 2014-05-08 06:30 | 9.9 | 14.4 | 13.9
| 2014-05-08 07:00 | 10.3 | 14.4 | 13.9
| 2014-05-08 07:30 | 10.8 | 14.4 | 13.9
| 2014-05-08 08:00 | 11.4 | 13.9 | 13.9
| 2014-05-08 08:30 | 12.3 | 13.9 | 13.9
| 2014-05-08 09:00 | 13.4 | 13.9 | 13.9
| 2014-05-08 09:30 | 13.8 | 13.9 | 13.9
| 2014-05-08 10:00 | 13.9 | 13.9 | 13.9
| 2014-05-08 10:30 | 14.1 | 13.9 | 13.9
| 2014-05-08 11:00 | 13.9 | 13.9 | 13.9
| 2014-05-08 11:30 | 14.6 | 13.9 | 13.9
| 2014-05-08 12:00 | 15.6 | 13.9 | 13.9
| 2014-05-08 12:30 | 16.3 | 14.4 | 13.9
| 2014-05-08 13:00 | 16.6 | 14.4 | 13.9
| 2014-05-08 13:30 | 18 | 14.4 | 13.9
| 2014-05-08 14:00 | 18.1 | 14.4 | 13.9
| 2014-05-08 14:30 | 18.2 | 14.4 | 13.9
| 2014-05-08 15:00 | 18.7 | 15 | 13.9
| 2014-05-08 15:30 | 18.4 | 15 | 13.9
| 2014-05-08 16:00 | 17.5 | 15 | 13.9
| 2014-05-08 16:30 | 17.4 | 15.6 | 13.9
| 2014-05-08 17:00 | 17.6 | 15.6 | 13.9
| 2014-05-08 17:30 | 17.2 | 15.6 | 13.9
| 2014-05-08 18:00 | 16.8 | 15.6 | 13.9
| 2014-05-08 18:30 | 16.2 | 15.6 | 13.9
| 2014-05-08 19:00 | 14.7 | 16.1 | 13.9
| 2014-05-08 19:30 | 13.8 | 16.1 | 13.9
| 2014-05-08 20:00 | 13.1 | 16.1 | 13.9
| 2014-05-08 20:30 | 12.8 | 16.1 | 13.9
| 2014-05-08 21:00 | 12.4 | 16.1 | 13.9
| 2014-05-08 21:30 | 12.3 | 15.6 | 13.9
| 2014-05-08 22:00 | 12.3 | 15.6 | 13.9
| 2014-05-08 22:30 | 12.1 | 15.6 | 13.9
| 2014-05-08 23:00 | 12.2 | 15.6 | 13.9
| 2014-05-08 23:30 | 12 | 15.6 | 13.9
| 2014-05-09 | 12.2 | 15.6 | 13.9
| 2014-05-09 00:30 | 12.3 | 15.6 | 13.9
| 2014-05-09 01:00 | 12.4 | 15 | 13.9
| 2014-05-09 01:30 | 12.2 | 15 | 13.9
| 2014-05-09 02:00 | 12 | 15 | 13.9
| 2014-05-09 02:30 | 12.7 | 15 | 13.9
| 2014-05-09 03:00 | 13 | 15 | 13.9
| 2014-05-09 03:30 | 12.9 | 15 | 13.9
| 2014-05-09 04:00 | 13.2 | 15 | 13.9
| 2014-05-09 04:30 | 13.2 | 14.4 | 13.9
| 2014-05-09 05:00 | 12.8 | 14.4 | 13.9
| 2014-05-09 05:30 | 13.1 | 14.4 | 13.9
| 2014-05-09 06:00 | 12.8 | 14.4 | 13.9
| 2014-05-09 06:30 | 12.9 | 14.4 | 13.9
| 2014-05-09 07:00 | 12.9 | 14.4 | 13.9
| 2014-05-09 07:30 | 13.4 | 14.4 | 13.9
| 2014-05-09 08:00 | 13.8 | 14.4 | 13.9
| 2014-05-09 08:30 | 13.8 | 14.4 | 13.9
| 2014-05-09 09:00 | 14.8 | 14.4 | 13.9
| 2014-05-09 09:30 | 16.3 | 14.4 | 13.9
| 2014-05-09 10:00 | 16.1 | 14.4 | 13.9
| 2014-05-09 10:30 | 17.2 | 14.4 | 13.9
| 2014-05-09 11:00 | 16.9 | 14.4 | 13.9
| 2014-05-09 11:30 | 18.2 | 14.4 | 13.9
| 2014-05-09 12:00 | 17.4 | 14.4 | 13.9
| 2014-05-09 12:30 | 17.9 | 14.4 | 13.9
| 2014-05-09 13:00 | 19 | 15 | 13.9
| 2014-05-09 13:30 | 18.2 | 15 | 13.9
| 2014-05-09 14:00 | 18.1 | 15 | 13.9
| 2014-05-09 14:30 | 17.2 | 15 | 13.9
| 2014-05-09 15:00 | 18.8 | 15 | 13.9
| 2014-05-09 15:30 | 19.4 | 15.6 | 13.9
| 2014-05-09 16:00 | 19 | 15.6 | 13.9
| 2014-05-09 16:30 | 18.8 | 15.6 | 13.9
| 2014-05-09 17:00 | 17.8 | 15.6 | 13.9
| 2014-05-09 17:30 | 18.5 | 15.6 | 13.9
| 2014-05-09 18:00 | 18.7 | 16.1 | 13.9
| 2014-05-09 18:30 | 17.3 | 16.1 | 13.9
| 2014-05-09 19:00 | 17 | 16.1 | 13.9
| 2014-05-09 19:30 | 17.2 | 16.1 | 13.9
| 2014-05-09 20:00 | 17 | 16.1 | 13.9
| 2014-05-09 20:30 | 16.7 | 16.1 | 13.9
| 2014-05-09 21:00 | 14.4 | 16.1 | 13.9
| 2014-05-09 21:30 | 14.8 | 16.1 | 13.9
| 2014-05-09 22:00 | 15 | 15.6 | 13.9
| 2014-05-09 22:30 | 14.1 | 15.6 | 13.9
| 2014-05-09 23:00 | 12.6 | 15.6 | 13.9
| 2014-05-09 23:30 | 11.9 | 15.6 | 13.9
| 2014-05-10 | 11.1 | 15.6 | 13.9
| 2014-05-10 00:30 | 10.1 | 15.6 | 13.9
| 2014-05-10 01:00 | 9.7 | 15 | 13.9
| 2014-05-10 01:30 | 9.2 | 15 | 13.9
| 2014-05-10 02:00 | 9.1 | 15 | 13.9
| 2014-05-10 02:30 | 8.7 | 15 | 13.9
| 2014-05-10 03:00 | 8.4 | 14.4 | 13.9
| 2014-05-10 03:30 | 8.2 | 14.4 | 13.9
| 2014-05-10 04:00 | 7.8 | 14.4 | 13.9
| 2014-05-10 04:30 | 7.8 | 14.4 | 13.9
| 2014-05-10 05:00 | 7.7 | 13.9 | 13.9
| 2014-05-10 05:30 | 7.4 | 13.9 | 13.9
| 2014-05-10 06:00 | 7.3 | 13.9 | 13.9
| 2014-05-10 06:30 | 7.9 | 13.9 | 13.9
| 2014-05-10 07:00 | 8.6 | 13.9 | 13.9
| 2014-05-10 07:30 | 10.3 | 13.3 | 13.9
| 2014-05-10 08:00 | 11.2 | 13.3 | 13.9
| 2014-05-10 08:30 | 12 | 13.3 | 13.9
| 2014-05-10 09:00 | 12.3 | 13.3 | 13.9
| 2014-05-10 09:30 | 13.1 | 13.3 | 13.9
| 2014-05-10 10:00 | 13.9 | 13.3 | 13.9
| 2014-05-10 10:30 | 14.6 | 13.3 | 13.9
| 2014-05-10 11:00 | 14.7 | 13.3 | 13.9
| 2014-05-10 11:30 | 15.7 | 13.3 | 13.9
| 2014-05-10 12:00 | 17.3 | 13.3 | 13.9
| 2014-05-10 12:30 | 17.8 | 13.3 | 13.9
| 2014-05-10 13:00 | 17.1 | 13.9 | 13.9
| 2014-05-10 13:30 | 15.8 | 13.9 | 13.9
| 2014-05-10 14:00 | 14.7 | 13.9 | 13.9
| 2014-05-10 14:30 | 15.1 | 14.4 | 13.9
| 2014-05-10 15:00 | 14.8 | 14.4 | 13.9
| 2014-05-10 15:30 | 14.2 | 14.4 | 13.9
| 2014-05-10 16:00 | 13.8 | 14.4 | 13.9
| 2014-05-10 16:30 | 13.8 | 14.4 | 13.9
| 2014-05-10 17:00 | 14.1 | 14.4 | 13.9
| 2014-05-10 17:30 | 13.6 | 15 | 13.9
| 2014-05-10 18:00 | 13.4 | 15 | 13.9
| 2014-05-10 18:30 | 12.8 | 15 | 13.9
| 2014-05-10 19:00 | 12.4 | 15 | 13.9
| 2014-05-10 19:30 | 12.1 | 15 | 13.9
| 2014-05-10 20:00 | 12.2 | 14.4 | 13.9
| 2014-05-10 20:30 | 12 | 14.4 | 13.9
| 2014-05-10 21:00 | 11.8 | 14.4 | 13.9
| 2014-05-10 21:30 | 12 | 14.4 | 13.9
| 2014-05-10 22:00 | 12.1 | 14.4 | 13.9
| 2014-05-10 22:30 | 12.3 | 14.4 | 13.9
| 2014-05-10 23:00 | 13.2 | 14.4 | 13.9
| 2014-05-10 23:30 | 12.6 | 14.4 | 13.9
| 2014-05-11 | 11.8 | 14.4 | 13.9
| 2014-05-11 00:30 | 11 | 14.4 | 13.9
| 2014-05-11 01:00 | 10.7 | 13.9 | 13.9
| 2014-05-11 01:30 | 10.9 | 13.9 | 13.9
| 2014-05-11 02:00 | 10.6 | 13.9 | 13.9
| 2014-05-11 02:30 | 11.1 | 13.9 | 13.9
| 2014-05-11 03:00 | 11.2 | 13.9 | 13.9
| 2014-05-11 03:30 | 11.1 | 13.9 | 13.9
| 2014-05-11 04:00 | 10.2 | 13.9 | 13.9
| 2014-05-11 04:30 | 10.5 | 13.9 | 13.9
| 2014-05-11 05:00 | 10.8 | 13.9 | 13.9
| 2014-05-11 05:30 | 10.6 | 13.9 | 13.9
| 2014-05-11 06:00 | 10.4 | 13.3 | 13.9
| 2014-05-11 06:30 | 10.4 | 13.3 | 13.9
| 2014-05-11 07:00 | 10.5 | 13.3 | 13.9
| 2014-05-11 07:30 | 10.4 | 13.3 | 13.9
| 2014-05-11 08:00 | 10.9 | 13.3 | 13.9
| 2014-05-11 08:30 | 11.2 | 13.3 | 13.9
| 2014-05-11 09:00 | 11.3 | 13.3 | 13.9
| 2014-05-11 09:30 | 11.7 | 13.3 | 13.9
| 2014-05-11 10:00 | 12.2 | 13.3 | 13.9
| 2014-05-11 10:30 | 12.3 | 13.3 | 13.9
| 2014-05-11 11:00 | 11.8 | 13.3 | 13.9
| 2014-05-11 11:30 | 10.1 | 13.3 | 13.9
| 2014-05-11 12:00 | 11.6 | 13.3 | 13.9
| 2014-05-11 12:30 | 13.7 | 13.3 | 13.9
| 2014-05-11 13:00 | 13.3 | 13.3 | 13.9
| 2014-05-11 13:30 | 14.3 | 13.3 | 13.9
| 2014-05-11 14:00 | 14.2 | 13.3 | 13.9
| 2014-05-11 14:30 | 15.4 | 13.3 | 13.9
| 2014-05-11 15:00 | 16.1 | 13.9 | 13.9
| 2014-05-11 15:30 | 13.7 | 13.9 | 13.9
| 2014-05-11 16:00 | 9.9 | 13.9 | 13.9
| 2014-05-11 16:30 | 11.5 | 13.9 | 13.9
| 2014-05-11 17:00 | 13.5 | 14.4 | 13.9
| 2014-05-11 17:30 | 13.3 | 14.4 | 13.9
| 2014-05-11 18:00 | 13.7 | 14.4 | 13.9
| 2014-05-11 18:30 | 14.6 | 14.4 | 13.9
| 2014-05-11 19:00 | 12.4 | 14.4 | 13.9
| 2014-05-11 19:30 | 11.8 | 14.4 | 13.9
| 2014-05-11 20:00 | 11.5 | 14.4 | 13.9
| 2014-05-11 20:30 | 11 | 14.4 | 13.9
| 2014-05-11 21:00 | 10.7 | 14.4 | 13.9
| 2014-05-11 21:30 | 9.7 | 14.4 | 13.9
| 2014-05-11 22:00 | 9.7 | 14.4 | 13.9
| 2014-05-11 22:30 | 9.8 | 14.4 | 13.9
| 2014-05-11 23:00 | 9.8 | 14.4 | 13.9
| 2014-05-11 23:30 | 9.3 | 13.9 | 13.9
| 2014-05-12 | 8.9 | 13.9 | 13.9
| 2014-05-12 00:30 | 9.1 | 13.9 | 13.9
| 2014-05-12 01:00 | 8.4 | 13.9 | 13.9
| 2014-05-12 01:30 | 8.4 | 13.9 | 13.9
| 2014-05-12 02:00 | 8.1 | 13.3 | 13.9
| 2014-05-12 02:30 | 7.8 | 13.3 | 13.9
| 2014-05-12 03:00 | 7.4 | 13.3 | 13.9
| 2014-05-12 03:30 | 8 | 13.3 | 13.9
| 2014-05-12 04:00 | 7.1 | 12.8 | 13.9
| 2014-05-12 04:30 | 7.2 | 12.8 | 13.9
| 2014-05-12 05:00 | 8.1 | 12.8 | 13.9
| 2014-05-12 05:30 | 8.2 | 12.8 | 13.9
| 2014-05-12 06:00 | 7.4 | 12.8 | 13.9
| 2014-05-12 06:30 | 7.1 | 12.2 | 13.9
| 2014-05-12 07:00 | 7.8 | 12.2 | 13.9
| 2014-05-12 07:30 | 8.5 | 12.2 | 13.9
| 2014-05-12 08:00 | 9.3 | 12.2 | 13.9
| 2014-05-12 08:30 | 10 | 12.2 | 13.9
| 2014-05-12 09:00 | 10.4 | 11.7 | 13.9
| 2014-05-12 09:30 | 11.6 | 11.7 | 13.9
| 2014-05-12 10:00 | 11.7 | 11.7 | 13.9
| 2014-05-12 10:30 | 11.4 | 11.7 | 13.9
| 2014-05-12 11:00 | 11.8 | 11.7 | 13.9
| 2014-05-12 11:30 | 11.9 | 11.7 | 13.9
| 2014-05-12 12:00 | 13.2 | 12.2 | 13.9
| 2014-05-12 12:30 | 12.9 | 12.2 | 13.9
| 2014-05-12 13:00 | 12.8 | 12.2 | 13.9
| 2014-05-12 13:30 | 14.1 | 12.2 | 13.9
| 2014-05-12 14:00 | 14.7 | 12.8 | 13.9
| 2014-05-12 14:30 | 14.2 | 12.8 | 13.9
| 2014-05-12 15:00 | 14.8 | 12.8 | 13.9
| 2014-05-12 15:30 | 16.2 | 13.3 | 13.9
| 2014-05-12 16:00 | 15.6 | 13.3 | 13.9
| 2014-05-12 16:30 | 13.8 | 13.3 | 13.9
| 2014-05-12 17:00 | 14.4 | 13.3 | 13.9
| 2014-05-12 17:30 | 14.9 | 13.9 | 13.9
| 2014-05-12 18:00 | 14.2 | 13.9 | 13.9
| 2014-05-12 18:30 | 14.6 | 13.9 | 13.9
| 2014-05-12 19:00 | 14.6 | 13.9 | 13.9
| 2014-05-12 19:30 | 12.6 | 13.9 | 13.9
| 2014-05-12 20:00 | 12.3 | 14.4 | 13.9
| 2014-05-12 20:30 | 11.4 | 14.4 | 13.3
| 2014-05-12 21:00 | 10.5 | 14.4 | 13.3
| 2014-05-12 21:30 | 10.1 | 13.9 | 13.3
| 2014-05-12 22:00 | 9.8 | 13.9 | 13.3
| 2014-05-12 22:30 | 9.7 | 13.9 | 13.3
| 2014-05-12 23:00 | 9.1 | 13.9 | 13.3
| 2014-05-12 23:30 | 8.4 | 13.9 | 13.3
| 2014-05-13 | 8.3 | 13.9 | 13.3
| 2014-05-13 00:30 | 8.4 | 13.9 | 13.3
| 2014-05-13 01:00 | 8.6 | 13.9 | 13.3
| 2014-05-13 01:30 | 8.7 | 13.3 | 13.3
| 2014-05-13 02:00 | 8.7 | 13.3 | 13.3
| 2014-05-13 02:30 | 8.7 | 13.3 | 13.3
| 2014-05-13 03:00 | 8.6 | 13.3 | 13.3
| 2014-05-13 03:30 | 8.3 | 13.3 | 13.3
| 2014-05-13 04:00 | 8.1 | 13.3 | 13.3
| 2014-05-13 04:30 | 8.1 | 12.8 | 13.3
| 2014-05-13 05:00 | 8.1 | 12.8 | 13.3
| 2014-05-13 05:30 | 8.1 | 12.8 | 13.3
| 2014-05-13 06:00 | 8.1 | 12.8 | 13.3
| 2014-05-13 06:30 | 8.2 | 12.8 | 13.3
| 2014-05-13 07:00 | 8.7 | 12.8 | 13.3
| 2014-05-13 07:30 | 8.8 | 12.8 | 13.3
| 2014-05-13 08:00 | 9.8 | 12.8 | 13.3
| 2014-05-13 08:30 | 10.3 | 12.2 | 13.3
| 2014-05-13 09:00 | 10.7 | 12.2 | 13.3
| 2014-05-13 09:30 | 11.4 | 12.2 | 13.3
| 2014-05-13 10:00 | 12.4 | 12.2 | 13.3
| 2014-05-13 10:30 | 13.1 | 12.2 | 13.3
| 2014-05-13 11:00 | 13.3 | 12.2 | 13.3
| 2014-05-13 11:30 | 13.5 | 12.2 | 13.3
| 2014-05-13 12:00 | 14.4 | 12.8 | 13.3
| 2014-05-13 12:30 | 12.6 | 12.8 | 13.3
| 2014-05-13 13:00 | 14.2 | 12.8 | 13.3
| 2014-05-13 13:30 | 14.1 | 13.3 | 13.3
| 2014-05-13 14:00 | 15.2 | 13.3 | 13.3
| 2014-05-13 14:30 | 15.7 | 13.3 | 13.3
| 2014-05-13 15:00 | 16.3 | 13.9 | 13.3
| 2014-05-13 15:30 | 17.2 | 13.9 | 13.3
| 2014-05-13 16:00 | 15.7 | 14.4 | 13.3
| 2014-05-13 16:30 | 14.4 | 14.4 | 13.3
| 2014-05-13 17:00 | 14.3 | 15 | 13.3
| 2014-05-13 17:30 | 14.3 | 15 | 13.3
| 2014-05-13 18:00 | 15.6 | 15 | 13.3
| 2014-05-13 18:30 | 14.8 | 15.6 | 13.3
| 2014-05-13 19:00 | 15.3 | 15.6 | 13.3
| 2014-05-13 19:30 | 13.5 | 15.6 | 13.3
| 2014-05-13 20:00 | 13 | 15.6 | 13.3
| 2014-05-13 20:30 | 12.6 | 15.6 | 13.3
| 2014-05-13 21:00 | 12.4 | 15.6 | 13.3
| 2014-05-13 21:30 | 12.1 | 15.6 | 13.3
| 2014-05-13 22:00 | 11.8 | 15.6 | 13.3
| 2014-05-13 22:30 | 11.6 | 15.6 | 13.3
| 2014-05-13 23:00 | 11.3 | 15.6 | 13.3
| 2014-05-13 23:30 | 11 | 15 | 13.3
| 2014-05-14 | 10.8 | 15 | 13.3
| 2014-05-14 00:30 | 10.3 | 15 | 13.3
| 2014-05-14 01:00 | 9.9 | 15 | 13.3
| 2014-05-14 01:30 | 9.7 | 15 | 13.3
| 2014-05-14 02:00 | 9.8 | 15 | 13.3
| 2014-05-14 02:30 | 9.5 | 14.4 | 13.3
| 2014-05-14 03:00 | 8.9 | 14.4 | 13.3
| 2014-05-14 03:30 | 8.3 | 14.4 | 13.3
| 2014-05-14 04:00 | 7.3 | 14.4 | 13.3
| 2014-05-14 04:30 | 6.7 | 13.9 | 13.3
| 2014-05-14 05:00 | 6.2 | 13.9 | 13.3
| 2014-05-14 05:30 | 5.6 | 13.9 | 13.3
| 2014-05-14 06:00 | 5.2 | 13.9 | 13.3
| 2014-05-14 06:30 | 4.4 | 13.3 | 13.3
| 2014-05-14 07:00 | 5.4 | 13.3 | 13.3
| 2014-05-14 07:30 | 7.4 | 13.3 | 13.3
| 2014-05-14 08:00 | 8.4 | 13.3 | 13.3
| 2014-05-14 08:30 | 9.2 | 12.8 | 13.3
| 2014-05-14 09:00 | 9.7 | 12.8 | 13.3
| 2014-05-14 09:30 | 10.3 | 12.8 | 13.3
| 2014-05-14 10:00 | 11.2 | 12.8 | 13.3
| 2014-05-14 10:30 | 11.4 | 12.8 | 13.3
| 2014-05-14 11:00 | 11.9 | 12.8 | 13.3
| 2014-05-14 11:30 | 12 | 12.8 | 13.3
| 2014-05-14 12:00 | 12.3 | 12.8 | 13.3
| 2014-05-14 12:30 | 13.2 | 12.8 | 13.3
| 2014-05-14 13:00 | 13.9 | 13.3 | 13.3
| 2014-05-14 13:30 | 14.3 | 13.3 | 13.3
| 2014-05-14 14:00 | 14.8 | 13.3 | 13.3
| 2014-05-14 14:30 | 14.9 | 13.9 | 13.3
| 2014-05-14 15:00 | 16.4 | 13.9 | 13.3
| 2014-05-14 15:30 | 16.6 | 14.4 | 13.3
| 2014-05-14 16:00 | 16.1 | 15 | 13.3
| 2014-05-14 16:30 | 16.8 | 15 | 13.3
| 2014-05-14 17:00 | 16.9 | 15.6 | 13.3
| 2014-05-14 17:30 | 17.5 | 15.6 | 13.3
| 2014-05-14 18:00 | 17.5 | 16.1 | 13.3
| 2014-05-14 18:30 | 15.8 | 16.1 | 13.3
| 2014-05-14 19:00 | 14.4 | 16.7 | 13.3
| 2014-05-14 19:30 | 14.9 | 16.7 | 13.3
| 2014-05-14 20:00 | 14.8 | 16.7 | 13.3
| 2014-05-14 20:30 | 14.3 | 16.7 | 13.3
| 2014-05-14 21:00 | 12.8 | 16.7 | 13.3
| 2014-05-14 21:30 | 11.3 | 16.7 | 13.3
| 2014-05-14 22:00 | 10.7 | 16.7 | 13.3
| 2014-05-14 22:30 | 10.2 | 16.7 | 13.3
| 2014-05-14 23:00 | 10.3 | 16.7 | 13.3
| 2014-05-14 23:30 | 10 | 16.7 | 13.3
| 2014-05-15 | 9.3 | 16.1 | 13.3
| 2014-05-15 00:30 | 8.8 | 16.1 | 13.3
| 2014-05-15 01:00 | 7.8 | 16.1 | 13.3
| 2014-05-15 01:30 | 7.1 | 16.1 | 13.3
| 2014-05-15 02:00 | 6.6 | 15.6 | 13.3
| 2014-05-15 02:30 | 6.1 | 15.6 | 13.3
| 2014-05-15 03:00 | 6.2 | 15.6 | 13.3
| 2014-05-15 03:30 | 5.6 | 15 | 13.3
| 2014-05-15 04:00 | 5.2 | 15 | 13.3
| 2014-05-15 04:30 | 4.8 | 15 | 13.3
| 2014-05-15 05:00 | 4.3 | 15 | 13.3
| 2014-05-15 05:30 | 4.2 | 14.4 | 13.3
| 2014-05-15 06:00 | 4.2 | 14.4 | 13.3
| 2014-05-15 06:30 | 4.3 | 14.4 | 13.3
| 2014-05-15 07:00 | 5.3 | 13.9 | 13.3
| 2014-05-15 07:30 | 6.6 | 13.9 | 13.3
| 2014-05-15 08:00 | 7.8 | 13.9 | 13.3
| 2014-05-15 08:30 | 8.6 | 13.3 | 13.3
| 2014-05-15 09:00 | 8.9 | 13.3 | 13.3
| 2014-05-15 09:30 | 8.9 | 13.3 | 13.3
| 2014-05-15 10:00 | 9.1 | 13.3 | 13.3
| 2014-05-15 10:30 | 9.7 | 13.3 | 13.3
| 2014-05-15 11:00 | 10.5 | 13.3 | 13.3
| 2014-05-15 11:30 | 11.7 | 13.3 | 13.3
| 2014-05-15 12:00 | 11.4 | 13.3 | 13.3
| 2014-05-15 12:30 | 11.3 | 13.3 | 13.3
| 2014-05-15 13:00 | 11 | 13.3 | 13.3
| 2014-05-15 13:30 | 11.6 | 13.9 | 13.3
| 2014-05-15 14:00 | 11.2 | 13.9 | 13.3
| 2014-05-15 14:30 | 12.8 | 13.9 | 13.3
| 2014-05-15 15:00 | 12.6 | 13.9 | 13.3
| 2014-05-15 15:30 | 13.3 | 14.4 | 13.3
| 2014-05-15 16:00 | 13.5 | 14.4 | 13.3
| 2014-05-15 16:30 | 13.7 | 14.4 | 13.3
| 2014-05-15 17:00 | 13.6 | 15 | 13.3
| 2014-05-15 17:30 | 14.5 | 15 | 13.3
| 2014-05-15 18:00 | 14.3 | 15 | 13.3
| 2014-05-15 18:30 | 14.2 | 15 | 13.3
| 2014-05-15 19:00 | 13.6 | 15.6 | 13.3
| 2014-05-15 19:30 | 13.4 | 15.6 | 13.3
| 2014-05-15 20:00 | 13.3 | 15.6 | 13.3
| 2014-05-15 20:30 | 13 | 15.6 | 13.3
| 2014-05-15 21:00 | 12.8 | 15.6 | 13.3
| 2014-05-15 21:30 | 12.4 | 15.6 | 13.3
| 2014-05-15 22:00 | 12.3 | 15.6 | 13.3
| 2014-05-15 22:30 | 12.1 | 15.6 | 13.3
| 2014-05-15 23:00 | 11.5 | 15.6 | 13.3
| 2014-05-15 23:30 | 11.1 | 15 | 13.3
| 2014-05-16 | 11.1 | 15 | 13.3
| 2014-05-16 00:30 | 10.8 | 15 | 13.3
| 2014-05-16 01:00 | 10.5 | 15 | 13.3
| 2014-05-16 01:30 | 9.7 | 15 | 13.3
| 2014-05-16 02:00 | 9.6 | 15 | 13.3
| 2014-05-16 02:30 | 8.9 | 14.4 | 13.3
| 2014-05-16 03:00 | 8.1 | 14.4 | 13.3
| 2014-05-16 03:30 | 7.5 | 14.4 | 13.3
| 2014-05-16 04:00 | 7.8 | 14.4 | 13.3
| 2014-05-16 04:30 | 7.8 | 13.9 | 13.3
| 2014-05-16 05:00 | 8.1 | 13.9 | 13.3
| 2014-05-16 05:30 | 8.3 | 13.9 | 13.3
| 2014-05-16 06:00 | 7.8 | 13.9 | 13.3
| 2014-05-16 06:30 | 7.9 | 13.9 | 13.3
| 2014-05-16 07:00 | 9 | 13.3 | 13.3
| 2014-05-16 07:30 | 10.3 | 13.3 | 13.3
| 2014-05-16 08:00 | 10.9 | 13.3 | 13.3
| 2014-05-16 08:30 | 11.2 | 13.3 | 13.3
| 2014-05-16 09:00 | 11.8 | 13.3 | 13.3
| 2014-05-16 09:30 | 12.3 | 13.3 | 13.3
| 2014-05-16 10:00 | 13.3 | 12.8 | 13.3
| 2014-05-16 10:30 | 14.3 | 12.8 | 13.3
| 2014-05-16 11:00 | 14.8 | 12.8 | 13.3
| 2014-05-16 11:30 | 15.4 | 13.3 | 13.3
| 2014-05-16 12:00 | 16.1 | 13.3 | 13.3
| 2014-05-16 12:30 | 16.5 | 13.3 | 13.3
| 2014-05-16 13:00 | 17.1 | 13.9 | 13.3
| 2014-05-16 13:30 | 18.1 | 13.9 | 13.3
| 2014-05-16 14:00 | 18.2 | 14.4 | 13.3
| 2014-05-16 14:30 | 18.3 | 15 | 13.3
| 2014-05-16 15:00 | 18.7 | 15.6 | 13.3
| 2014-05-16 15:30 | 18.5 | 15.6 | 13.3
| 2014-05-16 16:00 | 19.1 | 16.1 | 13.3
| 2014-05-16 16:30 | 18.7 | 16.7 | 13.3
| 2014-05-16 17:00 | 19 | 16.7 | 13.3
| 2014-05-16 17:30 | 19.7 | 17.2 | 13.3
| 2014-05-16 18:00 | 18.8 | 17.2 | 13.3
| 2014-05-16 18:30 | 19.4 | 17.8 | 13.3
| 2014-05-16 19:00 | 18.8 | 17.8 | 13.3
| 2014-05-16 19:30 | 18.8 | 18.3 | 13.3
| 2014-05-16 20:00 | 18.6 | 18.3 | 13.3
| 2014-05-16 20:30 | 17.7 | 18.3 | 13.3
| 2014-05-16 21:00 | 16.3 | 18.3 | 13.3
| 2014-05-16 21:30 | 15 | 18.3 | 13.3
| 2014-05-16 22:00 | 13.7 | 18.3 | 13.3
| 2014-05-16 22:30 | 12.9 | 18.3 | 13.3
| 2014-05-16 23:00 | 12.6 | 17.8 | 13.3
| 2014-05-16 23:30 | 11.6 | 17.8 | 13.3
| 2014-05-17 | 10.8 | 17.8 | 13.3
| 2014-05-17 00:30 | 10.3 | 17.2 | 13.3
| 2014-05-17 01:00 | 9.7 | 17.2 | 13.3
| 2014-05-17 01:30 | 9.2 | 17.2 | 13.3
| 2014-05-17 02:00 | 8.9 | 17.2 | 13.3
| 2014-05-17 02:30 | 8.9 | 16.7 | 13.3
| 2014-05-17 03:00 | 9.6 | 16.7 | 13.3
| 2014-05-17 03:30 | 9.8 | 16.7 | 13.3
| 2014-05-17 04:00 | 9.3 | 16.1 | 13.3
| 2014-05-17 04:30 | 8.6 | 16.1 | 13.3
| 2014-05-17 05:00 | 8.3 | 16.1 | 13.3
| 2014-05-17 05:30 | 7.8 | 16.1 | 13.3
| 2014-05-17 06:00 | 7.4 | 15.6 | 13.3
| 2014-05-17 06:30 | 7.3 | 15.6 | 13.3
| 2014-05-17 07:00 | 8.3 | 15.6 | 13.3
| 2014-05-17 07:30 | 9.8 | 15 | 13.3
| 2014-05-17 08:00 | 11.1 | 15 | 13.3
| 2014-05-17 08:30 | 12.1 | 15 | 13.3
| 2014-05-17 09:00 | 13.8 | 15 | 13.3
| 2014-05-17 09:30 | 14.5 | 14.4 | 13.3
| 2014-05-17 10:00 | 15.3 | 14.4 | 13.3
| 2014-05-17 10:30 | 16.1 | 14.4 | 13.3
| 2014-05-17 11:00 | 15.4 | 14.4 | 13.3
| 2014-05-17 11:30 | 16.7 | 14.4 | 13.3
| 2014-05-17 12:00 | 15.9 | 14.4 | 13.3
| 2014-05-17 12:30 | 17.3 | 15 | 13.3
| 2014-05-17 13:00 | 17.6 | 15 | 13.9
| 2014-05-17 13:30 | 17.9 | 15.6 | 13.9
| 2014-05-17 14:00 | 17.7 | 15.6 | 13.9
| 2014-05-17 14:30 | 18.6 | 16.1 | 13.9
| 2014-05-17 15:00 | 19.3 | 16.7 | 13.9
| 2014-05-17 15:30 | 19.3 | 16.7 | 13.9
| 2014-05-17 16:00 | 19.7 | 17.2 | 13.9
| 2014-05-17 16:30 | 19.8 | 17.8 | 13.9
| 2014-05-17 17:00 | 20.6 | 18.3 | 13.9
| 2014-05-17 17:30 | 19.8 | 18.3 | 13.9
| 2014-05-17 18:00 | 19.8 | 18.9 | 13.9
| 2014-05-17 18:30 | 20 | 18.9 | 13.9
| 2014-05-17 19:00 | 19.6 | 19.4 | 13.9
| 2014-05-17 19:30 | 19.3 | 19.4 | 13.9
| 2014-05-17 20:00 | 18.8 | 19.4 | 13.9
| 2014-05-17 20:30 | 18.4 | 19.4 | 13.9
| 2014-05-17 21:00 | 16.7 | 19.4 | 13.9
| 2014-05-17 21:30 | 15 | 19.4 | 13.9
| 2014-05-17 22:00 | 13.6 | 19.4 | 13.9
| 2014-05-17 22:30 | 12.8 | 19.4 | 13.9
| 2014-05-17 23:00 | 12.2 | 19.4 | 13.9
| 2014-05-17 23:30 | 11.7 | 19.4 | 13.9
| 2014-05-18 | 11.2 | 18.9 | 13.9
| 2014-05-18 00:30 | 10.9 | 18.9 | 13.9
| 2014-05-18 01:00 | 10.8 | 18.9 | 13.9
| 2014-05-18 01:30 | 10.3 | 18.3 | 13.9
| 2014-05-18 02:00 | 9.8 | 18.3 | 13.9
| 2014-05-18 02:30 | 9.6 | 18.3 | 13.9
| 2014-05-18 03:00 | 9.2 | 18.3 | 13.9
| 2014-05-18 03:30 | 8.4 | 17.8 | 13.9
| 2014-05-18 04:00 | 7.8 | 17.8 | 13.9
| 2014-05-18 04:30 | 7.6 | 17.8 | 13.9
| 2014-05-18 05:00 | 7.4 | 17.2 | 13.9
| 2014-05-18 05:30 | 7.2 | 17.2 | 13.9
| 2014-05-18 06:00 | 7 | 17.2 | 13.9
| 2014-05-18 06:30 | 7.1 | 16.7 | 13.9
| 2014-05-18 07:00 | 7.9 | 16.7 | 13.9
| 2014-05-18 07:30 | 8.7 | 16.7 | 13.9
| 2014-05-18 08:00 | 10.4 | 16.1 | 13.9
| 2014-05-18 08:30 | 12.2 | 16.1 | 13.9
| 2014-05-18 09:00 | 14.2 | 16.1 | 13.9
| 2014-05-18 09:30 | 15.5 | 16.1 | 13.9
| 2014-05-18 10:00 | 16.3 | 16.1 | 13.9
| 2014-05-18 10:30 | 17.4 | 16.1 | 13.9
| 2014-05-18 11:00 | 18.1 | 16.1 | 13.9
| 2014-05-18 11:30 | 18.4 | 16.1 | 13.9
| 2014-05-18 12:00 | 18.9 | 16.1 | 13.9
| 2014-05-18 12:30 | 19.7 | 16.1 | 13.9
| 2014-05-18 13:00 | 20.4 | 16.7 | 13.9
| 2014-05-18 13:30 | 20.7 | 16.7 | 13.9
| 2014-05-18 14:00 | 21 | 17.2 | 13.9
| 2014-05-18 14:30 | 21.1 | 17.2 | 13.9
| 2014-05-18 15:00 | 22.1 | 17.8 | 13.9
| 2014-05-18 15:30 | 20.5 | 17.8 | 13.9
| 2014-05-18 16:00 | 20.6 | 18.3 | 13.9
| 2014-05-18 16:30 | 20.9 | 18.3 | 13.9
| 2014-05-18 17:00 | 20.8 | 18.9 | 13.9
| 2014-05-18 17:30 | 20.7 | 18.9 | 13.9
| 2014-05-18 18:00 | 21.9 | 18.9 | 13.9
| 2014-05-18 18:30 | 21.9 | 19.4 | 13.9
| 2014-05-18 19:00 | 21.7 | 19.4 | 13.9
| 2014-05-18 19:30 | 20.7 | 19.4 | 13.9
| 2014-05-18 20:00 | 18.5 | 19.4 | 13.9
| 2014-05-18 20:30 | 18.3 | 19.4 | 13.9
| 2014-05-18 21:00 | 16.6 | 19.4 | 13.9
| 2014-05-18 21:30 | 15.8 | 19.4 | 13.9
| 2014-05-18 22:00 | 15.3 | 19.4 | 13.9
| 2014-05-18 22:30 | 14.6 | 19.4 | 13.9
| 2014-05-18 23:00 | 13.4 | 19.4 | 13.9
| 2014-05-18 23:30 | 12.4 | 18.9 | 13.9
| 2014-05-19 | 11.3 | 18.9 | 13.9
| 2014-05-19 00:30 | 10.7 | 18.9 | 13.9
| 2014-05-19 01:00 | 10.9 | 18.9 | 13.9
| 2014-05-19 01:30 | 10.3 | 18.3 | 13.9
| 2014-05-19 02:00 | 9.9 | 18.3 | 13.9
| 2014-05-19 02:30 | 10 | 18.3 | 13.9
| 2014-05-19 03:00 | 9.8 | 18.3 | 13.9
| 2014-05-19 03:30 | 9.2 | 17.8 | 13.9
| 2014-05-19 04:00 | 8.5 | 17.8 | 13.9
| 2014-05-19 04:30 | 8.1 | 17.8 | 13.9
| 2014-05-19 05:00 | 7.9 | 17.8 | 13.9
| 2014-05-19 05:30 | 7.7 | 17.2 | 13.9
| 2014-05-19 06:00 | 7.6 | 17.2 | 13.9
| 2014-05-19 06:30 | 7.7 | 17.2 | 13.9
| 2014-05-19 07:00 | 8.6 | 16.7 | 13.9
| 2014-05-19 07:30 | 9.8 | 16.7 | 13.9
| 2014-05-19 08:00 | 11.1 | 16.7 | 13.9
| 2014-05-19 08:30 | 13.2 | 16.7 | 14.4
| 2014-05-19 09:00 | 15.3 | 16.1 | 14.4
| 2014-05-19 09:30 | 16.9 | 16.1 | 14.4
| 2014-05-19 10:00 | 17.7 | 16.1 | 14.4
| 2014-05-19 10:30 | 18.7 | 16.1 | 14.4
| 2014-05-19 11:00 | 20 | 16.1 | 14.4
| 2014-05-19 11:30 | 20.8 | 16.1 | 14.4
| 2014-05-19 12:00 | 22.3 | 16.1 | 14.4
| 2014-05-19 12:30 | 22.7 | 16.7 | 14.4
| 2014-05-19 13:00 | 23.4 | 16.7 | 14.4
| 2014-05-19 13:30 | 23.3 | 17.2 | 14.4
| 2014-05-19 14:00 | 24 | 17.2 | 14.4
| 2014-05-19 14:30 | 24.8 | 17.8 | 14.4
| 2014-05-19 15:00 | 25.5 | 18.3 | 14.4
| 2014-05-19 15:30 | 25.7 | 18.3 | 14.4
| 2014-05-19 16:00 | 25.9 | 18.9 | 14.4
| 2014-05-19 16:30 | 25.9 | 19.4 | 14.4
| 2014-05-19 17:00 | 26.1 | 19.4 | 14.4
| 2014-05-19 17:30 | 26.3 | 20 | 14.4
| 2014-05-19 18:00 | 26 | 20.6 | 14.4
| 2014-05-19 18:30 | 25.4 | 20.6 | 14.4
| 2014-05-19 19:00 | 25.3 | 21.1 | 14.4
| 2014-05-19 19:30 | 24.2 | 21.1 | 14.4
| 2014-05-19 20:00 | 22.8 | 21.1 | 14.4
| 2014-05-19 20:30 | 22.2 | 21.1 | 14.4
| 2014-05-19 21:00 | 20.9 | 21.1 | 14.4
| 2014-05-19 21:30 | 19.4 | 21.1 | 14.4
| 2014-05-19 22:00 | 18 | 21.1 | 14.4
| 2014-05-19 22:30 | 16.6 | 21.1 | 14.4
| 2014-05-19 23:00 | 15.7 | 21.1 | 14.4
| 2014-05-19 23:30 | 15.3 | 21.1 | 14.4
| 2014-05-20 | 14.6 | 21.1 | 14.4
| 2014-05-20 00:30 | 14 | 20.6 | 14.4
| 2014-05-20 01:00 | 13.4 | 20.6 | 14.4
| 2014-05-20 01:30 | 13.1 | 20.6 | 14.4
| 2014-05-20 02:00 | 12.9 | 20 | 14.4
| 2014-05-20 02:30 | 12.5 | 20 | 14.4
| 2014-05-20 03:00 | 11.8 | 20 | 14.4
| 2014-05-20 03:30 | 11.2 | 20 | 14.4
| 2014-05-20 04:00 | 10.6 | 19.4 | 14.4
| 2014-05-20 04:30 | 10.4 | 19.4 | 14.4
| 2014-05-20 05:00 | 9.9 | 19.4 | 14.4
| 2014-05-20 05:30 | 9.6 | 18.9 | 14.4
| 2014-05-20 06:00 | 10.1 | 18.9 | 14.4
| 2014-05-20 06:30 | 10.8 | 18.9 | 14.4
| 2014-05-20 07:00 | 12.2 | 18.9 | 14.4
| 2014-05-20 07:30 | 13.8 | 18.3 | 14.4
| 2014-05-20 08:00 | 14.9 | 18.3 | 14.4
| 2014-05-20 08:30 | 15.2 | 18.3 | 14.4
| 2014-05-20 09:00 | 17.1 | 18.3 | 14.4
| 2014-05-20 09:30 | 18.6 | 18.3 | 14.4
| 2014-05-20 10:00 | 20.2 | 18.3 | 14.4
| 2014-05-20 10:30 | 21.6 | 18.3 | 14.4
| 2014-05-20 11:00 | 22.2 | 18.3 | 14.4
| 2014-05-20 11:30 | 23.6 | 18.3 | 14.4
| 2014-05-20 12:00 | 24.3 | 18.3 | 14.4
| 2014-05-20 12:30 | 25.2 | 18.3 | 14.4
| 2014-05-20 13:00 | 25.5 | 18.9 | 14.4
| 2014-05-20 13:30 | 26.2 | 18.9 | 14.4
| 2014-05-20 14:00 | 27.1 | 19.4 | 14.4
| 2014-05-20 14:30 | 27 | 19.4 | 14.4
| 2014-05-20 15:00 | 28 | 20 | 14.4
| 2014-05-20 15:30 | 28.7 | 20.6 | 14.4
| 2014-05-20 16:00 | 29 | 21.1 | 15
| 2014-05-20 16:30 | 29.3 | 21.1 | 15
| 2014-05-20 17:00 | 29.4 | 21.7 | 15
| 2014-05-20 17:30 | 29.4 | 22.2 | 15
| 2014-05-20 18:00 | 29.1 | 22.2 | 15
| 2014-05-20 18:30 | 28.9 | 22.8 | 15
| 2014-05-20 19:00 | 28.4 | 22.8 | 15
| 2014-05-20 19:30 | 27.3 | 23.3 | 15
| 2014-05-20 20:00 | 26.3 | 23.3 | 15
| 2014-05-20 20:30 | 25 | 23.3 | 15
| 2014-05-20 21:00 | 23.2 | 23.3 | 15
| 2014-05-20 21:30 | 21.7 | 23.3 | 15
| 2014-05-20 22:00 | 20.5 | 23.3 | 15
| 2014-05-20 22:30 | 19.8 | 23.3 | 15
| 2014-05-20 23:00 | 19.2 | 23.3 | 15
| 2014-05-20 23:30 | 18.8 | 23.3 | 15
| 2014-05-21 | 18.6 | 22.8 | 15
| 2014-05-21 00:30 | 17.3 | 22.8 | 15
| 2014-05-21 01:00 | 16.1 | 22.8 | 15
| 2014-05-21 01:30 | 15.6 | 22.2 | 15
| 2014-05-21 02:00 | 15.3 | 22.2 | 15
| 2014-05-21 02:30 | 14.7 | 22.2 | 15
| 2014-05-21 03:00 | 13.8 | 21.7 | 15
| 2014-05-21 03:30 | 13.6 | 21.7 | 15
| 2014-05-21 04:00 | 13.7 | 21.7 | 15
| 2014-05-21 04:30 | 13.2 | 21.7 | 15
| 2014-05-21 05:00 | 12.5 | 21.1 | 15
| 2014-05-21 05:30 | 12.3 | 21.1 | 15
| 2014-05-21 06:00 | 12.5 | 21.1 | 15
| 2014-05-21 06:30 | 12.9 | 20.6 | 15
| 2014-05-21 07:00 | 13.8 | 20.6 | 15
| 2014-05-21 07:30 | 15.4 | 20.6 | 15
| 2014-05-21 08:00 | 17.3 | 20.6 | 15
| 2014-05-21 08:30 | 18.7 | 20 | 15
| 2014-05-21 09:00 | 19.7 | 20 | 15
| 2014-05-21 09:30 | 21.1 | 20 | 15
| 2014-05-21 10:00 | 22.8 | 20 | 15
| 2014-05-21 10:30 | 24.8 | 20 | 15
| 2014-05-21 11:00 | 25.5 | 20 | 15
| 2014-05-21 11:30 | 26.8 | 20 | 15
| 2014-05-21 12:00 | 26.7 | 20 | 15
| 2014-05-21 12:30 | 28 | 20 | 15
| 2014-05-21 13:00 | 28.2 | 20.6 | 15
| 2014-05-21 13:30 | 29.8 | 20.6 | 15
| 2014-05-21 14:00 | 30.3 | 21.1 | 15
| 2014-05-21 14:30 | 29.7 | 21.1 | 15
| 2014-05-21 15:00 | 29.8 | 21.7 | 15
| 2014-05-21 15:30 | 30.7 | 22.2 | 15
| 2014-05-21 16:00 | 30.8 | 22.2 | 15
| 2014-05-21 16:30 | 30.6 | 22.8 | 15
| 2014-05-21 17:00 | 30.8 | 22.8 | 15
| 2014-05-21 17:30 | 30.9 | 23.3 | 15
| 2014-05-21 18:00 | 29.6 | 23.3 | 15.6
| 2014-05-21 18:30 | 28.9 | 23.9 | 15.6
| 2014-05-21 19:00 | 28.2 | 23.9 | 15.6
| 2014-05-21 19:30 | 27.3 | 23.9 | 15.6
| 2014-05-21 20:00 | 26.3 | 23.9 | 15.6
| 2014-05-21 20:30 | 25.1 | 23.9 | 15.6
| 2014-05-21 21:00 | 23.7 | 23.9 | 15.6
| 2014-05-21 21:30 | 22.1 | 23.9 | 15.6
| 2014-05-21 22:00 | 20.5 | 23.9 | 15.6
| 2014-05-21 22:30 | 19.7 | 23.9 | 15.6
| 2014-05-21 23:00 | 19.8 | 23.9 | 15.6
| 2014-05-21 23:30 | 20.8 | 23.9 | 15.6
| 2014-05-22 | 20.8 | 23.3 | 15.6
| 2014-05-22 00:30 | 20.3 | 23.3 | 15.6
| 2014-05-22 01:00 | 20.7 | 23.3 | 15.6
| 2014-05-22 01:30 | 20.7 | 23.3 | 15.6
| 2014-05-22 02:00 | 19.7 | 22.8 | 15.6
| 2014-05-22 02:30 | 19.7 | 22.8 | 15.6
| 2014-05-22 03:00 | 19.6 | 22.8 | 15.6
| 2014-05-22 03:30 | 18.3 | 22.2 | 15.6
| 2014-05-22 04:00 | 16.8 | 22.2 | 15.6
| 2014-05-22 04:30 | 16 | 22.2 | 15.6
| 2014-05-22 05:00 | 16.7 | 22.2 | 15.6
| 2014-05-22 05:30 | 15.7 | 21.7 | 15.6
| 2014-05-22 06:00 | 15.4 | 21.7 | 15.6
| 2014-05-22 06:30 | 16.3 | 21.7 | 15.6
| 2014-05-22 07:00 | 16.6 | 21.7 | 15.6
| 2014-05-22 07:30 | 17.4 | 21.1 | 15.6
| 2014-05-22 08:00 | 18.3 | 21.1 | 15.6
| 2014-05-22 08:30 | 19 | 21.1 | 15.6
| 2014-05-22 09:00 | 20.1 | 21.1 | 15.6
| 2014-05-22 09:30 | 21.2 | 21.1 | 15.6
| 2014-05-22 10:00 | 22.2 | 21.1 | 15.6
| 2014-05-22 10:30 | 22.9 | 20.6 | 15.6
| 2014-05-22 11:00 | 23.6 | 20.6 | 15.6
| 2014-05-22 11:30 | 24.3 | 20.6 | 15.6
| 2014-05-22 12:00 | 24.4 | 21.1 | 15.6
| 2014-05-22 12:30 | 25.3 | 21.1 | 15.6
| 2014-05-22 13:00 | 25.6 | 21.1 | 15.6
| 2014-05-22 13:30 | 26.3 | 21.7 | 16.1
| 2014-05-22 14:00 | 26.6 | 21.7 | 16.1
| 2014-05-22 14:30 | 27.2 | 22.2 | 16.1
| 2014-05-22 15:00 | 26.8 | 22.2 | 16.1
| 2014-05-22 15:30 | 26.3 | 22.8 | 16.1
| 2014-05-22 16:00 | 27.2 | 22.8 | 16.1
| 2014-05-22 16:30 | 27.3 | 23.3 | 16.1
| 2014-05-22 17:00 | 28.1 | 23.3 | 16.1
| 2014-05-22 17:30 | 28.1 | 23.9 | 16.1
| 2014-05-22 18:00 | 27.7 | 23.9 | 16.1
| 2014-05-22 18:30 | 26.3 | 24.4 | 16.1
| 2014-05-22 19:00 | 19.6 | 24.4 | 16.1
| 2014-05-22 19:30 | 17.2 | 24.4 | 16.1
| 2014-05-22 20:00 | 16.8 | 24.4 | 16.1
| 2014-05-22 20:30 | 16.9 | 24.4 | 16.1
| 2014-05-22 21:00 | 16.9 | 24.4 | 16.1
| 2014-05-22 21:30 | 16.9 | 24.4 | 16.1
| 2014-05-22 22:00 | 16.4 | 24.4 | 16.1
| 2014-05-22 22:30 | 16.1 | 23.9 | 16.1
| 2014-05-22 23:00 | 15.7 | 23.9 | 16.1
| 2014-05-22 23:30 | 15.4 | 23.9 | 16.1
| 2014-05-23 | 14.8 | 23.3 | 16.1
| 2014-05-23 00:30 | 14.1 | 23.3 | 16.1
| 2014-05-23 01:00 | 14 | 23.3 | 16.1
| 2014-05-23 01:30 | 14.1 | 22.8 | 16.1
| 2014-05-23 02:00 | 14 | 22.8 | 16.1
| 2014-05-23 02:30 | 14 | 22.2 | 16.1
| 2014-05-23 03:00 | 14.1 | 22.2 | 16.1
| 2014-05-23 03:30 | 13.9 | 22.2 | 16.1
| 2014-05-23 04:00 | 13.8 | 22.2 | 16.1
| 2014-05-23 04:30 | 13.8 | 21.7 | 16.1
| 2014-05-23 05:00 | 13.9 | 21.7 | 16.1
| 2014-05-23 05:30 | 14 | 21.7 | 16.1
| 2014-05-23 06:00 | 13.8 | 21.1 | 16.1
| 2014-05-23 06:30 | 14 | 21.1 | 16.1
| 2014-05-23 07:00 | 14.2 | 21.1 | 16.1
| 2014-05-23 07:30 | 14.3 | 21.1 | 16.1
| 2014-05-23 08:00 | 14.1 | 21.1 | 16.1
| 2014-05-23 08:30 | 13.8 | 20.6 | 16.1
| 2014-05-23 09:00 | 13.7 | 20.6 | 16.1
| 2014-05-23 09:30 | 13.7 | 20.6 | 16.1
| 2014-05-23 10:00 | 13.8 | 20.6 | 16.1
| 2014-05-23 10:30 | 14.1 | 20 | 16.1
| 2014-05-23 11:00 | 14.4 | 20 | 16.1
| 2014-05-23 11:30 | 15.2 | 20 | 16.1
| 2014-05-23 12:00 | 16.6 | 20 | 16.1
| 2014-05-23 12:30 | 17.8 | 20 | 16.1
| 2014-05-23 13:00 | 18.3 | 20 | 16.1
| 2014-05-23 13:30 | 17.6 | 20 | 16.1
| 2014-05-23 14:00 | 18.2 | 20 | 16.1
| 2014-05-23 14:30 | 19 | 20 | 16.1
| 2014-05-23 15:00 | 19.7 | 20.6 | 16.7
| 2014-05-23 15:30 | 20.6 | 20.6 | 16.7
| 2014-05-23 16:00 | 20.8 | 20.6 | 16.7
| 2014-05-23 16:30 | 21.8 | 21.1 | 16.7
| 2014-05-23 17:00 | 21.8 | 21.1 | 16.7
| 2014-05-23 17:30 | 23.3 | 21.1 | 16.7
| 2014-05-23 18:00 | 22.8 | 21.7 | 16.7
| 2014-05-23 18:30 | 22.3 | 21.7 | 16.7
| 2014-05-23 19:00 | 22.2 | 21.7 | 16.7
| 2014-05-23 19:30 | 21.6 | 21.7 | 16.7
| 2014-05-23 20:00 | 22.1 | 22.2 | 16.7
| 2014-05-23 20:30 | 21.3 | 22.2 | 16.7
| 2014-05-23 21:00 | 19.1 | 22.2 | 16.7
| 2014-05-23 21:30 | 17.1 | 21.7 | 16.7
| 2014-05-23 22:00 | 15.7 | 21.7 | 16.7
| 2014-05-23 22:30 | 14.9 | 21.7 | 16.7
| 2014-05-23 23:00 | 14.3 | 21.7 | 16.7
| 2014-05-23 23:30 | 14.1 | 21.7 | 16.7
| 2014-05-24 | 13.8 | 21.1 | 16.7
| 2014-05-24 00:30 | 13.3 | 21.1 | 16.7
| 2014-05-24 01:00 | 13.6 | 21.1 | 16.7
| 2014-05-24 01:30 | 13.4 | 20.6 | 16.7
| 2014-05-24 02:00 | 13.2 | 20.6 | 16.7
| 2014-05-24 02:30 | 12.6 | 20.6 | 16.7
| 2014-05-24 03:00 | 12 | 20 | 16.7
| 2014-05-24 03:30 | 11.6 | 20 | 16.7
| 2014-05-24 04:00 | 12.3 | 20 | 16.7
| 2014-05-24 04:30 | 13 | 20 | 16.7
| 2014-05-24 05:00 | 13.7 | 19.4 | 16.7
| 2014-05-24 05:30 | 13.1 | 19.4 | 16.7
| 2014-05-24 06:00 | 13.1 | 19.4 | 16.7
| 2014-05-24 06:30 | 13.1 | 19.4 | 16.7
| 2014-05-24 07:00 | 13.3 | 18.9 | 16.7
| 2014-05-24 07:30 | 13.9 | 18.9 | 16.7
| 2014-05-24 08:00 | 13.7 | 18.9 | 16.7
| 2014-05-24 08:30 | 13.6 | 18.9 | 16.7
| 2014-05-24 09:00 | 13.4 | 18.9 | 16.7
| 2014-05-24 09:30 | 13.7 | 18.9 | 16.7
| 2014-05-24 10:00 | 14.1 | 18.3 | 16.7
| 2014-05-24 10:30 | 14.3 | 18.3 | 16.7
| 2014-05-24 11:00 | 14.3 | 18.3 | 16.7
| 2014-05-24 11:30 | 14.9 | 18.3 | 16.7
| 2014-05-24 12:00 | 14.7 | 18.3 | 16.7
| 2014-05-24 12:30 | 14.2 | 18.3 | 16.7
| 2014-05-24 13:00 | 13.8 | 18.3 | 16.7
| 2014-05-24 13:30 | 14.9 | 18.3 | 16.7
| 2014-05-24 14:00 | 16.5 | 18.3 | 16.7
| 2014-05-24 14:30 | 17.7 | 18.9 | 16.7
| 2014-05-24 15:00 | 17.4 | 18.9 | 16.7
| 2014-05-24 15:30 | 18.9 | 18.9 | 16.7
| 2014-05-24 16:00 | 17.9 | 18.9 | 16.7
| 2014-05-24 16:30 | 18.2 | 18.9 | 16.7
| 2014-05-24 17:00 | 18.8 | 19.4 | 16.7
| 2014-05-24 17:30 | 19.1 | 19.4 | 16.7
| 2014-05-24 18:00 | 19.7 | 19.4 | 16.7
| 2014-05-24 18:30 | 19.1 | 19.4 | 16.7
| 2014-05-24 19:00 | 18.8 | 19.4 | 16.7
| 2014-05-24 19:30 | 18.6 | 19.4 | 16.7
| 2014-05-24 20:00 | 18.1 | 20 | 16.7
| 2014-05-24 20:30 | 16.9 | 20 | 16.7
| 2014-05-24 21:00 | 15.6 | 20 | 16.7
| 2014-05-24 21:30 | 13.7 | 19.4 | 16.7
| 2014-05-24 22:00 | 12.2 | 19.4 | 16.7
| 2014-05-24 22:30 | 11.1 | 19.4 | 16.7
| 2014-05-24 23:00 | 10.5 | 19.4 | 16.7
| 2014-05-24 23:30 | 10.1 | 19.4 | 16.7
| 2014-05-25 | 9.6 | 18.9 | 16.7
| 2014-05-25 00:30 | 9.2 | 18.9 | 16.7
| 2014-05-25 01:00 | 8.7 | 18.9 | 16.7
| 2014-05-25 01:30 | 8.2 | 18.9 | 16.7
| 2014-05-25 02:00 | 8 | 18.3 | 16.7
| 2014-05-25 02:30 | 7.6 | 18.3 | 16.7
| 2014-05-25 03:00 | 7 | 18.3 | 16.7
| 2014-05-25 03:30 | 6.7 | 17.8 | 16.7
| 2014-05-25 04:00 | 6.6 | 17.8 | 16.7
| 2014-05-25 04:30 | 6.4 | 17.8 | 16.7
| 2014-05-25 05:00 | 6.2 | 17.8 | 16.7
| 2014-05-25 05:30 | 6.1 | 17.2 | 16.7
| 2014-05-25 06:00 | 6.1 | 17.2 | 16.7
| 2014-05-25 06:30 | 6.2 | 17.2 | 16.7
| 2014-05-25 07:00 | 6.9 | 16.7 | 16.7
| 2014-05-25 07:30 | 8.7 | 16.7 | 16.7
| 2014-05-25 08:00 | 10.4 | 16.7 | 16.7
| 2014-05-25 08:30 | 13.1 | 16.7 | 16.7
| 2014-05-25 09:00 | 15.3 | 16.1 | 16.7
| 2014-05-25 09:30 | 16.8 | 16.1 | 16.7
| 2014-05-25 10:00 | 17.8 | 16.1 | 16.7
| 2014-05-25 10:30 | 18.7 | 16.1 | 16.7
| 2014-05-25 11:00 | 19.4 | 16.1 | 16.7
| 2014-05-25 11:30 | 21.1 | 16.1 | 16.7
| 2014-05-25 12:00 | 21.2 | 16.7 | 16.7
| 2014-05-25 12:30 | 21.5 | 16.7 | 16.7
| 2014-05-25 13:00 | 22.1 | 17.2 | 16.7
| 2014-05-25 13:30 | 22.3 | 17.2 | 16.7
| 2014-05-25 14:00 | 22.8 | 17.8 | 16.7
| 2014-05-25 14:30 | 23.3 | 18.3 | 16.7
| 2014-05-25 15:00 | 24.3 | 18.3 | 16.7
| 2014-05-25 15:30 | 24.4 | 18.9 | 16.7
| 2014-05-25 16:00 | 23.9 | 19.4 | 16.7
| 2014-05-25 16:30 | 23.6 | 20 | 16.7
| 2014-05-25 17:00 | 24.2 | 20 | 16.7
| 2014-05-25 17:30 | 24.3 | 20.6 | 16.7
| 2014-05-25 18:00 | 24.4 | 21.1 | 16.7
| 2014-05-25 18:30 | 24.2 | 21.1 | 16.7
| 2014-05-25 19:00 | 23.3 | 21.7 | 16.7
| 2014-05-25 19:30 | 22.5 | 21.7 | 16.7
| 2014-05-25 20:00 | 21.6 | 21.7 | 16.7
| 2014-05-25 20:30 | 20.7 | 21.7 | 16.7
| 2014-05-25 21:00 | 19.7 | 21.7 | 16.7
| 2014-05-25 21:30 | 18.8 | 21.7 | 16.7
| 2014-05-25 22:00 | 18.1 | 21.7 | 16.7
| 2014-05-25 22:30 | 17.4 | 21.7 | 16.7
| 2014-05-25 23:00 | 17.2 | 21.7 | 16.7
| 2014-05-25 23:30 | 17.2 | 21.7 | 16.7
| 2014-05-26 | 17.3 | 21.7 | 16.7
| 2014-05-26 00:30 | 16.9 | 21.1 | 16.7
| 2014-05-26 01:00 | 16.7 | 21.1 | 16.7
| 2014-05-26 01:30 | 16.4 | 21.1 | 16.7
| 2014-05-26 02:00 | 16.6 | 21.1 | 16.7
| 2014-05-26 02:30 | 16.4 | 20.6 | 16.7
| 2014-05-26 03:00 | 16.5 | 20.6 | 16.7
| 2014-05-26 03:30 | 16.1 | 20.6 | 16.7
| 2014-05-26 04:00 | 15.7 | 20.6 | 16.7
| 2014-05-26 04:30 | 15.2 | 20 | 16.7
| 2014-05-26 05:00 | 14.2 | 20 | 16.7
| 2014-05-26 05:30 | 13.7 | 20 | 16.7
| 2014-05-26 06:00 | 13.4 | 20 | 16.7
| 2014-05-26 06:30 | 13.4 | 19.4 | 16.7
| 2014-05-26 07:00 | 13.6 | 19.4 | 16.7
| 2014-05-26 07:30 | 14.2 | 19.4 | 16.7
| 2014-05-26 08:00 | 14.1 | 19.4 | 16.7
| 2014-05-26 08:30 | 13.8 | 19.4 | 16.7
| 2014-05-26 09:00 | 14.2 | 18.9 | 16.7
| 2014-05-26 09:30 | 14.4 | 18.9 | 16.7
| 2014-05-26 10:00 | 14.4 | 18.9 | 16.7
| 2014-05-26 10:30 | 14.4 | 18.9 | 16.7
| 2014-05-26 11:00 | 14.6 | 18.9 | 16.7
| 2014-05-26 11:30 | 15.7 | 18.9 | 16.7
| 2014-05-26 12:00 | 16.4 | 18.9 | 16.7
| 2014-05-26 12:30 | 17.1 | 18.9 | 16.7
| 2014-05-26 13:00 | 17.6 | 18.9 | 16.7
| 2014-05-26 13:30 | 18.1 | 18.9 | 16.7
| 2014-05-26 14:00 | 18.4 | 19.4 | 16.7
| 2014-05-26 14:30 | 18.7 | 19.4 | 16.7
| 2014-05-26 15:00 | 19.2 | 19.4 | 16.7
| 2014-05-26 15:30 | 19.6 | 19.4 | 16.7
| 2014-05-26 16:00 | 20 | 20 | 16.7
| 2014-05-26 16:30 | 20 | 20 | 16.7
| 2014-05-26 17:00 | 20.2 | 20 | 16.7
| 2014-05-26 17:30 | 20 | 20.6 | 16.7
| 2014-05-26 18:00 | 20.2 | 20.6 | 16.7
| 2014-05-26 18:30 | 20.4 | 20.6 | 16.7
| 2014-05-26 19:00 | 20.1 | 20.6 | 16.7
| 2014-05-26 19:30 | 19.8 | 20.6 | 16.7
| 2014-05-26 20:00 | 19.6 | 20.6 | 16.7
| 2014-05-26 20:30 | 19.1 | 20.6 | 16.7
| 2014-05-26 21:00 | 16.7 | 20.6 | 16.7
| 2014-05-26 21:30 | 15.2 | 20.6 | 16.7
| 2014-05-26 22:00 | 14.8 | 20.6 | 16.7
| 2014-05-26 22:30 | 14.9 | 20.6 | 16.7
| 2014-05-26 23:00 | 14.9 | 20.6 | 16.7
| 2014-05-26 23:30 | 14.9 | 20.6 | 16.7
| 2014-05-27 | 14.9 | 20 | 16.7
| 2014-05-27 00:30 | 14.7 | 20 | 16.7
| 2014-05-27 01:00 | 14.7 | 20 | 16.7
| 2014-05-27 01:30 | 14.8 | 20 | 16.7
| 2014-05-27 02:00 | 14.6 | 19.4 | 16.7
| 2014-05-27 02:30 | 14.4 | 19.4 | 16.7
| 2014-05-27 03:00 | 14.4 | 19.4 | 16.7
| 2014-05-27 03:30 | 14.4 | 19.4 | 16.7
| 2014-05-27 04:00 | 14.4 | 19.4 | 16.7
| 2014-05-27 04:30 | 14.4 | 18.9 | 16.7
| 2014-05-27 05:00 | 14.4 | 18.9 | 16.7
| 2014-05-27 05:30 | 14.2 | 18.9 | 16.7
| 2014-05-27 06:00 | 14.2 | 18.9 | 16.7
| 2014-05-27 06:30 | 14.3 | 18.9 | 16.7
| 2014-05-27 07:00 | 14.4 | 18.9 | 16.7
| 2014-05-27 07:30 | 14.6 | 18.3 | 16.7
| 2014-05-27 08:00 | 14.9 | 18.3 | 16.7
| 2014-05-27 08:30 | 15.5 | 18.3 | 16.7
| 2014-05-27 09:00 | 15.9 | 18.3 | 16.7
| 2014-05-27 09:30 | 16.3 | 18.3 | 16.7
| 2014-05-27 10:00 | 16.1 | 18.3 | 16.7
| 2014-05-27 10:30 | 16.9 | 18.3 | 16.7
| 2014-05-27 11:00 | 17.6 | 18.3 | 16.7
| 2014-05-27 11:30 | 17.3 | 18.3 | 16.7
| 2014-05-27 12:00 | 17.4 | 18.3 | 16.7
| 2014-05-27 12:30 | 18.2 | 18.3 | 16.7
| 2014-05-27 13:00 | 18.7 | 18.3 | 16.7
| 2014-05-27 13:30 | 19.3 | 18.9 | 16.7
| 2014-05-27 14:00 | 19.5 | 18.9 | 16.7
| 2014-05-27 14:30 | 20 | 18.9 | 16.7
| 2014-05-27 15:00 | 20.3 | 18.9 | 16.7
| 2014-05-27 15:30 | 18.5 | 19.4 | 16.7
| 2014-05-27 16:00 | 18.1 | 19.4 | 16.7
| 2014-05-27 16:30 | 18.3 | 19.4 | 16.7
| 2014-05-27 17:00 | 18 | 19.4 | 16.7
| 2014-05-27 17:30 | 18.1 | 19.4 | 16.7
| 2014-05-27 18:00 | 18.1 | 19.4 | 16.7
| 2014-05-27 18:30 | 17.8 | 19.4 | 16.7
| 2014-05-27 19:00 | 18.3 | 19.4 | 16.7
| 2014-05-27 19:30 | 17.8 | 19.4 | 16.7
| 2014-05-27 20:00 | 17.5 | 19.4 | 16.7
| 2014-05-27 20:30 | 16.9 | 19.4 | 16.7
| 2014-05-27 21:00 | 16.6 | 19.4 | 16.7
| 2014-05-27 21:30 | 16.2 | 19.4 | 16.7
| 2014-05-27 22:00 | 15.8 | 19.4 | 16.7
| 2014-05-27 22:30 | 15.6 | 19.4 | 16.7
| 2014-05-27 23:00 | 15.1 | 18.9 | 16.7
| 2014-05-27 23:30 | 14.8 | 18.9 | 16.7
| 2014-05-28 | 14.7 | 18.9 | 16.7
| 2014-05-28 00:30 | 14.7 | 18.9 | 16.7
| 2014-05-28 01:00 | 14.4 | 18.9 | 16.7
| 2014-05-28 01:30 | 14.1 | 18.3 | 16.7
| 2014-05-28 02:00 | 13.9 | 18.3 | 16.7
| 2014-05-28 02:30 | 13.6 | 18.3 | 16.7
| 2014-05-28 03:00 | 13.3 | 18.3 | 16.7
| 2014-05-28 03:30 | 12.9 | 18.3 | 16.7
| 2014-05-28 04:00 | 12.9 | 18.3 | 16.7
| 2014-05-28 04:30 | 12.4 | 18.3 | 16.7
| 2014-05-28 05:00 | 11.9 | 17.8 | 16.7
| 2014-05-28 05:30 | 11.8 | 17.8 | 16.7
| 2014-05-28 06:00 | 11.8 | 17.8 | 16.7
| 2014-05-28 06:30 | 12.4 | 17.8 | 16.7
| 2014-05-28 07:00 | 12.9 | 17.8 | 16.7
| 2014-05-28 07:30 | 13.3 | 17.2 | 16.7
| 2014-05-28 08:00 | 13.8 | 17.2 | 16.7
| 2014-05-28 08:30 | 14.2 | 17.2 | 16.7
| 2014-05-28 09:00 | 14.4 | 17.2 | 16.7
| 2014-05-28 09:30 | 15.1 | 17.2 | 16.7
| 2014-05-28 10:00 | 15.4 | 17.2 | 16.7
| 2014-05-28 10:30 | 15.6 | 17.2 | 16.7
| 2014-05-28 11:00 | 16.1 | 17.2 | 16.7
| 2014-05-28 11:30 | 16.2 | 17.2 | 16.7
| 2014-05-28 12:00 | 16.3 | 17.2 | 16.7
| 2014-05-28 12:30 | 16.8 | 17.2 | 16.7
| 2014-05-28 13:00 | 16.7 | 17.2 | 16.7
| 2014-05-28 13:30 | 16.9 | 17.2 | 16.7
| 2014-05-28 14:00 | 17.1 | 17.2 | 16.7
| 2014-05-28 14:30 | 17.6 | 17.2 | 16.7
| 2014-05-28 15:00 | 17.2 | 17.8 | 16.7
| 2014-05-28 15:30 | 18.2 | 17.8 | 16.7
| 2014-05-28 16:00 | 18.6 | 17.8 | 16.7
| 2014-05-28 16:30 | 18 | 17.8 | 16.7
| 2014-05-28 17:00 | 18.4 | 17.8 | 16.7
| 2014-05-28 17:30 | 19.5 | 17.8 | 16.7
| 2014-05-28 18:00 | 19.4 | 17.8 | 16.7
| 2014-05-28 18:30 | 19.2 | 18.3 | 16.7
| 2014-05-28 19:00 | 19.1 | 18.3 | 16.7
| 2014-05-28 19:30 | 19.3 | 18.3 | 16.7
| 2014-05-28 20:00 | 19.3 | 18.3 | 16.7
| 2014-05-28 20:30 | 18.9 | 18.3 | 16.7
| 2014-05-28 21:00 | 18 | 18.3 | 16.7
| 2014-05-28 21:30 | 17.1 | 18.3 | 16.7
| 2014-05-28 22:00 | 15.9 | 18.3 | 16.7
| 2014-05-28 22:30 | 14.9 | 18.3 | 16.7
| 2014-05-28 23:00 | 14.1 | 18.3 | 16.7
| 2014-05-28 23:30 | 13.6 | 18.3 | 16.7
| 2014-05-29 | 13.4 | 18.3 | 16.7
| 2014-05-29 00:30 | 13.2 | 18.3 | 16.7
| 2014-05-29 01:00 | 13.1 | 17.8 | 16.7
| 2014-05-29 01:30 | 12.7 | 17.8 | 16.7
| 2014-05-29 02:00 | 12.3 | 17.8 | 16.7
| 2014-05-29 02:30 | 12.1 | 17.8 | 16.7
| 2014-05-29 03:00 | 11.8 | 17.8 | 16.7
| 2014-05-29 03:30 | 11.7 | 17.2 | 16.7
| 2014-05-29 04:00 | 11.7 | 17.2 | 16.7
| 2014-05-29 04:30 | 11.6 | 17.2 | 16.7
| 2014-05-29 05:00 | 11.5 | 17.2 | 16.7
| 2014-05-29 05:30 | 11.4 | 17.2 | 16.7
| 2014-05-29 06:00 | 11.3 | 17.2 | 16.7
| 2014-05-29 06:30 | 11.6 | 16.7 | 16.7
| 2014-05-29 07:00 | 11.9 | 16.7 | 16.7
| 2014-05-29 07:30 | 12.3 | 16.7 | 16.7
| 2014-05-29 08:00 | 12.8 | 16.7 | 16.7
| 2014-05-29 08:30 | 13.2 | 16.7 | 16.7
| 2014-05-29 09:00 | 13.6 | 16.7 | 16.7
| 2014-05-29 09:30 | 13.8 | 16.7 | 16.7
| 2014-05-29 10:00 | 14.4 | 16.7 | 16.7
| 2014-05-29 10:30 | 14.8 | 16.7 | 16.7
| 2014-05-29 11:00 | 15.5 | 16.7 | 16.7
| 2014-05-29 11:30 | 16.1 | 16.7 | 16.7
| 2014-05-29 12:00 | 16.5 | 16.7 | 16.7
| 2014-05-29 12:30 | 16.8 | 16.7 | 16.7
| 2014-05-29 13:00 | 16.8 | 16.7 | 16.7
| 2014-05-29 13:30 | 16.7 | 17.2 | 16.7
| 2014-05-29 14:00 | 16.8 | 17.2 | 16.7
| 2014-05-29 14:30 | 16.9 | 17.2 | 16.7
| 2014-05-29 15:00 | 16.8 | 17.2 | 16.7
| 2014-05-29 15:30 | 17.1 | 17.2 | 16.7
| 2014-05-29 16:00 | 17.1 | 17.8 | 16.7
| 2014-05-29 16:30 | 17.3 | 17.8 | 16.7
| 2014-05-29 17:00 | 16.9 | 17.8 | 16.7
| 2014-05-29 17:30 | 16.4 | 17.8 | 16.7
| 2014-05-29 18:00 | 15.8 | 17.8 | 16.7
| 2014-05-29 18:30 | 15.4 | 17.8 | 16.7
| 2014-05-29 19:00 | 14.9 | 17.8 | 16.7
| 2014-05-29 19:30 | 14.5 | 17.8 | 16.7
| 2014-05-29 20:00 | 14.1 | 18.3 | 16.7
| 2014-05-29 20:30 | 13.3 | 18.3 | 16.7
| 2014-05-29 21:00 | 12.8 | 17.8 | 16.7
| 2014-05-29 21:30 | 12.2 | 17.8 | 16.7
| 2014-05-29 22:00 | 11.8 | 17.8 | 16.7
| 2014-05-29 22:30 | 11.4 | 17.8 | 16.7
| 2014-05-29 23:00 | 11.1 | 17.8 | 16.7
| 2014-05-29 23:30 | 10.9 | 17.8 | 16.7
| 2014-05-30 | 10.8 | 17.8 | 16.7
| 2014-05-30 00:30 | 10.8 | 17.8 | 16.7
| 2014-05-30 01:00 | 10.7 | 17.2 | 16.7
| 2014-05-30 01:30 | 10.6 | 17.2 | 16.7
| 2014-05-30 02:00 | 9.8 | 17.2 | 16.7
| 2014-05-30 02:30 | 9.6 | 17.2 | 16.7
| 2014-05-30 03:00 | 9.7 | 17.2 | 16.7
| 2014-05-30 03:30 | 9.8 | 16.7 | 16.7
| 2014-05-30 04:00 | 9.8 | 16.7 | 16.7
| 2014-05-30 04:30 | 9.7 | 16.7 | 16.7
| 2014-05-30 05:00 | 9.6 | 16.7 | 16.7
| 2014-05-30 05:30 | 9.3 | 16.7 | 16.7
| 2014-05-30 06:00 | 8.9 | 16.7 | 16.7
| 2014-05-30 06:30 | 9.1 | 16.1 | 16.7
| 2014-05-30 07:00 | 9.4 | 16.1 | 16.7
| 2014-05-30 07:30 | 10.3 | 16.1 | 16.7
| 2014-05-30 08:00 | 10.6 | 16.1 | 16.7
| 2014-05-30 08:30 | 11.2 | 16.1 | 16.7
| 2014-05-30 09:00 | 12.5 | 16.1 | 16.7
| 2014-05-30 09:30 | 12.8 | 16.1 | 16.7
| 2014-05-30 10:00 | 12.8 | 16.1 | 16.7
| 2014-05-30 10:30 | 12.9 | 16.1 | 16.7
| 2014-05-30 11:00 | 13.1 | 16.1 | 16.7
| 2014-05-30 11:30 | 13.4 | 16.1 | 16.7
| 2014-05-30 12:00 | 13.7 | 16.1 | 16.7
| 2014-05-30 12:30 | 13.7 | 16.1 | 16.1
| 2014-05-30 13:00 | 13.8 | 16.1 | 16.1
| 2014-05-30 13:30 | 14.4 | 16.1 | 16.1
| 2014-05-30 14:00 | 14.2 | 16.1 | 16.1
| 2014-05-30 14:30 | 13.8 | 16.1 | 16.1
| 2014-05-30 15:00 | 13.9 | 16.7 | 16.1
| 2014-05-30 15:30 | 14.1 | 16.7 | 16.1
| 2014-05-30 16:00 | 14.8 | 16.7 | 16.1
| 2014-05-30 16:30 | 14.8 | 16.7 | 16.1
| 2014-05-30 17:00 | 14.3 | 16.7 | 16.1
| 2014-05-30 17:30 | 15.1 | 16.7 | 16.1
| 2014-05-30 18:00 | 16.6 | 17.2 | 16.1
| 2014-05-30 18:30 | 15.7 | 17.2 | 16.1
| 2014-05-30 19:00 | 16 | 17.2 | 16.1
| 2014-05-30 19:30 | 15.2 | 17.2 | 16.1
| 2014-05-30 20:00 | 15.3 | 17.2 | 16.1
| 2014-05-30 20:30 | 14.9 | 17.2 | 16.1
| 2014-05-30 21:00 | 13.1 | 17.2 | 16.1
| 2014-05-30 21:30 | 11.3 | 17.2 | 16.1
| 2014-05-30 22:00 | 10.1 | 17.2 | 16.1
| 2014-05-30 22:30 | 9.2 | 17.2 | 16.1
| 2014-05-30 23:00 | 8.5 | 17.2 | 16.1
| 2014-05-30 23:30 | 7.7 | 16.7 | 16.1
| 2014-05-31 | 7.4 | 16.7 | 16.1
| 2014-05-31 00:30 | 6.8 | 16.7 | 16.1
| 2014-05-31 01:00 | 6.3 | 16.7 | 16.1
| 2014-05-31 01:30 | 6 | 16.1 | 16.1
| 2014-05-31 02:00 | 5.7 | 16.1 | 16.1
| 2014-05-31 02:30 | 5.5 | 16.1 | 16.1
| 2014-05-31 03:00 | 5.5 | 16.1 | 16.1
| 2014-05-31 03:30 | 5.2 | 15.6 | 16.1
| 2014-05-31 04:00 | 5 | 15.6 | 16.1
| 2014-05-31 04:30 | 4.8 | 15.6 | 16.1
| 2014-05-31 05:00 | 4.6 | 15.6 | 16.1
| 2014-05-31 05:30 | 4.3 | 15 | 16.1
| 2014-05-31 06:00 | 4.4 | 15 | 16.1
| 2014-05-31 06:30 | 4.9 | 15 | 16.1
| 2014-05-31 07:00 | 5.8 | 15 | 16.1
| 2014-05-31 07:30 | 7.1 | 14.4 | 16.1
| 2014-05-31 08:00 | 9.3 | 14.4 | 16.1
| 2014-05-31 08:30 | 11.4 | 14.4 | 16.1
| 2014-05-31 09:00 | 12.6 | 14.4 | 16.1
| 2014-05-31 09:30 | 13.8 | 14.4 | 16.1
| 2014-05-31 10:00 | 15.7 | 14.4 | 16.1
| 2014-05-31 10:30 | 16.4 | 14.4 | 16.1
| 2014-05-31 11:00 | 18.3 | 14.4 | 16.1
| 2014-05-31 11:30 | 19.6 | 14.4 | 16.1
| 2014-05-31 12:00 | 19.6 | 14.4 | 16.1
| 2014-05-31 12:30 | 19.3 | 15 | 16.1
| 2014-05-31 13:00 | 20.4 | 15 | 16.1
| 2014-05-31 13:30 | 19.9 | 15.6 | 16.1
| 2014-05-31 14:00 | 19.5 | 16.1 | 16.1
| 2014-05-31 14:30 | 20.6 | 16.7 | 16.1
| 2014-05-31 15:00 | 21.8 | 16.7 | 16.1
| 2014-05-31 15:30 | 20.5 | 17.2 | 16.1
| 2014-05-31 16:00 | 22.3 | 17.8 | 16.1
| 2014-05-31 16:30 | 21.2 | 18.3 | 16.1
| 2014-05-31 17:00 | 21.2 | 18.3 | 16.1
| 2014-05-31 17:30 | 22.8 | 18.9 | 16.1
| 2014-05-31 18:00 | 20.8 | 18.9 | 16.1
| 2014-05-31 18:30 | 20.1 | 19.4 | 16.1
| 2014-05-31 19:00 | 19.4 | 19.4 | 16.1
| 2014-05-31 19:30 | 19.5 | 19.4 | 16.1
| 2014-05-31 20:00 | 19.9 | 19.4 | 16.1
| 2014-05-31 20:30 | 18.6 | 19.4 | 16.1
| 2014-05-31 21:00 | 16.6 | 19.4 | 16.1
| 2014-05-31 21:30 | 14.9 | 19.4 | 16.1
| 2014-05-31 22:00 | 13.8 | 19.4 | 16.1
| 2014-05-31 22:30 | 12.8 | 19.4 | 16.1
| 2014-05-31 23:00 | 12.1 | 19.4 | 16.1
| 2014-05-31 23:30 | 11.9 | 18.9 | 16.1
| 2014-06-01 | 12.2 | 18.9 | 16.1
| 2014-06-01 00:30 | 12.3 | 18.9 | 16.1
| 2014-06-01 01:00 | 12.2 | 18.9 | 16.1
| 2014-06-01 01:30 | 12.3 | 18.3 | 16.1
| 2014-06-01 02:00 | 11.6 | 18.3 | 16.1
| 2014-06-01 02:30 | 11.3 | 18.3 | 16.1
| 2014-06-01 03:00 | 10.9 | 18.3 | 16.1
| 2014-06-01 03:30 | 10.2 | 18.3 | 16.1
| 2014-06-01 04:00 | 9.6 | 17.8 | 16.1
| 2014-06-01 04:30 | 9.6 | 17.8 | 16.1
| 2014-06-01 05:00 | 10.1 | 17.8 | 16.1
| 2014-06-01 05:30 | 10.3 | 17.8 | 16.1
| 2014-06-01 06:00 | 11.4 | 17.2 | 16.1
| 2014-06-01 06:30 | 11.9 | 17.2 | 16.1
| 2014-06-01 07:00 | 12.1 | 17.2 | 16.1
| 2014-06-01 07:30 | 12.7 | 17.2 | 16.1
| 2014-06-01 08:00 | 13.6 | 16.7 | 16.1
| 2014-06-01 08:30 | 14.3 | 16.7 | 16.1
| 2014-06-01 09:00 | 15.3 | 16.7 | 16.1
| 2014-06-01 09:30 | 16.2 | 16.7 | 16.1
| 2014-06-01 10:00 | 18.2 | 16.7 | 16.1
| 2014-06-01 10:30 | 18.6 | 16.7 | 16.1
| 2014-06-01 11:00 | 18.3 | 16.7 | 16.1
| 2014-06-01 11:30 | 18.8 | 16.7 | 16.1
| 2014-06-01 12:00 | 19.9 | 17.2 | 16.1
| 2014-06-01 12:30 | 21.1 | 17.2 | 16.1
| 2014-06-01 13:00 | 21.6 | 17.2 | 16.1
| 2014-06-01 13:30 | 20.6 | 17.8 | 16.1
| 2014-06-01 14:00 | 20.2 | 17.8 | 16.1
| 2014-06-01 14:30 | 19.9 | 18.3 | 16.1
| 2014-06-01 15:00 | 20.9 | 18.3 | 16.1
| 2014-06-01 15:30 | 21.7 | 18.9 | 16.1
| 2014-06-01 16:00 | 20.2 | 18.9 | 16.1
| 2014-06-01 16:30 | 20.2 | 19.4 | 16.1
| 2014-06-01 17:00 | 19.8 | 19.4 | 16.1
| 2014-06-01 17:30 | 20.1 | 19.4 | 16.1
| 2014-06-01 18:00 | 19.9 | 20 | 16.1
| 2014-06-01 18:30 | 19.6 | 20 | 16.1
| 2014-06-01 19:00 | 19.3 | 20 | 16.1
| 2014-06-01 19:30 | 18.7 | 20 | 16.1
| 2014-06-01 20:00 | 18.3 | 20 | 16.1
| 2014-06-01 20:30 | 17.5 | 20 | 16.1
| 2014-06-01 21:00 | 17 | 20 | 16.1
| 2014-06-01 21:30 | 16.4 | 20 | 16.1
| 2014-06-01 22:00 | 15.7 | 20 | 16.1
| 2014-06-01 22:30 | 15.5 | 20 | 16.1
| 2014-06-01 23:00 | 14.8 | 20 | 16.1
| 2014-06-01 23:30 | 14.3 | 20 | 16.1
| 2014-06-02 | 14 | 20 | 16.1
| 2014-06-02 00:30 | 13.4 | 19.4 | 16.1
| 2014-06-02 01:00 | 12.6 | 19.4 | 16.1
| 2014-06-02 01:30 | 11.8 | 19.4 | 16.1
| 2014-06-02 02:00 | 10.9 | 19.4 | 16.1
| 2014-06-02 02:30 | 10.4 | 18.9 | 16.1
| 2014-06-02 03:00 | 10.1 | 18.9 | 16.1
| 2014-06-02 03:30 | 9.8 | 18.9 | 16.1
| 2014-06-02 04:00 | 9.6 | 18.9 | 16.1
| 2014-06-02 04:30 | 9.8 | 18.3 | 16.1
| 2014-06-02 05:00 | 10.4 | 18.3 | 16.1
| 2014-06-02 05:30 | 10.6 | 18.3 | 16.1
| 2014-06-02 06:00 | 11.3 | 18.3 | 16.1
| 2014-06-02 06:30 | 11.4 | 17.8 | 16.1
| 2014-06-02 07:00 | 11.8 | 17.8 | 16.1
| 2014-06-02 07:30 | 12.6 | 17.8 | 16.1
| 2014-06-02 08:00 | 13.7 | 17.8 | 16.1
| 2014-06-02 08:30 | 14.7 | 17.8 | 16.1
| 2014-06-02 09:00 | 16 | 17.2 | 16.1
| 2014-06-02 09:30 | 16.7 | 17.2 | 16.1
| 2014-06-02 10:00 | 17.6 | 17.2 | 16.1
| 2014-06-02 10:30 | 18.4 | 17.2 | 16.1
| 2014-06-02 11:00 | 19.6 | 17.2 | 16.1
| 2014-06-02 11:30 | 20.2 | 17.2 | 16.1
| 2014-06-02 12:00 | 20.9 | 17.8 | 16.1
| 2014-06-02 12:30 | 20.9 | 17.8 | 16.1
| 2014-06-02 13:00 | 22.2 | 18.3 | 16.1
| 2014-06-02 13:30 | 21.8 | 18.3 | 16.1
| 2014-06-02 14:00 | 21.3 | 18.9 | 16.1
| 2014-06-02 14:30 | 21.7 | 19.4 | 16.1
| 2014-06-02 15:00 | 22.4 | 19.4 | 16.1
| 2014-06-02 15:30 | 22.4 | 20 | 16.1
| 2014-06-02 16:00 | 22.3 | 20.6 | 16.1
| 2014-06-02 16:30 | 22.2 | 20.6 | 16.1
| 2014-06-02 17:00 | 22.6 | 21.1 | 16.1
| 2014-06-02 17:30 | 22.7 | 21.1 | 16.1
| 2014-06-02 18:00 | 22.9 | 21.7 | 16.1
| 2014-06-02 18:30 | 22.9 | 21.7 | 16.1
| 2014-06-02 19:00 | 22.6 | 21.7 | 16.1
| 2014-06-02 19:30 | 22.3 | 22.2 | 16.1
| 2014-06-02 20:00 | 21.3 | 22.2 | 16.1
| 2014-06-02 20:30 | 19.9 | 22.2 | 16.1
| 2014-06-02 21:00 | 18.4 | 22.2 | 16.1
| 2014-06-02 21:30 | 17.3 | 22.2 | 16.1
| 2014-06-02 22:00 | 17.3 | 22.2 | 16.1
| 2014-06-02 22:30 | 15.6 | 22.2 | 16.1
| 2014-06-02 23:00 | 14.5 | 22.2 | 16.1
| 2014-06-02 23:30 | 14.5 | 21.7 | 16.1
| 2014-06-03 | 14.3 | 21.7 | 16.1
| 2014-06-03 00:30 | 13.8 | 21.7 | 16.1
| 2014-06-03 01:00 | 13.7 | 21.7 | 16.1
| 2014-06-03 01:30 | 13.7 | 21.1 | 16.1
| 2014-06-03 02:00 | 13.7 | 21.1 | 16.1
| 2014-06-03 02:30 | 13.3 | 21.1 | 16.1
| 2014-06-03 03:00 | 13.1 | 20.6 | 16.1
| 2014-06-03 03:30 | 13 | 20.6 | 16.1
| 2014-06-03 04:00 | 12.8 | 20.6 | 16.1
| 2014-06-03 04:30 | 12.6 | 20.6 | 16.1
| 2014-06-03 05:00 | 12.4 | 20 | 16.1
| 2014-06-03 05:30 | 12.2 | 20 | 16.1
| 2014-06-03 06:00 | 12.4 | 20 | 16.1
| 2014-06-03 06:30 | 12.6 | 20 | 16.1
| 2014-06-03 07:00 | 12.9 | 19.4 | 16.1
| 2014-06-03 07:30 | 13.8 | 19.4 | 16.1
| 2014-06-03 08:00 | 14.6 | 19.4 | 16.1
| 2014-06-03 08:30 | 15.6 | 19.4 | 16.1
| 2014-06-03 09:00 | 15.7 | 19.4 | 16.1
| 2014-06-03 09:30 | 15.9 | 18.9 | 16.1
| 2014-06-03 10:00 | 16.6 | 18.9 | 16.1
| 2014-06-03 10:30 | 17.4 | 18.9 | 16.1
| 2014-06-03 11:00 | 19.1 | 18.9 | 16.1
| 2014-06-03 11:30 | 20.3 | 19.4 | 16.1
| 2014-06-03 12:00 | 21.2 | 19.4 | 16.1
| 2014-06-03 12:30 | 21.3 | 19.4 | 16.1
| 2014-06-03 13:00 | 22.6 | 19.4 | 16.1
| 2014-06-03 13:30 | 22.7 | 20 | 16.1
| 2014-06-03 14:00 | 23.4 | 20 | 16.1
| 2014-06-03 14:30 | 23.9 | 20.6 | 16.1
| 2014-06-03 15:00 | 23.8 | 20.6 | 16.1
| 2014-06-03 15:30 | 22.6 | 21.1 | 16.1
| 2014-06-03 16:00 | 22.7 | 21.7 | 16.1
| 2014-06-03 16:30 | 21.3 | 21.7 | 16.1
| 2014-06-03 17:00 | 20.7 | 22.2 | 16.1
| 2014-06-03 17:30 | 21.3 | 22.2 | 16.1
| 2014-06-03 18:00 | 21.6 | 22.8 | 16.1
| 2014-06-03 18:30 | 21.6 | 22.8 | 16.1
| 2014-06-03 19:00 | 21.8 | 22.8 | 16.1
| 2014-06-03 19:30 | 21.1 | 23.3 | 16.1
| 2014-06-03 20:00 | 19.7 | 23.3 | 16.1
| 2014-06-03 20:30 | 18.4 | 23.3 | 16.1
| 2014-06-03 21:00 | 17.2 | 23.3 | 16.1
| 2014-06-03 21:30 | 16.7 | 23.3 | 16.1
| 2014-06-03 22:00 | 16.4 | 22.8 | 16.1
| 2014-06-03 22:30 | 16.3 | 22.8 | 16.1
| 2014-06-03 23:00 | 16.1 | 22.8 | 16.1
| 2014-06-03 23:30 | 15.8 | 22.8 | 16.7
| 2014-06-04 | 15.7 | 22.8 | 16.7
| 2014-06-04 00:30 | 15.1 | 22.2 | 16.7
| 2014-06-04 01:00 | 13.8 | 22.2 | 16.7
| 2014-06-04 01:30 | 12.9 | 22.2 | 16.7
| 2014-06-04 02:00 | 12.2 | 22.2 | 16.7
| 2014-06-04 02:30 | 11.7 | 21.7 | 16.7
| 2014-06-04 03:00 | 11.2 | 21.7 | 16.7
| 2014-06-04 03:30 | 11 | 21.7 | 16.7
| 2014-06-04 04:00 | 10.7 | 21.1 | 16.7
| 2014-06-04 04:30 | 10.4 | 21.1 | 16.7
| 2014-06-04 05:00 | 9.9 | 21.1 | 16.7
| 2014-06-04 05:30 | 9.9 | 20.6 | 16.7
| 2014-06-04 06:00 | 9.6 | 20.6 | 16.7
| 2014-06-04 06:30 | 9.8 | 20.6 | 16.7
| 2014-06-04 07:00 | 10.7 | 20.6 | 16.7
| 2014-06-04 07:30 | 12.6 | 20 | 16.7
| 2014-06-04 08:00 | 14.1 | 20 | 16.7
| 2014-06-04 08:30 | 15.5 | 20 | 16.7
| 2014-06-04 09:00 | 16.9 | 20 | 16.7
| 2014-06-04 09:30 | 17.8 | 19.4 | 16.7
| 2014-06-04 10:00 | 19.4 | 19.4 | 16.7
| 2014-06-04 10:30 | 20.3 | 19.4 | 16.7
| 2014-06-04 11:00 | 21.4 | 19.4 | 16.7
| 2014-06-04 11:30 | 22.4 | 19.4 | 16.7
| 2014-06-04 12:00 | 23.8 | 20 | 16.7
| 2014-06-04 12:30 | 23.8 | 20 | 16.7
| 2014-06-04 13:00 | 23.8 | 20 | 16.7
| 2014-06-04 13:30 | 23.2 | 20.6 | 16.7
| 2014-06-04 14:00 | 24.1 | 20.6 | 16.7
| 2014-06-04 14:30 | 23.1 | 21.1 | 16.7
| 2014-06-04 15:00 | 22.8 | 21.1 | 16.7
| 2014-06-04 15:30 | 21.9 | 21.7 | 16.7
| 2014-06-04 16:00 | 18.9 | 21.7 | 16.7
| 2014-06-04 16:30 | 17.7 | 22.2 | 16.7
| 2014-06-04 17:00 | 16.2 | 22.2 | 16.7
| 2014-06-04 17:30 | 15.6 | 22.2 | 16.7
| 2014-06-04 18:00 | 15.6 | 22.2 | 16.7
| 2014-06-04 18:30 | 15.8 | 22.2 | 16.7
| 2014-06-04 19:00 | 15.8 | 22.2 | 16.7
| 2014-06-04 19:30 | 15.2 | 22.2 | 16.7
| 2014-06-04 20:00 | 15 | 21.7 | 16.7
| 2014-06-04 20:30 | 14.9 | 21.7 | 16.7
| 2014-06-04 21:00 | 15 | 21.7 | 16.7
| 2014-06-04 21:30 | 14.7 | 21.7 | 16.7
| 2014-06-04 22:00 | 14.4 | 21.1 | 16.7
| 2014-06-04 22:30 | 14.6 | 21.1 | 16.7
| 2014-06-04 23:00 | 14.7 | 21.1 | 16.7
| 2014-06-04 23:30 | 14.5 | 21.1 | 16.7
| 2014-06-05 | 14.3 | 20.6 | 16.7
| 2014-06-05 00:30 | 13.6 | 20.6 | 16.7
| 2014-06-05 01:00 | 13.6 | 20.6 | 16.7
| 2014-06-05 01:30 | 13.6 | 20.6 | 16.7
| 2014-06-05 02:00 | 13.1 | 20 | 16.7
| 2014-06-05 02:30 | 12.1 | 20 | 16.7
| 2014-06-05 03:00 | 11.9 | 20 | 16.7
| 2014-06-05 03:30 | 11.6 | 19.4 | 16.7
| 2014-06-05 04:00 | 11.7 | 19.4 | 16.7
| 2014-06-05 04:30 | 11.3 | 19.4 | 16.7
| 2014-06-05 05:00 | 10.1 | 18.9 | 16.7
| 2014-06-05 05:30 | 8.4 | 18.9 | 16.7
| 2014-06-05 06:00 | 7.5 | 18.9 | 16.7
| 2014-06-05 06:30 | 9.1 | 18.9 | 16.7
| 2014-06-05 07:00 | 9.7 | 18.3 | 16.7
| 2014-06-05 07:30 | 10.1 | 18.3 | 16.7
| 2014-06-05 08:00 | 12 | 18.3 | 16.7
| 2014-06-05 08:30 | 13 | 18.3 | 16.7
| 2014-06-05 09:00 | 13.9 | 17.8 | 16.7
| 2014-06-05 09:30 | 14.3 | 17.8 | 16.7
| 2014-06-05 10:00 | 15.9 | 17.8 | 16.7
| 2014-06-05 10:30 | 16.3 | 17.8 | 16.7
| 2014-06-05 11:00 | 17.3 | 17.8 | 16.7
| 2014-06-05 11:30 | 17.4 | 17.8 | 17.2
| 2014-06-05 12:00 | 17.9 | 17.8 | 17.2
| 2014-06-05 12:30 | 18.2 | 17.8 | 17.2
| 2014-06-05 13:00 | 17.9 | 17.8 | 17.2
| 2014-06-05 13:30 | 18 | 18.3 | 17.2
| 2014-06-05 14:00 | 17.5 | 18.3 | 17.2
| 2014-06-05 14:30 | 17.9 | 18.3 | 17.2
| 2014-06-05 15:00 | 18.5 | 18.3 | 17.2
| 2014-06-05 15:30 | 18.7 | 18.9 | 17.2
| 2014-06-05 16:00 | 20.6 | 18.9 | 17.2
| 2014-06-05 16:30 | 20.4 | 18.9 | 17.2
| 2014-06-05 17:00 | 20.9 | 18.9 | 17.2
| 2014-06-05 17:30 | 20.7 | 18.9 | 17.2
| 2014-06-05 18:00 | 21.2 | 19.4 | 17.2
| 2014-06-05 18:30 | 20.2 | 19.4 | 17.2
| 2014-06-05 19:00 | 20.6 | 19.4 | 17.2
| 2014-06-05 19:30 | 20.7 | 20 | 17.2
| 2014-06-05 20:00 | 19.7 | 20 | 17.2
| 2014-06-05 20:30 | 19.2 | 20 | 17.2
| 2014-06-05 21:00 | 18.2 | 20 | 17.2
| 2014-06-05 21:30 | 15.8 | 20 | 17.2
| 2014-06-05 22:00 | 14.2 | 20 | 17.2
| 2014-06-05 22:30 | 12.8 | 20 | 17.2
| 2014-06-05 23:00 | 12.2 | 20 | 17.2
| 2014-06-05 23:30 | 11.3 | 19.4 | 17.2
| 2014-06-06 | 10.7 | 19.4 | 17.2
| 2014-06-06 00:30 | 10.1 | 19.4 | 17.2
| 2014-06-06 01:00 | 9.6 | 19.4 | 17.2
| 2014-06-06 01:30 | 9.2 | 18.9 | 17.2
| 2014-06-06 02:00 | 8.8 | 18.9 | 17.2
| 2014-06-06 02:30 | 8.5 | 18.9 | 17.2
| 2014-06-06 03:00 | 7.9 | 18.3 | 17.2
| 2014-06-06 03:30 | 7.6 | 18.3 | 17.2
| 2014-06-06 04:00 | 7.3 | 18.3 | 17.2
| 2014-06-06 04:30 | 7.1 | 18.3 | 17.2
| 2014-06-06 05:00 | 6.4 | 17.8 | 17.2
| 2014-06-06 05:30 | 6.1 | 17.8 | 17.2
| 2014-06-06 06:00 | 6.2 | 17.8 | 17.2
| 2014-06-06 06:30 | 6.7 | 17.2 | 17.2
| 2014-06-06 07:00 | 7.8 | 17.2 | 17.2
| 2014-06-06 07:30 | 9.5 | 17.2 | 17.2
| 2014-06-06 08:00 | 12.3 | 17.2 | 17.2
| 2014-06-06 08:30 | 14.5 | 16.7 | 17.2
| 2014-06-06 09:00 | 16.2 | 16.7 | 17.2
| 2014-06-06 09:30 | 17.2 | 16.7 | 17.2
| 2014-06-06 10:00 | 19.7 | 16.7 | 17.2
| 2014-06-06 10:30 | 19.8 | 16.7 | 17.2
| 2014-06-06 11:00 | 22.1 | 16.7 | 17.2
| 2014-06-06 11:30 | 23.2 | 16.7 | 17.2
| 2014-06-06 12:00 | 24.6 | 17.2 | 17.2
| 2014-06-06 12:30 | 24.9 | 17.2 | 17.2
| 2014-06-06 13:00 | 25.4 | 17.8 | 17.2
| 2014-06-06 13:30 | 26.3 | 18.3 | 17.2
| 2014-06-06 14:00 | 26.8 | 18.3 | 17.2
| 2014-06-06 14:30 | 27.2 | 18.9 | 17.2
| 2014-06-06 15:00 | 27.3 | 19.4 | 17.2
| 2014-06-06 15:30 | 27.8 | 20 | 17.2
| 2014-06-06 16:00 | 27.7 | 20.6 | 17.2
| 2014-06-06 16:30 | 27.9 | 21.1 | 17.2
| 2014-06-06 17:00 | 28.3 | 21.1 | 17.2
| 2014-06-06 17:30 | 28.1 | 21.7 | 17.2
| 2014-06-06 18:00 | 28.4 | 22.2 | 17.2
| 2014-06-06 18:30 | 28.7 | 22.2 | 16.7
| 2014-06-06 19:00 | 28.8 | 22.8 | 16.7
| 2014-06-06 19:30 | 28.6 | 22.8 | 16.7
| 2014-06-06 20:00 | 27.4 | 22.8 | 16.7
| 2014-06-06 20:30 | 26.7 | 23.3 | 16.7
| 2014-06-06 21:00 | 24.9 | 23.3 | 16.7
| 2014-06-06 21:30 | 22.2 | 23.3 | 16.7
| 2014-06-06 22:00 | 20.1 | 23.3 | 16.7
| 2014-06-06 22:30 | 18.6 | 22.8 | 16.7
| 2014-06-06 23:00 | 17.4 | 22.8 | 16.7
| 2014-06-06 23:30 | 16.6 | 22.8 | 16.7
| 2014-06-07 | 16.1 | 22.8 | 16.7
| 2014-06-07 00:30 | 15.6 | 22.2 | 16.7
| 2014-06-07 01:00 | 15.3 | 22.2 | 16.7
| 2014-06-07 01:30 | 15 | 22.2 | 16.7
| 2014-06-07 02:00 | 14.3 | 22.2 | 16.7
| 2014-06-07 02:30 | 13.8 | 21.7 | 16.7
| 2014-06-07 03:00 | 13.3 | 21.7 | 16.7
| 2014-06-07 03:30 | 12.6 | 21.7 | 16.7
| 2014-06-07 04:00 | 12.3 | 21.1 | 16.7
| 2014-06-07 04:30 | 12.1 | 21.1 | 16.7
| 2014-06-07 05:00 | 11.7 | 21.1 | 16.7
| 2014-06-07 05:30 | 11.3 | 20.6 | 16.7
| 2014-06-07 06:00 | 11.2 | 20.6 | 16.7
| 2014-06-07 06:30 | 11.4 | 20.6 | 16.7
| 2014-06-07 07:00 | 12.2 | 20.6 | 16.7
| 2014-06-07 07:30 | 13.7 | 20 | 16.7
| 2014-06-07 08:00 | 15.5 | 20 | 16.7
| 2014-06-07 08:30 | 17.9 | 20 | 16.7
| 2014-06-07 09:00 | 19.8 | 20 | 16.7
| 2014-06-07 09:30 | 21.9 | 19.4 | 16.7
| 2014-06-07 10:00 | 23.5 | 19.4 | 17.2
| 2014-06-07 10:30 | 25 | 19.4 | 17.2
| 2014-06-07 11:00 | 26.1 | 19.4 | 17.2
| 2014-06-07 11:30 | 26.9 | 19.4 | 17.2
| 2014-06-07 12:00 | 27.7 | 20 | 17.2
| 2014-06-07 12:30 | 28.8 | 20 | 17.2
| 2014-06-07 13:00 | 29.7 | 20.6 | 17.2
| 2014-06-07 13:30 | 30.4 | 20.6 | 17.2
| 2014-06-07 14:00 | 31 | 21.1 | 17.2
| 2014-06-07 14:30 | 32 | 21.7 | 17.2
| 2014-06-07 15:00 | 31.9 | 22.2 | 17.2
| 2014-06-07 15:30 | 31 | 22.2 | 17.2
| 2014-06-07 16:00 | 32.3 | 22.8 | 17.2
| 2014-06-07 16:30 | 31.5 | 23.3 | 17.2
| 2014-06-07 17:00 | 31.3 | 23.3 | 17.2
| 2014-06-07 17:30 | 31.3 | 23.9 | 17.2
| 2014-06-07 18:00 | 30.7 | 23.9 | 17.2
| 2014-06-07 18:30 | 29.8 | 24.4 | 17.2
| 2014-06-07 19:00 | 29.7 | 24.4 | 17.2
| 2014-06-07 19:30 | 30.7 | 24.4 | 17.2
| 2014-06-07 20:00 | 29.7 | 24.4 | 17.2
| 2014-06-07 20:30 | 29 | 25 | 17.2
| 2014-06-07 21:00 | 26.9 | 25 | 17.2
| 2014-06-07 21:30 | 24.3 | 25 | 17.2
| 2014-06-07 22:00 | 22.6 | 25 | 17.2
| 2014-06-07 22:30 | 21.6 | 24.4 | 17.2
| 2014-06-07 23:00 | 20.9 | 24.4 | 17.2
| 2014-06-07 23:30 | 20.5 | 24.4 | 17.2
| 2014-06-08 | 19.8 | 24.4 | 17.2
| 2014-06-08 00:30 | 19.1 | 24.4 | 17.2
| 2014-06-08 01:00 | 18.6 | 23.9 | 17.2
| 2014-06-08 01:30 | 17.7 | 23.9 | 17.2
| 2014-06-08 02:00 | 17 | 23.9 | 17.2
| 2014-06-08 02:30 | 16.5 | 23.9 | 17.2
| 2014-06-08 03:00 | 15.9 | 23.3 | 17.2
| 2014-06-08 03:30 | 15.5 | 23.3 | 17.2
| 2014-06-08 04:00 | 14.9 | 23.3 | 17.2
| 2014-06-08 04:30 | 14.7 | 23.3 | 17.2
| 2014-06-08 05:00 | 14.4 | 22.8 | 17.2
| 2014-06-08 05:30 | 13.9 | 22.8 | 17.2
| 2014-06-08 06:00 | 13.8 | 22.8 | 17.2
| 2014-06-08 06:30 | 14.2 | 22.2 | 17.2
| 2014-06-08 07:00 | 15.3 | 22.2 | 17.2
| 2014-06-08 07:30 | 16.5 | 22.2 | 17.2
| 2014-06-08 08:00 | 18.3 | 22.2 | 17.2
| 2014-06-08 08:30 | 20.7 | 21.7 | 17.2
| 2014-06-08 09:00 | 23.1 | 21.7 | 17.2
| 2014-06-08 09:30 | 24.5 | 21.7 | 17.2
| 2014-06-08 10:00 | 26 | 21.7 | 17.2
| 2014-06-08 10:30 | 26.8 | 21.7 | 17.2
| 2014-06-08 11:00 | 27.7 | 21.7 | 17.2
| 2014-06-08 11:30 | 29.3 | 21.7 | 17.2
| 2014-06-08 12:00 | 30.7 | 21.7 | 17.2
| 2014-06-08 12:30 | 31.9 | 22.2 | 17.2
| 2014-06-08 13:00 | 32.4 | 22.2 | 17.2
| 2014-06-08 13:30 | 33.7 | 22.2 | 17.2
| 2014-06-08 14:00 | 34.3 | 22.8 | 17.2
| 2014-06-08 14:30 | 34.3 | 23.3 | 17.2
| 2014-06-08 15:00 | 35.3 | 23.9 | 17.2
| 2014-06-08 15:30 | 35.6 | 23.9 | 17.2
| 2014-06-08 16:00 | 35.5 | 24.4 | 17.2
| 2014-06-08 16:30 | 35.4 | 25 | 17.2
| 2014-06-08 17:00 | 35.7 | 25 | 17.2
| 2014-06-08 17:30 | 35.6 | 25.6 | 17.2
| 2014-06-08 18:00 | 35.2 | 25.6 | 17.2
| 2014-06-08 18:30 | 34.9 | 26.1 | 17.2
| 2014-06-08 19:00 | 34.5 | 26.1 | 17.2
| 2014-06-08 19:30 | 33.9 | 26.7 | 17.2
| 2014-06-08 20:00 | 33.3 | 26.7 | 17.2
| 2014-06-08 20:30 | 31.5 | 26.7 | 17.2
| 2014-06-08 21:00 | 28.9 | 26.7 | 17.8
| 2014-06-08 21:30 | 26.4 | 26.7 | 17.8
| 2014-06-08 22:00 | 24.7 | 26.7 | 17.8
| 2014-06-08 22:30 | 23.4 | 26.7 | 17.8
| 2014-06-08 23:00 | 22.6 | 26.7 | 17.8
| 2014-06-08 23:30 | 21.5 | 26.1 | 17.8
| 2014-06-09 | 21.1 | 26.1 | 17.8
| 2014-06-09 00:30 | 20.9 | 26.1 | 17.8
| 2014-06-09 01:00 | 20.1 | 26.1 | 17.8
| 2014-06-09 01:30 | 19.4 | 25.6 | 17.8
| 2014-06-09 02:00 | 18.9 | 25.6 | 17.8
| 2014-06-09 02:30 | 19.3 | 25.6 | 17.8
| 2014-06-09 03:00 | 18.7 | 25.6 | 17.8
| 2014-06-09 03:30 | 18.7 | 25 | 17.8
| 2014-06-09 04:00 | 18.4 | 25 | 17.8
| 2014-06-09 04:30 | 18.5 | 25 | 17.8
| 2014-06-09 05:00 | 17.9 | 24.4 | 17.8
| 2014-06-09 05:30 | 17.8 | 24.4 | 17.8
| 2014-06-09 06:00 | 17.8 | 24.4 | 17.8
| 2014-06-09 06:30 | 18.7 | 23.9 | 17.8
| 2014-06-09 07:00 | 19.6 | 23.9 | 17.8
| 2014-06-09 07:30 | 20.3 | 23.9 | 17.8
| 2014-06-09 08:00 | 21.6 | 23.9 | 17.8
| 2014-06-09 08:30 | 22.9 | 23.9 | 17.8
| 2014-06-09 09:00 | 24.6 | 23.3 | 17.8
| 2014-06-09 09:30 | 25.9 | 23.3 | 17.8
| 2014-06-09 10:00 | 27.3 | 23.3 | 17.8
| 2014-06-09 10:30 | 28.7 | 23.3 | 17.8
| 2014-06-09 11:00 | 29.2 | 23.3 | 17.8
| 2014-06-09 11:30 | 29.9 | 23.3 | 17.8
| 2014-06-09 12:00 | 30.9 | 23.3 | 17.8
| 2014-06-09 12:30 | 31.8 | 23.9 | 17.8
| 2014-06-09 13:00 | 32.6 | 23.9 | 17.8
| 2014-06-09 13:30 | 33.3 | 24.4 | 17.8
| 2014-06-09 14:00 | 34.1 | 24.4 | 17.8
| 2014-06-09 14:30 | 34.3 | 25 | 17.8
| 2014-06-09 15:00 | 35.3 | 25 | 17.8
| 2014-06-09 15:30 | 35.6 | 25.6 | 17.8
| 2014-06-09 16:00 | 35.9 | 26.1 | 17.8
| 2014-06-09 16:30 | 36.1 | 26.1 | 17.8
| 2014-06-09 17:00 | 36.4 | 26.7 | 17.8
| 2014-06-09 17:30 | 35.8 | 27.2 | 17.8
| 2014-06-09 18:00 | 35.6 | 27.2 | 17.8
| 2014-06-09 18:30 | 35.5 | 27.8 | 17.8
| 2014-06-09 19:00 | 35.9 | 27.8 | 17.8
| 2014-06-09 19:30 | 35.2 | 27.8 | 18.3
| 2014-06-09 20:00 | 34.1 | 28.3 | 18.3
| 2014-06-09 20:30 | 31.9 | 28.3 | 18.3
| 2014-06-09 21:00 | 29.1 | 28.3 | 18.3
| 2014-06-09 21:30 | 27.4 | 28.3 | 18.3
| 2014-06-09 22:00 | 26.2 | 28.3 | 18.3
| 2014-06-09 22:30 | 24.8 | 28.3 | 18.3
| 2014-06-09 23:00 | 24.2 | 27.8 | 18.3
| 2014-06-09 23:30 | 24.4 | 27.8 | 18.3
| 2014-06-10 | 25.9 | 27.8 | 18.3
| 2014-06-10 00:30 | 25.4 | 27.8 | 18.3
| 2014-06-10 01:00 | 24.8 | 27.2 | 18.3
| 2014-06-10 01:30 | 24.2 | 27.2 | 18.3
| 2014-06-10 02:00 | 23.1 | 27.2 | 18.3
| 2014-06-10 02:30 | 22.2 | 27.2 | 18.3
| 2014-06-10 03:00 | 22.1 | 26.7 | 18.3
| 2014-06-10 03:30 | 21.6 | 26.7 | 18.3
| 2014-06-10 04:00 | 21.1 | 26.7 | 18.3
| 2014-06-10 04:30 | 20.6 | 26.7 | 18.3
| 2014-06-10 05:00 | 19.8 | 26.1 | 18.3
| 2014-06-10 05:30 | 19.2 | 26.1 | 18.3
| 2014-06-10 06:00 | 18.9 | 26.1 | 18.3
| 2014-06-10 06:30 | 20.4 | 25.6 | 18.3
| 2014-06-10 07:00 | 21.1 | 25.6 | 18.3
| 2014-06-10 07:30 | 21.6 | 25.6 | 18.3
| 2014-06-10 08:00 | 22.3 | 25.6 | 18.3
| 2014-06-10 08:30 | 22.8 | 25.6 | 18.3
| 2014-06-10 09:00 | 24.8 | 25 | 18.3
| 2014-06-10 09:30 | 23.4 | 25 | 18.3
| 2014-06-10 10:00 | 21.9 | 25 | 18.3
| 2014-06-10 10:30 | 21.8 | 25 | 18.3
| 2014-06-10 11:00 | 21.3 | 25 | 18.3
| 2014-06-10 11:30 | 22.2 | 25 | 18.3
| 2014-06-10 12:00 | 24 | 25 | 18.3
| 2014-06-10 12:30 | 25.2 | 25 | 18.3
| 2014-06-10 13:00 | 27.3 | 24.4 | 18.3
| 2014-06-10 13:30 | 28.2 | 24.4 | 18.3
| 2014-06-10 14:00 | 30.2 | 24.4 | 18.3
| 2014-06-10 14:30 | 30.1 | 25 | 18.3
| 2014-06-10 15:00 | 31.3 | 25 | 18.3
| 2014-06-10 15:30 | 32.5 | 25 | 18.3
| 2014-06-10 16:00 | 33.2 | 25.6 | 18.3
| 2014-06-10 16:30 | 33.9 | 25.6 | 18.3
| 2014-06-10 17:00 | 32.6 | 26.1 | 18.3
| 2014-06-10 17:30 | 32.7 | 26.7 | 18.3
| 2014-06-10 18:00 | 32.1 | 26.7 | 18.3
| 2014-06-10 18:30 | 31.7 | 27.2 | 18.3
| 2014-06-10 19:00 | 30.7 | 27.2 | 18.9
| 2014-06-10 19:30 | 29.9 | 27.2 | 18.9
| 2014-06-10 20:00 | 28.8 | 27.2 | 18.9
| 2014-06-10 20:30 | 27.9 | 27.2 | 18.9
| 2014-06-10 21:00 | 27.6 | 27.2 | 18.9
| 2014-06-10 21:30 | 26.6 | 27.2 | 18.9
| 2014-06-10 22:00 | 25.7 | 27.2 | 18.9
| 2014-06-10 22:30 | 25.1 | 27.2 | 18.9
| 2014-06-10 23:00 | 24.4 | 27.2 | 18.9
| 2014-06-10 23:30 | 24.3 | 27.2 | 18.9
| 2014-06-11 | 24.4 | 27.2 | 18.9
| 2014-06-11 00:30 | 23.9 | 27.2 | 18.9
| 2014-06-11 01:00 | 23.5 | 26.7 | 18.9
| 2014-06-11 01:30 | 22.9 | 26.7 | 18.9
| 2014-06-11 02:00 | 21.7 | 26.7 | 18.9
| 2014-06-11 02:30 | 21.2 | 26.7 | 18.9
| 2014-06-11 03:00 | 20.5 | 26.1 | 18.9
| 2014-06-11 03:30 | 19.9 | 26.1 | 18.9
| 2014-06-11 04:00 | 19.6 | 26.1 | 18.9
| 2014-06-11 04:30 | 19.9 | 26.1 | 18.9
| 2014-06-11 05:00 | 19.8 | 25.6 | 18.9
| 2014-06-11 05:30 | 19.4 | 25.6 | 18.9
| 2014-06-11 06:00 | 19.2 | 25.6 | 18.9
| 2014-06-11 06:30 | 19.1 | 25.6 | 18.9
| 2014-06-11 07:00 | 20.6 | 25.6 | 18.9
| 2014-06-11 07:30 | 21.3 | 25 | 18.9
| 2014-06-11 08:00 | 21.2 | 25 | 18.9
| 2014-06-11 08:30 | 21.5 | 25 | 18.9
| 2014-06-11 09:00 | 20.2 | 25 | 18.9
| 2014-06-11 09:30 | 21.4 | 25 | 18.9
| 2014-06-11 10:00 | 21.5 | 25 | 18.9
| 2014-06-11 10:30 | 20.4 | 25 | 18.9
| 2014-06-11 11:00 | 20.3 | 24.4 | 18.9
| 2014-06-11 11:30 | 21.3 | 24.4 | 18.9
| 2014-06-11 12:00 | 22.1 | 24.4 | 18.9
| 2014-06-11 12:30 | 22.9 | 24.4 | 18.9
| 2014-06-11 13:00 | 23.9 | 25 | 18.9
| 2014-06-11 13:30 | 25.2 | 25 | 18.9
| 2014-06-11 14:00 | 25.7 | 25 | 18.9
| 2014-06-11 14:30 | 25.8 | 25 | 18.9
| 2014-06-11 15:00 | 26.7 | 25.6 | 18.9
| 2014-06-11 15:30 | 26.8 | 25.6 | 18.9
| 2014-06-11 16:00 | 26.8 | 26.1 | 18.9
| 2014-06-11 16:30 | 27.6 | 26.1 | 18.9
| 2014-06-11 17:00 | 27 | 26.7 | 18.9
| 2014-06-11 17:30 | 27.6 | 26.7 | 18.9
| 2014-06-11 18:00 | 27.6 | 27.2 | 18.9
| 2014-06-11 18:30 | 27.3 | 27.2 | 19.4
| 2014-06-11 19:00 | 25.8 | 27.2 | 19.4
| 2014-06-11 19:30 | 25.5 | 27.2 | 19.4
| 2014-06-11 20:00 | 24.3 | 27.8 | 19.4
| 2014-06-11 20:30 | 23.8 | 27.8 | 19.4
| 2014-06-11 21:00 | 23.2 | 27.8 | 19.4
| 2014-06-11 21:30 | 22.5 | 27.8 | 19.4
| 2014-06-11 22:00 | 21.8 | 27.8 | 19.4
| 2014-06-11 22:30 | 21.2 | 27.2 | 19.4
| 2014-06-11 23:00 | 20.7 | 27.2 | 19.4
| 2014-06-11 23:30 | 19.8 | 27.2 | 19.4
| 2014-06-12 | 19.3 | 27.2 | 19.4
| 2014-06-12 00:30 | 19.4 | 27.2 | 19.4
| 2014-06-12 01:00 | 19.7 | 26.7 | 19.4
| 2014-06-12 01:30 | 19.4 | 26.7 | 19.4
| 2014-06-12 02:00 | 18.8 | 26.7 | 19.4
| 2014-06-12 02:30 | 18.2 | 26.1 | 19.4
| 2014-06-12 03:00 | 17.7 | 26.1 | 19.4
| 2014-06-12 03:30 | 17.1 | 26.1 | 19.4
| 2014-06-12 04:00 | 16.4 | 26.1 | 19.4
| 2014-06-12 04:30 | 16.3 | 25.6 | 19.4
| 2014-06-12 05:00 | 16.3 | 25.6 | 19.4
| 2014-06-12 05:30 | 16.7 | 25.6 | 19.4
| 2014-06-12 06:00 | 17.3 | 25.6 | 19.4
| 2014-06-12 06:30 | 17.4 | 25 | 19.4
| 2014-06-12 07:00 | 17.8 | 25 | 19.4
| 2014-06-12 07:30 | 18.7 | 25 | 19.4
| 2014-06-12 08:00 | 19.2 | 24.4 | 19.4
| 2014-06-12 08:30 | 19.7 | 24.4 | 19.4
| 2014-06-12 09:00 | 20.1 | 24.4 | 19.4
| 2014-06-12 09:30 | 20.4 | 24.4 | 19.4
| 2014-06-12 10:00 | 20.7 | 24.4 | 19.4
| 2014-06-12 10:30 | 21.8 | 24.4 | 19.4
| 2014-06-12 11:00 | 22.3 | 24.4 | 19.4
| 2014-06-12 11:30 | 22.9 | 24.4 | 19.4
| 2014-06-12 12:00 | 23.6 | 24.4 | 19.4
| 2014-06-12 12:30 | 24.3 | 24.4 | 19.4
| 2014-06-12 13:00 | 24.1 | 25 | 19.4
| 2014-06-12 13:30 | 25.1 | 25 | 19.4
| 2014-06-12 14:00 | 24.7 | 25 | 19.4
| 2014-06-12 14:30 | 25.2 | 25.6 | 19.4
| 2014-06-12 15:00 | 25.4 | 25.6 | 19.4
| 2014-06-12 15:30 | 25.9 | 25.6 | 19.4
| 2014-06-12 16:00 | 26.4 | 26.1 | 19.4
| 2014-06-12 16:30 | 26.4 | 26.1 | 19.4
| 2014-06-12 17:00 | 25.9 | 26.7 | 19.4
| 2014-06-12 17:30 | 27.2 | 26.7 | 19.4
| 2014-06-12 18:00 | 26.2 | 26.7 | 19.4
| 2014-06-12 18:30 | 26.5 | 27.2 | 19.4
| 2014-06-12 19:00 | 26.3 | 27.2 | 19.4
| 2014-06-12 19:30 | 26.6 | 27.2 | 19.4
| 2014-06-12 20:00 | 25.7 | 27.2 | 19.4
| 2014-06-12 20:30 | 25.1 | 27.2 | 19.4
| 2014-06-12 21:00 | 23.8 | 27.2 | 19.4
| 2014-06-12 21:30 | 21.8 | 27.2 | 19.4
| 2014-06-12 22:00 | 20.3 | 27.2 | 19.4
| 2014-06-12 22:30 | 19.4 | 27.2 | 19.4
| 2014-06-12 23:00 | 18.9 | 27.2 | 19.4
| 2014-06-12 23:30 | 18.7 | 27.2 | 19.4
| 2014-06-13 | 18.3 | 26.7 | 19.4
| 2014-06-13 00:30 | 17.8 | 26.7 | 19.4
| 2014-06-13 01:00 | 17.3 | 26.7 | 19.4
| 2014-06-13 01:30 | 16.7 | 26.7 | 19.4
| 2014-06-13 02:00 | 16.2 | 26.1 | 19.4
| 2014-06-13 02:30 | 15.8 | 26.1 | 19.4
| 2014-06-13 03:00 | 14.9 | 26.1 | 19.4
| 2014-06-13 03:30 | 14.1 | 25.6 | 19.4
| 2014-06-13 04:00 | 13.5 | 25.6 | 19.4
| 2014-06-13 04:30 | 13.1 | 25.6 | 19.4
| 2014-06-13 05:00 | 12.8 | 25 | 20
| 2014-06-13 05:30 | 12.7 | 25 | 20
| 2014-06-13 06:00 | 12.7 | 25 | 20
| 2014-06-13 06:30 | 13.3 | 24.4 | 20
| 2014-06-13 07:00 | 14.9 | 24.4 | 20
| 2014-06-13 07:30 | 15.7 | 24.4 | 20
| 2014-06-13 08:00 | 16.7 | 24.4 | 20
| 2014-06-13 08:30 | 17.8 | 23.9 | 20
| 2014-06-13 09:00 | 19.1 | 23.9 | 20
| 2014-06-13 09:30 | 20.3 | 23.9 | 20
| 2014-06-13 10:00 | 20.9 | 23.9 | 20
| 2014-06-13 10:30 | 22.5 | 23.9 | 20
| 2014-06-13 11:00 | 22.4 | 23.9 | 20
| 2014-06-13 11:30 | 22.8 | 23.9 | 20
| 2014-06-13 12:00 | 23.3 | 23.9 | 20
| 2014-06-13 12:30 | 23.8 | 23.9 | 20
| 2014-06-13 13:00 | 24 | 24.4 | 20
| 2014-06-13 13:30 | 24.6 | 24.4 | 20
| 2014-06-13 14:00 | 24.4 | 25 | 20
| 2014-06-13 14:30 | 24.8 | 25 | 20
| 2014-06-13 15:00 | 24.8 | 25.6 | 20
| 2014-06-13 15:30 | 24.9 | 25.6 | 20
| 2014-06-13 16:00 | 25.3 | 26.1 | 20
| 2014-06-13 16:30 | 25.5 | 26.7 | 20
| 2014-06-13 17:00 | 25.4 | 26.7 | 20
| 2014-06-13 17:30 | 25.4 | 27.2 | 20
| 2014-06-13 18:00 | 25.4 | 27.2 | 20
| 2014-06-13 18:30 | 25.1 | 27.2 | 20
| 2014-06-13 19:00 | 24.6 | 27.8 | 20
| 2014-06-13 19:30 | 24.2 | 27.8 | 20
| 2014-06-13 20:00 | 22.7 | 27.8 | 20
| 2014-06-13 20:30 | 21.7 | 27.8 | 20
| 2014-06-13 21:00 | 20.9 | 27.8 | 20
| 2014-06-13 21:30 | 19.9 | 27.8 | 20
| 2014-06-13 22:00 | 19.2 | 27.8 | 20
| 2014-06-13 22:30 | 18.4 | 27.8 | 20
| 2014-06-13 23:00 | 17.6 | 27.8 | 20
| 2014-06-13 23:30 | 16.5 | 27.2 | 20
| 2014-06-14 | 15.6 | 27.2 | 20
| 2014-06-14 00:30 | 14.8 | 27.2 | 20
| 2014-06-14 01:00 | 14.1 | 27.2 | 20
| 2014-06-14 01:30 | 13.6 | 26.7 | 20
| 2014-06-14 02:00 | 13.3 | 26.7 | 20
| 2014-06-14 02:30 | 12.9 | 26.1 | 20
| 2014-06-14 03:00 | 12.7 | 26.1 | 20
| 2014-06-14 03:30 | 12.7 | 26.1 | 20
| 2014-06-14 04:00 | 12.6 | 25.6 | 20
| 2014-06-14 04:30 | 12.1 | 25.6 | 20
| 2014-06-14 05:00 | 12.4 | 25.6 | 20
| 2014-06-14 05:30 | 12.5 | 25.6 | 20
| 2014-06-14 06:00 | 13.1 | 25 | 20
| 2014-06-14 06:30 | 14.2 | 25 | 20
| 2014-06-14 07:00 | 14.9 | 25 | 20
| 2014-06-14 07:30 | 16.1 | 24.4 | 20
| 2014-06-14 08:00 | 16.1 | 24.4 | 20
| 2014-06-14 08:30 | 16.1 | 24.4 | 20
| 2014-06-14 09:00 | 16.1 | 24.4 | 20
| 2014-06-14 09:30 | 16.6 | 24.4 | 20
| 2014-06-14 10:00 | 16.9 | 23.9 | 20
| 2014-06-14 10:30 | 17.3 | 23.9 | 20
| 2014-06-14 11:00 | 16.4 | 23.9 | 20
| 2014-06-14 11:30 | 18.1 | 23.9 | 20
| 2014-06-14 12:00 | 18.8 | 23.9 | 20
| 2014-06-14 12:30 | 19.7 | 24.4 | 20
| 2014-06-14 13:00 | 18.9 | 24.4 | 20
| 2014-06-14 13:30 | 19.1 | 24.4 | 20
| 2014-06-14 14:00 | 19.6 | 24.4 | 20
| 2014-06-14 14:30 | 19.5 | 24.4 | 20
| 2014-06-14 15:00 | 19.3 | 25 | 20
| 2014-06-14 15:30 | 19.2 | 25 | 20
| 2014-06-14 16:00 | 18.7 | 25 | 20
| 2014-06-14 16:30 | 17.8 | 25.6 | 20
| 2014-06-14 17:00 | 17.8 | 25.6 | 20
| 2014-06-14 17:30 | 18.6 | 25.6 | 20
| 2014-06-14 18:00 | 18.9 | 25.6 | 20
| 2014-06-14 18:30 | 19.5 | 25.6 | 20
| 2014-06-14 19:00 | 19.1 | 25.6 | 20
| 2014-06-14 19:30 | 19.4 | 25.6 | 20
| 2014-06-14 20:00 | 18.7 | 25.6 | 20
| 2014-06-14 20:30 | 17.9 | 25.6 | 20
| 2014-06-14 21:00 | 18.1 | 25.6 | 20
| 2014-06-14 21:30 | 17.3 | 25.6 | 20
| 2014-06-14 22:00 | 16 | 25.6 | 20
| 2014-06-14 22:30 | 14.9 | 25 | 20
| 2014-06-14 23:00 | 14.7 | 25 | 20
| 2014-06-14 23:30 | 14.5 | 25 | 20
| 2014-06-15 | 13.9 | 25 | 20
| 2014-06-15 00:30 | 12.9 | 25 | 20
| 2014-06-15 01:00 | 12.1 | 24.4 | 20
| 2014-06-15 01:30 | 12.1 | 24.4 | 20
| 2014-06-15 02:00 | 12.2 | 24.4 | 20
| 2014-06-15 02:30 | 11.8 | 24.4 | 20
| 2014-06-15 03:00 | 11.7 | 23.9 | 20
| 2014-06-15 03:30 | 11.4 | 23.9 | 20
| 2014-06-15 04:00 | 10.9 | 23.9 | 20
| 2014-06-15 04:30 | 10.4 | 23.3 | 20
| 2014-06-15 05:00 | 10.6 | 23.3 | 20
| 2014-06-15 05:30 | 10.6 | 23.3 | 20
| 2014-06-15 06:00 | 10.6 | 23.3 | 20
| 2014-06-15 06:30 | 11.2 | 22.8 | 20
| 2014-06-15 07:00 | 11.9 | 22.8 | 20
| 2014-06-15 07:30 | 12.9 | 22.8 | 20
| 2014-06-15 08:00 | 14.4 | 22.8 | 20
| 2014-06-15 08:30 | 15.9 | 22.2 | 20
| 2014-06-15 09:00 | 17.7 | 22.2 | 20
| 2014-06-15 09:30 | 18.3 | 22.2 | 20
| 2014-06-15 10:00 | 19.3 | 22.2 | 20
| 2014-06-15 10:30 | 20.8 | 22.2 | 20
| 2014-06-15 11:00 | 20.8 | 22.2 | 20
| 2014-06-15 11:30 | 21.3 | 22.2 | 20
| 2014-06-15 12:00 | 21.3 | 22.2 | 20
| 2014-06-15 12:30 | 22.7 | 22.2 | 20
| 2014-06-15 13:00 | 20.8 | 22.8 | 20
| 2014-06-15 13:30 | 21.4 | 22.8 | 20
| 2014-06-15 14:00 | 22.5 | 23.3 | 20
| 2014-06-15 14:30 | 21.8 | 23.3 | 20
| 2014-06-15 15:00 | 23 | 23.9 | 20
| 2014-06-15 15:30 | 21.7 | 23.9 | 20
| 2014-06-15 16:00 | 22.4 | 24.4 | 20
| 2014-06-15 16:30 | 21.9 | 24.4 | 20
| 2014-06-15 17:00 | 23.1 | 24.4 | 20
| 2014-06-15 17:30 | 22.9 | 25 | 20
| 2014-06-15 18:00 | 21.6 | 25 | 20
| 2014-06-15 18:30 | 22.3 | 25.6 | 20
| 2014-06-15 19:00 | 23.4 | 25.6 | 20
| 2014-06-15 19:30 | 23.6 | 25.6 | 20
| 2014-06-15 20:00 | 20.6 | 25.6 | 20
| 2014-06-15 20:30 | 20.1 | 25.6 | 20
| 2014-06-15 21:00 | 18.9 | 25.6 | 20
| 2014-06-15 21:30 | 18.1 | 25.6 | 20
| 2014-06-15 22:00 | 16.9 | 25.6 | 20
| 2014-06-15 22:30 | 15.7 | 25.6 | 20
| 2014-06-15 23:00 | 14.7 | 25.6 | 20
| 2014-06-15 23:30 | 13.9 | 25.6 | 20
| 2014-06-16 | 13.4 | 25.6 | 20
| 2014-06-16 00:30 | 12.8 | 25 | 20
| 2014-06-16 01:00 | 12.2 | 25 | 20
| 2014-06-16 01:30 | 11.7 | 25 | 20
| 2014-06-16 02:00 | 11.3 | 24.4 | 20
| 2014-06-16 02:30 | 10.8 | 24.4 | 20
| 2014-06-16 03:00 | 10.4 | 24.4 | 20
| 2014-06-16 03:30 | 10.6 | 23.9 | 20
| 2014-06-16 04:00 | 10.4 | 23.9 | 20
| 2014-06-16 04:30 | 10.2 | 23.9 | 20
| 2014-06-16 05:00 | 10.5 | 23.9 | 20
| 2014-06-16 05:30 | 11.2 | 23.3 | 20
| 2014-06-16 06:00 | 12.2 | 23.3 | 20
| 2014-06-16 06:30 | 12.8 | 23.3 | 20
| 2014-06-16 07:00 | 13.4 | 22.8 | 20
| 2014-06-16 07:30 | 13.8 | 22.8 | 20
| 2014-06-16 08:00 | 14.8 | 22.8 | 20
| 2014-06-16 08:30 | 15.8 | 22.8 | 20
| 2014-06-16 09:00 | 17 | 22.2 | 20
| 2014-06-16 09:30 | 18.8 | 22.2 | 20
| 2014-06-16 10:00 | 19.3 | 22.2 | 20
| 2014-06-16 10:30 | 19.7 | 22.2 | 20
| 2014-06-16 11:00 | 20.9 | 22.2 | 20
| 2014-06-16 11:30 | 20.6 | 22.2 | 20
| 2014-06-16 12:00 | 22.3 | 22.2 | 20
| 2014-06-16 12:30 | 20.6 | 22.8 | 20
| 2014-06-16 13:00 | 20.9 | 22.8 | 20
| 2014-06-16 13:30 | 21.3 | 22.8 | 20
| 2014-06-16 14:00 | 22.4 | 23.3 | 20
| 2014-06-16 14:30 | 22.4 | 23.3 | 20
| 2014-06-16 15:00 | 22.2 | 23.9 | 20
| 2014-06-16 15:30 | 22.2 | 23.9 | 20
| 2014-06-16 16:00 | 22.1 | 24.4 | 20
| 2014-06-16 16:30 | 22 | 24.4 | 20
| 2014-06-16 17:00 | 21.6 | 24.4 | 20
| 2014-06-16 17:30 | 21.1 | 25 | 20
| 2014-06-16 18:00 | 20.7 | 25 | 20
| 2014-06-16 18:30 | 20.4 | 25.6 | 20
| 2014-06-16 19:00 | 19.7 | 25.6 | 20
| 2014-06-16 19:30 | 19.1 | 25.6 | 20
| 2014-06-16 20:00 | 18.6 | 25.6 | 20
| 2014-06-16 20:30 | 18.4 | 25.6 | 20
| 2014-06-16 21:00 | 17.9 | 25.6 | 20
| 2014-06-16 21:30 | 17.2 | 25.6 | 20
| 2014-06-16 22:00 | 16.7 | 25.6 | 20
| 2014-06-16 22:30 | 16.2 | 25.6 | 20
| 2014-06-16 23:00 | 15.4 | 25.6 | 20
| 2014-06-16 23:30 | 14.2 | 25 | 20
| 2014-06-17 | 14.2 | 25 | 20
| 2014-06-17 00:30 | 14.2 | 25 | 20
| 2014-06-17 01:00 | 14.6 | 24.4 | 20
| 2014-06-17 01:30 | 14.2 | 24.4 | 20
| 2014-06-17 02:00 | 14 | 24.4 | 20
| 2014-06-17 02:30 | 14.1 | 24.4 | 20
| 2014-06-17 03:00 | 14.4 | 23.9 | 20
| 2014-06-17 03:30 | 14.5 | 23.9 | 20
| 2014-06-17 04:00 | 14.5 | 23.9 | 20
| 2014-06-17 04:30 | 14.4 | 23.9 | 20
| 2014-06-17 05:00 | 14.3 | 23.9 | 20
| 2014-06-17 05:30 | 14.3 | 23.3 | 20
| 2014-06-17 06:00 | 14.4 | 23.3 | 20
| 2014-06-17 06:30 | 14.6 | 23.3 | 20
| 2014-06-17 07:00 | 14.7 | 23.3 | 20
| 2014-06-17 07:30 | 14.9 | 23.3 | 20
| 2014-06-17 08:00 | 15.2 | 22.8 | 20
| 2014-06-17 08:30 | 15.5 | 22.8 | 20
| 2014-06-17 09:00 | 15.7 | 22.8 | 20
| 2014-06-17 09:30 | 16 | 22.8 | 20
| 2014-06-17 10:00 | 16.4 | 22.8 | 20
| 2014-06-17 10:30 | 17.4 | 22.8 | 20
| 2014-06-17 11:00 | 17.7 | 22.8 | 20
| 2014-06-17 11:30 | 18.7 | 22.8 | 20
| 2014-06-17 12:00 | 19.8 | 22.8 | 20
| 2014-06-17 12:30 | 19.6 | 22.8 | 20
| 2014-06-17 13:00 | 19.8 | 22.8 | 20
| 2014-06-17 13:30 | 20.2 | 23.3 | 20
| 2014-06-17 14:00 | 21.1 | 23.3 | 20
| 2014-06-17 14:30 | 20.4 | 23.3 | 20
| 2014-06-17 15:00 | 20.7 | 23.9 | 20
| 2014-06-17 15:30 | 21.2 | 23.9 | 20
| 2014-06-17 16:00 | 21.8 | 23.9 | 20
| 2014-06-17 16:30 | 21.7 | 23.9 | 20
| 2014-06-17 17:00 | 22.8 | 24.4 | 20
| 2014-06-17 17:30 | 22.2 | 24.4 | 20
| 2014-06-17 18:00 | 22 | 24.4 | 20
| 2014-06-17 18:30 | 22.1 | 24.4 | 20
| 2014-06-17 19:00 | 22.3 | 25 | 20
| 2014-06-17 19:30 | 21.6 | 25 | 20
| 2014-06-17 20:00 | 20.8 | 25 | 20
| 2014-06-17 20:30 | 20.5 | 25 | 20
| 2014-06-17 21:00 | 19.2 | 25 | 20
| 2014-06-17 21:30 | 17.9 | 25 | 20
| 2014-06-17 22:00 | 16.8 | 25 | 20
| 2014-06-17 22:30 | 15.9 | 25 | 20
| 2014-06-17 23:00 | 15 | 25 | 20
| 2014-06-17 23:30 | 14.1 | 25 | 20
| 2014-06-18 | 13.4 | 24.4 | 20
| 2014-06-18 00:30 | 12.9 | 24.4 | 20
| 2014-06-18 01:00 | 12.6 | 24.4 | 20
| 2014-06-18 01:30 | 12.3 | 24.4 | 20
| 2014-06-18 02:00 | 12.3 | 23.9 | 20
| 2014-06-18 02:30 | 12.2 | 23.9 | 20
| 2014-06-18 03:00 | 11.8 | 23.9 | 20
| 2014-06-18 03:30 | 11.7 | 23.9 | 20
| 2014-06-18 04:00 | 11.9 | 23.3 | 20
| 2014-06-18 04:30 | 12 | 23.3 | 20
| 2014-06-18 05:00 | 11.8 | 23.3 | 20
| 2014-06-18 05:30 | 11.9 | 23.3 | 20
| 2014-06-18 06:00 | 12.1 | 22.8 | 20
| 2014-06-18 06:30 | 12.6 | 22.8 | 20
| 2014-06-18 07:00 | 13.7 | 22.8 | 20
| 2014-06-18 07:30 | 14.6 | 22.2 | 20
| 2014-06-18 08:00 | 15.8 | 22.2 | 20
| 2014-06-18 08:30 | 17.4 | 22.2 | 20
| 2014-06-18 09:00 | 18.1 | 22.2 | 20
| 2014-06-18 09:30 | 19.6 | 22.2 | 20
| 2014-06-18 10:00 | 20.2 | 21.7 | 20
| 2014-06-18 10:30 | 21.2 | 21.7 | 20
| 2014-06-18 11:00 | 22.6 | 21.7 | 20
| 2014-06-18 11:30 | 21.9 | 21.7 | 20
| 2014-06-18 12:00 | 23.1 | 22.2 | 20
| 2014-06-18 12:30 | 23.9 | 22.2 | 20
| 2014-06-18 13:00 | 23.2 | 22.2 | 20
| 2014-06-18 13:30 | 25.1 | 22.8 | 20
| 2014-06-18 14:00 | 24.5 | 22.8 | 20
| 2014-06-18 14:30 | 25.3 | 23.3 | 20
| 2014-06-18 15:00 | 25.4 | 23.3 | 20
| 2014-06-18 15:30 | 27.1 | 23.9 | 20
| 2014-06-18 16:00 | 24.7 | 23.9 | 20
| 2014-06-18 16:30 | 25.9 | 24.4 | 20
| 2014-06-18 17:00 | 25.6 | 24.4 | 20
| 2014-06-18 17:30 | 25.2 | 24.4 | 20
| 2014-06-18 18:00 | 26.7 | 25 | 20
| 2014-06-18 18:30 | 26.1 | 25 | 20
| 2014-06-18 19:00 | 25.5 | 25 | 20
| 2014-06-18 19:30 | 24.3 | 25.6 | 20
| 2014-06-18 20:00 | 23.8 | 25.6 | 20
| 2014-06-18 20:30 | 23.1 | 25.6 | 20
| 2014-06-18 21:00 | 22.3 | 25.6 | 20
| 2014-06-18 21:30 | 21.3 | 25.6 | 20
| 2014-06-18 22:00 | 20.4 | 25.6 | 20
| 2014-06-18 22:30 | 19.5 | 25.6 | 20
| 2014-06-18 23:00 | 18.4 | 25.6 | 20
| 2014-06-18 23:30 | 17.1 | 25.6 | 20
| 2014-06-19 | 16.2 | 25.6 | 20
| 2014-06-19 00:30 | 15.5 | 25 | 20
| 2014-06-19 01:00 | 14.8 | 25 | 20
| 2014-06-19 01:30 | 14.7 | 25 | 20
| 2014-06-19 02:00 | 14.7 | 25 | 20
| 2014-06-19 02:30 | 13.9 | 24.4 | 20
| 2014-06-19 03:00 | 13.2 | 24.4 | 20
| 2014-06-19 03:30 | 12.7 | 24.4 | 20
| 2014-06-19 04:00 | 12.3 | 24.4 | 20
| 2014-06-19 04:30 | 11.9 | 23.9 | 20
| 2014-06-19 05:00 | 11.4 | 23.9 | 20
| 2014-06-19 05:30 | 11 | 23.9 | 20
| 2014-06-19 06:00 | 10.8 | 23.3 | 20
| 2014-06-19 06:30 | 11 | 23.3 | 20
| 2014-06-19 07:00 | 12.2 | 23.3 | 20
| 2014-06-19 07:30 | 13.9 | 23.3 | 20
| 2014-06-19 08:00 | 14.9 | 22.8 | 20
| 2014-06-19 08:30 | 16.1 | 22.8 | 20
| 2014-06-19 09:00 | 17.2 | 22.8 | 20
| 2014-06-19 09:30 | 18.3 | 22.8 | 20
| 2014-06-19 10:00 | 18.4 | 22.2 | 20
| 2014-06-19 10:30 | 18.9 | 22.2 | 20
| 2014-06-19 11:00 | 18.9 | 22.2 | 20
| 2014-06-19 11:30 | 19.2 | 22.2 | 20
| 2014-06-19 12:00 | 19.3 | 22.2 | 20
| 2014-06-19 12:30 | 19.9 | 22.8 | 20
| 2014-06-19 13:00 | 20.6 | 22.8 | 20
| 2014-06-19 13:30 | 21 | 22.8 | 20
| 2014-06-19 14:00 | 20.8 | 23.3 | 20
| 2014-06-19 14:30 | 21.3 | 23.3 | 20
| 2014-06-19 15:00 | 21.2 | 23.3 | 20
| 2014-06-19 15:30 | 21.7 | 23.9 | 20
| 2014-06-19 16:00 | 21.9 | 23.9 | 20
| 2014-06-19 16:30 | 22 | 24.4 | 20
| 2014-06-19 17:00 | 21.9 | 24.4 | 20
| 2014-06-19 17:30 | 21.3 | 25 | 20
| 2014-06-19 18:00 | 21.1 | 25 | 20
| 2014-06-19 18:30 | 20.9 | 25.6 | 20
| 2014-06-19 19:00 | 19.7 | 25.6 | 20
| 2014-06-19 19:30 | 19.2 | 25.6 | 20
| 2014-06-19 20:00 | 18.7 | 25.6 | 20
| 2014-06-19 20:30 | 18.1 | 26.1 | 20
| 2014-06-19 21:00 | 17.7 | 26.1 | 20
| 2014-06-19 21:30 | 17.3 | 26.1 | 20
| 2014-06-19 22:00 | 15.6 | 26.1 | 20
| 2014-06-19 22:30 | 14.3 | 25.6 | 20
| 2014-06-19 23:00 | 14.1 | 25.6 | 20
| 2014-06-19 23:30 | 14.2 | 25.6 | 20
| 2014-06-20 | 14.2 | 25.6 | 20
| 2014-06-20 00:30 | 14.1 | 25.6 | 20
| 2014-06-20 01:00 | 13.9 | 25 | 20
| 2014-06-20 01:30 | 14 | 25 | 20
| 2014-06-20 02:00 | 13.7 | 25 | 20
| 2014-06-20 02:30 | 13.7 | 24.4 | 20
| 2014-06-20 03:00 | 13.9 | 24.4 | 20
| 2014-06-20 03:30 | 14.1 | 24.4 | 20
| 2014-06-20 04:00 | 13.8 | 23.9 | 20
| 2014-06-20 04:30 | 13.1 | 23.9 | 20
| 2014-06-20 05:00 | 12.6 | 23.9 | 20
| 2014-06-20 05:30 | 12.8 | 23.9 | 20
| 2014-06-20 06:00 | 13.1 | 23.3 | 20
| 2014-06-20 06:30 | 13.3 | 23.3 | 20
| 2014-06-20 07:00 | 13.6 | 23.3 | 20
| 2014-06-20 07:30 | 13.9 | 23.3 | 20
| 2014-06-20 08:00 | 14.4 | 22.8 | 20
| 2014-06-20 08:30 | 14.4 | 22.8 | 20
| 2014-06-20 09:00 | 14.4 | 22.8 | 20
| 2014-06-20 09:30 | 14.8 | 22.8 | 20
| 2014-06-20 10:00 | 14.7 | 22.2 | 20
| 2014-06-20 10:30 | 14.2 | 22.2 | 20
| 2014-06-20 11:00 | 14.8 | 22.2 | 20
| 2014-06-20 11:30 | 15.3 | 22.2 | 20
| 2014-06-20 12:00 | 16.4 | 22.2 | 20
| 2014-06-20 12:30 | 16.6 | 22.2 | 20
| 2014-06-20 13:00 | 17.4 | 22.2 | 20
| 2014-06-20 13:30 | 17.4 | 22.2 | 20
| 2014-06-20 14:00 | 18.1 | 22.2 | 20
| 2014-06-20 14:30 | 17.3 | 22.2 | 20
| 2014-06-20 15:00 | 17 | 22.2 | 20
| 2014-06-20 15:30 | 17.3 | 22.2 | 20
| 2014-06-20 16:00 | 17.4 | 22.2 | 20
| 2014-06-20 16:30 | 17.6 | 22.2 | 20
| 2014-06-20 17:00 | 19.3 | 22.2 | 20
| 2014-06-20 17:30 | 19.4 | 22.2 | 20
| 2014-06-20 18:00 | 18.3 | 22.8 | 20
| 2014-06-20 18:30 | 18.5 | 22.8 | 20
| 2014-06-20 19:00 | 18.4 | 22.8 | 20
| 2014-06-20 19:30 | 18 | 22.8 | 20
| 2014-06-20 20:00 | 17.5 | 22.8 | 20
| 2014-06-20 20:30 | 17.3 | 22.8 | 20
| 2014-06-20 21:00 | 17 | 22.8 | 20
| 2014-06-20 21:30 | 16.8 | 22.8 | 20
| 2014-06-20 22:00 | 16.1 | 22.8 | 20
| 2014-06-20 22:30 | 15.3 | 22.8 | 20
| 2014-06-20 23:00 | 14.7 | 22.8 | 20
| 2014-06-20 23:30 | 13.7 | 22.8 | 20
| 2014-06-21 | 12.6 | 22.2 | 20
| 2014-06-21 00:30 | 12.3 | 22.2 | 20
| 2014-06-21 01:00 | 11.8 | 22.2 | 20
| 2014-06-21 01:30 | 11.2 | 22.2 | 20
| 2014-06-21 02:00 | 10.9 | 22.2 | 20
| 2014-06-21 02:30 | 10.8 | 21.7 | 20
| 2014-06-21 03:00 | 10.8 | 21.7 | 20
| 2014-06-21 03:30 | 10.7 | 21.7 | 20
| 2014-06-21 04:00 | 10.7 | 21.7 | 20
| 2014-06-21 04:30 | 10.7 | 21.7 | 20
| 2014-06-21 05:00 | 10.7 | 21.1 | 20
| 2014-06-21 05:30 | 10.8 | 21.1 | 20
| 2014-06-21 06:00 | 11 | 21.1 | 20
| 2014-06-21 06:30 | 11.5 | 21.1 | 20
| 2014-06-21 07:00 | 12.2 | 20.6 | 20
| 2014-06-21 07:30 | 12.7 | 20.6 | 20
| 2014-06-21 08:00 | 14.2 | 20.6 | 20
| 2014-06-21 08:30 | 14.9 | 20.6 | 20
| 2014-06-21 09:00 | 15.8 | 20.6 | 20
| 2014-06-21 09:30 | 16.8 | 20.6 | 20
| 2014-06-21 10:00 | 17.6 | 20.6 | 20
| 2014-06-21 10:30 | 17.8 | 20.6 | 20
| 2014-06-21 11:00 | 18 | 20.6 | 20
| 2014-06-21 11:30 | 18.7 | 20.6 | 20
| 2014-06-21 12:00 | 19 | 20.6 | 20
| 2014-06-21 12:30 | 18.6 | 20.6 | 20
| 2014-06-21 13:00 | 20 | 21.1 | 20
| 2014-06-21 13:30 | 20.3 | 21.1 | 20
| 2014-06-21 14:00 | 19.8 | 21.1 | 20
| 2014-06-21 14:30 | 20 | 21.7 | 20
| 2014-06-21 15:00 | 20.9 | 21.7 | 20
| 2014-06-21 15:30 | 20.4 | 22.2 | 20
| 2014-06-21 16:00 | 21.1 | 22.2 | 20
| 2014-06-21 16:30 | 21.2 | 22.8 | 20
| 2014-06-21 17:00 | 21.5 | 22.8 | 20
| 2014-06-21 17:30 | 21.3 | 23.3 | 20
| 2014-06-21 18:00 | 21 | 23.3 | 20
| 2014-06-21 18:30 | 20.7 | 23.9 | 20
| 2014-06-21 19:00 | 20.3 | 23.9 | 20
| 2014-06-21 19:30 | 20.4 | 23.9 | 20
| 2014-06-21 20:00 | 20.7 | 23.9 | 20
| 2014-06-21 20:30 | 20.3 | 23.9 | 20
| 2014-06-21 21:00 | 19.4 | 23.9 | 20
| 2014-06-21 21:30 | 17.6 | 23.9 | 20
| 2014-06-21 22:00 | 15.7 | 23.9 | 20
| 2014-06-21 22:30 | 14.4 | 23.9 | 20
| 2014-06-21 23:00 | 13.3 | 23.9 | 20
| 2014-06-21 23:30 | 12.6 | 23.9 | 20
| 2014-06-22 | 12 | 23.9 | 20
| 2014-06-22 00:30 | 11.3 | 23.3 | 20
| 2014-06-22 01:00 | 10.3 | 23.3 | 20
| 2014-06-22 01:30 | 10.2 | 23.3 | 20
| 2014-06-22 02:00 | 9.2 | 23.3 | 20
| 2014-06-22 02:30 | 8.7 | 22.8 | 20
| 2014-06-22 03:00 | 8.6 | 22.8 | 20
| 2014-06-22 03:30 | 8.6 | 22.8 | 20
| 2014-06-22 04:00 | 8.4 | 22.2 | 20
| 2014-06-22 04:30 | 8.3 | 22.2 | 20
| 2014-06-22 05:00 | 8.1 | 22.2 | 20
| 2014-06-22 05:30 | 7.7 | 21.7 | 20
| 2014-06-22 06:00 | 7.4 | 21.7 | 20
| 2014-06-22 06:30 | 7.8 | 21.7 | 20
| 2014-06-22 07:00 | 8.9 | 21.1 | 20
| 2014-06-22 07:30 | 11.1 | 21.1 | 20
| 2014-06-22 08:00 | 13.4 | 21.1 | 20
| 2014-06-22 08:30 | 15.6 | 21.1 | 20
| 2014-06-22 09:00 | 16.9 | 20.6 | 20
| 2014-06-22 09:30 | 18.1 | 20.6 | 20
| 2014-06-22 10:00 | 19.7 | 20.6 | 20
| 2014-06-22 10:30 | 20.2 | 20.6 | 20
| 2014-06-22 11:00 | 21.3 | 20.6 | 20
| 2014-06-22 11:30 | 21.8 | 20.6 | 20
| 2014-06-22 12:00 | 20.9 | 20.6 | 20
| 2014-06-22 12:30 | 21.7 | 21.1 | 20
| 2014-06-22 13:00 | 21.9 | 21.1 | 20
| 2014-06-22 13:30 | 22.7 | 21.1 | 20
| 2014-06-22 14:00 | 22.5 | 21.7 | 20
| 2014-06-22 14:30 | 22.8 | 21.7 | 20
| 2014-06-22 15:00 | 22.9 | 22.2 | 20
| 2014-06-22 15:30 | 23 | 22.2 | 20
| 2014-06-22 16:00 | 23.8 | 22.8 | 20
| 2014-06-22 16:30 | 23.4 | 22.8 | 20
| 2014-06-22 17:00 | 23.3 | 23.3 | 20
| 2014-06-22 17:30 | 23.7 | 23.3 | 20
| 2014-06-22 18:00 | 23.4 | 23.9 | 20
| 2014-06-22 18:30 | 23.2 | 23.9 | 20
| 2014-06-22 19:00 | 23 | 24.4 | 20
| 2014-06-22 19:30 | 22.7 | 24.4 | 20
| 2014-06-22 20:00 | 22.1 | 24.4 | 20
| 2014-06-22 20:30 | 21.5 | 24.4 | 20
| 2014-06-22 21:00 | 20.4 | 24.4 | 20
| 2014-06-22 21:30 | 19.1 | 24.4 | 20
| 2014-06-22 22:00 | 17.6 | 24.4 | 20
| 2014-06-22 22:30 | 16.1 | 24.4 | 20
| 2014-06-22 23:00 | 15.1 | 24.4 | 20
| 2014-06-22 23:30 | 14.3 | 24.4 | 20
| 2014-06-23 | 13.6 | 24.4 | 20
| 2014-06-23 00:30 | 12.9 | 24.4 | 20
| 2014-06-23 01:00 | 12.3 | 23.9 | 20
| 2014-06-23 01:30 | 11.7 | 23.9 | 20
| 2014-06-23 02:00 | 11.2 | 23.9 | 20
| 2014-06-23 02:30 | 10.7 | 23.3 | 20
| 2014-06-23 03:00 | 10.3 | 23.3 | 20
| 2014-06-23 03:30 | 10.2 | 23.3 | 20
| 2014-06-23 04:00 | 10 | 23.3 | 20
| 2014-06-23 04:30 | 9.9 | 22.8 | 20
| 2014-06-23 05:00 | 9.6 | 22.8 | 20
| 2014-06-23 05:30 | 9.4 | 22.8 | 20
| 2014-06-23 06:00 | 10 | 22.2 | 20
| 2014-06-23 06:30 | 10.3 | 22.2 | 20
| 2014-06-23 07:00 | 11.5 | 22.2 | 20
| 2014-06-23 07:30 | 13.6 | 21.7 | 20
| 2014-06-23 08:00 | 14.7 | 21.7 | 20
| 2014-06-23 08:30 | 15.4 | 21.7 | 20
| 2014-06-23 09:00 | 16.3 | 21.7 | 20
| 2014-06-23 09:30 | 17.7 | 21.1 | 20
| 2014-06-23 10:00 | 18.3 | 21.1 | 20
| 2014-06-23 10:30 | 20.1 | 21.1 | 20
| 2014-06-23 11:00 | 19.8 | 21.1 | 20
| 2014-06-23 11:30 | 19.9 | 21.1 | 20
| 2014-06-23 12:00 | 20.7 | 21.1 | 20
| 2014-06-23 12:30 | 20.7 | 21.7 | 20
| 2014-06-23 13:00 | 21.7 | 21.7 | 20
| 2014-06-23 13:30 | 22.8 | 22.2 | 20
| 2014-06-23 14:00 | 22.4 | 22.2 | 20
| 2014-06-23 14:30 | 23.4 | 22.8 | 20
| 2014-06-23 15:00 | 22.9 | 23.3 | 20
| 2014-06-23 15:30 | 22.8 | 23.3 | 20
| 2014-06-23 16:00 | 23 | 23.9 | 20
| 2014-06-23 16:30 | 23.6 | 23.9 | 20
| 2014-06-23 17:00 | 22.9 | 24.4 | 20
| 2014-06-23 17:30 | 22.8 | 24.4 | 20
| 2014-06-23 18:00 | 22.5 | 25 | 20
| 2014-06-23 18:30 | 22 | 25.6 | 20
| 2014-06-23 19:00 | 21.5 | 25.6 | 20
| 2014-06-23 19:30 | 21.2 | 25.6 | 20
| 2014-06-23 20:00 | 20.3 | 25.6 | 20
| 2014-06-23 20:30 | 19.8 | 25.6 | 20
| 2014-06-23 21:00 | 19.4 | 25.6 | 20
| 2014-06-23 21:30 | 18.9 | 25.6 | 20
| 2014-06-23 22:00 | 18.5 | 25.6 | 20
| 2014-06-23 22:30 | 17.8 | 25.6 | 20
| 2014-06-23 23:00 | 17.1 | 25.6 | 20
| 2014-06-23 23:30 | 16.3 | 25.6 | 20
| 2014-06-24 | 15.8 | 25.6 | 20
| 2014-06-24 00:30 | 15 | 25 | 20
| 2014-06-24 01:00 | 14.4 | 25 | 20
| 2014-06-24 01:30 | 13.9 | 25 | 20
| 2014-06-24 02:00 | 13.3 | 24.4 | 20
| 2014-06-24 02:30 | 12.5 | 24.4 | 20
| 2014-06-24 03:00 | 11.8 | 24.4 | 20
| 2014-06-24 03:30 | 11.3 | 24.4 | 20
| 2014-06-24 04:00 | 10.8 | 23.9 | 20
| 2014-06-24 04:30 | 10.3 | 23.9 | 20
| 2014-06-24 05:00 | 10.2 | 23.9 | 20
| 2014-06-24 05:30 | 9.9 | 23.3 | 20
| 2014-06-24 06:00 | 10 | 23.3 | 20
| 2014-06-24 06:30 | 10.5 | 23.3 | 20
| 2014-06-24 07:00 | 12.2 | 22.8 | 20
| 2014-06-24 07:30 | 13.8 | 22.8 | 20
| 2014-06-24 08:00 | 15.3 | 22.8 | 20
| 2014-06-24 08:30 | 16.5 | 22.2 | 20
| 2014-06-24 09:00 | 17.9 | 22.2 | 20
| 2014-06-24 09:30 | 18.8 | 22.2 | 20
| 2014-06-24 10:00 | 19.8 | 22.2 | 20
| 2014-06-24 10:30 | 21.6 | 22.2 | 20
| 2014-06-24 11:00 | 21.6 | 22.2 | 20
| 2014-06-24 11:30 | 22.7 | 22.2 | 20
| 2014-06-24 12:00 | 22.7 | 22.2 | 20
| 2014-06-24 12:30 | 22.8 | 22.2 | 20
| 2014-06-24 13:00 | 23.8 | 22.8 | 20
| 2014-06-24 13:30 | 23.9 | 22.8 | 20
| 2014-06-24 14:00 | 23.8 | 23.3 | 20
| 2014-06-24 14:30 | 25.2 | 23.3 | 20
| 2014-06-24 15:00 | 24.2 | 23.9 | 20
| 2014-06-24 15:30 | 24.7 | 23.9 | 20
| 2014-06-24 16:00 | 25.1 | 24.4 | 20
| 2014-06-24 16:30 | 25.1 | 24.4 | 20
| 2014-06-24 17:00 | 25.6 | 25 | 20
| 2014-06-24 17:30 | 25.3 | 25 | 20
| 2014-06-24 18:00 | 24.6 | 25 | 20
| 2014-06-24 18:30 | 24.3 | 25.6 | 20
| 2014-06-24 19:00 | 23.1 | 25.6 | 20
| 2014-06-24 19:30 | 23.2 | 25.6 | 20
| 2014-06-24 20:00 | 22.1 | 26.1 | 20
| 2014-06-24 20:30 | 20.2 | 26.1 | 20
| 2014-06-24 21:00 | 19.5 | 26.1 | 20
| 2014-06-24 21:30 | 19.1 | 26.1 | 20
| 2014-06-24 22:00 | 17.6 | 26.1 | 20
| 2014-06-24 22:30 | 15.7 | 25.6 | 20
| 2014-06-24 23:00 | 15 | 25.6 | 20
| 2014-06-24 23:30 | 14.7 | 25.6 | 20
| 2014-06-25 | 14.3 | 25.6 | 20
| 2014-06-25 00:30 | 14.4 | 25.6 | 20
| 2014-06-25 01:00 | 14.2 | 25 | 20
| 2014-06-25 01:30 | 13.8 | 25 | 20
| 2014-06-25 02:00 | 13.3 | 25 | 20
| 2014-06-25 02:30 | 12.9 | 24.4 | 20
| 2014-06-25 03:00 | 12.2 | 24.4 | 20
| 2014-06-25 03:30 | 11.7 | 24.4 | 20
| 2014-06-25 04:00 | 11.4 | 24.4 | 20
| 2014-06-25 04:30 | 11.1 | 23.9 | 20
| 2014-06-25 05:00 | 11.1 | 23.9 | 20
| 2014-06-25 05:30 | 11.1 | 23.9 | 20
| 2014-06-25 06:00 | 10.8 | 23.3 | 20
| 2014-06-25 06:30 | 11.3 | 23.3 | 20
| 2014-06-25 07:00 | 12.3 | 23.3 | 20
| 2014-06-25 07:30 | 13.1 | 22.8 | 20
| 2014-06-25 08:00 | 13.4 | 22.8 | 20
| 2014-06-25 08:30 | 13.6 | 22.8 | 20
| 2014-06-25 09:00 | 14.2 | 22.8 | 20
| 2014-06-25 09:30 | 14.7 | 22.2 | 20
| 2014-06-25 10:00 | 14.9 | 22.2 | 20
| 2014-06-25 10:30 | 15.3 | 22.2 | 20
| 2014-06-25 11:00 | 16.4 | 22.2 | 20
| 2014-06-25 11:30 | 16.9 | 22.2 | 20
| 2014-06-25 12:00 | 17.6 | 22.2 | 20
| 2014-06-25 12:30 | 18.4 | 22.2 | 20
| 2014-06-25 13:00 | 18.2 | 22.2 | 20
| 2014-06-25 13:30 | 18.8 | 22.2 | 20
| 2014-06-25 14:00 | 20 | 22.2 | 20
| 2014-06-25 14:30 | 19.8 | 22.8 | 20
| 2014-06-25 15:00 | 19.6 | 22.8 | 20
| 2014-06-25 15:30 | 19.9 | 22.8 | 20
| 2014-06-25 16:00 | 19.8 | 23.3 | 20
| 2014-06-25 16:30 | 19.4 | 23.3 | 20
| 2014-06-25 17:00 | 19.2 | 23.3 | 20
| 2014-06-25 17:30 | 19.1 | 23.9 | 20
| 2014-06-25 18:00 | 20.6 | 23.9 | 20
| 2014-06-25 18:30 | 20.5 | 23.9 | 20
| 2014-06-25 19:00 | 20.6 | 23.9 | 20
| 2014-06-25 19:30 | 20.7 | 24.4 | 20
| 2014-06-25 20:00 | 19.4 | 24.4 | 20
| 2014-06-25 20:30 | 18.2 | 24.4 | 20
| 2014-06-25 21:00 | 17.3 | 24.4 | 20
| 2014-06-25 21:30 | 16.3 | 24.4 | 20
| 2014-06-25 22:00 | 14.8 | 24.4 | 20
| 2014-06-25 22:30 | 13.9 | 24.4 | 20
| 2014-06-25 23:00 | 13.7 | 24.4 | 20
| 2014-06-25 23:30 | 13.3 | 24.4 | 20
| 2014-06-26 | 12.5 | 23.9 | 20
| 2014-06-26 00:30 | 11.7 | 23.9 | 20
| 2014-06-26 01:00 | 11.1 | 23.9 | 20
| 2014-06-26 01:30 | 10.4 | 23.9 | 20
| 2014-06-26 02:00 | 9.8 | 23.3 | 20
| 2014-06-26 02:30 | 9.8 | 23.3 | 20
| 2014-06-26 03:00 | 9 | 23.3 | 20
| 2014-06-26 03:30 | 8.4 | 23.3 | 20
| 2014-06-26 04:00 | 7.9 | 22.8 | 20
| 2014-06-26 04:30 | 7.7 | 22.8 | 20
| 2014-06-26 05:00 | 7.6 | 22.8 | 20
| 2014-06-26 05:30 | 7.6 | 22.2 | 20
| 2014-06-26 06:00 | 7.8 | 22.2 | 20
| 2014-06-26 06:30 | 8.9 | 22.2 | 20
| 2014-06-26 07:00 | 9.8 | 21.7 | 20
| 2014-06-26 07:30 | 11.7 | 21.7 | 20
| 2014-06-26 08:00 | 13.7 | 21.7 | 20
| 2014-06-26 08:30 | 15.2 | 21.7 | 20
| 2014-06-26 09:00 | 15.9 | 21.1 | 20
| 2014-06-26 09:30 | 16.6 | 21.1 | 20
| 2014-06-26 10:00 | 17.4 | 21.1 | 20
| 2014-06-26 10:30 | 17.2 | 21.1 | 20
| 2014-06-26 11:00 | 17.9 | 21.1 | 20
| 2014-06-26 11:30 | 18.3 | 21.1 | 20
| 2014-06-26 12:00 | 19 | 21.7 | 20
| 2014-06-26 12:30 | 20 | 21.7 | 20
| 2014-06-26 13:00 | 20.7 | 21.7 | 20
| 2014-06-26 13:30 | 20.1 | 21.7 | 20
| 2014-06-26 14:00 | 21.7 | 22.2 | 20
| 2014-06-26 14:30 | 21 | 22.2 | 20
| 2014-06-26 15:00 | 20.6 | 22.8 | 20
| 2014-06-26 15:30 | 21.8 | 23.3 | 20
| 2014-06-26 16:00 | 22.4 | 23.3 | 20
| 2014-06-26 16:30 | 22.8 | 23.3 | 20
| 2014-06-26 17:00 | 22.1 | 23.9 | 20
| 2014-06-26 17:30 | 23 | 23.9 | 20
| 2014-06-26 18:00 | 22.8 | 24.4 | 20
| 2014-06-26 18:30 | 22.8 | 24.4 | 20
| 2014-06-26 19:00 | 22 | 24.4 | 20
| 2014-06-26 19:30 | 22.1 | 25 | 20
| 2014-06-26 20:00 | 21.2 | 25 | 20
| 2014-06-26 20:30 | 20.7 | 25 | 20
| 2014-06-26 21:00 | 20.4 | 25 | 20
| 2014-06-26 21:30 | 18.6 | 25 | 20
| 2014-06-26 22:00 | 16.7 | 25 | 20
| 2014-06-26 22:30 | 15.2 | 25 | 20
| 2014-06-26 23:00 | 14.2 | 25 | 20
| 2014-06-26 23:30 | 13.1 | 25 | 20
| 2014-06-27 | 13 | 24.4 | 20
| 2014-06-27 00:30 | 12.9 | 24.4 | 20
| 2014-06-27 01:00 | 11.8 | 24.4 | 20
| 2014-06-27 01:30 | 11.7 | 24.4 | 20
| 2014-06-27 02:00 | 11.6 | 23.9 | 20
| 2014-06-27 02:30 | 10.9 | 23.9 | 20
| 2014-06-27 03:00 | 9.7 | 23.9 | 20
| 2014-06-27 03:30 | 9.6 | 23.3 | 20
| 2014-06-27 04:00 | 9.6 | 23.3 | 20
| 2014-06-27 04:30 | 9.4 | 23.3 | 20
| 2014-06-27 05:00 | 8.8 | 23.3 | 20
| 2014-06-27 05:30 | 8.4 | 22.8 | 20
| 2014-06-27 06:00 | 8.6 | 22.8 | 20
| 2014-06-27 06:30 | 8.9 | 22.8 | 20
| 2014-06-27 07:00 | 9.8 | 22.2 | 20
| 2014-06-27 07:30 | 11.3 | 22.2 | 20
| 2014-06-27 08:00 | 14.3 | 22.2 | 20
| 2014-06-27 08:30 | 16.6 | 22.2 | 20
| 2014-06-27 09:00 | 18.5 | 21.7 | 20
| 2014-06-27 09:30 | 20.1 | 21.7 | 20
| 2014-06-27 10:00 | 21.2 | 21.7 | 20
| 2014-06-27 10:30 | 21.8 | 21.7 | 20
| 2014-06-27 11:00 | 22.3 | 21.7 | 20
| 2014-06-27 11:30 | 23.6 | 21.7 | 20
| 2014-06-27 12:00 | 24.5 | 21.7 | 20
| 2014-06-27 12:30 | 24.3 | 21.7 | 20
| 2014-06-27 13:00 | 25.1 | 22.2 | 20
| 2014-06-27 13:30 | 26.2 | 22.2 | 20
| 2014-06-27 14:00 | 25 | 22.2 | 20
| 2014-06-27 14:30 | 25.2 | 22.8 | 20
| 2014-06-27 15:00 | 26.6 | 23.3 | 20
| 2014-06-27 15:30 | 27 | 23.3 | 20
| 2014-06-27 16:00 | 27.4 | 23.9 | 20
| 2014-06-27 16:30 | 27.4 | 23.9 | 20
| 2014-06-27 17:00 | 26.8 | 23.9 | 20
| 2014-06-27 17:30 | 26.1 | 24.4 | 20
| 2014-06-27 18:00 | 26.1 | 24.4 | 20
| 2014-06-27 18:30 | 25 | 25 | 20
| 2014-06-27 19:00 | 22.3 | 25 | 20
| 2014-06-27 19:30 | 22.1 | 25 | 20
| 2014-06-27 20:00 | 21.7 | 25.6 | 20
| 2014-06-27 20:30 | 20.9 | 25.6 | 20
| 2014-06-27 21:00 | 19.9 | 25 | 20
| 2014-06-27 21:30 | 19.6 | 25 | 20
| 2014-06-27 22:00 | 19.1 | 25 | 20
| 2014-06-27 22:30 | 18.3 | 25 | 20
| 2014-06-27 23:00 | 17.4 | 25 | 20
| 2014-06-27 23:30 | 17.1 | 25 | 20
| 2014-06-28 | 17.4 | 25 | 20
| 2014-06-28 00:30 | 16.4 | 24.4 | 20
| 2014-06-28 01:00 | 15.8 | 24.4 | 20
| 2014-06-28 01:30 | 15.4 | 24.4 | 20
| 2014-06-28 02:00 | 15 | 24.4 | 20
| 2014-06-28 02:30 | 14.6 | 23.9 | 20
| 2014-06-28 03:00 | 14.2 | 23.9 | 20
| 2014-06-28 03:30 | 13.8 | 23.9 | 20
| 2014-06-28 04:00 | 13.5 | 23.9 | 20
| 2014-06-28 04:30 | 13.1 | 23.9 | 20
| 2014-06-28 05:00 | 13 | 23.3 | 20
| 2014-06-28 05:30 | 13.4 | 23.3 | 20
| 2014-06-28 06:00 | 13.4 | 23.3 | 20
| 2014-06-28 06:30 | 13.7 | 23.3 | 20
| 2014-06-28 07:00 | 14.2 | 22.8 | 20
| 2014-06-28 07:30 | 14.9 | 22.8 | 20
| 2014-06-28 08:00 | 16.2 | 22.8 | 20
| 2014-06-28 08:30 | 17.6 | 22.8 | 20
| 2014-06-28 09:00 | 18.4 | 22.2 | 20
| 2014-06-28 09:30 | 19.2 | 22.2 | 20
| 2014-06-28 10:00 | 19.8 | 22.2 | 20
| 2014-06-28 10:30 | 20.8 | 22.2 | 20
| 2014-06-28 11:00 | 21.1 | 22.2 | 20
| 2014-06-28 11:30 | 20.7 | 22.2 | 20
| 2014-06-28 12:00 | 20.8 | 22.2 | 20
| 2014-06-28 12:30 | 19.9 | 22.2 | 20
| 2014-06-28 13:00 | 19.8 | 22.8 | 20
| 2014-06-28 13:30 | 19.4 | 22.8 | 20
| 2014-06-28 14:00 | 19.5 | 22.8 | 20.6
| 2014-06-28 14:30 | 19.3 | 22.8 | 20.6
| 2014-06-28 15:00 | 19.3 | 22.8 | 20.6
| 2014-06-28 15:30 | 19.3 | 22.8 | 20.6
| 2014-06-28 16:00 | 19.6 | 22.8 | 20.6
| 2014-06-28 16:30 | 20.8 | 22.8 | 20.6
| 2014-06-28 17:00 | 21.6 | 22.8 | 20.6
| 2014-06-28 17:30 | 21.1 | 22.8 | 20.6
| 2014-06-28 18:00 | 20.9 | 22.8 | 20.6
| 2014-06-28 18:30 | 21.8 | 22.8 | 20.6
| 2014-06-28 19:00 | 21.2 | 22.8 | 20.6
| 2014-06-28 19:30 | 20.8 | 22.8 | 20.6
| 2014-06-28 20:00 | 20.9 | 22.8 | 20.6
| 2014-06-28 20:30 | 20.9 | 22.8 | 20.6
| 2014-06-28 21:00 | 20.3 | 22.8 | 20.6
| 2014-06-28 21:30 | 19.8 | 22.8 | 20.6
| 2014-06-28 22:00 | 19.2 | 22.8 | 20.6
| 2014-06-28 22:30 | 18.9 | 22.8 | 20.6
| 2014-06-28 23:00 | 17.7 | 22.8 | 20.6
| 2014-06-28 23:30 | 17.3 | 22.8 | 20.6
| 2014-06-29 | 16.2 | 22.8 | 20.6
| 2014-06-29 00:30 | 15.5 | 22.8 | 20.6
| 2014-06-29 01:00 | 15.2 | 22.2 | 20.6
| 2014-06-29 01:30 | 15.2 | 22.2 | 20.6
| 2014-06-29 02:00 | 15.1 | 22.2 | 20.6
| 2014-06-29 02:30 | 15.2 | 22.2 | 20.6
| 2014-06-29 03:00 | 15.6 | 22.2 | 20.6
| 2014-06-29 03:30 | 15.7 | 21.7 | 20.6
| 2014-06-29 04:00 | 15.7 | 21.7 | 20.6
| 2014-06-29 04:30 | 15.8 | 21.7 | 20.6
| 2014-06-29 05:00 | 15.9 | 21.7 | 20.6
| 2014-06-29 05:30 | 16.1 | 21.1 | 20.6
| 2014-06-29 06:00 | 16.1 | 21.1 | 20.6
| 2014-06-29 06:30 | 16.3 | 21.1 | 20.6
| 2014-06-29 07:00 | 16.4 | 21.1 | 20.6
| 2014-06-29 07:30 | 16.1 | 21.1 | 20.6
| 2014-06-29 08:00 | 16 | 21.1 | 20.6
| 2014-06-29 08:30 | 16.1 | 20.6 | 20.6
| 2014-06-29 09:00 | 15.8 | 20.6 | 20.6
| 2014-06-29 09:30 | 15 | 20.6 | 20.6
| 2014-06-29 10:00 | 15.1 | 20.6 | 20.6
| 2014-06-29 10:30 | 15.4 | 20.6 | 20.6
| 2014-06-29 11:00 | 15.6 | 20.6 | 20.6
| 2014-06-29 11:30 | 15.8 | 20.6 | 20
| 2014-06-29 12:00 | 16.9 | 20.6 | 20
| 2014-06-29 12:30 | 16.9 | 20.6 | 20
| 2014-06-29 13:00 | 17.8 | 20.6 | 20
| 2014-06-29 13:30 | 18.3 | 20.6 | 20
| 2014-06-29 14:00 | 17.2 | 20.6 | 20
| 2014-06-29 14:30 | 15.8 | 20.6 | 20
| 2014-06-29 15:00 | 17.1 | 20.6 | 20
| 2014-06-29 15:30 | 18 | 20.6 | 20
| 2014-06-29 16:00 | 18.9 | 20.6 | 20
| 2014-06-29 16:30 | 20.1 | 21.1 | 20
| 2014-06-29 17:00 | 19.6 | 21.1 | 20
| 2014-06-29 17:30 | 19.6 | 21.1 | 20
| 2014-06-29 18:00 | 20.1 | 21.1 | 20
| 2014-06-29 18:30 | 19.1 | 21.7 | 20
| 2014-06-29 19:00 | 19.1 | 21.7 | 20
| 2014-06-29 19:30 | 18.2 | 21.7 | 20
| 2014-06-29 20:00 | 18.2 | 21.7 | 20
| 2014-06-29 20:30 | 16.9 | 21.7 | 20
| 2014-06-29 21:00 | 16.1 | 21.7 | 20
| 2014-06-29 21:30 | 15.7 | 21.7 | 20
| 2014-06-29 22:00 | 15.5 | 21.7 | 20
| 2014-06-29 22:30 | 15.3 | 21.7 | 20
| 2014-06-29 23:00 | 14.6 | 21.1 | 20
| 2014-06-29 23:30 | 14.2 | 21.1 | 20
| 2014-06-30 | 14 | 21.1 | 20
| 2014-06-30 00:30 | 13.7 | 21.1 | 20
| 2014-06-30 01:00 | 13.3 | 21.1 | 20
| 2014-06-30 01:30 | 13.3 | 20.6 | 20
| 2014-06-30 02:00 | 13.3 | 20.6 | 20
| 2014-06-30 02:30 | 13.3 | 20.6 | 20
| 2014-06-30 03:00 | 13.2 | 20.6 | 20
| 2014-06-30 03:30 | 13.2 | 20.6 | 20
| 2014-06-30 04:00 | 13.5 | 20 | 20
| 2014-06-30 04:30 | 13.5 | 20 | 20
| 2014-06-30 05:00 | 13.4 | 20 | 20
| 2014-06-30 05:30 | 13.2 | 20 | 20
| 2014-06-30 06:00 | 13.2 | 20 | 20
| 2014-06-30 06:30 | 13.3 | 20 | 20
| 2014-06-30 07:00 | 13.6 | 19.4 | 20
| 2014-06-30 07:30 | 13.7 | 19.4 | 20
| 2014-06-30 08:00 | 13.9 | 19.4 | 20
| 2014-06-30 08:30 | 14.3 | 19.4 | 20
| 2014-06-30 09:00 | 15.3 | 19.4 | 20
| 2014-06-30 09:30 | 15.6 | 19.4 | 20
| 2014-06-30 10:00 | 16.4 | 19.4 | 20
| 2014-06-30 10:30 | 17.6 | 19.4 | 20
| 2014-06-30 11:00 | 16.8 | 19.4 | 20
| 2014-06-30 11:30 | 17.4 | 19.4 | 20
| 2014-06-30 12:00 | 19.1 | 19.4 | 20
| 2014-06-30 12:30 | 19.1 | 19.4 | 20
| 2014-06-30 13:00 | 18.2 | 19.4 | 20
| 2014-06-30 13:30 | 20.6 | 20 | 20
| 2014-06-30 14:00 | 21 | 20 | 20
| 2014-06-30 14:30 | 20.6 | 20 | 20
| 2014-06-30 15:00 | 19.1 | 20.6 | 20
| 2014-06-30 15:30 | 17.8 | 20.6 | 20
| 2014-06-30 16:00 | 20 | 20.6 | 20
| 2014-06-30 16:30 | 22.4 | 21.1 | 20
| 2014-06-30 17:00 | 20.8 | 21.1 | 20
| 2014-06-30 17:30 | 21.3 | 21.1 | 20
| 2014-06-30 18:00 | 21.7 | 21.1 | 20
| 2014-06-30 18:30 | 20.5 | 21.7 | 20
| 2014-06-30 19:00 | 20.6 | 21.7 | 20
| 2014-06-30 19:30 | 19.7 | 21.7 | 20
| 2014-06-30 20:00 | 19.7 | 21.7 | 20
| 2014-06-30 20:30 | 18.9 | 21.7 | 20
| 2014-06-30 21:00 | 17.9 | 21.7 | 20
| 2014-06-30 21:30 | 17.3 | 21.7 | 20
| 2014-06-30 22:00 | 16.8 | 21.7 | 20
| 2014-06-30 22:30 | 16.6 | 21.7 | 20
| 2014-06-30 23:00 | 16.2 | 21.1 | 20
| 2014-06-30 23:30 | 15.6 | 21.1 | 20
| 2014-07-01 | 14.8 | 21.1 | 20
| 2014-07-01 00:30 | 13.7 | 21.1 | 20
| 2014-07-01 01:00 | 12.6 | 20.6 | 20
| 2014-07-01 01:30 | 11.6 | 20.6 | 20
| 2014-07-01 02:00 | 10.8 | 20.6 | 20
| 2014-07-01 02:30 | 10.4 | 20.6 | 20
| 2014-07-01 03:00 | 9.8 | 20 | 20
| 2014-07-01 03:30 | 9.5 | 20 | 20
| 2014-07-01 04:00 | 9.1 | 20 | 20
| 2014-07-01 04:30 | 8.8 | 19.4 | 20
| 2014-07-01 05:00 | 8.5 | 19.4 | 20
| 2014-07-01 05:30 | 8.4 | 19.4 | 20
| 2014-07-01 06:00 | 8.6 | 19.4 | 20
| 2014-07-01 06:30 | 9 | 18.9 | 20
| 2014-07-01 07:00 | 9.8 | 18.9 | 20
| 2014-07-01 07:30 | 11.3 | 18.9 | 20
| 2014-07-01 08:00 | 13.3 | 18.3 | 20
| 2014-07-01 08:30 | 15.2 | 18.3 | 20
| 2014-07-01 09:00 | 16.1 | 18.3 | 20
| 2014-07-01 09:30 | 17.2 | 18.3 | 20
| 2014-07-01 10:00 | 18 | 18.3 | 20
| 2014-07-01 10:30 | 18.8 | 18.3 | 20
| 2014-07-01 11:00 | 19.6 | 18.3 | 20
| 2014-07-01 11:30 | 19.7 | 18.3 | 20
| 2014-07-01 12:00 | 19.2 | 18.3 | 20
| 2014-07-01 12:30 | 21.2 | 18.9 | 20
| 2014-07-01 13:00 | 21.3 | 18.9 | 20
| 2014-07-01 13:30 | 22.4 | 19.4 | 20
| 2014-07-01 14:00 | 22.5 | 19.4 | 20
| 2014-07-01 14:30 | 22.4 | 20 | 20
| 2014-07-01 15:00 | 23.4 | 20.6 | 20
| 2014-07-01 15:30 | 23.6 | 20.6 | 20
| 2014-07-01 16:00 | 23.4 | 21.1 | 20
| 2014-07-01 16:30 | 23.7 | 21.1 | 20
| 2014-07-01 17:00 | 23.5 | 21.7 | 20
| 2014-07-01 17:30 | 23.4 | 22.2 | 20
| 2014-07-01 18:00 | 23.6 | 22.2 | 20
| 2014-07-01 18:30 | 23.6 | 22.8 | 20
| 2014-07-01 19:00 | 22.4 | 22.8 | 20
| 2014-07-01 19:30 | 22.3 | 23.3 | 20
| 2014-07-01 20:00 | 22.3 | 23.3 | 19.4
| 2014-07-01 20:30 | 21.6 | 23.3 | 19.4
| 2014-07-01 21:00 | 20.4 | 23.3 | 19.4
| 2014-07-01 21:30 | 18.9 | 23.3 | 19.4
| 2014-07-01 22:00 | 17.7 | 23.3 | 19.4
| 2014-07-01 22:30 | 16.6 | 23.3 | 19.4
| 2014-07-01 23:00 | 15.6 | 23.3 | 19.4
| 2014-07-01 23:30 | 14.8 | 22.8 | 19.4
| 2014-07-02 | 14.2 | 22.8 | 19.4
| 2014-07-02 00:30 | 13.6 | 22.8 | 19.4
| 2014-07-02 01:00 | 13.1 | 22.2 | 19.4
| 2014-07-02 01:30 | 12.2 | 22.2 | 19.4
| 2014-07-02 02:00 | 11.7 | 22.2 | 19.4
| 2014-07-02 02:30 | 11.7 | 21.7 | 19.4
| 2014-07-02 03:00 | 11.4 | 21.7 | 19.4
| 2014-07-02 03:30 | 10.9 | 21.7 | 19.4
| 2014-07-02 04:00 | 11.1 | 21.1 | 19.4
| 2014-07-02 04:30 | 11 | 21.1 | 19.4
| 2014-07-02 05:00 | 10.9 | 21.1 | 19.4
| 2014-07-02 05:30 | 10.8 | 20.6 | 19.4
| 2014-07-02 06:00 | 10.7 | 20.6 | 19.4
| 2014-07-02 06:30 | 11.1 | 20.6 | 19.4
| 2014-07-02 07:00 | 12 | 20 | 19.4
| 2014-07-02 07:30 | 13.3 | 20 | 19.4
| 2014-07-02 08:00 | 14.4 | 20 | 19.4
| 2014-07-02 08:30 | 15.7 | 20 | 19.4
| 2014-07-02 09:00 | 17.6 | 19.4 | 19.4
| 2014-07-02 09:30 | 19.1 | 19.4 | 19.4
| 2014-07-02 10:00 | 19.7 | 19.4 | 19.4
| 2014-07-02 10:30 | 20.4 | 19.4 | 19.4
| 2014-07-02 11:00 | 21.1 | 19.4 | 19.4
| 2014-07-02 11:30 | 21.3 | 19.4 | 19.4
| 2014-07-02 12:00 | 21.7 | 19.4 | 19.4
| 2014-07-02 12:30 | 22.7 | 20 | 19.4
| 2014-07-02 13:00 | 22.7 | 20 | 19.4
| 2014-07-02 13:30 | 23.4 | 20.6 | 19.4
| 2014-07-02 14:00 | 23.7 | 21.1 | 19.4
| 2014-07-02 14:30 | 24.1 | 21.1 | 19.4
| 2014-07-02 15:00 | 23.2 | 21.7 | 19.4
| 2014-07-02 15:30 | 23.1 | 22.2 | 19.4
| 2014-07-02 16:00 | 24.7 | 22.8 | 19.4
| 2014-07-02 16:30 | 24.4 | 22.8 | 19.4
| 2014-07-02 17:00 | 25.2 | 23.3 | 19.4
| 2014-07-02 17:30 | 25.9 | 23.3 | 19.4
| 2014-07-02 18:00 | 25.4 | 23.9 | 19.4
| 2014-07-02 18:30 | 24.7 | 23.9 | 19.4
| 2014-07-02 19:00 | 25.5 | 24.4 | 19.4
| 2014-07-02 19:30 | 24.9 | 24.4 | 19.4
| 2014-07-02 20:00 | 24.5 | 24.4 | 19.4
| 2014-07-02 20:30 | 23.8 | 24.4 | 19.4
| 2014-07-02 21:00 | 22.6 | 24.4 | 19.4
| 2014-07-02 21:30 | 21 | 24.4 | 19.4
| 2014-07-02 22:00 | 19.2 | 24.4 | 19.4
| 2014-07-02 22:30 | 17.7 | 24.4 | 19.4
| 2014-07-02 23:00 | 16.6 | 24.4 | 19.4
| 2014-07-02 23:30 | 15.7 | 24.4 | 19.4
| 2014-07-03 | 14.6 | 23.9 | 19.4
| 2014-07-03 00:30 | 13.6 | 23.9 | 19.4
| 2014-07-03 01:00 | 13.2 | 23.9 | 19.4
| 2014-07-03 01:30 | 12.7 | 23.3 | 19.4
| 2014-07-03 02:00 | 12.2 | 23.3 | 19.4
| 2014-07-03 02:30 | 12.2 | 23.3 | 19.4
| 2014-07-03 03:00 | 11.6 | 22.8 | 19.4
| 2014-07-03 03:30 | 10.8 | 22.8 | 19.4
| 2014-07-03 04:00 | 10.7 | 22.2 | 19.4
| 2014-07-03 04:30 | 10.4 | 22.2 | 19.4
| 2014-07-03 05:00 | 9.9 | 22.2 | 19.4
| 2014-07-03 05:30 | 9.6 | 21.7 | 19.4
| 2014-07-03 06:00 | 9.8 | 21.7 | 19.4
| 2014-07-03 06:30 | 10.1 | 21.7 | 19.4
| 2014-07-03 07:00 | 11.2 | 21.7 | 19.4
| 2014-07-03 07:30 | 12.3 | 21.1 | 19.4
| 2014-07-03 08:00 | 14.7 | 21.1 | 19.4
| 2014-07-03 08:30 | 16.3 | 21.1 | 19.4
| 2014-07-03 09:00 | 17.8 | 20.6 | 19.4
| 2014-07-03 09:30 | 19.6 | 20.6 | 19.4
| 2014-07-03 10:00 | 21.1 | 20.6 | 19.4
| 2014-07-03 10:30 | 21.9 | 20.6 | 19.4
| 2014-07-03 11:00 | 23.3 | 20.6 | 19.4
| 2014-07-03 11:30 | 24.2 | 20.6 | 19.4
| 2014-07-03 12:00 | 25 | 21.1 | 19.4
| 2014-07-03 12:30 | 25.8 | 21.1 | 19.4
| 2014-07-03 13:00 | 26.7 | 21.1 | 19.4
| 2014-07-03 13:30 | 27.6 | 21.7 | 19.4
| 2014-07-03 14:00 | 28.3 | 22.2 | 19.4
| 2014-07-03 14:30 | 29 | 22.2 | 19.4
| 2014-07-03 15:00 | 29.4 | 22.8 | 19.4
| 2014-07-03 15:30 | 29.9 | 23.3 | 19.4
| 2014-07-03 16:00 | 29.9 | 23.9 | 19.4
| 2014-07-03 16:30 | 30.1 | 23.9 | 19.4
| 2014-07-03 17:00 | 30.2 | 24.4 | 19.4
| 2014-07-03 17:30 | 30.3 | 25 | 19.4
| 2014-07-03 18:00 | 30 | 25 | 19.4
| 2014-07-03 18:30 | 29.7 | 25.6 | 19.4
| 2014-07-03 19:00 | 29.6 | 25.6 | 19.4
| 2014-07-03 19:30 | 29.1 | 26.1 | 19.4
| 2014-07-03 20:00 | 28.7 | 26.1 | 19.4
| 2014-07-03 20:30 | 28.4 | 26.1 | 19.4
| 2014-07-03 21:00 | 26.9 | 26.1 | 19.4
| 2014-07-03 21:30 | 24.4 | 26.1 | 19.4
| 2014-07-03 22:00 | 22.6 | 26.1 | 19.4
| 2014-07-03 22:30 | 21.3 | 26.1 | 19.4
| 2014-07-03 23:00 | 20.3 | 26.1 | 19.4
| 2014-07-03 23:30 | 19.6 | 26.1 | 19.4
| 2014-07-04 | 19 | 25.6 | 19.4
| 2014-07-04 00:30 | 18.5 | 25.6 | 19.4
| 2014-07-04 01:00 | 17.9 | 25.6 | 19.4
| 2014-07-04 01:30 | 17.1 | 25.6 | 19.4
| 2014-07-04 02:00 | 16.3 | 25 | 19.4
| 2014-07-04 02:30 | 15.4 | 25 | 19.4
| 2014-07-04 03:00 | 15.1 | 24.4 | 19.4
| 2014-07-04 03:30 | 14.9 | 24.4 | 19.4
| 2014-07-04 04:00 | 14.8 | 24.4 | 19.4
| 2014-07-04 04:30 | 14.6 | 24.4 | 19.4
| 2014-07-04 05:00 | 13.8 | 23.9 | 19.4
| 2014-07-04 05:30 | 13.1 | 23.9 | 19.4
| 2014-07-04 06:00 | 13.1 | 23.9 | 19.4
| 2014-07-04 06:30 | 13.2 | 23.3 | 19.4
| 2014-07-04 07:00 | 13.9 | 23.3 | 19.4
| 2014-07-04 07:30 | 15.4 | 23.3 | 20
| 2014-07-04 08:00 | 18.1 | 22.8 | 20
| 2014-07-04 08:30 | 20.6 | 22.8 | 20
| 2014-07-04 09:00 | 22.1 | 22.8 | 20
| 2014-07-04 09:30 | 22.9 | 22.8 | 20
| 2014-07-04 10:00 | 24.1 | 22.2 | 20
| 2014-07-04 10:30 | 25.4 | 22.2 | 20
| 2014-07-04 11:00 | 26.9 | 22.2 | 20
| 2014-07-04 11:30 | 27.2 | 22.8 | 20
| 2014-07-04 12:00 | 29.5 | 22.8 | 20
| 2014-07-04 12:30 | 30.5 | 22.8 | 20
| 2014-07-04 13:00 | 30.6 | 23.3 | 20
| 2014-07-04 13:30 | 31.8 | 23.3 | 20
| 2014-07-04 14:00 | 31.4 | 23.9 | 20
| 2014-07-04 14:30 | 31.2 | 24.4 | 20
| 2014-07-04 15:00 | 30.9 | 24.4 | 20
| 2014-07-04 15:30 | 29.9 | 25 | 20
| 2014-07-04 16:00 | 31.2 | 25.6 | 20
| 2014-07-04 16:30 | 31.1 | 25.6 | 20
| 2014-07-04 17:00 | 30.2 | 25.6 | 20
| 2014-07-04 17:30 | 30.1 | 26.1 | 20
| 2014-07-04 18:00 | 29.8 | 26.1 | 20
| 2014-07-04 18:30 | 29.2 | 26.7 | 20
| 2014-07-04 19:00 | 28.7 | 26.7 | 20
| 2014-07-04 19:30 | 28.1 | 26.7 | 20
| 2014-07-04 20:00 | 27.4 | 26.7 | 20
| 2014-07-04 20:30 | 26.1 | 26.7 | 20
| 2014-07-04 21:00 | 25.2 | 26.7 | 20
| 2014-07-04 21:30 | 23.8 | 26.7 | 20
| 2014-07-04 22:00 | 22.8 | 26.7 | 20
| 2014-07-04 22:30 | 21.6 | 26.7 | 20
| 2014-07-04 23:00 | 20.7 | 26.7 | 20
| 2014-07-04 23:30 | 20.9 | 26.1 | 20
| 2014-07-05 | 20.4 | 26.1 | 20
| 2014-07-05 00:30 | 19.2 | 26.1 | 20
| 2014-07-05 01:00 | 18.3 | 26.1 | 20
| 2014-07-05 01:30 | 18.7 | 25.6 | 20
| 2014-07-05 02:00 | 18.4 | 25.6 | 20
| 2014-07-05 02:30 | 18.7 | 25.6 | 20
| 2014-07-05 03:00 | 19.2 | 25.6 | 20
| 2014-07-05 03:30 | 18.8 | 25 | 20
| 2014-07-05 04:00 | 18.6 | 25 | 20
| 2014-07-05 04:30 | 18.3 | 25 | 20
| 2014-07-05 05:00 | 18.3 | 24.4 | 20
| 2014-07-05 05:30 | 18.3 | 24.4 | 20
| 2014-07-05 06:00 | 18.5 | 24.4 | 20
| 2014-07-05 06:30 | 18.6 | 24.4 | 20
| 2014-07-05 07:00 | 18.9 | 24.4 | 20
| 2014-07-05 07:30 | 19.7 | 23.9 | 20
| 2014-07-05 08:00 | 19.9 | 23.9 | 20
| 2014-07-05 08:30 | 20.2 | 23.9 | 20
| 2014-07-05 09:00 | 20.8 | 23.9 | 20
| 2014-07-05 09:30 | 20.7 | 23.9 | 20
| 2014-07-05 10:00 | 21.2 | 23.9 | 20
| 2014-07-05 10:30 | 21.7 | 23.9 | 20
| 2014-07-05 11:00 | 22.9 | 23.9 | 20
| 2014-07-05 11:30 | 23 | 23.9 | 20
| 2014-07-05 12:00 | 23.9 | 23.9 | 20
| 2014-07-05 12:30 | 24.2 | 23.9 | 20
| 2014-07-05 13:00 | 23.8 | 23.9 | 20
| 2014-07-05 13:30 | 21.1 | 23.9 | 20
| 2014-07-05 14:00 | 19.3 | 23.9 | 20
| 2014-07-05 14:30 | 19.7 | 24.4 | 20
| 2014-07-05 15:00 | 20.2 | 24.4 | 20
| 2014-07-05 15:30 | 19.7 | 24.4 | 20
| 2014-07-05 16:00 | 20.1 | 24.4 | 20
| 2014-07-05 16:30 | 20.9 | 24.4 | 20
| 2014-07-05 17:00 | 19.8 | 24.4 | 20
| 2014-07-05 17:30 | 20.1 | 24.4 | 20
| 2014-07-05 18:00 | 20.4 | 24.4 | 20
| 2014-07-05 18:30 | 20.6 | 24.4 | 20
| 2014-07-05 19:00 | 20.2 | 24.4 | 20
| 2014-07-05 19:30 | 20.2 | 24.4 | 20
| 2014-07-05 20:00 | 20.1 | 23.9 | 20
| 2014-07-05 20:30 | 20.1 | 23.9 | 20
| 2014-07-05 21:00 | 20.1 | 23.9 | 20.6
| 2014-07-05 21:30 | 19.9 | 23.9 | 20.6
| 2014-07-05 22:00 | 19.9 | 23.9 | 20.6
| 2014-07-05 22:30 | 20.1 | 23.9 | 20.6
| 2014-07-05 23:00 | 20.2 | 23.9 | 20.6
| 2014-07-05 23:30 | 20.2 | 23.3 | 20.6
| 2014-07-06 | 20.2 | 23.3 | 20.6
| 2014-07-06 00:30 | 20.3 | 23.3 | 20.6
| 2014-07-06 01:00 | 20.3 | 23.3 | 20.6
| 2014-07-06 01:30 | 19.7 | 23.3 | 20.6
| 2014-07-06 02:00 | 19.1 | 23.3 | 20.6
| 2014-07-06 02:30 | 18.8 | 22.8 | 20.6
| 2014-07-06 03:00 | 18.4 | 22.8 | 20.6
| 2014-07-06 03:30 | 18.1 | 22.8 | 20.6
| 2014-07-06 04:00 | 17.8 | 22.8 | 20.6
| 2014-07-06 04:30 | 17.6 | 22.8 | 20.6
| 2014-07-06 05:00 | 17.5 | 22.2 | 20.6
| 2014-07-06 05:30 | 17.6 | 22.2 | 20.6
| 2014-07-06 06:00 | 17.5 | 22.2 | 20.6
| 2014-07-06 06:30 | 17.4 | 22.2 | 20.6
| 2014-07-06 07:00 | 17.9 | 22.2 | 20.6
| 2014-07-06 07:30 | 19.3 | 22.2 | 20.6
| 2014-07-06 08:00 | 20.3 | 21.7 | 20.6
| 2014-07-06 08:30 | 22.1 | 21.7 | 20.6
| 2014-07-06 09:00 | 23.6 | 21.7 | 20.6
| 2014-07-06 09:30 | 24.6 | 21.7 | 20.6
| 2014-07-06 10:00 | 25.7 | 21.7 | 20.6
| 2014-07-06 10:30 | 26.3 | 21.7 | 20.6
| 2014-07-06 11:00 | 27.3 | 21.7 | 20.6
| 2014-07-06 11:30 | 28.3 | 22.2 | 20.6
| 2014-07-06 12:00 | 28.8 | 22.2 | 20.6
| 2014-07-06 12:30 | 29.3 | 22.2 | 20.6
| 2014-07-06 13:00 | 30.1 | 22.8 | 20.6
| 2014-07-06 13:30 | 29.8 | 23.3 | 20.6
| 2014-07-06 14:00 | 30.1 | 23.3 | 20.6
| 2014-07-06 14:30 | 29.7 | 23.9 | 20.6
| 2014-07-06 15:00 | 30.4 | 23.9 | 20.6
| 2014-07-06 15:30 | 32.1 | 24.4 | 20.6
| 2014-07-06 16:00 | 30.6 | 24.4 | 20.6
| 2014-07-06 16:30 | 30.2 | 25 | 20.6
| 2014-07-06 17:00 | 30.3 | 25.6 | 20.6
| 2014-07-06 17:30 | 31.7 | 25.6 | 20.6
| 2014-07-06 18:00 | 31.8 | 25.6 | 20.6
| 2014-07-06 18:30 | 31.3 | 26.1 | 20.6
| 2014-07-06 19:00 | 31.2 | 26.1 | 20.6
| 2014-07-06 19:30 | 30.6 | 26.1 | 20.6
| 2014-07-06 20:00 | 30.1 | 26.7 | 20.6
| 2014-07-06 20:30 | 28.8 | 26.7 | 20.6
| 2014-07-06 21:00 | 27.2 | 26.7 | 20.6
| 2014-07-06 21:30 | 22.2 | 26.7 | 20.6
| 2014-07-06 22:00 | 18.3 | 26.7 | 20.6
| 2014-07-06 22:30 | 18 | 26.7 | 20.6
| 2014-07-06 23:00 | 17.6 | 26.7 | 20.6
| 2014-07-06 23:30 | 17.3 | 26.1 | 20.6
| 2014-07-07 | 17.3 | 26.1 | 20.6
| 2014-07-07 00:30 | 17.3 | 26.1 | 20.6
| 2014-07-07 01:00 | 17.4 | 25.6 | 20.6
| 2014-07-07 01:30 | 17.4 | 25.6 | 20.6
| 2014-07-07 02:00 | 17.4 | 25.6 | 20.6
| 2014-07-07 02:30 | 17.2 | 25 | 20.6
| 2014-07-07 03:00 | 17.2 | 25 | 20.6
| 2014-07-07 03:30 | 17.2 | 24.4 | 20.6
| 2014-07-07 04:00 | 17.1 | 24.4 | 20.6
| 2014-07-07 04:30 | 17 | 24.4 | 20.6
| 2014-07-07 05:00 | 17 | 24.4 | 20.6
| 2014-07-07 05:30 | 16.9 | 23.9 | 20.6
| 2014-07-07 06:00 | 17.1 | 23.9 | 20.6
| 2014-07-07 06:30 | 17.1 | 23.9 | 20.6
| 2014-07-07 07:00 | 17.2 | 23.9 | 20.6
| 2014-07-07 07:30 | 16.9 | 23.3 | 20.6
| 2014-07-07 08:00 | 16.8 | 23.3 | 20.6
| 2014-07-07 08:30 | 16.8 | 23.3 | 20.6
| 2014-07-07 09:00 | 16.8 | 23.3 | 20.6
| 2014-07-07 09:30 | 17.2 | 23.3 | 20.6
| 2014-07-07 10:00 | 18 | 23.3 | 20.6
| 2014-07-07 10:30 | 18.4 | 22.8 | 20.6
| 2014-07-07 11:00 | 19.1 | 22.8 | 20.6
| 2014-07-07 11:30 | 19.5 | 22.8 | 20.6
| 2014-07-07 12:00 | 20.4 | 22.8 | 20.6
| 2014-07-07 12:30 | 21.3 | 23.3 | 20.6
| 2014-07-07 13:00 | 21.9 | 23.3 | 20.6
| 2014-07-07 13:30 | 21.8 | 23.3 | 20.6
| 2014-07-07 14:00 | 22.6 | 23.3 | 20.6
| 2014-07-07 14:30 | 23.1 | 23.9 | 20.6
| 2014-07-07 15:00 | 23.9 | 23.9 | 20.6
| 2014-07-07 15:30 | 24.1 | 23.9 | 20.6
| 2014-07-07 16:00 | 24.4 | 23.9 | 20.6
| 2014-07-07 16:30 | 23.8 | 24.4 | 20.6
| 2014-07-07 17:00 | 23.6 | 24.4 | 20.6
| 2014-07-07 17:30 | 23.6 | 24.4 | 20.6
| 2014-07-07 18:00 | 24.2 | 24.4 | 20.6
| 2014-07-07 18:30 | 24.3 | 24.4 | 20.6
| 2014-07-07 19:00 | 23.4 | 24.4 | 20.6
| 2014-07-07 19:30 | 22.8 | 24.4 | 20.6
| 2014-07-07 20:00 | 22.3 | 24.4 | 20.6
| 2014-07-07 20:30 | 21.9 | 24.4 | 20.6
| 2014-07-07 21:00 | 21.7 | 24.4 | 20.6
| 2014-07-07 21:30 | 21.4 | 24.4 | 20.6
| 2014-07-07 22:00 | 20.9 | 24.4 | 20.6
| 2014-07-07 22:30 | 20.7 | 24.4 | 20.6
| 2014-07-07 23:00 | 20.6 | 24.4 | 20.6
| 2014-07-07 23:30 | 20.5 | 23.9 | 20.6
| 2014-07-08 | 20.3 | 23.9 | 20.6
| 2014-07-08 00:30 | 19.7 | 23.9 | 20.6
| 2014-07-08 01:00 | 18.5 | 23.9 | 20.6
| 2014-07-08 01:30 | 17.7 | 23.9 | 20.6
| 2014-07-08 02:00 | 17.3 | 23.3 | 20.6
| 2014-07-08 02:30 | 16.9 | 23.3 | 20.6
| 2014-07-08 03:00 | 16.7 | 23.3 | 20.6
| 2014-07-08 03:30 | 16.3 | 23.3 | 20.6
| 2014-07-08 04:00 | 16.4 | 23.3 | 20.6
| 2014-07-08 04:30 | 16.4 | 22.8 | 20.6
| 2014-07-08 05:00 | 16.6 | 22.8 | 20.6
| 2014-07-08 05:30 | 16.7 | 22.8 | 20.6
| 2014-07-08 06:00 | 16.7 | 22.2 | 20.6
| 2014-07-08 06:30 | 16.8 | 22.2 | 20.6
| 2014-07-08 07:00 | 16.8 | 22.2 | 20.6
| 2014-07-08 07:30 | 16.8 | 22.2 | 20.6
| 2014-07-08 08:00 | 16.8 | 22.2 | 20.6
| 2014-07-08 08:30 | 16.8 | 22.2 | 20.6
| 2014-07-08 09:00 | 16.5 | 22.2 | 20.6
| 2014-07-08 09:30 | 16.4 | 22.2 | 20.6
| 2014-07-08 10:00 | 16.6 | 21.7 | 20.6
| 2014-07-08 10:30 | 16.5 | 21.7 | 20.6
| 2014-07-08 11:00 | 16.9 | 21.7 | 20.6
| 2014-07-08 11:30 | 16.8 | 21.7 | 20.6
| 2014-07-08 12:00 | 16.9 | 21.7 | 20.6
| 2014-07-08 12:30 | 17.2 | 21.7 | 20.6
| 2014-07-08 13:00 | 17 | 21.7 | 20.6
| 2014-07-08 13:30 | 16.8 | 21.7 | 20.6
| 2014-07-08 14:00 | 16.6 | 21.7 | 20.6
| 2014-07-08 14:30 | 16.2 | 21.7 | 20.6
| 2014-07-08 15:00 | 16.1 | 21.7 | 20.6
| 2014-07-08 15:30 | 16.2 | 21.7 | 20.6
| 2014-07-08 16:00 | 16.6 | 21.7 | 20.6
| 2014-07-08 16:30 | 16.9 | 21.7 | 20.6
| 2014-07-08 17:00 | 16.8 | 21.7 | 20.6
| 2014-07-08 17:30 | 16.6 | 21.7 | 20.6
| 2014-07-08 18:00 | 16.3 | 21.7 | 20.6
| 2014-07-08 18:30 | 16 | 21.7 | 20.6
| 2014-07-08 19:00 | 15.5 | 21.7 | 20.6
| 2014-07-08 19:30 | 15.2 | 21.7 | 20.6
| 2014-07-08 20:00 | 14.9 | 21.1 | 20.6
| 2014-07-08 20:30 | 14.7 | 21.1 | 20.6
| 2014-07-08 21:00 | 14.6 | 21.1 | 20.6
| 2014-07-08 21:30 | 14.3 | 21.1 | 20.6
| 2014-07-08 22:00 | 14.2 | 21.1 | 20.6
| 2014-07-08 22:30 | 14.1 | 21.1 | 20.6
| 2014-07-08 23:00 | 13.8 | 21.1 | 20.6
| 2014-07-08 23:30 | 13.6 | 20.6 | 20.6
| 2014-07-09 | 13.4 | 20.6 | 20.6
| 2014-07-09 00:30 | 13.3 | 20.6 | 20.6
| 2014-07-09 01:00 | 13.1 | 20.6 | 20.6
| 2014-07-09 01:30 | 12.9 | 20.6 | 20.6
| 2014-07-09 02:00 | 12.8 | 20 | 20.6
| 2014-07-09 02:30 | 12.7 | 20 | 20.6
| 2014-07-09 03:00 | 12.7 | 20 | 20.6
| 2014-07-09 03:30 | 12.6 | 20 | 20.6
| 2014-07-09 04:00 | 12.3 | 20 | 20.6
| 2014-07-09 04:30 | 12.1 | 19.4 | 20.6
| 2014-07-09 05:00 | 11.8 | 19.4 | 20.6
| 2014-07-09 05:30 | 11.7 | 19.4 | 20.6
| 2014-07-09 06:00 | 11.6 | 19.4 | 20.6
| 2014-07-09 06:30 | 11.5 | 19.4 | 20.6
| 2014-07-09 07:00 | 11.5 | 19.4 | 20.6
| 2014-07-09 07:30 | 11.6 | 18.9 | 20.6
| 2014-07-09 08:00 | 11.7 | 18.9 | 20.6
| 2014-07-09 08:30 | 11.9 | 18.9 | 20.6
| 2014-07-09 09:00 | 12.1 | 18.9 | 20.6
| 2014-07-09 09:30 | 12.1 | 18.9 | 20.6
| 2014-07-09 10:00 | 12.2 | 18.3 | 20.6
| 2014-07-09 10:30 | 12.2 | 18.3 | 20.6
| 2014-07-09 11:00 | 12.4 | 18.3 | 20.6
| 2014-07-09 11:30 | 12.5 | 18.3 | 20.6
| 2014-07-09 12:00 | 12.6 | 18.3 | 20.6
| 2014-07-09 12:30 | 12.7 | 18.3 | 20.6
| 2014-07-09 13:00 | 13.1 | 18.3 | 20.6
| 2014-07-09 13:30 | 13.3 | 18.3 | 20.6
| 2014-07-09 14:00 | 13.4 | 18.3 | 20.6
| 2014-07-09 14:30 | 13.6 | 18.3 | 20.6
| 2014-07-09 15:00 | 13.7 | 18.3 | 20.6
| 2014-07-09 15:30 | 13.7 | 18.3 | 20.6
| 2014-07-09 16:00 | 13.7 | 18.3 | 20.6
| 2014-07-09 16:30 | 13.6 | 18.3 | 20.6
| 2014-07-09 17:00 | 13.7 | 18.3 | 20.6
| 2014-07-09 17:30 | 13.8 | 18.3 | 20.6
| 2014-07-09 18:00 | 13.9 | 18.3 | 20.6
| 2014-07-09 18:30 | 13.7 | 18.3 | 20.6
| 2014-07-09 19:00 | 13.6 | 18.3 | 20.6
| 2014-07-09 19:30 | 13.3 | 18.3 | 20.6
| 2014-07-09 20:00 | 13.2 | 18.3 | 20.6
| 2014-07-09 20:30 | 13.2 | 17.8 | 20.6
| 2014-07-09 21:00 | 13 | 17.8 | 20.6
| 2014-07-09 21:30 | 12.9 | 17.8 | 20.6
| 2014-07-09 22:00 | 12.9 | 17.8 | 20.6
| 2014-07-09 22:30 | 12.9 | 17.8 | 20.6
| 2014-07-09 23:00 | 12.8 | 17.8 | 20.6
| 2014-07-09 23:30 | 12.7 | 17.8 | 20.6
| 2014-07-10 | 12.6 | 17.8 | 20
| 2014-07-10 00:30 | 12.4 | 17.8 | 20
| 2014-07-10 01:00 | 12.3 | 17.8 | 20
| 2014-07-10 01:30 | 12.3 | 17.8 | 20
| 2014-07-10 02:00 | 12.3 | 17.8 | 20
| 2014-07-10 02:30 | 12.3 | 17.8 | 20
| 2014-07-10 03:00 | 12.3 | 17.8 | 20
| 2014-07-10 03:30 | 12.3 | 17.8 | 20
| 2014-07-10 04:00 | 12.3 | 17.2 | 20
| 2014-07-10 04:30 | 12.3 | 17.2 | 20
| 2014-07-10 05:00 | 12.3 | 17.2 | 20
| 2014-07-10 05:30 | 12.4 | 17.2 | 20
| 2014-07-10 06:00 | 12.4 | 17.2 | 20
| 2014-07-10 06:30 | 12.6 | 17.2 | 20
| 2014-07-10 07:00 | 12.7 | 17.2 | 20
| 2014-07-10 07:30 | 12.8 | 17.2 | 20
| 2014-07-10 08:00 | 13 | 17.2 | 20
| 2014-07-10 08:30 | 13.3 | 17.2 | 20
| 2014-07-10 09:00 | 13.6 | 17.2 | 20
| 2014-07-10 09:30 | 13.8 | 17.2 | 20
| 2014-07-10 10:00 | 14.3 | 17.2 | 20
| 2014-07-10 10:30 | 14.9 | 17.2 | 20
| 2014-07-10 11:00 | 14.9 | 17.2 | 20
| 2014-07-10 11:30 | 15.4 | 17.2 | 20
| 2014-07-10 12:00 | 15.7 | 17.2 | 20
| 2014-07-10 12:30 | 16.7 | 17.2 | 20
| 2014-07-10 13:00 | 16.8 | 17.8 | 20
| 2014-07-10 13:30 | 17 | 17.8 | 20
| 2014-07-10 14:00 | 17.1 | 17.8 | 20
| 2014-07-10 14:30 | 17.6 | 17.8 | 20
| 2014-07-10 15:00 | 18.3 | 18.3 | 20
| 2014-07-10 15:30 | 18.9 | 18.3 | 20
| 2014-07-10 16:00 | 20.4 | 18.3 | 20
| 2014-07-10 16:30 | 20 | 18.3 | 20
| 2014-07-10 17:00 | 21.1 | 18.3 | 20
| 2014-07-10 17:30 | 21.7 | 18.9 | 20
| 2014-07-10 18:00 | 21.9 | 18.9 | 20
| 2014-07-10 18:30 | 22 | 19.4 | 20
| 2014-07-10 19:00 | 21.7 | 19.4 | 20
| 2014-07-10 19:30 | 21.7 | 19.4 | 20
| 2014-07-10 20:00 | 20.4 | 19.4 | 20
| 2014-07-10 20:30 | 19.4 | 20 | 19.4
| 2014-07-10 21:00 | 18 | 20 | 19.4
| 2014-07-10 21:30 | 17.1 | 20 | 19.4
| 2014-07-10 22:00 | 16.4 | 20 | 19.4
| 2014-07-10 22:30 | 16.2 | 20 | 19.4
| 2014-07-10 23:00 | 16.2 | 20 | 19.4
| 2014-07-10 23:30 | 16.3 | 20 | 19.4
| 2014-07-11 | 15.9 | 19.4 | 19.4
| 2014-07-11 00:30 | 15.6 | 19.4 | 19.4
| 2014-07-11 01:00 | 15.4 | 19.4 | 19.4
| 2014-07-11 01:30 | 15.1 | 19.4 | 19.4
| 2014-07-11 02:00 | 14.9 | 19.4 | 19.4
| 2014-07-11 02:30 | 14.6 | 19.4 | 19.4
| 2014-07-11 03:00 | 14.2 | 19.4 | 19.4
| 2014-07-11 03:30 | 13.9 | 18.9 | 19.4
| 2014-07-11 04:00 | 13.6 | 18.9 | 19.4
| 2014-07-11 04:30 | 13.4 | 18.9 | 19.4
| 2014-07-11 05:00 | 13.3 | 18.9 | 19.4
| 2014-07-11 05:30 | 12.7 | 18.9 | 19.4
| 2014-07-11 06:00 | 12.7 | 18.9 | 19.4
| 2014-07-11 06:30 | 13 | 18.3 | 19.4
| 2014-07-11 07:00 | 13.9 | 18.3 | 19.4
| 2014-07-11 07:30 | 14.5 | 18.3 | 19.4
| 2014-07-11 08:00 | 15.4 | 18.3 | 19.4
| 2014-07-11 08:30 | 16.1 | 18.3 | 19.4
| 2014-07-11 09:00 | 16.7 | 18.3 | 19.4
| 2014-07-11 09:30 | 17.1 | 18.3 | 19.4
| 2014-07-11 10:00 | 17.8 | 18.3 | 19.4
| 2014-07-11 10:30 | 18.7 | 18.3 | 19.4
| 2014-07-11 11:00 | 19.4 | 18.3 | 19.4
| 2014-07-11 11:30 | 20.7 | 18.3 | 19.4
| 2014-07-11 12:00 | 21.4 | 18.3 | 19.4
| 2014-07-11 12:30 | 22.3 | 18.9 | 19.4
| 2014-07-11 13:00 | 22.8 | 18.9 | 19.4
| 2014-07-11 13:30 | 24 | 19.4 | 19.4
| 2014-07-11 14:00 | 24.7 | 19.4 | 19.4
| 2014-07-11 14:30 | 25.8 | 20 | 19.4
| 2014-07-11 15:00 | 24.9 | 20 | 19.4
| 2014-07-11 15:30 | 26 | 20.6 | 19.4
| 2014-07-11 16:00 | 25.2 | 20.6 | 19.4
| 2014-07-11 16:30 | 21.4 | 21.1 | 19.4
| 2014-07-11 17:00 | 17.4 | 21.1 | 19.4
| 2014-07-11 17:30 | 17.6 | 21.7 | 19.4
| 2014-07-11 18:00 | 17.9 | 21.7 | 19.4
| 2014-07-11 18:30 | 18.2 | 21.7 | 19.4
| 2014-07-11 19:00 | 18.1 | 21.7 | 19.4
| 2014-07-11 19:30 | 18.6 | 21.7 | 19.4
| 2014-07-11 20:00 | 19.3 | 21.7 | 19.4
| 2014-07-11 20:30 | 19.2 | 21.7 | 19.4
| 2014-07-11 21:00 | 18.5 | 21.1 | 19.4
| 2014-07-11 21:30 | 18.2 | 21.1 | 19.4
| 2014-07-11 22:00 | 17.9 | 21.1 | 19.4
| 2014-07-11 22:30 | 17.7 | 21.1 | 19.4
| 2014-07-11 23:00 | 17.1 | 21.1 | 19.4
| 2014-07-11 23:30 | 16.7 | 21.1 | 19.4
| 2014-07-12 | 16.7 | 21.1 | 19.4
| 2014-07-12 00:30 | 16.7 | 21.1 | 19.4
| 2014-07-12 01:00 | 16.5 | 20.6 | 19.4
| 2014-07-12 01:30 | 16.6 | 20.6 | 19.4
| 2014-07-12 02:00 | 16.9 | 20.6 | 19.4
| 2014-07-12 02:30 | 16.4 | 20.6 | 19.4
| 2014-07-12 03:00 | 16.3 | 20.6 | 19.4
| 2014-07-12 03:30 | 16.3 | 20 | 19.4
| 2014-07-12 04:00 | 16.1 | 20 | 19.4
| 2014-07-12 04:30 | 15.9 | 20 | 19.4
| 2014-07-12 05:00 | 15.7 | 20 | 19.4
| 2014-07-12 05:30 | 15.4 | 20 | 19.4
| 2014-07-12 06:00 | 15.3 | 20 | 19.4
| 2014-07-12 06:30 | 15.5 | 20 | 19.4
| 2014-07-12 07:00 | 16.3 | 19.4 | 19.4
| 2014-07-12 07:30 | 16.8 | 19.4 | 19.4
| 2014-07-12 08:00 | 17.2 | 19.4 | 19.4
| 2014-07-12 08:30 | 17.7 | 19.4 | 19.4
| 2014-07-12 09:00 | 18.8 | 19.4 | 19.4
| 2014-07-12 09:30 | 19.4 | 19.4 | 19.4
| 2014-07-12 10:00 | 20.4 | 19.4 | 19.4
| 2014-07-12 10:30 | 21 | 19.4 | 19.4
| 2014-07-12 11:00 | 22.1 | 19.4 | 19.4
| 2014-07-12 11:30 | 22.4 | 19.4 | 19.4
| 2014-07-12 12:00 | 22.6 | 20 | 19.4
| 2014-07-12 12:30 | 23.4 | 20 | 19.4
| 2014-07-12 13:00 | 23.9 | 20 | 19.4
| 2014-07-12 13:30 | 24.4 | 20.6 | 19.4
| 2014-07-12 14:00 | 23.9 | 20.6 | 19.4
| 2014-07-12 14:30 | 25.3 | 21.1 | 19.4
| 2014-07-12 15:00 | 25.7 | 21.1 | 19.4
| 2014-07-12 15:30 | 25.3 | 21.1 | 19.4
| 2014-07-12 16:00 | 25.6 | 21.7 | 19.4
| 2014-07-12 16:30 | 24.9 | 21.7 | 19.4
| 2014-07-12 17:00 | 25.9 | 22.2 | 19.4
| 2014-07-12 17:30 | 25.7 | 22.2 | 19.4
| 2014-07-12 18:00 | 25.4 | 22.2 | 19.4
| 2014-07-12 18:30 | 24.1 | 22.8 | 19.4
| 2014-07-12 19:00 | 22.9 | 22.8 | 19.4
| 2014-07-12 19:30 | 22.6 | 22.8 | 19.4
| 2014-07-12 20:00 | 21.7 | 22.8 | 19.4
| 2014-07-12 20:30 | 21.2 | 22.8 | 19.4
| 2014-07-12 21:00 | 20.6 | 22.8 | 19.4
| 2014-07-12 21:30 | 19.3 | 22.8 | 19.4
| 2014-07-12 22:00 | 19.8 | 22.8 | 19.4
| 2014-07-12 22:30 | 19.4 | 22.8 | 19.4
| 2014-07-12 23:00 | 18.5 | 22.8 | 19.4
| 2014-07-12 23:30 | 17.3 | 22.2 | 19.4
| 2014-07-13 | 17.8 | 22.2 | 19.4
| 2014-07-13 00:30 | 17.3 | 22.2 | 19.4
| 2014-07-13 01:00 | 16.4 | 22.2 | 19.4
| 2014-07-13 01:30 | 15.8 | 21.7 | 19.4
| 2014-07-13 02:00 | 15.4 | 21.7 | 19.4
| 2014-07-13 02:30 | 15.2 | 21.7 | 19.4
| 2014-07-13 03:00 | 15.7 | 21.7 | 19.4
| 2014-07-13 03:30 | 16.2 | 21.1 | 19.4
| 2014-07-13 04:00 | 16.4 | 21.1 | 19.4
| 2014-07-13 04:30 | 16.4 | 21.1 | 19.4
| 2014-07-13 05:00 | 16.4 | 21.1 | 19.4
| 2014-07-13 05:30 | 16.4 | 21.1 | 19.4
| 2014-07-13 06:00 | 16.4 | 21.1 | 19.4
| 2014-07-13 06:30 | 16.6 | 20.6 | 19.4
| 2014-07-13 07:00 | 16.3 | 20.6 | 19.4
| 2014-07-13 07:30 | 15.9 | 20.6 | 19.4
| 2014-07-13 08:00 | 16 | 20.6 | 19.4
| 2014-07-13 08:30 | 16.1 | 20.6 | 19.4
| 2014-07-13 09:00 | 16.2 | 20.6 | 19.4
| 2014-07-13 09:30 | 16.3 | 20.6 | 19.4
| 2014-07-13 10:00 | 16.3 | 20.6 | 19.4
| 2014-07-13 10:30 | 17.4 | 20 | 19.4
| 2014-07-13 11:00 | 17.7 | 20 | 19.4
| 2014-07-13 11:30 | 18.2 | 20 | 19.4
| 2014-07-13 12:00 | 18.7 | 20 | 19.4
| 2014-07-13 12:30 | 18.9 | 20 | 19.4
| 2014-07-13 13:00 | 19.9 | 20.6 | 19.4
| 2014-07-13 13:30 | 21.2 | 20.6 | 19.4
| 2014-07-13 14:00 | 20.4 | 20.6 | 19.4
| 2014-07-13 14:30 | 20.8 | 20.6 | 19.4
| 2014-07-13 15:00 | 21.7 | 20.6 | 19.4
| 2014-07-13 15:30 | 22.5 | 20.6 | 19.4
| 2014-07-13 16:00 | 22.2 | 20.6 | 19.4
| 2014-07-13 16:30 | 22.8 | 21.1 | 19.4
| 2014-07-13 17:00 | 20.9 | 21.1 | 19.4
| 2014-07-13 17:30 | 21.8 | 21.1 | 19.4
| 2014-07-13 18:00 | 21.6 | 21.1 | 19.4
| 2014-07-13 18:30 | 21.3 | 21.1 | 19.4
| 2014-07-13 19:00 | 21 | 21.1 | 19.4
| 2014-07-13 19:30 | 20.7 | 21.7 | 19.4
| 2014-07-13 20:00 | 20.1 | 21.7 | 19.4
| 2014-07-13 20:30 | 19.7 | 21.7 | 19.4
| 2014-07-13 21:00 | 19.1 | 21.7 | 19.4
| 2014-07-13 21:30 | 18.2 | 21.1 | 19.4
| 2014-07-13 22:00 | 17.8 | 21.1 | 19.4
| 2014-07-13 22:30 | 17.3 | 21.1 | 19.4
| 2014-07-13 23:00 | 17.3 | 21.1 | 19.4
| 2014-07-13 23:30 | 17.7 | 21.1 | 19.4
| 2014-07-14 | 17.8 | 21.1 | 19.4
| 2014-07-14 00:30 | 17.8 | 21.1 | 19.4
| 2014-07-14 01:00 | 17.7 | 21.1 | 19.4
| 2014-07-14 01:30 | 17.6 | 20.6 | 19.4
| 2014-07-14 02:00 | 17.2 | 20.6 | 19.4
| 2014-07-14 02:30 | 17.1 | 20.6 | 19.4
| 2014-07-14 03:00 | 16.9 | 20.6 | 19.4
| 2014-07-14 03:30 | 17.2 | 20.6 | 19.4
| 2014-07-14 04:00 | 17.3 | 20.6 | 19.4
| 2014-07-14 04:30 | 17.2 | 20.6 | 19.4
| 2014-07-14 05:00 | 17.2 | 20 | 19.4
| 2014-07-14 05:30 | 17.2 | 20 | 19.4
| 2014-07-14 06:00 | 17.2 | 20 | 19.4
| 2014-07-14 06:30 | 17.3 | 20 | 19.4
| 2014-07-14 07:00 | 17.6 | 20 | 19.4
| 2014-07-14 07:30 | 17.5 | 20 | 19.4
| 2014-07-14 08:00 | 18.1 | 20 | 19.4
| 2014-07-14 08:30 | 18.6 | 20 | 19.4
| 2014-07-14 09:00 | 19.5 | 20 | 19.4
| 2014-07-14 09:30 | 19.4 | 20 | 19.4
| 2014-07-14 10:00 | 20.6 | 20 | 19.4
| 2014-07-14 10:30 | 20.8 | 20 | 19.4
| 2014-07-14 11:00 | 21.9 | 20 | 19.4
| 2014-07-14 11:30 | 21.3 | 20 | 19.4
| 2014-07-14 12:00 | 21.3 | 20 | 19.4
| 2014-07-14 12:30 | 24.1 | 20 | 19.4
| 2014-07-14 13:00 | 23.9 | 20.6 | 19.4
| 2014-07-14 13:30 | 25.3 | 20.6 | 19.4
| 2014-07-14 14:00 | 25.6 | 20.6 | 19.4
| 2014-07-14 14:30 | 26.4 | 21.1 | 19.4
| 2014-07-14 15:00 | 26 | 21.1 | 19.4
| 2014-07-14 15:30 | 26.7 | 21.7 | 19.4
| 2014-07-14 16:00 | 27.2 | 21.7 | 19.4
| 2014-07-14 16:30 | 27.1 | 22.2 | 19.4
| 2014-07-14 17:00 | 27.2 | 22.2 | 19.4
| 2014-07-14 17:30 | 27.2 | 22.8 | 19.4
| 2014-07-14 18:00 | 25.7 | 22.8 | 19.4
| 2014-07-14 18:30 | 24.9 | 23.3 | 19.4
| 2014-07-14 19:00 | 24.2 | 23.3 | 19.4
| 2014-07-14 19:30 | 23.3 | 23.3 | 19.4
| 2014-07-14 20:00 | 23.8 | 23.3 | 19.4
| 2014-07-14 20:30 | 23.3 | 23.3 | 19.4
| 2014-07-14 21:00 | 21.9 | 23.3 | 19.4
| 2014-07-14 21:30 | 20.6 | 23.3 | 19.4
| 2014-07-14 22:00 | 19.7 | 23.3 | 19.4
| 2014-07-14 22:30 | 19.3 | 23.3 | 19.4
| 2014-07-14 23:00 | 19.7 | 23.3 | 19.4
| 2014-07-14 23:30 | 19.1 | 23.3 | 19.4
| 2014-07-15 | 18.7 | 22.8 | 19.4
| 2014-07-15 00:30 | 19.3 | 22.8 | 19.4
| 2014-07-15 01:00 | 19.6 | 22.8 | 19.4
| 2014-07-15 01:30 | 19.7 | 22.8 | 19.4
| 2014-07-15 02:00 | 19.2 | 22.2 | 19.4
| 2014-07-15 02:30 | 17.7 | 22.2 | 19.4
| 2014-07-15 03:00 | 16.9 | 22.2 | 19.4
| 2014-07-15 03:30 | 16.4 | 22.2 | 19.4
| 2014-07-15 04:00 | 15.8 | 22.2 | 19.4
| 2014-07-15 04:30 | 15.6 | 21.7 | 19.4
| 2014-07-15 05:00 | 15.1 | 21.7 | 19.4
| 2014-07-15 05:30 | 14.6 | 21.7 | 19.4
| 2014-07-15 06:00 | 14.6 | 21.7 | 19.4
| 2014-07-15 06:30 | 14.8 | 21.1 | 19.4
| 2014-07-15 07:00 | 15.3 | 21.1 | 19.4
| 2014-07-15 07:30 | 16.5 | 21.1 | 19.4
| 2014-07-15 08:00 | 17.8 | 21.1 | 19.4
| 2014-07-15 08:30 | 18.6 | 21.1 | 19.4
| 2014-07-15 09:00 | 19.3 | 20.6 | 19.4
| 2014-07-15 09:30 | 20.3 | 20.6 | 19.4
| 2014-07-15 10:00 | 21.6 | 20.6 | 19.4
| 2014-07-15 10:30 | 22.3 | 20.6 | 19.4
| 2014-07-15 11:00 | 22.9 | 20.6 | 19.4
| 2014-07-15 11:30 | 24.1 | 20.6 | 19.4
| 2014-07-15 12:00 | 24.8 | 21.1 | 19.4
| 2014-07-15 12:30 | 25.3 | 21.1 | 19.4
| 2014-07-15 13:00 | 25.8 | 21.1 | 19.4
| 2014-07-15 13:30 | 26.2 | 21.7 | 19.4
| 2014-07-15 14:00 | 25.8 | 22.2 | 19.4
| 2014-07-15 14:30 | 25.9 | 22.2 | 19.4
| 2014-07-15 15:00 | 25.9 | 22.8 | 19.4
| 2014-07-15 15:30 | 27.3 | 23.3 | 19.4
| 2014-07-15 16:00 | 27.9 | 23.3 | 19.4
| 2014-07-15 16:30 | 26.3 | 23.9 | 19.4
| 2014-07-15 17:00 | 26.9 | 23.9 | 19.4
| 2014-07-15 17:30 | 27.6 | 24.4 | 19.4
| 2014-07-15 18:00 | 27.4 | 24.4 | 19.4
| 2014-07-15 18:30 | 26.1 | 24.4 | 19.4
| 2014-07-15 19:00 | 25.8 | 25 | 19.4
| 2014-07-15 19:30 | 25 | 25 | 19.4
| 2014-07-15 20:00 | 26.4 | 25 | 19.4
| 2014-07-15 20:30 | 26 | 25 | 19.4
| 2014-07-15 21:00 | 24.9 | 25 | 19.4
| 2014-07-15 21:30 | 23.4 | 25 | 19.4
| 2014-07-15 22:00 | 22.1 | 25 | 19.4
| 2014-07-15 22:30 | 21.1 | 25 | 19.4
| 2014-07-15 23:00 | 20.1 | 24.4 | 19.4
| 2014-07-15 23:30 | 19.5 | 24.4 | 19.4
| 2014-07-16 | 18.7 | 24.4 | 19.4
| 2014-07-16 00:30 | 18 | 24.4 | 19.4
| 2014-07-16 01:00 | 17.3 | 23.9 | 19.4
| 2014-07-16 01:30 | 16.7 | 23.9 | 19.4
| 2014-07-16 02:00 | 16.3 | 23.9 | 19.4
| 2014-07-16 02:30 | 16.3 | 23.9 | 19.4
| 2014-07-16 03:00 | 16.4 | 23.3 | 19.4
| 2014-07-16 03:30 | 16.3 | 23.3 | 19.4
| 2014-07-16 04:00 | 16.3 | 23.3 | 19.4
| 2014-07-16 04:30 | 16.7 | 23.3 | 19.4
| 2014-07-16 05:00 | 17.2 | 22.8 | 19.4
| 2014-07-16 05:30 | 17.4 | 22.8 | 19.4
| 2014-07-16 06:00 | 17.4 | 22.8 | 19.4
| 2014-07-16 06:30 | 17.7 | 22.8 | 19.4
| 2014-07-16 07:00 | 18.2 | 22.2 | 19.4
| 2014-07-16 07:30 | 18.8 | 22.2 | 19.4
| 2014-07-16 08:00 | 19.5 | 22.2 | 19.4
| 2014-07-16 08:30 | 19.7 | 22.2 | 19.4
| 2014-07-16 09:00 | 19.8 | 22.2 | 19.4
| 2014-07-16 09:30 | 20 | 22.2 | 19.4
| 2014-07-16 10:00 | 20.2 | 22.2 | 19.4
| 2014-07-16 10:30 | 20.9 | 22.2 | 19.4
| 2014-07-16 11:00 | 21.7 | 22.2 | 19.4
| 2014-07-16 11:30 | 22.7 | 22.2 | 19.4
| 2014-07-16 12:00 | 24 | 22.2 | 19.4
| 2014-07-16 12:30 | 24.2 | 22.2 | 19.4
| 2014-07-16 13:00 | 25.3 | 22.2 | 19.4
| 2014-07-16 13:30 | 25.9 | 22.2 | 19.4
| 2014-07-16 14:00 | 26.8 | 22.8 | 20
| 2014-07-16 14:30 | 27.5 | 23.3 | 20
| 2014-07-16 15:00 | 28 | 23.3 | 20
| 2014-07-16 15:30 | 28.6 | 23.9 | 20
| 2014-07-16 16:00 | 28.3 | 23.9 | 20
| 2014-07-16 16:30 | 29.1 | 24.4 | 20
| 2014-07-16 17:00 | 28.8 | 24.4 | 20
| 2014-07-16 17:30 | 29.3 | 25 | 20
| 2014-07-16 18:00 | 28.9 | 25.6 | 20
| 2014-07-16 18:30 | 28.9 | 25.6 | 20
| 2014-07-16 19:00 | 28.5 | 26.1 | 20
| 2014-07-16 19:30 | 28.4 | 26.1 | 20
| 2014-07-16 20:00 | 28.4 | 26.1 | 20
| 2014-07-16 20:30 | 26.9 | 26.1 | 20
| 2014-07-16 21:00 | 25.3 | 26.7 | 20
| 2014-07-16 21:30 | 23 | 26.7 | 20
| 2014-07-16 22:00 | 21.6 | 26.1 | 20
| 2014-07-16 22:30 | 20.3 | 26.1 | 20
| 2014-07-16 23:00 | 19.6 | 26.1 | 20
| 2014-07-16 23:30 | 18.8 | 26.1 | 20
| 2014-07-17 | 18.2 | 26.1 | 20
| 2014-07-17 00:30 | 17.6 | 25.6 | 20
| 2014-07-17 01:00 | 17 | 25.6 | 20
| 2014-07-17 01:30 | 16.7 | 25.6 | 20
| 2014-07-17 02:00 | 16.4 | 25 | 20
| 2014-07-17 02:30 | 16.1 | 25 | 20
| 2014-07-17 03:00 | 15.7 | 25 | 20
| 2014-07-17 03:30 | 15.3 | 24.4 | 20
| 2014-07-17 04:00 | 15.1 | 24.4 | 20
| 2014-07-17 04:30 | 14.8 | 24.4 | 20
| 2014-07-17 05:00 | 14.5 | 24.4 | 20
| 2014-07-17 05:30 | 14.2 | 23.9 | 20
| 2014-07-17 06:00 | 14.1 | 23.9 | 20
| 2014-07-17 06:30 | 14.2 | 23.9 | 20
| 2014-07-17 07:00 | 14.8 | 23.3 | 20
| 2014-07-17 07:30 | 15.6 | 23.3 | 20
| 2014-07-17 08:00 | 17.2 | 23.3 | 20
| 2014-07-17 08:30 | 19.1 | 23.3 | 20
| 2014-07-17 09:00 | 21.1 | 22.8 | 20
| 2014-07-17 09:30 | 22.9 | 22.8 | 20
| 2014-07-17 10:00 | 24.1 | 22.8 | 20
| 2014-07-17 10:30 | 25.1 | 22.8 | 20
| 2014-07-17 11:00 | 26.3 | 22.8 | 20
| 2014-07-17 11:30 | 27.3 | 22.8 | 20
| 2014-07-17 12:00 | 28.1 | 22.8 | 20
| 2014-07-17 12:30 | 28.5 | 23.3 | 20
| 2014-07-17 13:00 | 29.2 | 23.3 | 20
| 2014-07-17 13:30 | 29.7 | 23.9 | 20
| 2014-07-17 14:00 | 29.3 | 23.9 | 20
| 2014-07-17 14:30 | 29.2 | 24.4 | 20
| 2014-07-17 15:00 | 29.8 | 24.4 | 20
| 2014-07-17 15:30 | 30.7 | 25 | 20
| 2014-07-17 16:00 | 30.7 | 25.6 | 20
| 2014-07-17 16:30 | 30.7 | 25.6 | 20
| 2014-07-17 17:00 | 30.8 | 26.1 | 20
| 2014-07-17 17:30 | 30.6 | 26.7 | 20
| 2014-07-17 18:00 | 31.6 | 26.7 | 20
| 2014-07-17 18:30 | 31.6 | 27.2 | 20
| 2014-07-17 19:00 | 30.9 | 27.2 | 20
| 2014-07-17 19:30 | 30.9 | 27.2 | 20
| 2014-07-17 20:00 | 30.5 | 27.2 | 20
| 2014-07-17 20:30 | 29.5 | 27.2 | 20
| 2014-07-17 21:00 | 27.8 | 27.2 | 20
| 2014-07-17 21:30 | 25.2 | 27.2 | 20
| 2014-07-17 22:00 | 23.6 | 27.2 | 20
| 2014-07-17 22:30 | 22.6 | 27.2 | 20
| 2014-07-17 23:00 | 21.7 | 27.2 | 20
| 2014-07-17 23:30 | 21 | 27.2 | 20
| 2014-07-18 | 20.6 | 27.2 | 20
| 2014-07-18 00:30 | 20.3 | 26.7 | 20
| 2014-07-18 01:00 | 20.1 | 26.7 | 20
| 2014-07-18 01:30 | 19.3 | 26.7 | 20
| 2014-07-18 02:00 | 18.6 | 26.7 | 20
| 2014-07-18 02:30 | 17.9 | 26.1 | 20
| 2014-07-18 03:00 | 17.3 | 26.1 | 20.6
| 2014-07-18 03:30 | 16.8 | 25.6 | 20.6
| 2014-07-18 04:00 | 16.3 | 25.6 | 20.6
| 2014-07-18 04:30 | 16.2 | 25.6 | 20.6
| 2014-07-18 05:00 | 16 | 25.6 | 20.6
| 2014-07-18 05:30 | 15.8 | 25 | 20.6
| 2014-07-18 06:00 | 15.4 | 25 | 20.6
| 2014-07-18 06:30 | 15.7 | 25 | 20.6
| 2014-07-18 07:00 | 17 | 24.4 | 20.6
| 2014-07-18 07:30 | 18.4 | 24.4 | 20.6
| 2014-07-18 08:00 | 20.1 | 24.4 | 20.6
| 2014-07-18 08:30 | 21.8 | 24.4 | 20.6
| 2014-07-18 09:00 | 23.8 | 23.9 | 20.6
| 2014-07-18 09:30 | 25.6 | 23.9 | 20.6
| 2014-07-18 10:00 | 26.7 | 23.9 | 20.6
| 2014-07-18 10:30 | 29.1 | 23.9 | 20.6
| 2014-07-18 11:00 | 29.8 | 23.9 | 20.6
| 2014-07-18 11:30 | 30.8 | 23.9 | 20.6
| 2014-07-18 12:00 | 31.7 | 23.9 | 20.6
| 2014-07-18 12:30 | 32.1 | 24.4 | 20.6
| 2014-07-18 13:00 | 32.5 | 24.4 | 20.6
| 2014-07-18 13:30 | 33.9 | 24.4 | 20.6
| 2014-07-18 14:00 | 34.2 | 25 | 20.6
| 2014-07-18 14:30 | 33.6 | 25.6 | 20.6
| 2014-07-18 15:00 | 34.4 | 25.6 | 20.6
| 2014-07-18 15:30 | 34.6 | 26.1 | 20.6
| 2014-07-18 16:00 | 34.8 | 26.7 | 20.6
| 2014-07-18 16:30 | 34.3 | 27.2 | 20.6
| 2014-07-18 17:00 | 34.6 | 27.2 | 20.6
| 2014-07-18 17:30 | 34.3 | 27.8 | 20.6
| 2014-07-18 18:00 | 35.1 | 27.8 | 20.6
| 2014-07-18 18:30 | 34.8 | 28.3 | 20.6
| 2014-07-18 19:00 | 34.7 | 28.3 | 20.6
| 2014-07-18 19:30 | 34.1 | 28.3 | 20.6
| 2014-07-18 20:00 | 33.2 | 28.9 | 20.6
| 2014-07-18 20:30 | 31.4 | 28.9 | 20.6
| 2014-07-18 21:00 | 29 | 28.9 | 20.6
| 2014-07-18 21:30 | 26.7 | 28.9 | 20.6
| 2014-07-18 22:00 | 24.7 | 28.9 | 20.6
| 2014-07-18 22:30 | 23.5 | 28.3 | 20.6
| 2014-07-18 23:00 | 22.8 | 28.3 | 20.6
| 2014-07-18 23:30 | 22.6 | 28.3 | 20.6
| 2014-07-19 | 22.6 | 28.3 | 20.6
| 2014-07-19 00:30 | 21.4 | 28.3 | 20.6
| 2014-07-19 01:00 | 20.9 | 27.8 | 20.6
| 2014-07-19 01:30 | 20.1 | 27.8 | 20.6
| 2014-07-19 02:00 | 19.4 | 27.8 | 20.6
| 2014-07-19 02:30 | 19.3 | 27.2 | 20.6
| 2014-07-19 03:00 | 19.2 | 27.2 | 20.6
| 2014-07-19 03:30 | 18.4 | 27.2 | 20.6
| 2014-07-19 04:00 | 18.1 | 26.7 | 20.6
| 2014-07-19 04:30 | 17.6 | 26.7 | 20.6
| 2014-07-19 05:00 | 16.8 | 26.7 | 20.6
| 2014-07-19 05:30 | 16.4 | 26.1 | 20.6
| 2014-07-19 06:00 | 16.1 | 26.1 | 20.6
| 2014-07-19 06:30 | 16.2 | 26.1 | 21.1
| 2014-07-19 07:00 | 16.4 | 25.6 | 21.1
| 2014-07-19 07:30 | 16.8 | 25.6 | 21.1
| 2014-07-19 08:00 | 18.6 | 25.6 | 21.1
| 2014-07-19 08:30 | 21.8 | 25.6 | 21.1
| 2014-07-19 09:00 | 25.2 | 25 | 21.1
| 2014-07-19 09:30 | 27.4 | 25 | 21.1
| 2014-07-19 10:00 | 28.8 | 25 | 21.1
| 2014-07-19 10:30 | 30.2 | 25 | 21.1
| 2014-07-19 11:00 | 32 | 25 | 21.1
| 2014-07-19 11:30 | 32.9 | 25 | 21.1
| 2014-07-19 12:00 | 33.4 | 25 | 21.1
| 2014-07-19 12:30 | 33.9 | 25.6 | 21.1
| 2014-07-19 13:00 | 34.8 | 25.6 | 21.1
| 2014-07-19 13:30 | 34.6 | 25.6 | 21.1
| 2014-07-19 14:00 | 34.8 | 26.1 | 21.1
| 2014-07-19 14:30 | 35.4 | 26.7 | 21.1
| 2014-07-19 15:00 | 35.4 | 26.7 | 21.1
| 2014-07-19 15:30 | 36.2 | 27.2 | 21.1
| 2014-07-19 16:00 | 35.6 | 27.2 | 21.1
| 2014-07-19 16:30 | 35.1 | 27.8 | 21.1
| 2014-07-19 17:00 | 35.5 | 28.3 | 21.1
| 2014-07-19 17:30 | 34.7 | 28.3 | 21.1
| 2014-07-19 18:00 | 33.8 | 28.9 | 21.1
| 2014-07-19 18:30 | 34 | 28.9 | 21.1
| 2014-07-19 19:00 | 34.8 | 29.4 | 21.1
| 2014-07-19 19:30 | 33.9 | 29.4 | 21.1
| 2014-07-19 20:00 | 33 | 29.4 | 21.1
| 2014-07-19 20:30 | 30.7 | 29.4 | 21.1
| 2014-07-19 21:00 | 27.8 | 29.4 | 21.1
| 2014-07-19 21:30 | 26.1 | 29.4 | 21.1
| 2014-07-19 22:00 | 25.3 | 29.4 | 21.1
| 2014-07-19 22:30 | 25.1 | 29.4 | 21.1
| 2014-07-19 23:00 | 25.1 | 29.4 | 21.1
| 2014-07-19 23:30 | 24.8 | 28.9 | 21.1
| 2014-07-20 | 23.2 | 28.9 | 21.1
| 2014-07-20 00:30 | 22.3 | 28.9 | 21.1
| 2014-07-20 01:00 | 22.3 | 28.9 | 21.1
| 2014-07-20 01:30 | 22.2 | 28.3 | 21.1
| 2014-07-20 02:00 | 22 | 28.3 | 21.1
| 2014-07-20 02:30 | 21.5 | 28.3 | 21.1
| 2014-07-20 03:00 | 21.1 | 28.3 | 21.1
| 2014-07-20 03:30 | 20.5 | 27.8 | 21.1
| 2014-07-20 04:00 | 20.4 | 27.8 | 21.1
| 2014-07-20 04:30 | 20.3 | 27.8 | 21.1
| 2014-07-20 05:00 | 20.1 | 27.2 | 21.1
| 2014-07-20 05:30 | 19.8 | 27.2 | 21.1
| 2014-07-20 06:00 | 19.4 | 27.2 | 21.1
| 2014-07-20 06:30 | 19.3 | 27.2 | 21.1
| 2014-07-20 07:00 | 19.9 | 27.2 | 21.1
| 2014-07-20 07:30 | 21.2 | 26.7 | 21.1
| 2014-07-20 08:00 | 22.5 | 26.7 | 21.7
| 2014-07-20 08:30 | 23.1 | 26.7 | 21.7
| 2014-07-20 09:00 | 23.8 | 26.7 | 21.7
| 2014-07-20 09:30 | 24 | 26.7 | 21.7
| 2014-07-20 10:00 | 25.4 | 26.7 | 21.7
| 2014-07-20 10:30 | 25.2 | 26.1 | 21.7
| 2014-07-20 11:00 | 25.2 | 26.1 | 21.7
| 2014-07-20 11:30 | 27.1 | 26.1 | 21.7
| 2014-07-20 12:00 | 28.9 | 26.1 | 21.7
| 2014-07-20 12:30 | 28.8 | 26.1 | 21.7
| 2014-07-20 13:00 | 29.7 | 26.7 | 21.7
| 2014-07-20 13:30 | 30.4 | 26.7 | 21.7
| 2014-07-20 14:00 | 29.9 | 26.7 | 21.7
| 2014-07-20 14:30 | 28.5 | 26.7 | 21.7
| 2014-07-20 15:00 | 27.7 | 27.2 | 21.7
| 2014-07-20 15:30 | 27.7 | 27.2 | 21.7
| 2014-07-20 16:00 | 27.9 | 27.2 | 21.7
| 2014-07-20 16:30 | 26.3 | 27.2 | 21.7
| 2014-07-20 17:00 | 26 | 27.2 | 21.7
| 2014-07-20 17:30 | 26.2 | 27.8 | 21.7
| 2014-07-20 18:00 | 24.4 | 27.8 | 21.7
| 2014-07-20 18:30 | 23.1 | 27.8 | 21.7
| 2014-07-20 19:00 | 21.4 | 27.8 | 21.7
| 2014-07-20 19:30 | 20.8 | 27.8 | 21.7
| 2014-07-20 20:00 | 20.3 | 27.8 | 21.7
| 2014-07-20 20:30 | 20.1 | 27.8 | 21.7
| 2014-07-20 21:00 | 19.8 | 27.8 | 21.7
| 2014-07-20 21:30 | 19.9 | 27.2 | 21.7
| 2014-07-20 22:00 | 19.8 | 27.2 | 21.7
| 2014-07-20 22:30 | 19.6 | 27.2 | 21.7
| 2014-07-20 23:00 | 19.4 | 27.2 | 21.7
| 2014-07-20 23:30 | 19.5 | 27.2 | 21.7
| 2014-07-21 | 19.3 | 26.7 | 21.7
| 2014-07-21 00:30 | 19.1 | 26.7 | 21.7
| 2014-07-21 01:00 | 18.9 | 26.7 | 21.7
| 2014-07-21 01:30 | 18.8 | 26.7 | 21.7
| 2014-07-21 02:00 | 18.7 | 26.1 | 21.7
| 2014-07-21 02:30 | 18.5 | 26.1 | 21.7
| 2014-07-21 03:00 | 18.4 | 26.1 | 21.7
| 2014-07-21 03:30 | 18.3 | 26.1 | 21.7
| 2014-07-21 04:00 | 18.7 | 25.6 | 21.7
| 2014-07-21 04:30 | 18.7 | 25.6 | 21.7
| 2014-07-21 05:00 | 18.7 | 25.6 | 21.7
| 2014-07-21 05:30 | 18.4 | 25.6 | 21.7
| 2014-07-21 06:00 | 18.4 | 25.6 | 21.7
| 2014-07-21 06:30 | 18.2 | 25 | 21.7
| 2014-07-21 07:00 | 18.5 | 25 | 21.7
| 2014-07-21 07:30 | 18.4 | 25 | 21.7
| 2014-07-21 08:00 | 18.7 | 24.4 | 21.7
| 2014-07-21 08:30 | 19.1 | 24.4 | 21.7
| 2014-07-21 09:00 | 19.4 | 24.4 | 21.7
| 2014-07-21 09:30 | 19.8 | 24.4 | 21.7
| 2014-07-21 10:00 | 20.1 | 24.4 | 21.7
| 2014-07-21 10:30 | 20.4 | 24.4 | 21.7
| 2014-07-21 11:00 | 20.7 | 24.4 | 21.7
| 2014-07-21 11:30 | 21.1 | 24.4 | 21.7
| 2014-07-21 12:00 | 21.6 | 24.4 | 21.7
| 2014-07-21 12:30 | 22.2 | 24.4 | 21.7
| 2014-07-21 13:00 | 23.7 | 24.4 | 21.7
| 2014-07-21 13:30 | 23.2 | 24.4 | 21.7
| 2014-07-21 14:00 | 22.7 | 24.4 | 21.7
| 2014-07-21 14:30 | 22.8 | 25 | 22.2
| 2014-07-21 15:00 | 23.7 | 25 | 22.2
| 2014-07-21 15:30 | 23.4 | 25 | 22.2
| 2014-07-21 16:00 | 24.4 | 25 | 22.2
| 2014-07-21 16:30 | 25 | 25 | 22.2
| 2014-07-21 17:00 | 24.6 | 25.6 | 22.2
| 2014-07-21 17:30 | 24.3 | 25.6 | 22.2
| 2014-07-21 18:00 | 24.7 | 25.6 | 22.2
| 2014-07-21 18:30 | 24.2 | 25.6 | 22.2
| 2014-07-21 19:00 | 23.6 | 25.6 | 22.2
| 2014-07-21 19:30 | 23.2 | 25.6 | 22.2
| 2014-07-21 20:00 | 23.2 | 25.6 | 22.2
| 2014-07-21 20:30 | 22.9 | 25.6 | 22.2
| 2014-07-21 21:00 | 22.6 | 25.6 | 22.2
| 2014-07-21 21:30 | 22.2 | 25.6 | 22.2
| 2014-07-21 22:00 | 21.7 | 25.6 | 22.2
| 2014-07-21 22:30 | 21.3 | 25.6 | 22.2
| 2014-07-21 23:00 | 20.7 | 25.6 | 22.2
| 2014-07-21 23:30 | 19.9 | 25.6 | 22.2
| 2014-07-22 | 19.6 | 25.6 | 22.2
| 2014-07-22 00:30 | 19.3 | 25 | 22.2
| 2014-07-22 01:00 | 19.2 | 25 | 22.2
| 2014-07-22 01:30 | 19.2 | 25 | 22.2
| 2014-07-22 02:00 | 19.2 | 25 | 22.2
| 2014-07-22 02:30 | 19.3 | 24.4 | 22.2
| 2014-07-22 03:00 | 19.4 | 24.4 | 22.2
| 2014-07-22 03:30 | 19.3 | 24.4 | 22.2
| 2014-07-22 04:00 | 19.3 | 24.4 | 22.2
| 2014-07-22 04:30 | 19.4 | 24.4 | 22.2
| 2014-07-22 05:00 | 19.6 | 24.4 | 22.2
| 2014-07-22 05:30 | 19.7 | 23.9 | 22.2
| 2014-07-22 06:00 | 19.7 | 23.9 | 22.2
| 2014-07-22 06:30 | 19.6 | 23.9 | 22.2
| 2014-07-22 07:00 | 19.6 | 23.9 | 22.2
| 2014-07-22 07:30 | 19.8 | 23.9 | 22.2
| 2014-07-22 08:00 | 20.1 | 23.9 | 22.2
| 2014-07-22 08:30 | 20.1 | 23.9 | 22.2
| 2014-07-22 09:00 | 20.6 | 23.3 | 22.2
| 2014-07-22 09:30 | 20.8 | 23.3 | 22.2
| 2014-07-22 10:00 | 21.8 | 23.3 | 22.2
| 2014-07-22 10:30 | 22.6 | 23.3 | 22.2
| 2014-07-22 11:00 | 23.1 | 23.3 | 22.2
| 2014-07-22 11:30 | 24.4 | 23.3 | 22.2
| 2014-07-22 12:00 | 25.8 | 23.9 | 22.2
| 2014-07-22 12:30 | 25.9 | 23.9 | 22.2
| 2014-07-22 13:00 | 26.6 | 23.9 | 22.2
| 2014-07-22 13:30 | 26.7 | 23.9 | 22.2
| 2014-07-22 14:00 | 26.9 | 24.4 | 22.2
| 2014-07-22 14:30 | 26.9 | 24.4 | 22.2
| 2014-07-22 15:00 | 27.4 | 24.4 | 22.2
| 2014-07-22 15:30 | 27.7 | 25 | 22.2
| 2014-07-22 16:00 | 27.7 | 25 | 22.2
| 2014-07-22 16:30 | 27.7 | 25 | 22.2
| 2014-07-22 17:00 | 28.7 | 25.6 | 22.2
| 2014-07-22 17:30 | 29.1 | 25.6 | 22.2
| 2014-07-22 18:00 | 28.1 | 25.6 | 22.2
| 2014-07-22 18:30 | 28.4 | 25.6 | 22.2
| 2014-07-22 19:00 | 28.8 | 25.6 | 22.2
| 2014-07-22 19:30 | 27.7 | 25.6 | 22.2
| 2014-07-22 20:00 | 27.1 | 25.6 | 22.2
| 2014-07-22 20:30 | 26.5 | 25.6 | 22.2
| 2014-07-22 21:00 | 25.4 | 25.6 | 22.2
| 2014-07-22 21:30 | 24.3 | 25.6 | 22.2
| 2014-07-22 22:00 | 23.5 | 25.6 | 22.2
| 2014-07-22 22:30 | 22.6 | 25.6 | 22.2
| 2014-07-22 23:00 | 21.8 | 25.6 | 22.2
| 2014-07-22 23:30 | 21.4 | 25.6 | 22.2
| 2014-07-23 | 21.3 | 25 | 22.2
| 2014-07-23 00:30 | 20.9 | 25 | 22.2
| 2014-07-23 01:00 | 20.2 | 25 | 22.2
| 2014-07-23 01:30 | 19.7 | 25 | 22.2
| 2014-07-23 02:00 | 19.5 | 25 | 22.2
| 2014-07-23 02:30 | 19.2 | 24.4 | 22.2
| 2014-07-23 03:00 | 19.1 | 24.4 | 22.2
| 2014-07-23 03:30 | 18.9 | 24.4 | 22.2
| 2014-07-23 04:00 | 18.6 | 24.4 | 22.2
| 2014-07-23 04:30 | 18.3 | 23.9 | 22.2
| 2014-07-23 05:00 | 18.2 | 23.9 | 22.2
| 2014-07-23 05:30 | 18.3 | 23.9 | 22.2
| 2014-07-23 06:00 | 18.3 | 23.9 | 22.2
| 2014-07-23 06:30 | 18.4 | 23.9 | 22.2
| 2014-07-23 07:00 | 18.7 | 23.3 | 22.2
| 2014-07-23 07:30 | 19 | 23.3 | 22.2
| 2014-07-23 08:00 | 20.3 | 23.3 | 22.2
| 2014-07-23 08:30 | 21.6 | 23.3 | 22.2
| 2014-07-23 09:00 | 22.9 | 23.3 | 22.2
| 2014-07-23 09:30 | 22.3 | 23.3 | 22.2
| 2014-07-23 10:00 | 22.7 | 23.3 | 22.2
| 2014-07-23 10:30 | 23.5 | 23.3 | 22.2
| 2014-07-23 11:00 | 24.6 | 23.3 | 22.2
| 2014-07-23 11:30 | 26 | 23.3 | 22.2
| 2014-07-23 12:00 | 28.2 | 23.3 | 22.2
| 2014-07-23 12:30 | 28 | 23.3 | 22.2
| 2014-07-23 13:00 | 28.8 | 23.3 | 22.2
| 2014-07-23 13:30 | 28.6 | 23.9 | 22.2
| 2014-07-23 14:00 | 30.2 | 23.9 | 22.2
| 2014-07-23 14:30 | 29.7 | 24.4 | 22.2
| 2014-07-23 15:00 | 29.7 | 24.4 | 22.2
| 2014-07-23 15:30 | 28.6 | 25 | 22.2
| 2014-07-23 16:00 | 30 | 25 | 22.2
| 2014-07-23 16:30 | 29.2 | 25.6 | 22.2
| 2014-07-23 17:00 | 30.4 | 25.6 | 22.2
| 2014-07-23 17:30 | 30.4 | 25.6 | 21.7
| 2014-07-23 18:00 | 30.2 | 26.1 | 21.7
| 2014-07-23 18:30 | 30.3 | 26.1 | 21.7
| 2014-07-23 19:00 | 30.1 | 26.1 | 21.7
| 2014-07-23 19:30 | 29.5 | 26.1 | 21.7
| 2014-07-23 20:00 | 28.7 | 26.1 | 21.7
| 2014-07-23 20:30 | 27.8 | 26.1 | 21.7
| 2014-07-23 21:00 | 26.2 | 26.1 | 21.7
| 2014-07-23 21:30 | 24.4 | 26.1 | 21.7
| 2014-07-23 22:00 | 23 | 26.1 | 21.7
| 2014-07-23 22:30 | 22.3 | 26.1 | 21.7
| 2014-07-23 23:00 | 21.7 | 26.1 | 21.7
| 2014-07-23 23:30 | 21.2 | 26.1 | 21.7
| 2014-07-24 | 20.3 | 25.6 | 21.7
| 2014-07-24 00:30 | 19.3 | 25.6 | 21.7
| 2014-07-24 01:00 | 19.3 | 25.6 | 21.7
| 2014-07-24 01:30 | 19.2 | 25.6 | 21.7
| 2014-07-24 02:00 | 18.8 | 25 | 21.7
| 2014-07-24 02:30 | 18.8 | 25 | 21.7
| 2014-07-24 03:00 | 18.6 | 25 | 21.7
| 2014-07-24 03:30 | 18.4 | 25 | 21.7
| 2014-07-24 04:00 | 18 | 24.4 | 21.7
| 2014-07-24 04:30 | 17.8 | 24.4 | 21.7
| 2014-07-24 05:00 | 17.6 | 24.4 | 21.7
| 2014-07-24 05:30 | 16.8 | 24.4 | 21.7
| 2014-07-24 06:00 | 16.7 | 23.9 | 21.7
| 2014-07-24 06:30 | 17 | 23.9 | 21.7
| 2014-07-24 07:00 | 17.5 | 23.9 | 21.7
| 2014-07-24 07:30 | 18.3 | 23.9 | 21.7
| 2014-07-24 08:00 | 18.9 | 23.3 | 21.7
| 2014-07-24 08:30 | 19.9 | 23.3 | 21.7
| 2014-07-24 09:00 | 21.1 | 23.3 | 21.7
| 2014-07-24 09:30 | 21.9 | 23.3 | 21.7
| 2014-07-24 10:00 | 23.2 | 23.3 | 21.7
| 2014-07-24 10:30 | 23.8 | 23.3 | 21.7
| 2014-07-24 11:00 | 24.6 | 22.8 | 21.7
| 2014-07-24 11:30 | 25.7 | 23.3 | 21.7
| 2014-07-24 12:00 | 25.8 | 23.3 | 21.7
| 2014-07-24 12:30 | 26.3 | 23.3 | 21.7
| 2014-07-24 13:00 | 26.2 | 23.3 | 21.7
| 2014-07-24 13:30 | 27.3 | 23.9 | 21.7
| 2014-07-24 14:00 | 27.8 | 23.9 | 21.7
| 2014-07-24 14:30 | 28.3 | 24.4 | 22.2
| 2014-07-24 15:00 | 28.2 | 24.4 | 22.2
| 2014-07-24 15:30 | 27.9 | 25 | 22.2
| 2014-07-24 16:00 | 28.3 | 25 | 22.2
| 2014-07-24 16:30 | 28.9 | 25.6 | 22.2
| 2014-07-24 17:00 | 29 | 25.6 | 22.2
| 2014-07-24 17:30 | 28.3 | 26.1 | 22.2
| 2014-07-24 18:00 | 27.8 | 26.1 | 22.2
| 2014-07-24 18:30 | 25.7 | 26.7 | 22.2
| 2014-07-24 19:00 | 25.5 | 26.7 | 22.2
| 2014-07-24 19:30 | 25.4 | 26.7 | 22.2
| 2014-07-24 20:00 | 24.8 | 26.7 | 22.2
| 2014-07-24 20:30 | 23.7 | 26.7 | 22.2
| 2014-07-24 21:00 | 22.3 | 26.7 | 22.2
| 2014-07-24 21:30 | 18.5 | 26.7 | 22.2
| 2014-07-24 22:00 | 18.1 | 26.7 | 21.7
| 2014-07-24 22:30 | 17.9 | 26.7 | 21.7
| 2014-07-24 23:00 | 17.3 | 26.1 | 21.7
| 2014-07-24 23:30 | 16.7 | 26.1 | 21.7
| 2014-07-25 | 16.7 | 26.1 | 21.7
| 2014-07-25 00:30 | 16.4 | 26.1 | 21.7
| 2014-07-25 01:00 | 16.1 | 25.6 | 21.7
| 2014-07-25 01:30 | 15.8 | 25.6 | 21.7
| 2014-07-25 02:00 | 15.4 | 25.6 | 21.7
| 2014-07-25 02:30 | 15.4 | 25 | 21.7
| 2014-07-25 03:00 | 15.3 | 25 | 21.7
| 2014-07-25 03:30 | 15.2 | 25 | 21.7
| 2014-07-25 04:00 | 15.3 | 24.4 | 21.7
| 2014-07-25 04:30 | 15.4 | 24.4 | 22.2
| 2014-07-25 05:00 | 15.3 | 24.4 | 22.2
| 2014-07-25 05:30 | 15.1 | 23.9 | 22.2
| 2014-07-25 06:00 | 15 | 23.9 | 22.2
| 2014-07-25 06:30 | 14.9 | 23.9 | 22.2
| 2014-07-25 07:00 | 15.1 | 23.9 | 22.2
| 2014-07-25 07:30 | 15.6 | 23.3 | 22.2
| 2014-07-25 08:00 | 16.3 | 23.3 | 22.2
| 2014-07-25 08:30 | 17.4 | 23.3 | 22.2
| 2014-07-25 09:00 | 19 | 23.3 | 22.2
| 2014-07-25 09:30 | 19.9 | 23.3 | 22.2
| 2014-07-25 10:00 | 20.8 | 22.8 | 22.2
| 2014-07-25 10:30 | 21.1 | 22.8 | 22.2
| 2014-07-25 11:00 | 22.1 | 22.8 | 22.2
| 2014-07-25 11:30 | 22.6 | 22.8 | 22.2
| 2014-07-25 12:00 | 23.9 | 22.8 | 22.2
| 2014-07-25 12:30 | 23.8 | 23.3 | 22.2
| 2014-07-25 13:00 | 24.3 | 23.3 | 22.2
| 2014-07-25 13:30 | 24.5 | 23.3 | 22.2
| 2014-07-25 14:00 | 25.6 | 23.9 | 22.2
| 2014-07-25 14:30 | 26.4 | 23.9 | 22.2
| 2014-07-25 15:00 | 26.2 | 24.4 | 22.2
| 2014-07-25 15:30 | 26 | 24.4 | 22.2
| 2014-07-25 16:00 | 25.6 | 25 | 22.2
| 2014-07-25 16:30 | 24.8 | 25 | 22.2
| 2014-07-25 17:00 | 24.4 | 25.6 | 22.2
| 2014-07-25 17:30 | 22.6 | 25.6 | 22.2
| 2014-07-25 18:00 | 24.2 | 25.6 | 22.2
| 2014-07-25 18:30 | 24.3 | 25.6 | 22.2
| 2014-07-25 19:00 | 23.2 | 25.6 | 22.2
| 2014-07-25 19:30 | 22.8 | 25.6 | 22.2
| 2014-07-25 20:00 | 22.6 | 25.6 | 22.2
| 2014-07-25 20:30 | 22.4 | 25.6 | 22.2
| 2014-07-25 21:00 | 21.4 | 25.6 | 22.2
| 2014-07-25 21:30 | 20.1 | 25.6 | 22.2
| 2014-07-25 22:00 | 19.1 | 25.6 | 22.2
| 2014-07-25 22:30 | 18.3 | 25 | 22.2
| 2014-07-25 23:00 | 17.7 | 25 | 22.2
| 2014-07-25 23:30 | 17.2 | 25 | 22.2
| 2014-07-26 | 16.8 | 25 | 22.2
| 2014-07-26 00:30 | 16.4 | 24.4 | 22.2
| 2014-07-26 01:00 | 16.2 | 24.4 | 22.2
| 2014-07-26 01:30 | 16 | 24.4 | 22.2
| 2014-07-26 02:00 | 15.8 | 24.4 | 22.2
| 2014-07-26 02:30 | 15.5 | 23.9 | 22.2
| 2014-07-26 03:00 | 15.3 | 23.9 | 22.2
| 2014-07-26 03:30 | 15.1 | 23.9 | 22.2
| 2014-07-26 04:00 | 15 | 23.9 | 22.2
| 2014-07-26 04:30 | 14.8 | 23.3 | 22.2
| 2014-07-26 05:00 | 14.6 | 23.3 | 22.2
| 2014-07-26 05:30 | 14.9 | 23.3 | 22.2
| 2014-07-26 06:00 | 14.3 | 23.3 | 22.2
| 2014-07-26 06:30 | 14.5 | 23.3 | 22.2
| 2014-07-26 07:00 | 15.1 | 22.8 | 22.2
| 2014-07-26 07:30 | 16.1 | 22.8 | 22.2
| 2014-07-26 08:00 | 16.9 | 22.8 | 22.2
| 2014-07-26 08:30 | 18.1 | 22.8 | 22.2
| 2014-07-26 09:00 | 19.2 | 22.2 | 22.2
| 2014-07-26 09:30 | 20.4 | 22.2 | 22.2
| 2014-07-26 10:00 | 21.6 | 22.2 | 22.2
| 2014-07-26 10:30 | 23.2 | 22.2 | 22.2
| 2014-07-26 11:00 | 23.3 | 22.2 | 22.2
| 2014-07-26 11:30 | 23.9 | 22.2 | 22.2
| 2014-07-26 12:00 | 24.3 | 22.2 | 22.2
| 2014-07-26 12:30 | 25.2 | 22.8 | 22.2
| 2014-07-26 13:00 | 26.1 | 22.8 | 22.2
| 2014-07-26 13:30 | 26.4 | 23.3 | 22.2
| 2014-07-26 14:00 | 26.4 | 23.3 | 22.2
| 2014-07-26 14:30 | 26.9 | 23.3 | 22.2
| 2014-07-26 15:00 | 27.5 | 23.9 | 22.2
| 2014-07-26 15:30 | 27.3 | 23.9 | 22.2
| 2014-07-26 16:00 | 27.9 | 24.4 | 22.2
| 2014-07-26 16:30 | 28.1 | 24.4 | 22.2
| 2014-07-26 17:00 | 28.1 | 24.4 | 22.2
| 2014-07-26 17:30 | 27.8 | 25 | 22.2
| 2014-07-26 18:00 | 27.4 | 25 | 22.2
| 2014-07-26 18:30 | 26.2 | 25.6 | 22.2
| 2014-07-26 19:00 | 25.3 | 25.6 | 22.2
| 2014-07-26 19:30 | 24.8 | 25.6 | 22.2
| 2014-07-26 20:00 | 24.6 | 25.6 | 22.2
| 2014-07-26 20:30 | 24.4 | 25.6 | 22.2
| 2014-07-26 21:00 | 23.6 | 25.6 | 22.2
| 2014-07-26 21:30 | 22.7 | 25.6 | 22.2
| 2014-07-26 22:00 | 21.9 | 25.6 | 22.2
| 2014-07-26 22:30 | 21.3 | 25.6 | 22.2
| 2014-07-26 23:00 | 21.1 | 25.6 | 22.2
| 2014-07-26 23:30 | 20.7 | 25.6 | 22.2
| 2014-07-27 | 20.2 | 25.6 | 22.2
| 2014-07-27 00:30 | 19.7 | 25.6 | 22.2
| 2014-07-27 01:00 | 19.2 | 25.6 | 22.2
| 2014-07-27 01:30 | 18.8 | 25 | 22.2
| 2014-07-27 02:00 | 18.7 | 25 | 22.2
| 2014-07-27 02:30 | 18.4 | 25 | 22.2
| 2014-07-27 03:00 | 18.3 | 25 | 22.2
| 2014-07-27 03:30 | 18.1 | 24.4 | 22.2
| 2014-07-27 04:00 | 17.7 | 24.4 | 22.2
| 2014-07-27 04:30 | 17.4 | 24.4 | 22.2
| 2014-07-27 05:00 | 17.2 | 24.4 | 22.2
| 2014-07-27 05:30 | 16.9 | 24.4 | 22.2
| 2014-07-27 06:00 | 16.7 | 23.9 | 22.2
| 2014-07-27 06:30 | 16.8 | 23.9 | 22.2
| 2014-07-27 07:00 | 17 | 23.9 | 22.2
| 2014-07-27 07:30 | 17.6 | 23.9 | 22.2
| 2014-07-27 08:00 | 18.2 | 23.9 | 22.2
| 2014-07-27 08:30 | 19.2 | 23.9 | 22.2
| 2014-07-27 09:00 | 20.4 | 23.3 | 22.2
| 2014-07-27 09:30 | 21.4 | 23.3 | 22.2
| 2014-07-27 10:00 | 22.5 | 23.3 | 22.2
| 2014-07-27 10:30 | 23.7 | 23.3 | 22.2
| 2014-07-27 11:00 | 24.7 | 23.3 | 22.2
| 2014-07-27 11:30 | 25.1 | 23.3 | 22.2
| 2014-07-27 12:00 | 25.8 | 23.3 | 22.2
| 2014-07-27 12:30 | 26.6 | 23.9 | 22.2
| 2014-07-27 13:00 | 26.6 | 23.9 | 22.2
| 2014-07-27 13:30 | 27.5 | 23.9 | 22.2
| 2014-07-27 14:00 | 27.2 | 24.4 | 22.2
| 2014-07-27 14:30 | 28.4 | 24.4 | 22.2
| 2014-07-27 15:00 | 28.8 | 25 | 22.2
| 2014-07-27 15:30 | 29.2 | 25 | 22.2
| 2014-07-27 16:00 | 28.5 | 25.6 | 22.2
| 2014-07-27 16:30 | 29 | 25.6 | 22.2
| 2014-07-27 17:00 | 27.8 | 26.1 | 22.2
| 2014-07-27 17:30 | 28 | 26.1 | 22.2
| 2014-07-27 18:00 | 28.9 | 26.7 | 22.2
| 2014-07-27 18:30 | 28.8 | 26.7 | 22.2
| 2014-07-27 19:00 | 28.6 | 26.7 | 22.2
| 2014-07-27 19:30 | 27.4 | 26.7 | 22.2
| 2014-07-27 20:00 | 26.8 | 26.7 | 22.2
| 2014-07-27 20:30 | 26.8 | 27.2 | 22.2
| 2014-07-27 21:00 | 26.2 | 27.2 | 22.2
| 2014-07-27 21:30 | 24.1 | 27.2 | 22.2
| 2014-07-27 22:00 | 22.5 | 27.2 | 22.2
| 2014-07-27 22:30 | 21.7 | 26.7 | 22.2
| 2014-07-27 23:00 | 20.9 | 26.7 | 22.2
| 2014-07-27 23:30 | 20.2 | 26.7 | 22.2
| 2014-07-28 | 19.6 | 26.7 | 22.2
| 2014-07-28 00:30 | 19.3 | 26.7 | 22.2
| 2014-07-28 01:00 | 19.1 | 26.7 | 22.2
| 2014-07-28 01:30 | 18.7 | 26.1 | 22.2
| 2014-07-28 02:00 | 18.3 | 26.1 | 22.2
| 2014-07-28 02:30 | 18.1 | 26.1 | 22.2
| 2014-07-28 03:00 | 17.7 | 25.6 | 22.2
| 2014-07-28 03:30 | 17.6 | 25.6 | 22.2
| 2014-07-28 04:00 | 17.4 | 25.6 | 22.2
| 2014-07-28 04:30 | 17.2 | 25.6 | 22.2
| 2014-07-28 05:00 | 17.1 | 25.6 | 22.2
| 2014-07-28 05:30 | 16.9 | 25 | 22.2
| 2014-07-28 06:00 | 16.9 | 25 | 22.2
| 2014-07-28 06:30 | 16.7 | 25 | 22.2
| 2014-07-28 07:00 | 17 | 25 | 22.2
| 2014-07-28 07:30 | 17.9 | 24.4 | 22.2
| 2014-07-28 08:00 | 18.8 | 24.4 | 22.2
| 2014-07-28 08:30 | 19.9 | 24.4 | 22.2
| 2014-07-28 09:00 | 21.1 | 24.4 | 22.2
| 2014-07-28 09:30 | 22.2 | 24.4 | 22.2
| 2014-07-28 10:00 | 24.2 | 24.4 | 22.2
| 2014-07-28 10:30 | 25.6 | 24.4 | 22.2
| 2014-07-28 11:00 | 25.8 | 24.4 | 22.2
| 2014-07-28 11:30 | 26.9 | 24.4 | 22.2
| 2014-07-28 12:00 | 27.3 | 24.4 | 22.2
| 2014-07-28 12:30 | 28.3 | 24.4 | 22.2
| 2014-07-28 13:00 | 28 | 24.4 | 22.2
| 2014-07-28 13:30 | 27.5 | 25 | 22.2
| 2014-07-28 14:00 | 28.1 | 25 | 22.2
| 2014-07-28 14:30 | 29.6 | 25.6 | 22.2
| 2014-07-28 15:00 | 30.1 | 25.6 | 22.2
| 2014-07-28 15:30 | 29.4 | 25.6 | 22.2
| 2014-07-28 16:00 | 28.5 | 26.1 | 22.2
| 2014-07-28 16:30 | 27.3 | 26.1 | 22.2
| 2014-07-28 17:00 | 25.5 | 26.7 | 22.2
| 2014-07-28 17:30 | 23.9 | 26.7 | 22.2
| 2014-07-28 18:00 | 25.2 | 26.7 | 22.2
| 2014-07-28 18:30 | 26.4 | 27.2 | 22.2
| 2014-07-28 19:00 | 27.3 | 27.2 | 22.2
| 2014-07-28 19:30 | 25.2 | 27.2 | 22.2
| 2014-07-28 20:00 | 24.3 | 27.2 | 22.2
| 2014-07-28 20:30 | 23.5 | 27.2 | 22.2
| 2014-07-28 21:00 | 22.6 | 27.2 | 22.2
| 2014-07-28 21:30 | 21.7 | 27.2 | 22.2
| 2014-07-28 22:00 | 21.6 | 27.2 | 22.2
| 2014-07-28 22:30 | 20.4 | 27.2 | 22.2
| 2014-07-28 23:00 | 19.3 | 26.7 | 22.2
| 2014-07-28 23:30 | 19.3 | 26.7 | 22.2
| 2014-07-29 | 18.9 | 26.7 | 22.2
| 2014-07-29 00:30 | 19 | 26.7 | 22.2
| 2014-07-29 01:00 | 19.1 | 26.7 | 22.2
| 2014-07-29 01:30 | 18.7 | 26.1 | 22.2
| 2014-07-29 02:00 | 18.6 | 26.1 | 22.2
| 2014-07-29 02:30 | 18.5 | 26.1 | 22.2
| 2014-07-29 03:00 | 18.7 | 25.6 | 22.2
| 2014-07-29 03:30 | 18.5 | 25.6 | 22.2
| 2014-07-29 04:00 | 18.3 | 25.6 | 22.2
| 2014-07-29 04:30 | 18.4 | 25.6 | 22.2
| 2014-07-29 05:00 | 18.4 | 25.6 | 22.2
| 2014-07-29 05:30 | 18.4 | 25 | 22.2
| 2014-07-29 06:00 | 18.6 | 25 | 22.2
| 2014-07-29 06:30 | 18.6 | 25 | 22.2
| 2014-07-29 07:00 | 18.9 | 25 | 22.2
| 2014-07-29 07:30 | 19.1 | 25 | 22.2
| 2014-07-29 08:00 | 19.4 | 24.4 | 22.2
| 2014-07-29 08:30 | 19.8 | 24.4 | 22.2
| 2014-07-29 09:00 | 20.4 | 24.4 | 22.2
| 2014-07-29 09:30 | 21.5 | 24.4 | 22.2
| 2014-07-29 10:00 | 21.8 | 24.4 | 22.2
| 2014-07-29 10:30 | 22.4 | 24.4 | 22.2
| 2014-07-29 11:00 | 23.2 | 24.4 | 22.2
| 2014-07-29 11:30 | 23.4 | 24.4 | 22.2
| 2014-07-29 12:00 | 24 | 24.4 | 22.2
| 2014-07-29 12:30 | 24.6 | 24.4 | 22.2
| 2014-07-29 13:00 | 24.9 | 24.4 | 22.2
| 2014-07-29 13:30 | 25.2 | 25 | 22.2
| 2014-07-29 14:00 | 25.6 | 25 | 22.2
| 2014-07-29 14:30 | 24.3 | 25 | 22.2
| 2014-07-29 15:00 | 23.9 | 25.6 | 22.2
| 2014-07-29 15:30 | 23.9 | 25.6 | 22.2
| 2014-07-29 16:00 | 21.5 | 25.6 | 22.2
| 2014-07-29 16:30 | 21.3 | 25.6 | 22.2
| 2014-07-29 17:00 | 21.8 | 25.6 | 22.2
| 2014-07-29 17:30 | 22.9 | 25.6 | 22.2
| 2014-07-29 18:00 | 22.7 | 25.6 | 22.2
| 2014-07-29 18:30 | 21.8 | 25.6 | 22.2
| 2014-07-29 19:00 | 20.3 | 25.6 | 22.2
| 2014-07-29 19:30 | 19.8 | 25.6 | 22.2
| 2014-07-29 20:00 | 19.9 | 25.6 | 22.2
| 2014-07-29 20:30 | 19.9 | 25.6 | 22.2
| 2014-07-29 21:00 | 19.8 | 25.6 | 22.2
| 2014-07-29 21:30 | 19.4 | 25.6 | 22.2
| 2014-07-29 22:00 | 19.2 | 25.6 | 22.2
| 2014-07-29 22:30 | 19.2 | 25.6 | 22.2
| 2014-07-29 23:00 | 18.9 | 25 | 22.2
| 2014-07-29 23:30 | 18.8 | 25 | 22.2
| 2014-07-30 | 18.8 | 25 | 22.2
| 2014-07-30 00:30 | 18.8 | 25 | 22.2
| 2014-07-30 01:00 | 18.9 | 25 | 22.2
| 2014-07-30 01:30 | 18.9 | 24.4 | 22.2
| 2014-07-30 02:00 | 18.7 | 24.4 | 22.2
| 2014-07-30 02:30 | 18.8 | 24.4 | 22.2
| 2014-07-30 03:00 | 18.8 | 24.4 | 22.2
| 2014-07-30 03:30 | 18.7 | 24.4 | 22.2
| 2014-07-30 04:00 | 18.6 | 24.4 | 22.2
| 2014-07-30 04:30 | 18.6 | 23.9 | 22.2
| 2014-07-30 05:00 | 18.7 | 23.9 | 22.2
| 2014-07-30 05:30 | 18.8 | 23.9 | 22.2
| 2014-07-30 06:00 | 18.8 | 23.9 | 22.2
| 2014-07-30 06:30 | 18.8 | 23.9 | 22.2
| 2014-07-30 07:00 | 18.9 | 23.9 | 22.2
| 2014-07-30 07:30 | 19.1 | 23.9 | 22.2
| 2014-07-30 08:00 | 19.2 | 23.9 | 22.2
| 2014-07-30 08:30 | 19.3 | 23.9 | 22.2
| 2014-07-30 09:00 | 19.5 | 23.3 | 22.2
| 2014-07-30 09:30 | 19.8 | 23.3 | 22.2
| 2014-07-30 10:00 | 20.1 | 23.3 | 22.2
| 2014-07-30 10:30 | 20.5 | 23.3 | 22.2
| 2014-07-30 11:00 | 20.7 | 23.3 | 22.2
| 2014-07-30 11:30 | 20.8 | 23.3 | 22.2
| 2014-07-30 12:00 | 21.3 | 23.3 | 22.2
| 2014-07-30 12:30 | 20.6 | 23.3 | 22.2
| 2014-07-30 13:00 | 21.2 | 23.3 | 22.2
| 2014-07-30 13:30 | 22.3 | 23.3 | 22.2
| 2014-07-30 14:00 | 22.6 | 23.3 | 22.2
| 2014-07-30 14:30 | 22.6 | 23.3 | 22.2
| 2014-07-30 15:00 | 21.9 | 23.9 | 22.2
| 2014-07-30 15:30 | 21.6 | 23.9 | 22.2
| 2014-07-30 16:00 | 21.3 | 23.9 | 22.2
| 2014-07-30 16:30 | 21.7 | 23.9 | 22.2
| 2014-07-30 17:00 | 21.6 | 23.9 | 22.2
| 2014-07-30 17:30 | 21.8 | 23.9 | 22.2
| 2014-07-30 18:00 | 21.8 | 23.9 | 22.2
| 2014-07-30 18:30 | 21.7 | 23.9 | 22.2
| 2014-07-30 19:00 | 21.5 | 23.9 | 22.2
| 2014-07-30 19:30 | 21.4 | 23.9 | 22.2
| 2014-07-30 20:00 | 21.2 | 23.9 | 22.2
| 2014-07-30 20:30 | 21 | 23.9 | 22.2
| 2014-07-30 21:00 | 20.5 | 23.9 | 22.2
| 2014-07-30 21:30 | 20.1 | 23.9 | 22.2
| 2014-07-30 22:00 | 19.7 | 23.9 | 22.2
| 2014-07-30 22:30 | 19.3 | 23.9 | 22.2
| 2014-07-30 23:00 | 19.3 | 23.9 | 22.2
| 2014-07-30 23:30 | 19.2 | 23.3 | 22.2
| 2014-07-31 | 19.3 | 23.3 | 22.2
| 2014-07-31 00:30 | 19.8 | 23.3 | 22.2
| 2014-07-31 01:00 | 19.4 | 23.3 | 22.2
| 2014-07-31 01:30 | 18.8 | 23.3 | 22.2
| 2014-07-31 02:00 | 18.1 | 23.3 | 22.2
| 2014-07-31 02:30 | 18.1 | 23.3 | 22.2
| 2014-07-31 03:00 | 18.2 | 23.3 | 22.2
| 2014-07-31 03:30 | 17.9 | 22.8 | 22.2
| 2014-07-31 04:00 | 17.6 | 22.8 | 22.2
| 2014-07-31 04:30 | 17.3 | 22.8 | 22.2
| 2014-07-31 05:00 | 16.7 | 22.8 | 22.2
| 2014-07-31 05:30 | 16.1 | 22.8 | 22.2
| 2014-07-31 06:00 | 15.6 | 22.2 | 22.2
| 2014-07-31 06:30 | 15.6 | 22.2 | 22.2
| 2014-07-31 07:00 | 15.9 | 22.2 | 22.2
| 2014-07-31 07:30 | 16.2 | 22.2 | 22.2
| 2014-07-31 08:00 | 17.1 | 22.2 | 22.2
| 2014-07-31 08:30 | 18.1 | 22.2 | 22.2
| 2014-07-31 09:00 | 19.3 | 22.2 | 22.2
| 2014-07-31 09:30 | 20.4 | 22.2 | 22.2
| 2014-07-31 10:00 | 21.1 | 21.7 | 22.2
| 2014-07-31 10:30 | 21.7 | 21.7 | 22.2
| 2014-07-31 11:00 | 21.4 | 21.7 | 22.2
| 2014-07-31 11:30 | 22 | 21.7 | 22.2
| 2014-07-31 12:00 | 23.1 | 22.2 | 22.2
| 2014-07-31 12:30 | 23.3 | 22.2 | 22.2
| 2014-07-31 13:00 | 24.3 | 22.2 | 22.2
| 2014-07-31 13:30 | 24.8 | 22.2 | 22.2
| 2014-07-31 14:00 | 24.3 | 22.8 | 22.2
| 2014-07-31 14:30 | 25 | 22.8 | 22.2
| 2014-07-31 15:00 | 25.9 | 23.3 | 22.2
| 2014-07-31 15:30 | 24.8 | 23.3 | 22.2
| 2014-07-31 16:00 | 26.9 | 23.3 | 22.2
| 2014-07-31 16:30 | 27.5 | 23.9 | 22.2
| 2014-07-31 17:00 | 27.7 | 23.9 | 22.2
| 2014-07-31 17:30 | 27.5 | 23.9 | 22.2
| 2014-07-31 18:00 | 27.9 | 24.4 | 22.2
| 2014-07-31 18:30 | 27.8 | 24.4 | 22.2
| 2014-07-31 19:00 | 27.4 | 24.4 | 22.2
| 2014-07-31 19:30 | 27.3 | 25 | 22.2
| 2014-07-31 20:00 | 26.9 | 25 | 22.2
| 2014-07-31 20:30 | 25.6 | 25 | 22.2
| 2014-07-31 21:00 | 22.7 | 25 | 22.2
| 2014-07-31 21:30 | 20.5 | 25 | 22.2
| 2014-07-31 22:00 | 19.3 | 25 | 22.2
| 2014-07-31 22:30 | 18.5 | 25 | 22.2
| 2014-07-31 23:00 | 17.9 | 25 | 22.2
| 2014-07-31 23:30 | 17.3 | 25 | 22.2
| 2014-08-01 | 16.7 | 24.4 | 22.2
| 2014-08-01 00:30 | 16.3 | 24.4 | 22.2
| 2014-08-01 01:00 | 15.9 | 24.4 | 22.2
| 2014-08-01 01:30 | 15.6 | 24.4 | 22.2
| 2014-08-01 02:00 | 15.4 | 23.9 | 22.2
| 2014-08-01 02:30 | 15.3 | 23.9 | 22.2
| 2014-08-01 03:00 | 15.1 | 23.9 | 22.2
| 2014-08-01 03:30 | 14.8 | 23.9 | 22.2
| 2014-08-01 04:00 | 14.7 | 23.9 | 22.2
| 2014-08-01 04:30 | 14.4 | 23.3 | 22.2
| 2014-08-01 05:00 | 14.3 | 23.3 | 22.2
| 2014-08-01 05:30 | 14 | 23.3 | 22.2
| 2014-08-01 06:00 | 13.9 | 23.3 | 22.2
| 2014-08-01 06:30 | 13.9 | 22.8 | 22.2
| 2014-08-01 07:00 | 14.1 | 22.8 | 22.2
| 2014-08-01 07:30 | 15.1 | 22.8 | 22.2
| 2014-08-01 08:00 | 16.5 | 22.8 | 22.2
| 2014-08-01 08:30 | 17.9 | 22.2 | 22.2
| 2014-08-01 09:00 | 20 | 22.2 | 22.2
| 2014-08-01 09:30 | 21.9 | 22.2 | 22.2
| 2014-08-01 10:00 | 23.2 | 22.2 | 22.2
| 2014-08-01 10:30 | 24.6 | 22.2 | 22.2
| 2014-08-01 11:00 | 25.5 | 22.2 | 22.2
| 2014-08-01 11:30 | 26 | 22.2 | 22.2
| 2014-08-01 12:00 | 25.9 | 22.2 | 22.2
| 2014-08-01 12:30 | 25.7 | 22.8 | 22.2
| 2014-08-01 13:00 | 26.3 | 22.8 | 22.2
| 2014-08-01 13:30 | 27.9 | 22.8 | 22.2
| 2014-08-01 14:00 | 26.4 | 23.3 | 22.2
| 2014-08-01 14:30 | 27.5 | 23.3 | 22.2
| 2014-08-01 15:00 | 27.5 | 23.9 | 22.2
| 2014-08-01 15:30 | 27.8 | 23.9 | 22.2
| 2014-08-01 16:00 | 28.4 | 23.9 | 22.2
| 2014-08-01 16:30 | 29.2 | 24.4 | 22.2
| 2014-08-01 17:00 | 29.1 | 24.4 | 22.2
| 2014-08-01 17:30 | 28.7 | 24.4 | 22.2
| 2014-08-01 18:00 | 29.3 | 25 | 22.2
| 2014-08-01 18:30 | 29.8 | 25 | 22.2
| 2014-08-01 19:00 | 28.6 | 25 | 22.2
| 2014-08-01 19:30 | 27.9 | 25.6 | 22.2
| 2014-08-01 20:00 | 27.3 | 25.6 | 22.2
| 2014-08-01 20:30 | 25.8 | 25.6 | 22.2
| 2014-08-01 21:00 | 23.4 | 25.6 | 22.2
| 2014-08-01 21:30 | 21.4 | 25.6 | 22.2
| 2014-08-01 22:00 | 20.3 | 25.6 | 22.2
| 2014-08-01 22:30 | 19.6 | 25.6 | 22.2
| 2014-08-01 23:00 | 18.9 | 25.6 | 22.2
| 2014-08-01 23:30 | 18.3 | 25 | 22.2
| 2014-08-02 | 17.9 | 25 | 22.2
| 2014-08-02 00:30 | 17.4 | 25 | 22.2
| 2014-08-02 01:00 | 16.5 | 25 | 22.2
| 2014-08-02 01:30 | 16.1 | 24.4 | 22.2
| 2014-08-02 02:00 | 15.3 | 24.4 | 22.2
| 2014-08-02 02:30 | 14.7 | 24.4 | 22.2
| 2014-08-02 03:00 | 14.6 | 24.4 | 22.2
| 2014-08-02 03:30 | 14.6 | 23.9 | 22.2
| 2014-08-02 04:00 | 14.4 | 23.9 | 22.2
| 2014-08-02 04:30 | 14.3 | 23.9 | 22.2
| 2014-08-02 05:00 | 14.1 | 23.9 | 22.2
| 2014-08-02 05:30 | 14 | 23.3 | 22.2
| 2014-08-02 06:00 | 13.7 | 23.3 | 22.2
| 2014-08-02 06:30 | 13.5 | 23.3 | 22.2
| 2014-08-02 07:00 | 15.2 | 23.3 | 22.2
| 2014-08-02 07:30 | 16.1 | 23.3 | 22.2
| 2014-08-02 08:00 | 16.7 | 22.8 | 22.2
| 2014-08-02 08:30 | 17.4 | 22.8 | 22.2
| 2014-08-02 09:00 | 19.1 | 22.8 | 22.2
| 2014-08-02 09:30 | 20.3 | 22.8 | 22.2
| 2014-08-02 10:00 | 21.7 | 22.8 | 22.2
| 2014-08-02 10:30 | 22.1 | 22.8 | 22.2
| 2014-08-02 11:00 | 22.4 | 22.8 | 22.2
| 2014-08-02 11:30 | 23.4 | 22.8 | 22.2
| 2014-08-02 12:00 | 23.7 | 22.8 | 22.2
| 2014-08-02 12:30 | 25.2 | 22.8 | 22.2
| 2014-08-02 13:00 | 24.9 | 22.8 | 22.2
| 2014-08-02 13:30 | 25.6 | 22.8 | 22.2
| 2014-08-02 14:00 | 26.5 | 23.3 | 22.2
| 2014-08-02 14:30 | 25.7 | 23.3 | 22.2
| 2014-08-02 15:00 | 25.2 | 23.3 | 22.2
| 2014-08-02 15:30 | 23.3 | 23.9 | 22.2
| 2014-08-02 16:00 | 23.4 | 23.9 | 22.2
| 2014-08-02 16:30 | 25 | 23.9 | 22.2
| 2014-08-02 17:00 | 26.1 | 23.9 | 22.2
| 2014-08-02 17:30 | 26.3 | 24.4 | 22.2
| 2014-08-02 18:00 | 27.2 | 24.4 | 22.2
| 2014-08-02 18:30 | 26.9 | 24.4 | 22.2
| 2014-08-02 19:00 | 24.8 | 24.4 | 22.2
| 2014-08-02 19:30 | 24.1 | 24.4 | 22.2
| 2014-08-02 20:00 | 23.9 | 24.4 | 22.2
| 2014-08-02 20:30 | 23.1 | 24.4 | 22.2
| 2014-08-02 21:00 | 22.1 | 24.4 | 22.2
| 2014-08-02 21:30 | 21.2 | 24.4 | 22.2
| 2014-08-02 22:00 | 20.8 | 24.4 | 22.2
| 2014-08-02 22:30 | 20.4 | 24.4 | 22.2
| 2014-08-02 23:00 | 20.4 | 24.4 | 22.2
| 2014-08-02 23:30 | 20.4 | 24.4 | 22.2
| 2014-08-03 | 20.2 | 24.4 | 22.2
| 2014-08-03 00:30 | 19.7 | 24.4 | 22.2
| 2014-08-03 01:00 | 19.8 | 23.9 | 22.2
| 2014-08-03 01:30 | 19.2 | 23.9 | 22.2
| 2014-08-03 02:00 | 18.5 | 23.9 | 22.2
| 2014-08-03 02:30 | 18.1 | 23.9 | 22.2
| 2014-08-03 03:00 | 18.1 | 23.9 | 22.2
| 2014-08-03 03:30 | 18.4 | 23.9 | 22.2
| 2014-08-03 04:00 | 19 | 23.9 | 22.2
| 2014-08-03 04:30 | 19.2 | 23.3 | 22.2
| 2014-08-03 05:00 | 19.1 | 23.3 | 22.2
| 2014-08-03 05:30 | 18.6 | 23.3 | 22.2
| 2014-08-03 06:00 | 18.3 | 23.3 | 22.2
| 2014-08-03 06:30 | 18.4 | 23.3 | 22.2
| 2014-08-03 07:00 | 18.4 | 23.3 | 22.2
| 2014-08-03 07:30 | 18.7 | 23.3 | 22.2
| 2014-08-03 08:00 | 20 | 23.3 | 22.2
| 2014-08-03 08:30 | 20.3 | 22.8 | 22.2
| 2014-08-03 09:00 | 21.3 | 22.8 | 22.2
| 2014-08-03 09:30 | 22.2 | 22.8 | 22.2
| 2014-08-03 10:00 | 22.5 | 22.8 | 22.2
| 2014-08-03 10:30 | 22.8 | 22.8 | 22.2
| 2014-08-03 11:00 | 23.8 | 22.8 | 22.2
| 2014-08-03 11:30 | 23.8 | 22.8 | 22.2
| 2014-08-03 12:00 | 23.7 | 22.8 | 22.2
| 2014-08-03 12:30 | 23.8 | 23.3 | 22.2
| 2014-08-03 13:00 | 24.4 | 23.3 | 22.2
| 2014-08-03 13:30 | 24.4 | 23.3 | 22.2
| 2014-08-03 14:00 | 24.7 | 23.3 | 22.2
| 2014-08-03 14:30 | 24.6 | 23.9 | 22.2
| 2014-08-03 15:00 | 24.9 | 23.9 | 22.2
| 2014-08-03 15:30 | 25.3 | 23.9 | 22.2
| 2014-08-03 16:00 | 26.3 | 23.9 | 22.2
| 2014-08-03 16:30 | 23.8 | 24.4 | 22.2
| 2014-08-03 17:00 | 22.8 | 24.4 | 22.2
| 2014-08-03 17:30 | 23.4 | 24.4 | 22.2
| 2014-08-03 18:00 | 22.3 | 24.4 | 22.2
| 2014-08-03 18:30 | 20.6 | 24.4 | 22.2
| 2014-08-03 19:00 | 20.5 | 24.4 | 22.2
| 2014-08-03 19:30 | 22.2 | 24.4 | 22.2
| 2014-08-03 20:00 | 22.1 | 24.4 | 22.2
| 2014-08-03 20:30 | 21.7 | 24.4 | 22.2
| 2014-08-03 21:00 | 20.4 | 24.4 | 22.2
| 2014-08-03 21:30 | 19.4 | 24.4 | 22.2
| 2014-08-03 22:00 | 18.7 | 24.4 | 22.2
| 2014-08-03 22:30 | 18.4 | 24.4 | 22.2
| 2014-08-03 23:00 | 18.1 | 24.4 | 22.2
| 2014-08-03 23:30 | 17.8 | 24.4 | 22.2
| 2014-08-04 | 18.3 | 24.4 | 22.2
| 2014-08-04 00:30 | 17.7 | 23.9 | 22.2
| 2014-08-04 01:00 | 17.1 | 23.9 | 22.2
| 2014-08-04 01:30 | 16.8 | 23.9 | 21.7
| 2014-08-04 02:00 | 16.6 | 23.9 | 21.7
| 2014-08-04 02:30 | 16.4 | 23.9 | 21.7
| 2014-08-04 03:00 | 16.2 | 23.3 | 21.7
| 2014-08-04 03:30 | 16.1 | 23.3 | 21.7
| 2014-08-04 04:00 | 15.7 | 23.3 | 21.7
| 2014-08-04 04:30 | 15.7 | 23.3 | 21.7
| 2014-08-04 05:00 | 15.2 | 23.3 | 21.7
| 2014-08-04 05:30 | 15.2 | 23.3 | 21.7
| 2014-08-04 06:00 | 15.3 | 22.8 | 21.7
| 2014-08-04 06:30 | 15.3 | 22.8 | 21.7
| 2014-08-04 07:00 | 15.9 | 22.8 | 21.7
| 2014-08-04 07:30 | 17.4 | 22.8 | 21.7
| 2014-08-04 08:00 | 17.7 | 22.2 | 21.7
| 2014-08-04 08:30 | 18.2 | 22.2 | 21.7
| 2014-08-04 09:00 | 19.3 | 22.2 | 21.7
| 2014-08-04 09:30 | 20.4 | 22.2 | 21.7
| 2014-08-04 10:00 | 20.7 | 22.2 | 21.7
| 2014-08-04 10:30 | 22.1 | 22.2 | 21.7
| 2014-08-04 11:00 | 22.8 | 22.2 | 21.7
| 2014-08-04 11:30 | 23.8 | 22.2 | 21.7
| 2014-08-04 12:00 | 23.3 | 22.2 | 21.7
| 2014-08-04 12:30 | 25.1 | 22.2 | 21.7
| 2014-08-04 13:00 | 25 | 22.8 | 21.7
| 2014-08-04 13:30 | 24.9 | 22.8 | 21.7
| 2014-08-04 14:00 | 25.1 | 23.3 | 21.7
| 2014-08-04 14:30 | 26.7 | 23.3 | 21.7
| 2014-08-04 15:00 | 27.2 | 23.3 | 21.7
| 2014-08-04 15:30 | 26.4 | 23.9 | 21.7
| 2014-08-04 16:00 | 27.4 | 23.9 | 21.7
| 2014-08-04 16:30 | 27.8 | 23.9 | 21.7
| 2014-08-04 17:00 | 28.2 | 24.4 | 21.7
| 2014-08-04 17:30 | 24.6 | 24.4 | 21.7
| 2014-08-04 18:00 | 24.1 | 24.4 | 21.7
| 2014-08-04 18:30 | 22.3 | 25 | 21.7
| 2014-08-04 19:00 | 19.3 | 25 | 21.7
| 2014-08-04 19:30 | 19 | 25 | 21.7
| 2014-08-04 20:00 | 18.7 | 25 | 21.7
| 2014-08-04 20:30 | 18.6 | 25 | 21.7
| 2014-08-04 21:00 | 18.1 | 25 | 21.7
| 2014-08-04 21:30 | 17.3 | 25 | 21.7
| 2014-08-04 22:00 | 16.8 | 25 | 21.7
| 2014-08-04 22:30 | 16.7 | 24.4 | 21.7
| 2014-08-04 23:00 | 16.4 | 24.4 | 21.7
| 2014-08-04 23:30 | 15.9 | 24.4 | 21.7
| 2014-08-05 | 15.7 | 24.4 | 21.7
| 2014-08-05 00:30 | 15.4 | 24.4 | 21.7
| 2014-08-05 01:00 | 15.1 | 23.9 | 21.7
| 2014-08-05 01:30 | 14.7 | 23.9 | 21.7
| 2014-08-05 02:00 | 14.5 | 23.9 | 21.7
| 2014-08-05 02:30 | 14.4 | 23.9 | 21.7
| 2014-08-05 03:00 | 14.2 | 23.3 | 21.7
| 2014-08-05 03:30 | 14 | 23.3 | 21.7
| 2014-08-05 04:00 | 13.8 | 23.3 | 21.7
| 2014-08-05 04:30 | 13.9 | 23.3 | 21.7
| 2014-08-05 05:00 | 13.9 | 22.8 | 21.7
| 2014-08-05 05:30 | 13.6 | 22.8 | 21.7
| 2014-08-05 06:00 | 13.5 | 22.8 | 21.7
| 2014-08-05 06:30 | 13.5 | 22.8 | 21.7
| 2014-08-05 07:00 | 13.9 | 22.2 | 21.7
| 2014-08-05 07:30 | 15.3 | 22.2 | 21.7
| 2014-08-05 08:00 | 15.5 | 22.2 | 21.7
| 2014-08-05 08:30 | 15.8 | 22.2 | 21.7
| 2014-08-05 09:00 | 16.6 | 22.2 | 21.7
| 2014-08-05 09:30 | 17.1 | 22.2 | 21.7
| 2014-08-05 10:00 | 17.6 | 21.7 | 21.7
| 2014-08-05 10:30 | 18.3 | 21.7 | 21.7
| 2014-08-05 11:00 | 19.6 | 21.7 | 21.7
| 2014-08-05 11:30 | 20.4 | 22.2 | 21.7
| 2014-08-05 12:00 | 20.4 | 22.2 | 21.7
| 2014-08-05 12:30 | 20.8 | 22.2 | 21.7
| 2014-08-05 13:00 | 21.3 | 22.2 | 21.7
| 2014-08-05 13:30 | 21.3 | 22.2 | 21.7
| 2014-08-05 14:00 | 21.2 | 22.2 | 21.7
| 2014-08-05 14:30 | 21.8 | 22.8 | 21.7
| 2014-08-05 15:00 | 22.3 | 22.8 | 21.7
| 2014-08-05 15:30 | 23.4 | 22.8 | 21.7
| 2014-08-05 16:00 | 24 | 22.8 | 21.7
| 2014-08-05 16:30 | 24.2 | 22.8 | 21.7
| 2014-08-05 17:00 | 23.3 | 23.3 | 21.7
| 2014-08-05 17:30 | 23.6 | 23.3 | 21.7
| 2014-08-05 18:00 | 23.9 | 23.3 | 21.7
| 2014-08-05 18:30 | 23.8 | 23.3 | 21.7
| 2014-08-05 19:00 | 23.9 | 23.9 | 21.7
| 2014-08-05 19:30 | 23.3 | 23.9 | 21.7
| 2014-08-05 20:00 | 23.1 | 23.9 | 21.7
| 2014-08-05 20:30 | 21.6 | 23.9 | 21.7
| 2014-08-05 21:00 | 19.8 | 23.9 | 21.7
| 2014-08-05 21:30 | 18.3 | 23.9 | 21.7
| 2014-08-05 22:00 | 17.6 | 23.9 | 21.7
| 2014-08-05 22:30 | 17 | 23.9 | 21.7
| 2014-08-05 23:00 | 16.7 | 23.9 | 21.7
| 2014-08-05 23:30 | 16.5 | 23.3 | 21.7
| 2014-08-06 | 16.1 | 23.3 | 21.7
| 2014-08-06 00:30 | 15.5 | 23.3 | 21.7
| 2014-08-06 01:00 | 15.1 | 23.3 | 21.7
| 2014-08-06 01:30 | 14.7 | 23.3 | 21.7
| 2014-08-06 02:00 | 14.2 | 23.3 | 21.7
| 2014-08-06 02:30 | 13.8 | 22.8 | 21.7
| 2014-08-06 03:00 | 13.2 | 22.8 | 21.7
| 2014-08-06 03:30 | 13.3 | 22.8 | 21.7
| 2014-08-06 04:00 | 12.9 | 22.8 | 21.7
| 2014-08-06 04:30 | 12.3 | 22.2 | 21.7
| 2014-08-06 05:00 | 12.4 | 22.2 | 21.7
| 2014-08-06 05:30 | 12.2 | 22.2 | 21.7
| 2014-08-06 06:00 | 12.3 | 22.2 | 21.7
| 2014-08-06 06:30 | 12.6 | 22.2 | 21.7
| 2014-08-06 07:00 | 13.2 | 21.7 | 21.7
| 2014-08-06 07:30 | 13.9 | 21.7 | 21.7
| 2014-08-06 08:00 | 14.8 | 21.7 | 21.7
| 2014-08-06 08:30 | 15.7 | 21.7 | 21.7
| 2014-08-06 09:00 | 17.1 | 21.7 | 21.7
| 2014-08-06 09:30 | 18.4 | 21.7 | 21.7
| 2014-08-06 10:00 | 19.8 | 21.7 | 21.7
| 2014-08-06 10:30 | 20.7 | 21.1 | 21.7
| 2014-08-06 11:00 | 21.9 | 21.1 | 21.7
| 2014-08-06 11:30 | 22.9 | 21.7 | 21.7
| 2014-08-06 12:00 | 23.8 | 21.7 | 21.7
| 2014-08-06 12:30 | 24.3 | 21.7 | 21.7
| 2014-08-06 13:00 | 24.9 | 21.7 | 21.7
| 2014-08-06 13:30 | 25.6 | 22.2 | 21.7
| 2014-08-06 14:00 | 26.4 | 22.2 | 21.7
| 2014-08-06 14:30 | 26.3 | 22.2 | 21.7
| 2014-08-06 15:00 | 26.7 | 22.8 | 21.7
| 2014-08-06 15:30 | 27.6 | 23.3 | 21.7
| 2014-08-06 16:00 | 26.8 | 23.3 | 21.7
| 2014-08-06 16:30 | 26.8 | 23.9 | 21.7
| 2014-08-06 17:00 | 26.8 | 23.9 | 21.7
| 2014-08-06 17:30 | 26.1 | 23.9 | 21.7
| 2014-08-06 18:00 | 26.3 | 24.4 | 21.7
| 2014-08-06 18:30 | 25.2 | 24.4 | 21.7
| 2014-08-06 19:00 | 24.7 | 24.4 | 21.7
| 2014-08-06 19:30 | 23.9 | 24.4 | 21.7
| 2014-08-06 20:00 | 23.1 | 24.4 | 21.7
| 2014-08-06 20:30 | 22.2 | 24.4 | 21.7
| 2014-08-06 21:00 | 21 | 24.4 | 21.7
| 2014-08-06 21:30 | 21.1 | 24.4 | 21.7
| 2014-08-06 22:00 | 20.3 | 24.4 | 21.7
| 2014-08-06 22:30 | 19.5 | 24.4 | 21.7
| 2014-08-06 23:00 | 18.9 | 24.4 | 21.7
| 2014-08-06 23:30 | 18.4 | 24.4 | 21.7
| 2014-08-07 | 18 | 24.4 | 21.7
| 2014-08-07 00:30 | 17.8 | 24.4 | 21.7
| 2014-08-07 01:00 | 17.9 | 24.4 | 21.7
| 2014-08-07 01:30 | 17.8 | 23.9 | 21.7
| 2014-08-07 02:00 | 17.8 | 23.9 | 21.7
| 2014-08-07 02:30 | 17.7 | 23.9 | 21.7
| 2014-08-07 03:00 | 17.6 | 23.9 | 21.7
| 2014-08-07 03:30 | 17.7 | 23.9 | 21.7
| 2014-08-07 04:00 | 17.7 | 23.9 | 21.7
| 2014-08-07 04:30 | 17.4 | 23.9 | 21.7
| 2014-08-07 05:00 | 17.3 | 23.3 | 21.7
| 2014-08-07 05:30 | 17 | 23.3 | 21.7
| 2014-08-07 06:00 | 16.5 | 23.3 | 21.7
| 2014-08-07 06:30 | 16.1 | 23.3 | 21.7
| 2014-08-07 07:00 | 16.1 | 23.3 | 21.7
| 2014-08-07 07:30 | 16.2 | 23.3 | 21.7
| 2014-08-07 08:00 | 16.4 | 23.3 | 21.7
| 2014-08-07 08:30 | 16.7 | 23.3 | 21.7
| 2014-08-07 09:00 | 17.1 | 22.8 | 21.7
| 2014-08-07 09:30 | 17.6 | 22.8 | 21.7
| 2014-08-07 10:00 | 17.9 | 22.8 | 21.7
| 2014-08-07 10:30 | 18.7 | 22.8 | 21.7
| 2014-08-07 11:00 | 19.7 | 22.8 | 21.7
| 2014-08-07 11:30 | 20.6 | 22.8 | 21.7
| 2014-08-07 12:00 | 21.6 | 22.8 | 21.7
| 2014-08-07 12:30 | 21.9 | 22.8 | 21.7
| 2014-08-07 13:00 | 23.1 | 22.8 | 21.7
| 2014-08-07 13:30 | 24.3 | 22.8 | 21.7
| 2014-08-07 14:00 | 25.2 | 23.3 | 21.7
| 2014-08-07 14:30 | 24.8 | 23.3 | 21.7
| 2014-08-07 15:00 | 24.8 | 23.3 | 21.7
| 2014-08-07 15:30 | 24.7 | 23.9 | 21.7
| 2014-08-07 16:00 | 25.3 | 23.9 | 21.7
| 2014-08-07 16:30 | 25.2 | 23.9 | 21.7
| 2014-08-07 17:00 | 25.5 | 24.4 | 21.7
| 2014-08-07 17:30 | 25.3 | 24.4 | 21.7
| 2014-08-07 18:00 | 25.1 | 24.4 | 21.7
| 2014-08-07 18:30 | 25.2 | 24.4 | 21.7
| 2014-08-07 19:00 | 26.6 | 24.4 | 21.7
| 2014-08-07 19:30 | 25.8 | 24.4 | 21.7
| 2014-08-07 20:00 | 25.8 | 24.4 | 21.7
| 2014-08-07 20:30 | 24.8 | 24.4 | 21.7
| 2014-08-07 21:00 | 21.7 | 24.4 | 21.7
| 2014-08-07 21:30 | 19.9 | 24.4 | 21.7
| 2014-08-07 22:00 | 18.8 | 24.4 | 21.7
| 2014-08-07 22:30 | 18.2 | 24.4 | 21.7
| 2014-08-07 23:00 | 17.3 | 24.4 | 21.7
| 2014-08-07 23:30 | 17.3 | 24.4 | 21.7
| 2014-08-08 | 17 | 24.4 | 21.7
| 2014-08-08 00:30 | 16.6 | 24.4 | 21.7
| 2014-08-08 01:00 | 16.1 | 23.9 | 21.7
| 2014-08-08 01:30 | 15.6 | 23.9 | 21.7
| 2014-08-08 02:00 | 15.2 | 23.9 | 21.7
| 2014-08-08 02:30 | 14.7 | 23.9 | 21.7
| 2014-08-08 03:00 | 14.5 | 23.9 | 21.7
| 2014-08-08 03:30 | 14.2 | 23.9 | 21.7
| 2014-08-08 04:00 | 13.6 | 23.3 | 21.7
| 2014-08-08 04:30 | 13.8 | 23.3 | 21.7
| 2014-08-08 05:00 | 13.6 | 23.3 | 21.7
| 2014-08-08 05:30 | 13.5 | 23.3 | 21.7
| 2014-08-08 06:00 | 12.8 | 23.3 | 21.7
| 2014-08-08 06:30 | 13.1 | 22.8 | 21.7
| 2014-08-08 07:00 | 12.9 | 22.8 | 21.7
| 2014-08-08 07:30 | 13.6 | 22.8 | 21.7
| 2014-08-08 08:00 | 14.8 | 22.8 | 21.7
| 2014-08-08 08:30 | 16.1 | 22.2 | 21.7
| 2014-08-08 09:00 | 18.6 | 22.2 | 21.7
| 2014-08-08 09:30 | 20.3 | 22.2 | 21.7
| 2014-08-08 10:00 | 21.9 | 22.2 | 21.7
| 2014-08-08 10:30 | 23.3 | 22.2 | 21.7
| 2014-08-08 11:00 | 24.3 | 22.2 | 21.7
| 2014-08-08 11:30 | 25.8 | 22.2 | 21.7
| 2014-08-08 12:00 | 26.4 | 22.2 | 21.7
| 2014-08-08 12:30 | 27.2 | 22.2 | 21.7
| 2014-08-08 13:00 | 27.3 | 22.8 | 21.7
| 2014-08-08 13:30 | 27.7 | 22.8 | 21.7
| 2014-08-08 14:00 | 29.2 | 22.8 | 21.7
| 2014-08-08 14:30 | 28.1 | 23.3 | 21.7
| 2014-08-08 15:00 | 28.3 | 23.3 | 21.7
| 2014-08-08 15:30 | 28.1 | 23.9 | 21.7
| 2014-08-08 16:00 | 28.3 | 23.9 | 21.7
| 2014-08-08 16:30 | 28.1 | 23.9 | 21.7
| 2014-08-08 17:00 | 27.2 | 24.4 | 21.7
| 2014-08-08 17:30 | 24.6 | 24.4 | 21.7
| 2014-08-08 18:00 | 25.4 | 24.4 | 21.7
| 2014-08-08 18:30 | 26.1 | 24.4 | 21.7
| 2014-08-08 19:00 | 27.5 | 24.4 | 21.7
| 2014-08-08 19:30 | 27.1 | 25 | 21.7
| 2014-08-08 20:00 | 26.4 | 25 | 21.7
| 2014-08-08 20:30 | 24.7 | 25 | 21.7
| 2014-08-08 21:00 | 23.3 | 25 | 21.7
| 2014-08-08 21:30 | 21.9 | 25 | 21.7
| 2014-08-08 22:00 | 21.1 | 25 | 21.7
| 2014-08-08 22:30 | 20.7 | 25 | 21.7
| 2014-08-08 23:00 | 20.2 | 24.4 | 21.7
| 2014-08-08 23:30 | 20 | 24.4 | 21.7
| 2014-08-09 | 19.7 | 24.4 | 21.7
| 2014-08-09 00:30 | 19.3 | 24.4 | 21.7
| 2014-08-09 01:00 | 18.9 | 24.4 | 21.7
| 2014-08-09 01:30 | 18.8 | 24.4 | 21.7
| 2014-08-09 02:00 | 18.6 | 24.4 | 21.7
| 2014-08-09 02:30 | 18.4 | 23.9 | 21.7
| 2014-08-09 03:00 | 18.4 | 23.9 | 21.7
| 2014-08-09 03:30 | 18.3 | 23.9 | 21.7
| 2014-08-09 04:00 | 18 | 23.9 | 21.7
| 2014-08-09 04:30 | 20.5 | 23.9 | 21.7
| 2014-08-09 05:00 | 20.9 | 23.9 | 21.7
| 2014-08-09 05:30 | 20.4 | 23.9 | 21.7
| 2014-08-09 06:00 | 20.5 | 23.3 | 21.7
| 2014-08-09 06:30 | 20.7 | 23.3 | 21.7
| 2014-08-09 07:00 | 20.8 | 23.3 | 21.7
| 2014-08-09 07:30 | 21.1 | 23.3 | 21.7
| 2014-08-09 08:00 | 21.8 | 23.3 | 21.7
| 2014-08-09 08:30 | 21.6 | 23.3 | 21.7
| 2014-08-09 09:00 | 22.2 | 23.3 | 21.7
| 2014-08-09 09:30 | 21.8 | 23.3 | 21.7
| 2014-08-09 10:00 | 22.5 | 23.3 | 21.7
| 2014-08-09 10:30 | 22.3 | 23.3 | 21.7
| 2014-08-09 11:00 | 22.6 | 23.3 | 21.7
| 2014-08-09 11:30 | 23.6 | 23.3 | 21.7
| 2014-08-09 12:00 | 25 | 23.3 | 21.7
| 2014-08-09 12:30 | 24.6 | 23.3 | 21.7
| 2014-08-09 13:00 | 23.8 | 23.3 | 21.7
| 2014-08-09 13:30 | 23.6 | 23.3 | 21.7
| 2014-08-09 14:00 | 24.7 | 23.3 | 21.7
| 2014-08-09 14:30 | 25.6 | 23.3 | 21.7
| 2014-08-09 15:00 | 25.2 | 23.9 | 21.7
| 2014-08-09 15:30 | 25.2 | 23.9 | 21.7
| 2014-08-09 16:00 | 26.8 | 23.9 | 21.7
| 2014-08-09 16:30 | 26.5 | 23.9 | 21.7
| 2014-08-09 17:00 | 26.8 | 24.4 | 21.7
| 2014-08-09 17:30 | 26.4 | 24.4 | 21.7
| 2014-08-09 18:00 | 26.1 | 24.4 | 21.7
| 2014-08-09 18:30 | 25.9 | 24.4 | 21.7
| 2014-08-09 19:00 | 25.3 | 25 | 21.7
| 2014-08-09 19:30 | 24.7 | 25 | 21.7
| 2014-08-09 20:00 | 24.2 | 25 | 21.7
| 2014-08-09 20:30 | 22.9 | 25 | 21.7
| 2014-08-09 21:00 | 20.8 | 25 | 21.7
| 2014-08-09 21:30 | 19.2 | 25 | 21.7
| 2014-08-09 22:00 | 17.9 | 25 | 21.7
| 2014-08-09 22:30 | 17.2 | 25 | 21.7
| 2014-08-09 23:00 | 16.6 | 25 | 21.7
| 2014-08-09 23:30 | 16.6 | 25 | 21.7
| 2014-08-10 | 16.3 | 24.4 | 21.7
| 2014-08-10 00:30 | 16.4 | 24.4 | 21.7
| 2014-08-10 01:00 | 16.4 | 24.4 | 21.7
| 2014-08-10 01:30 | 17.1 | 24.4 | 21.7
| 2014-08-10 02:00 | 17.7 | 24.4 | 21.7
| 2014-08-10 02:30 | 18.1 | 23.9 | 21.7
| 2014-08-10 03:00 | 17.2 | 23.9 | 21.7
| 2014-08-10 03:30 | 16.6 | 23.9 | 21.7
| 2014-08-10 04:00 | 16.3 | 23.9 | 21.7
| 2014-08-10 04:30 | 16.3 | 23.9 | 21.7
| 2014-08-10 05:00 | 16.1 | 23.9 | 21.7
| 2014-08-10 05:30 | 16.1 | 23.9 | 21.7
| 2014-08-10 06:00 | 15.9 | 23.3 | 21.7
| 2014-08-10 06:30 | 15.7 | 23.3 | 21.7
| 2014-08-10 07:00 | 15.6 | 23.3 | 21.7
| 2014-08-10 07:30 | 15.7 | 23.3 | 21.7
| 2014-08-10 08:00 | 16.1 | 23.3 | 21.7
| 2014-08-10 08:30 | 16.7 | 23.3 | 21.7
| 2014-08-10 09:00 | 17.3 | 22.8 | 21.7
| 2014-08-10 09:30 | 17.7 | 22.8 | 21.7
| 2014-08-10 10:00 | 18.8 | 22.8 | 21.7
| 2014-08-10 10:30 | 20.6 | 22.8 | 21.7
| 2014-08-10 11:00 | 23.1 | 22.8 | 21.7
| 2014-08-10 11:30 | 24.3 | 22.8 | 21.7
| 2014-08-10 12:00 | 25.4 | 22.8 | 21.7
| 2014-08-10 12:30 | 25.2 | 22.8 | 21.7
| 2014-08-10 13:00 | 26.9 | 23.3 | 21.7
| 2014-08-10 13:30 | 25.9 | 23.3 | 21.7
| 2014-08-10 14:00 | 25.8 | 23.3 | 21.7
| 2014-08-10 14:30 | 26.1 | 23.3 | 21.7
| 2014-08-10 15:00 | 25.7 | 23.9 | 21.7
| 2014-08-10 15:30 | 25.2 | 23.9 | 21.7
| 2014-08-10 16:00 | 25.3 | 23.9 | 21.7
| 2014-08-10 16:30 | 25.3 | 23.9 | 21.7
| 2014-08-10 17:00 | 25.9 | 23.9 | 21.7
| 2014-08-10 17:30 | 26.4 | 23.9 | 21.7
| 2014-08-10 18:00 | 25.6 | 24.4 | 21.7
| 2014-08-10 18:30 | 25 | 24.4 | 21.7
| 2014-08-10 19:00 | 23.7 | 24.4 | 21.7
| 2014-08-10 19:30 | 20.6 | 24.4 | 21.7
| 2014-08-10 20:00 | 19.1 | 24.4 | 21.7
| 2014-08-10 20:30 | 17.9 | 24.4 | 21.7
| 2014-08-10 21:00 | 17.9 | 23.9 | 21.7
| 2014-08-10 21:30 | 18.3 | 23.9 | 21.7
| 2014-08-10 22:00 | 18.3 | 23.9 | 21.7
| 2014-08-10 22:30 | 18.6 | 23.9 | 21.7
| 2014-08-10 23:00 | 18.8 | 23.9 | 21.7
| 2014-08-10 23:30 | 18.6 | 23.9 | 21.7
| 2014-08-11 | 18.6 | 23.9 | 21.7
| 2014-08-11 00:30 | 18.6 | 23.3 | 21.7
| 2014-08-11 01:00 | 18.7 | 23.3 | 21.7
| 2014-08-11 01:30 | 19 | 23.3 | 21.7
| 2014-08-11 02:00 | 18.8 | 23.3 | 21.7
| 2014-08-11 02:30 | 18.7 | 23.3 | 21.7
| 2014-08-11 03:00 | 18.3 | 23.3 | 21.7
| 2014-08-11 03:30 | 17.3 | 22.8 | 21.7
| 2014-08-11 04:00 | 16.7 | 22.8 | 21.7
| 2014-08-11 04:30 | 15.8 | 22.8 | 21.7
| 2014-08-11 05:00 | 15.2 | 22.8 | 21.7
| 2014-08-11 05:30 | 14.2 | 22.8 | 21.7
| 2014-08-11 06:00 | 13.4 | 22.2 | 21.7
| 2014-08-11 06:30 | 13.2 | 22.2 | 21.7
| 2014-08-11 07:00 | 13.6 | 22.2 | 21.7
| 2014-08-11 07:30 | 13.9 | 22.2 | 21.7
| 2014-08-11 08:00 | 15.7 | 22.2 | 21.7
| 2014-08-11 08:30 | 16.2 | 21.7 | 21.7
| 2014-08-11 09:00 | 17.7 | 21.7 | 21.7
| 2014-08-11 09:30 | 18.4 | 21.7 | 21.7
| 2014-08-11 10:00 | 19.1 | 21.7 | 21.7
| 2014-08-11 10:30 | 19.9 | 21.7 | 21.7
| 2014-08-11 11:00 | 21.1 | 21.7 | 21.7
| 2014-08-11 11:30 | 21.7 | 21.7 | 21.7
| 2014-08-11 12:00 | 22.2 | 21.7 | 21.7
| 2014-08-11 12:30 | 22.9 | 21.7 | 21.7
| 2014-08-11 13:00 | 22.4 | 21.7 | 21.7
| 2014-08-11 13:30 | 23.9 | 21.7 | 21.7
| 2014-08-11 14:00 | 23.7 | 22.2 | 21.7
| 2014-08-11 14:30 | 23.6 | 22.2 | 21.7
| 2014-08-11 15:00 | 23.3 | 22.2 | 21.7
| 2014-08-11 15:30 | 22.6 | 22.8 | 21.7
| 2014-08-11 16:00 | 21.9 | 22.8 | 21.7
| 2014-08-11 16:30 | 22.5 | 22.8 | 21.7
| 2014-08-11 17:00 | 21.1 | 23.3 | 21.7
| 2014-08-11 17:30 | 20.3 | 23.3 | 21.7
| 2014-08-11 18:00 | 20.2 | 23.3 | 21.7
| 2014-08-11 18:30 | 20.9 | 23.3 | 21.7
| 2014-08-11 19:00 | 20.6 | 23.3 | 21.7
| 2014-08-11 19:30 | 20.3 | 23.3 | 21.7
| 2014-08-11 20:00 | 19.7 | 23.3 | 21.7
| 2014-08-11 20:30 | 18.8 | 23.3 | 21.7
| 2014-08-11 21:00 | 17.6 | 23.3 | 21.7
| 2014-08-11 21:30 | 16.3 | 22.8 | 21.7
| 2014-08-11 22:00 | 15.8 | 22.8 | 21.7
| 2014-08-11 22:30 | 15.6 | 22.8 | 21.7
| 2014-08-11 23:00 | 15.4 | 22.8 | 21.7
| 2014-08-11 23:30 | 14.7 | 22.8 | 21.7
| 2014-08-12 | 14.7 | 22.2 | 21.7
| 2014-08-12 00:30 | 14.4 | 22.2 | 21.7
| 2014-08-12 01:00 | 13.7 | 22.2 | 21.7
| 2014-08-12 01:30 | 13.3 | 22.2 | 21.7
| 2014-08-12 02:00 | 13.2 | 21.7 | 21.7
| 2014-08-12 02:30 | 14.1 | 21.7 | 21.7
| 2014-08-12 03:00 | 14.6 | 21.7 | 21.7
| 2014-08-12 03:30 | 14.3 | 21.7 | 21.7
| 2014-08-12 04:00 | 14.9 | 21.1 | 21.7
| 2014-08-12 04:30 | 15 | 21.1 | 21.7
| 2014-08-12 05:00 | 15.1 | 21.1 | 21.7
| 2014-08-12 05:30 | 15.1 | 21.1 | 21.7
| 2014-08-12 06:00 | 14.4 | 21.1 | 21.7
| 2014-08-12 06:30 | 14.7 | 20.6 | 21.7
| 2014-08-12 07:00 | 15.2 | 20.6 | 21.7
| 2014-08-12 07:30 | 15.4 | 20.6 | 21.7
| 2014-08-12 08:00 | 16.6 | 20.6 | 21.7
| 2014-08-12 08:30 | 16.8 | 20.6 | 21.7
| 2014-08-12 09:00 | 17.6 | 20.6 | 21.7
| 2014-08-12 09:30 | 18.1 | 20.6 | 21.7
| 2014-08-12 10:00 | 19 | 20.6 | 21.7
| 2014-08-12 10:30 | 19.8 | 20.6 | 21.7
| 2014-08-12 11:00 | 21.2 | 20.6 | 21.7
| 2014-08-12 11:30 | 20 | 20.6 | 21.7
| 2014-08-12 12:00 | 21.2 | 20.6 | 21.7
| 2014-08-12 12:30 | 22.8 | 20.6 | 21.7
| 2014-08-12 13:00 | 23 | 20.6 | 21.7
| 2014-08-12 13:30 | 23.4 | 21.1 | 21.7
| 2014-08-12 14:00 | 23.7 | 21.1 | 21.7
| 2014-08-12 14:30 | 23.8 | 21.1 | 21.7
| 2014-08-12 15:00 | 22.2 | 21.7 | 21.7
| 2014-08-12 15:30 | 23.7 | 21.7 | 21.7
| 2014-08-12 16:00 | 23.6 | 22.2 | 21.7
| 2014-08-12 16:30 | 24.7 | 22.2 | 21.7
| 2014-08-12 17:00 | 24.7 | 22.2 | 21.7
| 2014-08-12 17:30 | 23.4 | 22.2 | 21.7
| 2014-08-12 18:00 | 24.1 | 22.8 | 21.7
| 2014-08-12 18:30 | 23.5 | 22.8 | 21.7
| 2014-08-12 19:00 | 22.8 | 22.8 | 21.7
| 2014-08-12 19:30 | 22.2 | 22.8 | 21.7
| 2014-08-12 20:00 | 21.3 | 22.8 | 21.7
| 2014-08-12 20:30 | 19.4 | 22.8 | 21.7
| 2014-08-12 21:00 | 17.8 | 22.8 | 21.7
| 2014-08-12 21:30 | 16.8 | 22.8 | 21.7
| 2014-08-12 22:00 | 16.2 | 22.8 | 21.7
| 2014-08-12 22:30 | 15.6 | 22.2 | 21.7
| 2014-08-12 23:00 | 15.2 | 22.2 | 21.7
| 2014-08-12 23:30 | 14.5 | 22.2 | 21.7
| 2014-08-13 | 14.3 | 22.2 | 21.7
| 2014-08-13 00:30 | 14.4 | 22.2 | 21.7
| 2014-08-13 01:00 | 14.3 | 21.7 | 21.7
| 2014-08-13 01:30 | 14.4 | 21.7 | 21.7
| 2014-08-13 02:00 | 14.5 | 21.7 | 21.7
| 2014-08-13 02:30 | 14.7 | 21.7 | 21.7
| 2014-08-13 03:00 | 14.7 | 21.7 | 21.7
| 2014-08-13 03:30 | 14.4 | 21.1 | 21.7
| 2014-08-13 04:00 | 13.9 | 21.1 | 21.7
| 2014-08-13 04:30 | 13.4 | 21.1 | 21.7
| 2014-08-13 05:00 | 12.9 | 21.1 | 21.7
| 2014-08-13 05:30 | 12.6 | 21.1 | 21.7
| 2014-08-13 06:00 | 12.3 | 21.1 | 21.7
| 2014-08-13 06:30 | 12.8 | 20.6 | 21.7
| 2014-08-13 07:00 | 13.4 | 20.6 | 21.7
| 2014-08-13 07:30 | 13.7 | 20.6 | 21.7
| 2014-08-13 08:00 | 14.9 | 20.6 | 21.1
| 2014-08-13 08:30 | 16.6 | 20.6 | 21.1
| 2014-08-13 09:00 | 17.5 | 20.6 | 21.1
| 2014-08-13 09:30 | 18.3 | 20 | 21.1
| 2014-08-13 10:00 | 18.9 | 20 | 21.1
| 2014-08-13 10:30 | 19.9 | 20 | 21.1
| 2014-08-13 11:00 | 20.3 | 20 | 21.1
| 2014-08-13 11:30 | 20.3 | 20 | 21.1
| 2014-08-13 12:00 | 20.5 | 20.6 | 21.1
| 2014-08-13 12:30 | 20.2 | 20.6 | 21.1
| 2014-08-13 13:00 | 19.6 | 20.6 | 21.1
| 2014-08-13 13:30 | 18.7 | 20.6 | 21.1
| 2014-08-13 14:00 | 18.1 | 20.6 | 21.1
| 2014-08-13 14:30 | 18.1 | 20.6 | 21.1
| 2014-08-13 15:00 | 17.9 | 20.6 | 21.1
| 2014-08-13 15:30 | 17.9 | 20.6 | 21.1
| 2014-08-13 16:00 | 18.1 | 20.6 | 21.1
| 2014-08-13 16:30 | 17.3 | 20.6 | 21.1
| 2014-08-13 17:00 | 16.2 | 20.6 | 21.1
| 2014-08-13 17:30 | 16.1 | 20.6 | 21.1
| 2014-08-13 18:00 | 16.6 | 20.6 | 21.1
| 2014-08-13 18:30 | 16.5 | 20.6 | 21.1
| 2014-08-13 19:00 | 16.2 | 20.6 | 21.1
| 2014-08-13 19:30 | 15.9 | 20.6 | 21.1
| 2014-08-13 20:00 | 15.6 | 20.6 | 21.1
| 2014-08-13 20:30 | 15.5 | 20.6 | 21.1
| 2014-08-13 21:00 | 15.3 | 20.6 | 21.1
| 2014-08-13 21:30 | 15.2 | 20.6 | 21.1
| 2014-08-13 22:00 | 15.1 | 20.6 | 21.1
| 2014-08-13 22:30 | 15 | 20.6 | 21.1
| 2014-08-13 23:00 | 14.9 | 20.6 | 21.1
| 2014-08-13 23:30 | 14.8 | 20.6 | 21.1
| 2014-08-14 | 14.8 | 20.6 | 21.1
| 2014-08-14 00:30 | 14.7 | 20 | 21.1
| 2014-08-14 01:00 | 13.9 | 20 | 21.1
| 2014-08-14 01:30 | 13.9 | 20 | 21.1
| 2014-08-14 02:00 | 13.9 | 20 | 21.1
| 2014-08-14 02:30 | 13.8 | 20 | 21.1
| 2014-08-14 03:00 | 14.1 | 20 | 21.1
| 2014-08-14 03:30 | 14.4 | 20 | 21.1
| 2014-08-14 04:00 | 14.4 | 20 | 21.1
| 2014-08-14 04:30 | 14.3 | 19.4 | 21.1
| 2014-08-14 05:00 | 14.2 | 19.4 | 21.1
| 2014-08-14 05:30 | 13.8 | 19.4 | 21.1
| 2014-08-14 06:00 | 13.4 | 19.4 | 21.1
| 2014-08-14 06:30 | 13.1 | 19.4 | 21.1
| 2014-08-14 07:00 | 13.5 | 19.4 | 21.1
| 2014-08-14 07:30 | 13.6 | 19.4 | 21.1
| 2014-08-14 08:00 | 14.1 | 19.4 | 21.1
| 2014-08-14 08:30 | 14.8 | 18.9 | 21.1
| 2014-08-14 09:00 | 15.9 | 18.9 | 21.1
| 2014-08-14 09:30 | 16.4 | 18.9 | 21.1
| 2014-08-14 10:00 | 16.3 | 18.9 | 21.1
| 2014-08-14 10:30 | 17.6 | 18.9 | 21.1
| 2014-08-14 11:00 | 17.6 | 18.9 | 21.1
| 2014-08-14 11:30 | 19.6 | 18.9 | 21.1
| 2014-08-14 12:00 | 19.4 | 18.9 | 21.1
| 2014-08-14 12:30 | 20.2 | 19.4 | 21.1
| 2014-08-14 13:00 | 20.4 | 19.4 | 21.1
| 2014-08-14 13:30 | 20.4 | 19.4 | 21.1
| 2014-08-14 14:00 | 20.2 | 20 | 21.1
| 2014-08-14 14:30 | 20.3 | 20 | 21.1
| 2014-08-14 15:00 | 20.8 | 20.6 | 21.1
| 2014-08-14 15:30 | 19.5 | 20.6 | 21.1
| 2014-08-14 16:00 | 21.1 | 20.6 | 21.1
| 2014-08-14 16:30 | 20.6 | 21.1 | 21.1
| 2014-08-14 17:00 | 20.8 | 21.1 | 21.1
| 2014-08-14 17:30 | 21.4 | 21.1 | 21.1
| 2014-08-14 18:00 | 20.9 | 21.1 | 21.1
| 2014-08-14 18:30 | 18.8 | 21.1 | 21.1
| 2014-08-14 19:00 | 17.6 | 21.7 | 21.1
| 2014-08-14 19:30 | 18.1 | 21.7 | 21.1
| 2014-08-14 20:00 | 16.4 | 21.7 | 21.1
| 2014-08-14 20:30 | 15.4 | 21.7 | 21.1
| 2014-08-14 21:00 | 14.6 | 21.1 | 21.1
| 2014-08-14 21:30 | 13.9 | 21.1 | 21.1
| 2014-08-14 22:00 | 13.9 | 21.1 | 21.1
| 2014-08-14 22:30 | 14.4 | 21.1 | 21.1
| 2014-08-14 23:00 | 14.2 | 21.1 | 21.1
| 2014-08-14 23:30 | 13.8 | 21.1 | 21.1
| 2014-08-15 | 13.6 | 20.6 | 21.1
| 2014-08-15 00:30 | 13.4 | 20.6 | 21.1
| 2014-08-15 01:00 | 13.4 | 20.6 | 21.1
| 2014-08-15 01:30 | 13.2 | 20.6 | 21.1
| 2014-08-15 02:00 | 13.4 | 20.6 | 21.1
| 2014-08-15 02:30 | 13.7 | 20 | 21.1
| 2014-08-15 03:00 | 13.8 | 20 | 21.1
| 2014-08-15 03:30 | 13.8 | 20 | 21.1
| 2014-08-15 04:00 | 13.6 | 20 | 21.1
| 2014-08-15 04:30 | 13.6 | 20 | 21.1
| 2014-08-15 05:00 | 13.8 | 20 | 21.1
| 2014-08-15 05:30 | 13.9 | 19.4 | 21.1
| 2014-08-15 06:00 | 13.6 | 19.4 | 21.1
| 2014-08-15 06:30 | 13.8 | 19.4 | 21.1
| 2014-08-15 07:00 | 13.9 | 19.4 | 21.1
| 2014-08-15 07:30 | 14.1 | 19.4 | 20.6
| 2014-08-15 08:00 | 14.3 | 19.4 | 20.6
| 2014-08-15 08:30 | 14.6 | 19.4 | 20.6
| 2014-08-15 09:00 | 15 | 19.4 | 20.6
| 2014-08-15 09:30 | 15.6 | 18.9 | 20.6
| 2014-08-15 10:00 | 15.8 | 18.9 | 20.6
| 2014-08-15 10:30 | 15.7 | 18.9 | 20.6
| 2014-08-15 11:00 | 16.6 | 18.9 | 20.6
| 2014-08-15 11:30 | 16.7 | 19.4 | 20.6
| 2014-08-15 12:00 | 17.2 | 19.4 | 20.6
| 2014-08-15 12:30 | 17.3 | 19.4 | 20.6
| 2014-08-15 13:00 | 17.4 | 19.4 | 20.6
| 2014-08-15 13:30 | 16.4 | 19.4 | 20.6
| 2014-08-15 14:00 | 13.9 | 19.4 | 20.6
| 2014-08-15 14:30 | 13.9 | 19.4 | 20.6
| 2014-08-15 15:00 | 14.6 | 19.4 | 20.6
| 2014-08-15 15:30 | 15.7 | 19.4 | 20.6
| 2014-08-15 16:00 | 15.9 | 19.4 | 20.6
| 2014-08-15 16:30 | 13.3 | 19.4 | 20.6
| 2014-08-15 17:00 | 12.9 | 19.4 | 20.6
| 2014-08-15 17:30 | 12.7 | 19.4 | 20.6
| 2014-08-15 18:00 | 12.9 | 19.4 | 20.6
| 2014-08-15 18:30 | 13.3 | 19.4 | 20.6
| 2014-08-15 19:00 | 13.5 | 19.4 | 20.6
| 2014-08-15 19:30 | 13.8 | 19.4 | 20.6
| 2014-08-15 20:00 | 13.7 | 19.4 | 20.6
| 2014-08-15 20:30 | 13.5 | 19.4 | 20.6
| 2014-08-15 21:00 | 13.1 | 19.4 | 20.6
| 2014-08-15 21:30 | 12.6 | 18.9 | 20.6
| 2014-08-15 22:00 | 12.4 | 18.9 | 20.6
| 2014-08-15 22:30 | 12.6 | 18.9 | 20.6
| 2014-08-15 23:00 | 12.8 | 18.9 | 20.6
| 2014-08-15 23:30 | 12.5 | 18.9 | 20.6
| 2014-08-16 | 12.7 | 18.9 | 20.6
| 2014-08-16 00:30 | 12.8 | 18.9 | 20.6
| 2014-08-16 01:00 | 12.8 | 18.9 | 20.6
| 2014-08-16 01:30 | 12.8 | 18.3 | 20.6
| 2014-08-16 02:00 | 12.8 | 18.3 | 20.6
| 2014-08-16 02:30 | 12.8 | 18.3 | 20.6
| 2014-08-16 03:00 | 12.7 | 18.3 | 20.6
| 2014-08-16 03:30 | 12.7 | 18.3 | 20.6
| 2014-08-16 04:00 | 12.4 | 18.3 | 20.6
| 2014-08-16 04:30 | 12.3 | 18.3 | 20.6
| 2014-08-16 05:00 | 12.7 | 18.3 | 20.6
| 2014-08-16 05:30 | 12.9 | 18.3 | 20.6
| 2014-08-16 06:00 | 12.9 | 18.3 | 20.6
| 2014-08-16 06:30 | 12.9 | 18.3 | 20.6
| 2014-08-16 07:00 | 13.2 | 17.8 | 20.6
| 2014-08-16 07:30 | 13.4 | 17.8 | 20.6
| 2014-08-16 08:00 | 13.6 | 17.8 | 20.6
| 2014-08-16 08:30 | 14.1 | 17.8 | 20.6
| 2014-08-16 09:00 | 15.3 | 17.8 | 20.6
| 2014-08-16 09:30 | 15.2 | 17.8 | 20.6
| 2014-08-16 10:00 | 16.2 | 17.8 | 20.6
| 2014-08-16 10:30 | 16.9 | 17.8 | 20.6
| 2014-08-16 11:00 | 16.9 | 17.8 | 20.6
| 2014-08-16 11:30 | 17.7 | 17.8 | 20.6
| 2014-08-16 12:00 | 18.5 | 17.8 | 20.6
| 2014-08-16 12:30 | 19.2 | 18.3 | 20.6
| 2014-08-16 13:00 | 19.2 | 18.3 | 20.6
| 2014-08-16 13:30 | 16.1 | 18.3 | 20.6
| 2014-08-16 14:00 | 16.9 | 18.3 | 20.6
| 2014-08-16 14:30 | 16.3 | 18.9 | 20.6
| 2014-08-16 15:00 | 18.4 | 18.9 | 20.6
| 2014-08-16 15:30 | 18.6 | 18.9 | 20.6
| 2014-08-16 16:00 | 19 | 18.9 | 20.6
| 2014-08-16 16:30 | 18.9 | 19.4 | 20.6
| 2014-08-16 17:00 | 18.6 | 19.4 | 20.6
| 2014-08-16 17:30 | 18.4 | 19.4 | 20.6
| 2014-08-16 18:00 | 19.6 | 19.4 | 20.6
| 2014-08-16 18:30 | 19.9 | 19.4 | 20.6
| 2014-08-16 19:00 | 19.9 | 19.4 | 20.6
| 2014-08-16 19:30 | 18.5 | 20 | 20.6
| 2014-08-16 20:00 | 16.8 | 20 | 20.6
| 2014-08-16 20:30 | 15.8 | 20 | 20.6
| 2014-08-16 21:00 | 15.4 | 20 | 20.6
| 2014-08-16 21:30 | 14.7 | 20 | 20.6
| 2014-08-16 22:00 | 14.3 | 19.4 | 20.6
| 2014-08-16 22:30 | 14.2 | 19.4 | 20.6
| 2014-08-16 23:00 | 14 | 19.4 | 20.6
| 2014-08-16 23:30 | 13.8 | 19.4 | 20
| 2014-08-17 | 13.6 | 19.4 | 20
| 2014-08-17 00:30 | 13.6 | 19.4 | 20
| 2014-08-17 01:00 | 13.6 | 19.4 | 20
| 2014-08-17 01:30 | 13.8 | 19.4 | 20
| 2014-08-17 02:00 | 14 | 18.9 | 20
| 2014-08-17 02:30 | 14 | 18.9 | 20
| 2014-08-17 03:00 | 13.9 | 18.9 | 20
| 2014-08-17 03:30 | 13.8 | 18.9 | 20
| 2014-08-17 04:00 | 13.9 | 18.9 | 20
| 2014-08-17 04:30 | 13.9 | 18.9 | 20
| 2014-08-17 05:00 | 14 | 18.9 | 20
| 2014-08-17 05:30 | 13.9 | 18.9 | 20
| 2014-08-17 06:00 | 13.8 | 18.3 | 20
| 2014-08-17 06:30 | 13.8 | 18.3 | 20
| 2014-08-17 07:00 | 13.9 | 18.3 | 20
| 2014-08-17 07:30 | 14 | 18.3 | 20
| 2014-08-17 08:00 | 14.2 | 18.3 | 20
| 2014-08-17 08:30 | 15.4 | 18.3 | 20
| 2014-08-17 09:00 | 15.4 | 18.3 | 20
| 2014-08-17 09:30 | 16.7 | 18.3 | 20
| 2014-08-17 10:00 | 17.1 | 18.3 | 20
| 2014-08-17 10:30 | 18.2 | 18.3 | 20
| 2014-08-17 11:00 | 18.2 | 18.3 | 20
| 2014-08-17 11:30 | 19.1 | 18.3 | 20
| 2014-08-17 12:00 | 18.7 | 18.3 | 20
| 2014-08-17 12:30 | 18.7 | 18.3 | 20
| 2014-08-17 13:00 | 18.9 | 18.3 | 20
| 2014-08-17 13:30 | 20.7 | 18.9 | 20
| 2014-08-17 14:00 | 21.4 | 18.9 | 20
| 2014-08-17 14:30 | 21.6 | 18.9 | 20
| 2014-08-17 15:00 | 21.5 | 18.9 | 20
| 2014-08-17 15:30 | 21.6 | 18.9 | 20
| 2014-08-17 16:00 | 21 | 19.4 | 20
| 2014-08-17 16:30 | 20.1 | 19.4 | 20
| 2014-08-17 17:00 | 20.4 | 19.4 | 20
| 2014-08-17 17:30 | 19.6 | 19.4 | 20
| 2014-08-17 18:00 | 19.2 | 19.4 | 20
| 2014-08-17 18:30 | 19 | 20 | 20
| 2014-08-17 19:00 | 18.7 | 20 | 20
| 2014-08-17 19:30 | 18.7 | 20 | 20
| 2014-08-17 20:00 | 18.5 | 20 | 20
| 2014-08-17 20:30 | 18.3 | 19.4 | 20
| 2014-08-17 21:00 | 17.5 | 19.4 | 20
| 2014-08-17 21:30 | 17.1 | 19.4 | 20
| 2014-08-17 22:00 | 17.2 | 19.4 | 20
| 2014-08-17 22:30 | 17.5 | 19.4 | 20
| 2014-08-17 23:00 | 17.6 | 19.4 | 20
| 2014-08-17 23:30 | 17.5 | 19.4 | 20
| 2014-08-18 | 17.2 | 19.4 | 20
| 2014-08-18 00:30 | 16.6 | 19.4 | 20
| 2014-08-18 01:00 | 16.1 | 18.9 | 20
| 2014-08-18 01:30 | 15.7 | 18.9 | 20
| 2014-08-18 02:00 | 15.2 | 18.9 | 20
| 2014-08-18 02:30 | 14.9 | 18.9 | 20
| 2014-08-18 03:00 | 14.7 | 18.9 | 20
| 2014-08-18 03:30 | 15.6 | 18.9 | 20
| 2014-08-18 04:00 | 14.8 | 18.9 | 20
| 2014-08-18 04:30 | 14.2 | 18.3 | 20
| 2014-08-18 05:00 | 13.8 | 18.3 | 20
| 2014-08-18 05:30 | 14.1 | 18.3 | 20
| 2014-08-18 06:00 | 13.8 | 18.3 | 20
| 2014-08-18 06:30 | 14.1 | 18.3 | 20
| 2014-08-18 07:00 | 14.3 | 18.3 | 20
| 2014-08-18 07:30 | 15.1 | 18.3 | 20
| 2014-08-18 08:00 | 15.6 | 17.8 | 20
| 2014-08-18 08:30 | 16.2 | 17.8 | 20
| 2014-08-18 09:00 | 16.1 | 17.8 | 20
| 2014-08-18 09:30 | 16.3 | 17.8 | 20
| 2014-08-18 10:00 | 16.5 | 17.8 | 20
| 2014-08-18 10:30 | 16.1 | 17.8 | 20
| 2014-08-18 11:00 | 16.9 | 17.8 | 20
| 2014-08-18 11:30 | 17.6 | 17.8 | 20
| 2014-08-18 12:00 | 17.6 | 17.8 | 20
| 2014-08-18 12:30 | 14.8 | 17.8 | 20
| 2014-08-18 13:00 | 14.1 | 17.8 | 20
| 2014-08-18 13:30 | 15 | 17.8 | 20
| 2014-08-18 14:00 | 16.3 | 17.8 | 20
| 2014-08-18 14:30 | 15.4 | 17.8 | 20
| 2014-08-18 15:00 | 15.6 | 18.3 | 20
| 2014-08-18 15:30 | 15.3 | 18.3 | 20
| 2014-08-18 16:00 | 16.4 | 18.3 | 20
| 2014-08-18 16:30 | 16 | 18.3 | 20
| 2014-08-18 17:00 | 16.2 | 18.3 | 20
| 2014-08-18 17:30 | 17.9 | 18.3 | 20
| 2014-08-18 18:00 | 18.5 | 18.3 | 20
| 2014-08-18 18:30 | 18.2 | 18.3 | 20
| 2014-08-18 19:00 | 16.3 | 18.3 | 20
| 2014-08-18 19:30 | 15 | 18.3 | 20
| 2014-08-18 20:00 | 14.7 | 18.3 | 20
| 2014-08-18 20:30 | 14.1 | 18.3 | 20
| 2014-08-18 21:00 | 12.9 | 18.3 | 20
| 2014-08-18 21:30 | 12.2 | 18.3 | 20
| 2014-08-18 22:00 | 11.8 | 18.3 | 20
| 2014-08-18 22:30 | 12.2 | 18.3 | 20
| 2014-08-18 23:00 | 12 | 18.3 | 19.4
| 2014-08-18 23:30 | 12.1 | 18.3 | 19.4
| 2014-08-19 | 12.4 | 17.8 | 19.4
| 2014-08-19 00:30 | 12.3 | 17.8 | 19.4
| 2014-08-19 01:00 | 11.9 | 17.8 | 19.4
| 2014-08-19 01:30 | 11.7 | 17.8 | 19.4
| 2014-08-19 02:00 | 11.6 | 17.8 | 19.4
| 2014-08-19 02:30 | 11.3 | 17.8 | 19.4
| 2014-08-19 03:00 | 10.8 | 17.8 | 19.4
| 2014-08-19 03:30 | 10.5 | 17.2 | 19.4
| 2014-08-19 04:00 | 10.2 | 17.2 | 19.4
| 2014-08-19 04:30 | 9.8 | 17.2 | 19.4
| 2014-08-19 05:00 | 9.6 | 17.2 | 19.4
| 2014-08-19 05:30 | 9.5 | 17.2 | 19.4
| 2014-08-19 06:00 | 9.2 | 16.7 | 19.4
| 2014-08-19 06:30 | 9.4 | 16.7 | 19.4
| 2014-08-19 07:00 | 9.4 | 16.7 | 19.4
| 2014-08-19 07:30 | 10.4 | 16.7 | 19.4
| 2014-08-19 08:00 | 11.7 | 16.7 | 19.4
| 2014-08-19 08:30 | 12.8 | 16.7 | 19.4
| 2014-08-19 09:00 | 13.9 | 16.1 | 19.4
| 2014-08-19 09:30 | 14.7 | 16.1 | 19.4
| 2014-08-19 10:00 | 15.5 | 16.1 | 19.4
| 2014-08-19 10:30 | 16.9 | 16.1 | 19.4
| 2014-08-19 11:00 | 17.3 | 16.1 | 19.4
| 2014-08-19 11:30 | 17.3 | 16.1 | 19.4
| 2014-08-19 12:00 | 19.8 | 16.7 | 19.4
| 2014-08-19 12:30 | 20.8 | 16.7 | 19.4
| 2014-08-19 13:00 | 21.3 | 16.7 | 19.4
| 2014-08-19 13:30 | 21.4 | 17.2 | 19.4
| 2014-08-19 14:00 | 20.9 | 17.2 | 19.4
| 2014-08-19 14:30 | 19.8 | 17.2 | 19.4
| 2014-08-19 15:00 | 20.9 | 17.8 | 19.4
| 2014-08-19 15:30 | 21.9 | 17.8 | 19.4
| 2014-08-19 16:00 | 21.2 | 18.3 | 19.4
| 2014-08-19 16:30 | 20.9 | 18.3 | 19.4
| 2014-08-19 17:00 | 18 | 18.3 | 19.4
| 2014-08-19 17:30 | 17.6 | 18.3 | 19.4
| 2014-08-19 18:00 | 17.1 | 18.3 | 19.4
| 2014-08-19 18:30 | 17.1 | 18.9 | 19.4
| 2014-08-19 19:00 | 15.6 | 18.9 | 19.4
| 2014-08-19 19:30 | 15.9 | 18.9 | 19.4
| 2014-08-19 20:00 | 15.2 | 18.9 | 19.4
| 2014-08-19 20:30 | 14.6 | 18.9 | 19.4
| 2014-08-19 21:00 | 14.4 | 18.3 | 19.4
| 2014-08-19 21:30 | 15.1 | 18.3 | 19.4
| 2014-08-19 22:00 | 14.7 | 18.3 | 19.4
| 2014-08-19 22:30 | 14.6 | 18.3 | 19.4
| 2014-08-19 23:00 | 14.2 | 18.3 | 19.4
| 2014-08-19 23:30 | 13.5 | 18.3 | 19.4
| 2014-08-20 | 13.1 | 18.3 | 19.4
| 2014-08-20 00:30 | 12.4 | 18.3 | 19.4
| 2014-08-20 01:00 | 11.6 | 18.3 | 19.4
| 2014-08-20 01:30 | 10.6 | 17.8 | 19.4
| 2014-08-20 02:00 | 9.9 | 17.8 | 19.4
| 2014-08-20 02:30 | 9.3 | 17.8 | 19.4
| 2014-08-20 03:00 | 8.8 | 17.8 | 19.4
| 2014-08-20 03:30 | 8.6 | 17.8 | 19.4
| 2014-08-20 04:00 | 8.2 | 17.2 | 19.4
| 2014-08-20 04:30 | 7.9 | 17.2 | 19.4
| 2014-08-20 05:00 | 7.6 | 17.2 | 19.4
| 2014-08-20 05:30 | 7.3 | 17.2 | 19.4
| 2014-08-20 06:00 | 7.2 | 17.2 | 19.4
| 2014-08-20 06:30 | 7 | 16.7 | 19.4
| 2014-08-20 07:00 | 6.7 | 16.7 | 19.4
| 2014-08-20 07:30 | 7 | 16.7 | 19.4
| 2014-08-20 08:00 | 8.3 | 16.7 | 19.4
| 2014-08-20 08:30 | 10.2 | 16.1 | 19.4
| 2014-08-20 09:00 | 11.6 | 16.1 | 19.4
| 2014-08-20 09:30 | 13.1 | 16.1 | 19.4
| 2014-08-20 10:00 | 14.7 | 16.1 | 19.4
| 2014-08-20 10:30 | 15.4 | 16.1 | 19.4
| 2014-08-20 11:00 | 15.6 | 16.1 | 19.4
| 2014-08-20 11:30 | 16.7 | 16.1 | 19.4
| 2014-08-20 12:00 | 17.6 | 16.1 | 19.4
| 2014-08-20 12:30 | 18 | 16.1 | 19.4
| 2014-08-20 13:00 | 18.1 | 16.1 | 19.4
| 2014-08-20 13:30 | 18.3 | 16.7 | 19.4
| 2014-08-20 14:00 | 18.4 | 16.7 | 19.4
| 2014-08-20 14:30 | 18.3 | 16.7 | 19.4
| 2014-08-20 15:00 | 18.9 | 17.2 | 18.9
| 2014-08-20 15:30 | 19.4 | 17.2 | 18.9
| 2014-08-20 16:00 | 19.2 | 17.8 | 18.9
| 2014-08-20 16:30 | 19 | 17.8 | 18.9
| 2014-08-20 17:00 | 19.9 | 17.8 | 18.9
| 2014-08-20 17:30 | 18.5 | 17.8 | 18.9
| 2014-08-20 18:00 | 18.6 | 18.3 | 18.9
| 2014-08-20 18:30 | 18.7 | 18.3 | 18.9
| 2014-08-20 19:00 | 17.4 | 18.3 | 18.9
| 2014-08-20 19:30 | 16 | 18.3 | 18.9
| 2014-08-20 20:00 | 15.2 | 18.3 | 18.9
| 2014-08-20 20:30 | 14.3 | 18.3 | 18.9
| 2014-08-20 21:00 | 13.3 | 18.3 | 18.9
| 2014-08-20 21:30 | 12.7 | 18.3 | 18.9
| 2014-08-20 22:00 | 12.4 | 18.3 | 18.9
| 2014-08-20 22:30 | 12.1 | 18.3 | 18.9
| 2014-08-20 23:00 | 11.7 | 18.3 | 18.9
| 2014-08-20 23:30 | 11.3 | 18.3 | 18.9
| 2014-08-21 | 11.4 | 17.8 | 18.9
| 2014-08-21 00:30 | 11.7 | 17.8 | 18.9
| 2014-08-21 01:00 | 11.6 | 17.8 | 18.9
| 2014-08-21 01:30 | 11.3 | 17.8 | 18.9
| 2014-08-21 02:00 | 10.9 | 17.8 | 18.9
| 2014-08-21 02:30 | 10.8 | 17.8 | 18.9
| 2014-08-21 03:00 | 10.4 | 17.2 | 18.9
| 2014-08-21 03:30 | 9.6 | 17.2 | 18.9
| 2014-08-21 04:00 | 9.1 | 17.2 | 18.9
| 2014-08-21 04:30 | 8.7 | 17.2 | 18.9
| 2014-08-21 05:00 | 8.3 | 17.2 | 18.9
| 2014-08-21 05:30 | 8.2 | 17.2 | 18.9
| 2014-08-21 06:00 | 8.3 | 16.7 | 18.9
| 2014-08-21 06:30 | 8.2 | 16.7 | 18.9
| 2014-08-21 07:00 | 8.1 | 16.7 | 18.9
| 2014-08-21 07:30 | 8.2 | 16.7 | 18.9
| 2014-08-21 08:00 | 9.3 | 16.7 | 18.9
| 2014-08-21 08:30 | 10.5 | 16.1 | 18.9
| 2014-08-21 09:00 | 12 | 16.1 | 18.9
| 2014-08-21 09:30 | 13.3 | 16.1 | 18.9
| 2014-08-21 10:00 | 14.4 | 16.1 | 18.9
| 2014-08-21 10:30 | 15.6 | 16.1 | 18.9
| 2014-08-21 11:00 | 16.3 | 16.1 | 18.9
| 2014-08-21 11:30 | 17.2 | 16.1 | 18.9
| 2014-08-21 12:00 | 17.8 | 16.1 | 18.9
| 2014-08-21 12:30 | 18.7 | 16.1 | 18.9
| 2014-08-21 13:00 | 17.8 | 16.1 | 18.9
| 2014-08-21 13:30 | 17.3 | 16.7 | 18.9
| 2014-08-21 14:00 | 18.6 | 16.7 | 18.9
| 2014-08-21 14:30 | 19.9 | 17.2 | 18.9
| 2014-08-21 15:00 | 19.5 | 17.2 | 18.9
| 2014-08-21 15:30 | 20.4 | 17.2 | 18.9
| 2014-08-21 16:00 | 20.8 | 17.8 | 18.9
| 2014-08-21 16:30 | 21.4 | 17.8 | 18.9
| 2014-08-21 17:00 | 21.1 | 17.8 | 18.9
| 2014-08-21 17:30 | 21.4 | 17.8 | 18.9
| 2014-08-21 18:00 | 21.3 | 18.3 | 18.9
| 2014-08-21 18:30 | 19.9 | 18.3 | 18.9
| 2014-08-21 19:00 | 20 | 18.3 | 18.9
| 2014-08-21 19:30 | 18.8 | 18.3 | 18.9
| 2014-08-21 20:00 | 17.7 | 18.3 | 18.9
| 2014-08-21 20:30 | 15.8 | 18.3 | 18.9
| 2014-08-21 21:00 | 14.3 | 18.3 | 18.9
| 2014-08-21 21:30 | 12.9 | 18.3 | 18.9
| 2014-08-21 22:00 | 12.1 | 18.3 | 18.9
| 2014-08-21 22:30 | 11.4 | 18.3 | 18.9
| 2014-08-21 23:00 | 10.9 | 18.3 | 18.9
| 2014-08-21 23:30 | 10.3 | 18.3 | 18.9
| 2014-08-22 | 10 | 18.3 | 18.9
| 2014-08-22 00:30 | 9.6 | 17.8 | 18.9
| 2014-08-22 01:00 | 9.3 | 17.8 | 18.9
| 2014-08-22 01:30 | 8.9 | 17.8 | 18.9
| 2014-08-22 02:00 | 8.6 | 17.8 | 18.9
| 2014-08-22 02:30 | 8.2 | 17.2 | 18.9
| 2014-08-22 03:00 | 7.7 | 17.2 | 18.9
| 2014-08-22 03:30 | 7.6 | 17.2 | 18.9
| 2014-08-22 04:00 | 7.2 | 17.2 | 18.9
| 2014-08-22 04:30 | 7.1 | 17.2 | 18.9
| 2014-08-22 05:00 | 7 | 16.7 | 18.9
| 2014-08-22 05:30 | 6.9 | 16.7 | 18.9
| 2014-08-22 06:00 | 6.9 | 16.7 | 18.9
| 2014-08-22 06:30 | 6.8 | 16.7 | 18.9
| 2014-08-22 07:00 | 6.8 | 16.1 | 18.9
| 2014-08-22 07:30 | 7.1 | 16.1 | 18.9
| 2014-08-22 08:00 | 8.2 | 16.1 | 18.9
| 2014-08-22 08:30 | 10.2 | 16.1 | 18.9
| 2014-08-22 09:00 | 12.3 | 16.1 | 18.9
| 2014-08-22 09:30 | 13.9 | 16.1 | 18.9
| 2014-08-22 10:00 | 15.7 | 16.1 | 18.9
| 2014-08-22 10:30 | 16.7 | 16.1 | 18.9
| 2014-08-22 11:00 | 18 | 16.1 | 18.9
| 2014-08-22 11:30 | 18.8 | 16.1 | 18.9
| 2014-08-22 12:00 | 19.3 | 16.1 | 18.9
| 2014-08-22 12:30 | 19.4 | 16.1 | 18.9
| 2014-08-22 13:00 | 19.6 | 16.1 | 18.9
| 2014-08-22 13:30 | 19.8 | 16.7 | 18.9
| 2014-08-22 14:00 | 21.9 | 16.7 | 18.9
| 2014-08-22 14:30 | 20.3 | 16.7 | 18.9
| 2014-08-22 15:00 | 19.9 | 17.2 | 18.9
| 2014-08-22 15:30 | 19.6 | 17.2 | 18.9
| 2014-08-22 16:00 | 20.6 | 17.2 | 18.9
| 2014-08-22 16:30 | 20.3 | 17.8 | 18.9
| 2014-08-22 17:00 | 21.1 | 17.8 | 18.9
| 2014-08-22 17:30 | 20.2 | 17.8 | 18.9
| 2014-08-22 18:00 | 19.8 | 17.8 | 18.9
| 2014-08-22 18:30 | 19.6 | 17.8 | 18.9
| 2014-08-22 19:00 | 19.3 | 18.3 | 18.9
| 2014-08-22 19:30 | 18.6 | 18.3 | 18.9
| 2014-08-22 20:00 | 17.5 | 18.3 | 18.9
| 2014-08-22 20:30 | 16.4 | 18.3 | 18.9
| 2014-08-22 21:00 | 16.1 | 18.3 | 18.9
| 2014-08-22 21:30 | 15.7 | 18.3 | 18.9
| 2014-08-22 22:00 | 14.9 | 18.3 | 18.9
| 2014-08-22 22:30 | 14.9 | 18.3 | 18.9
| 2014-08-22 23:00 | 15.4 | 18.3 | 18.3
| 2014-08-22 23:30 | 14.2 | 17.8 | 18.3
| 2014-08-23 | 14 | 17.8 | 18.3
| 2014-08-23 00:30 | 13.1 | 17.8 | 18.3
| 2014-08-23 01:00 | 12.7 | 17.8 | 18.3
| 2014-08-23 01:30 | 12.5 | 17.8 | 18.3
| 2014-08-23 02:00 | 12.4 | 17.8 | 18.3
| 2014-08-23 02:30 | 12.2 | 17.8 | 18.3
| 2014-08-23 03:00 | 12.1 | 17.8 | 18.3
| 2014-08-23 03:30 | 11.8 | 17.2 | 18.3
| 2014-08-23 04:00 | 11.6 | 17.2 | 18.3
| 2014-08-23 04:30 | 11.4 | 17.2 | 18.3
| 2014-08-23 05:00 | 11.4 | 17.2 | 18.3
| 2014-08-23 05:30 | 11.7 | 17.2 | 18.3
| 2014-08-23 06:00 | 12.2 | 17.2 | 18.3
| 2014-08-23 06:30 | 12.6 | 17.2 | 18.3
| 2014-08-23 07:00 | 12.9 | 16.7 | 18.3
| 2014-08-23 07:30 | 13.2 | 16.7 | 18.3
| 2014-08-23 08:00 | 13.4 | 16.7 | 18.3
| 2014-08-23 08:30 | 13.8 | 16.7 | 18.3
| 2014-08-23 09:00 | 13.8 | 16.7 | 18.3
| 2014-08-23 09:30 | 14.2 | 16.7 | 18.3
| 2014-08-23 10:00 | 14.9 | 16.7 | 18.3
| 2014-08-23 10:30 | 15.7 | 16.7 | 18.3
| 2014-08-23 11:00 | 16.2 | 16.7 | 18.3
| 2014-08-23 11:30 | 17.9 | 16.7 | 18.3
| 2014-08-23 12:00 | 18.8 | 16.7 | 18.3
| 2014-08-23 12:30 | 17.7 | 16.7 | 18.3
| 2014-08-23 13:00 | 17.9 | 16.7 | 18.3
| 2014-08-23 13:30 | 18.3 | 17.2 | 18.3
| 2014-08-23 14:00 | 17.7 | 17.2 | 18.3
| 2014-08-23 14:30 | 17.2 | 17.2 | 18.3
| 2014-08-23 15:00 | 16.9 | 17.2 | 18.3
| 2014-08-23 15:30 | 17.5 | 17.2 | 18.3
| 2014-08-23 16:00 | 16.9 | 17.8 | 18.3
| 2014-08-23 16:30 | 17.6 | 17.8 | 18.3
| 2014-08-23 17:00 | 17.4 | 17.8 | 18.3
| 2014-08-23 17:30 | 17.3 | 17.8 | 18.3
| 2014-08-23 18:00 | 16.8 | 17.8 | 18.3
| 2014-08-23 18:30 | 15.7 | 17.8 | 18.3
| 2014-08-23 19:00 | 12.6 | 17.8 | 18.3
| 2014-08-23 19:30 | 12.6 | 17.8 | 18.3
| 2014-08-23 20:00 | 12.3 | 17.8 | 18.3
| 2014-08-23 20:30 | 12 | 17.8 | 18.3
| 2014-08-23 21:00 | 11.9 | 17.8 | 18.3
| 2014-08-23 21:30 | 11.8 | 17.8 | 18.3
| 2014-08-23 22:00 | 11.6 | 17.8 | 18.3
| 2014-08-23 22:30 | 11.5 | 17.8 | 18.3
| 2014-08-23 23:00 | 11.4 | 17.8 | 18.3
| 2014-08-23 23:30 | 11.3 | 17.8 | 18.3
| 2014-08-24 | 11.1 | 17.2 | 18.3
| 2014-08-24 00:30 | 10.5 | 17.2 | 18.3
| 2014-08-24 01:00 | 10.3 | 17.2 | 18.3
| 2014-08-24 01:30 | 10.1 | 17.2 | 18.3
| 2014-08-24 02:00 | 9.6 | 17.2 | 18.3
| 2014-08-24 02:30 | 9.5 | 17.2 | 18.3
| 2014-08-24 03:00 | 9.1 | 16.7 | 18.3
| 2014-08-24 03:30 | 8.6 | 16.7 | 18.3
| 2014-08-24 04:00 | 8.3 | 16.7 | 18.3
| 2014-08-24 04:30 | 8.1 | 16.7 | 18.3
| 2014-08-24 05:00 | 8.2 | 16.7 | 18.3
| 2014-08-24 05:30 | 8.7 | 16.7 | 18.3
| 2014-08-24 06:00 | 8.6 | 16.1 | 18.3
| 2014-08-24 06:30 | 9 | 16.1 | 18.3
| 2014-08-24 07:00 | 8.4 | 16.1 | 18.3
| 2014-08-24 07:30 | 8.4 | 16.1 | 18.3
| 2014-08-24 08:00 | 9.4 | 16.1 | 18.3
| 2014-08-24 08:30 | 10.3 | 16.1 | 18.3
| 2014-08-24 09:00 | 11.2 | 16.1 | 18.3
| 2014-08-24 09:30 | 12.4 | 15.6 | 18.3
| 2014-08-24 10:00 | 13.1 | 15.6 | 18.3
| 2014-08-24 10:30 | 14.7 | 15.6 | 18.3
| 2014-08-24 11:00 | 14.9 | 15.6 | 18.3
| 2014-08-24 11:30 | 15.2 | 15.6 | 18.3
| 2014-08-24 12:00 | 15.8 | 15.6 | 18.3
| 2014-08-24 12:30 | 16.8 | 15.6 | 18.3
| 2014-08-24 13:00 | 16.9 | 16.1 | 18.3
| 2014-08-24 13:30 | 16.7 | 16.1 | 18.3
| 2014-08-24 14:00 | 16.5 | 16.1 | 18.3
| 2014-08-24 14:30 | 17.7 | 16.1 | 18.3
| 2014-08-24 15:00 | 15.9 | 16.1 | 18.3
| 2014-08-24 15:30 | 17.4 | 16.7 | 18.3
| 2014-08-24 16:00 | 18.7 | 16.7 | 18.3
| 2014-08-24 16:30 | 16.8 | 16.7 | 18.3
| 2014-08-24 17:00 | 14.2 | 16.7 | 18.3
| 2014-08-24 17:30 | 14.7 | 17.2 | 18.3
| 2014-08-24 18:00 | 15.2 | 17.2 | 18.3
| 2014-08-24 18:30 | 15.7 | 17.2 | 18.3
| 2014-08-24 19:00 | 16.2 | 17.2 | 18.3
| 2014-08-24 19:30 | 15 | 17.2 | 18.3
| 2014-08-24 20:00 | 14.1 | 17.2 | 18.3
| 2014-08-24 20:30 | 12.7 | 17.2 | 18.3
| 2014-08-24 21:00 | 12.3 | 17.2 | 18.3
| 2014-08-24 21:30 | 11.6 | 17.2 | 18.3
| 2014-08-24 22:00 | 11 | 17.2 | 18.3
| 2014-08-24 22:30 | 10.4 | 17.2 | 18.3
| 2014-08-24 23:00 | 9.9 | 17.2 | 18.3
| 2014-08-24 23:30 | 9.7 | 16.7 | 18.3
| 2014-08-25 | 9.4 | 16.7 | 18.3
| 2014-08-25 00:30 | 9 | 16.7 | 18.3
| 2014-08-25 01:00 | 8.8 | 16.7 | 18.3
| 2014-08-25 01:30 | 8.4 | 16.7 | 18.3
| 2014-08-25 02:00 | 8.5 | 16.7 | 18.3
| 2014-08-25 02:30 | 8.8 | 16.1 | 18.3
| 2014-08-25 03:00 | 8.9 | 16.1 | 18.3
| 2014-08-25 03:30 | 8.9 | 16.1 | 18.3
| 2014-08-25 04:00 | 9 | 16.1 | 18.3
| 2014-08-25 04:30 | 8.8 | 16.1 | 18.3
| 2014-08-25 05:00 | 8.8 | 16.1 | 18.3
| 2014-08-25 05:30 | 9 | 15.6 | 18.3
| 2014-08-25 06:00 | 9 | 15.6 | 18.3
| 2014-08-25 06:30 | 9.1 | 15.6 | 18.3
| 2014-08-25 07:00 | 9.2 | 15.6 | 18.3
| 2014-08-25 07:30 | 9.4 | 15.6 | 18.3
| 2014-08-25 08:00 | 9.9 | 15.6 | 18.3
| 2014-08-25 08:30 | 10.9 | 15.6 | 18.3
| 2014-08-25 09:00 | 12 | 15.6 | 18.3
| 2014-08-25 09:30 | 12.4 | 15.6 | 18.3
| 2014-08-25 10:00 | 13 | 15.6 | 18.3
| 2014-08-25 10:30 | 13.2 | 15.6 | 18.3
| 2014-08-25 11:00 | 14.6 | 15.6 | 18.3
| 2014-08-25 11:30 | 16.9 | 15.6 | 18.3
| 2014-08-25 12:00 | 16.6 | 15.6 | 18.3
| 2014-08-25 12:30 | 17.1 | 15.6 | 18.3
| 2014-08-25 13:00 | 17.3 | 15.6 | 18.3
| 2014-08-25 13:30 | 17.5 | 15.6 | 18.3
| 2014-08-25 14:00 | 19 | 16.1 | 18.3
| 2014-08-25 14:30 | 19 | 16.1 | 18.3
| 2014-08-25 15:00 | 19.3 | 16.1 | 18.3
| 2014-08-25 15:30 | 19.4 | 16.1 | 18.3
| 2014-08-25 16:00 | 18.7 | 16.7 | 18.3
| 2014-08-25 16:30 | 19.3 | 16.7 | 18.3
| 2014-08-25 17:00 | 18.6 | 16.7 | 18.3
| 2014-08-25 17:30 | 18.1 | 16.7 | 18.3
| 2014-08-25 18:00 | 17.5 | 16.7 | 18.3
| 2014-08-25 18:30 | 16.9 | 17.2 | 18.3
| 2014-08-25 19:00 | 16.4 | 17.2 | 18.3
| 2014-08-25 19:30 | 15.9 | 17.2 | 18.3
| 2014-08-25 20:00 | 15.6 | 17.2 | 18.3
| 2014-08-25 20:30 | 15.1 | 17.2 | 18.3
| 2014-08-25 21:00 | 14.9 | 17.2 | 18.3
| 2014-08-25 21:30 | 15.1 | 17.2 | 18.3
| 2014-08-25 22:00 | 14.3 | 17.2 | 18.3
| 2014-08-25 22:30 | 13.7 | 17.2 | 18.3
| 2014-08-25 23:00 | 13.4 | 16.7 | 18.3
| 2014-08-25 23:30 | 13.2 | 16.7 | 18.3
| 2014-08-26 | 12.9 | 16.7 | 18.3
| 2014-08-26 00:30 | 12.4 | 16.7 | 18.3
| 2014-08-26 01:00 | 12.4 | 16.7 | 18.3
| 2014-08-26 01:30 | 12.6 | 16.7 | 18.3
| 2014-08-26 02:00 | 12.7 | 16.7 | 18.3
| 2014-08-26 02:30 | 12.6 | 16.7 | 18.3
| 2014-08-26 03:00 | 12.7 | 16.7 | 18.3
| 2014-08-26 03:30 | 12.6 | 16.7 | 18.3
| 2014-08-26 04:00 | 12.4 | 16.7 | 18.3
| 2014-08-26 04:30 | 12.4 | 16.1 | 18.3
| 2014-08-26 05:00 | 12.4 | 16.1 | 18.3
| 2014-08-26 05:30 | 12.4 | 16.1 | 18.3
| 2014-08-26 06:00 | 12.6 | 16.1 | 18.3
| 2014-08-26 06:30 | 12.7 | 16.1 | 18.3
| 2014-08-26 07:00 | 12.9 | 16.1 | 18.3
| 2014-08-26 07:30 | 13.1 | 16.1 | 17.8
| 2014-08-26 08:00 | 13.2 | 16.1 | 17.8
| 2014-08-26 08:30 | 13.4 | 16.1 | 17.8
| 2014-08-26 09:00 | 13.7 | 16.1 | 17.8
| 2014-08-26 09:30 | 14.2 | 16.1 | 17.8
| 2014-08-26 10:00 | 14.6 | 16.1 | 17.8
| 2014-08-26 10:30 | 15.7 | 16.1 | 17.8
| 2014-08-26 11:00 | 16.9 | 16.1 | 17.8
| 2014-08-26 11:30 | 18.8 | 16.1 | 17.8
| 2014-08-26 12:00 | 18.6 | 16.1 | 17.8
| 2014-08-26 12:30 | 19.3 | 16.1 | 17.8
| 2014-08-26 13:00 | 19.9 | 16.1 | 17.8
| 2014-08-26 13:30 | 20.1 | 16.1 | 17.8
| 2014-08-26 14:00 | 20.1 | 16.7 | 17.8
| 2014-08-26 14:30 | 19.8 | 16.7 | 17.8
| 2014-08-26 15:00 | 19.9 | 16.7 | 17.8
| 2014-08-26 15:30 | 21.4 | 16.7 | 17.8
| 2014-08-26 16:00 | 22.7 | 17.2 | 17.8
| 2014-08-26 16:30 | 21.9 | 17.2 | 17.8
| 2014-08-26 17:00 | 21.2 | 17.2 | 17.8
| 2014-08-26 17:30 | 20.8 | 17.2 | 17.8
| 2014-08-26 18:00 | 20.4 | 17.8 | 17.8
| 2014-08-26 18:30 | 19.7 | 17.8 | 17.8
| 2014-08-26 19:00 | 18.1 | 17.8 | 17.8
| 2014-08-26 19:30 | 16.4 | 17.8 | 17.8
| 2014-08-26 20:00 | 15.9 | 17.8 | 17.8
| 2014-08-26 20:30 | 15.9 | 17.8 | 17.8
| 2014-08-26 21:00 | 15.7 | 17.8 | 17.8
| 2014-08-26 21:30 | 15.6 | 17.8 | 17.8
| 2014-08-26 22:00 | 15.2 | 17.8 | 17.8
| 2014-08-26 22:30 | 15.2 | 17.8 | 17.8
| 2014-08-26 23:00 | 15.2 | 17.8 | 17.8
| 2014-08-26 23:30 | 15.1 | 17.8 | 17.8
| 2014-08-27 | 14.8 | 17.8 | 17.8
| 2014-08-27 00:30 | 14.6 | 17.8 | 17.8
| 2014-08-27 01:00 | 14.3 | 17.8 | 17.8
| 2014-08-27 01:30 | 14 | 17.8 | 17.8
| 2014-08-27 02:00 | 13.9 | 17.2 | 17.8
| 2014-08-27 02:30 | 13.8 | 17.2 | 17.8
| 2014-08-27 03:00 | 13.8 | 17.2 | 17.8
| 2014-08-27 03:30 | 13.7 | 17.2 | 17.8
| 2014-08-27 04:00 | 13.4 | 17.2 | 17.8
| 2014-08-27 04:30 | 13.3 | 17.2 | 17.8
| 2014-08-27 05:00 | 13.2 | 17.2 | 17.8
| 2014-08-27 05:30 | 13.1 | 17.2 | 17.8
| 2014-08-27 06:00 | 12.8 | 17.2 | 17.8
| 2014-08-27 06:30 | 12.8 | 17.2 | 17.8
| 2014-08-27 07:00 | 12.8 | 16.7 | 17.8
| 2014-08-27 07:30 | 12.8 | 16.7 | 17.8
| 2014-08-27 08:00 | 13.2 | 16.7 | 17.8
| 2014-08-27 08:30 | 13.4 | 16.7 | 17.8
| 2014-08-27 09:00 | 13.6 | 16.7 | 17.8
| 2014-08-27 09:30 | 13.9 | 16.7 | 17.8
| 2014-08-27 10:00 | 14.8 | 16.7 | 17.8
| 2014-08-27 10:30 | 14.8 | 16.7 | 17.8
| 2014-08-27 11:00 | 15.5 | 16.7 | 17.8
| 2014-08-27 11:30 | 15.9 | 16.7 | 17.8
| 2014-08-27 12:00 | 16.6 | 16.7 | 17.8
| 2014-08-27 12:30 | 17.1 | 16.7 | 17.8
| 2014-08-27 13:00 | 17.2 | 16.7 | 17.8
| 2014-08-27 13:30 | 18.6 | 17.2 | 17.8
| 2014-08-27 14:00 | 18.4 | 17.2 | 17.8
| 2014-08-27 14:30 | 19.7 | 17.2 | 17.8
| 2014-08-27 15:00 | 20.9 | 17.2 | 17.8
| 2014-08-27 15:30 | 21.4 | 17.8 | 17.8
| 2014-08-27 16:00 | 21.2 | 17.8 | 17.8
| 2014-08-27 16:30 | 21.7 | 17.8 | 17.8
| 2014-08-27 17:00 | 21.7 | 18.3 | 17.8
| 2014-08-27 17:30 | 21.8 | 18.3 | 17.8
| 2014-08-27 18:00 | 21.8 | 18.3 | 17.8
| 2014-08-27 18:30 | 21.5 | 18.3 | 17.8
| 2014-08-27 19:00 | 21.1 | 18.9 | 17.8
| 2014-08-27 19:30 | 20.1 | 18.9 | 17.8
| 2014-08-27 20:00 | 18.2 | 18.9 | 17.8
| 2014-08-27 20:30 | 16.6 | 18.9 | 17.8
| 2014-08-27 21:00 | 15.2 | 18.9 | 17.8
| 2014-08-27 21:30 | 14.4 | 18.9 | 17.8
| 2014-08-27 22:00 | 13.8 | 18.9 | 17.8
| 2014-08-27 22:30 | 13.2 | 18.9 | 17.8
| 2014-08-27 23:00 | 12.7 | 18.3 | 17.8
| 2014-08-27 23:30 | 12.3 | 18.3 | 17.8
| 2014-08-28 | 11.8 | 18.3 | 17.8
| 2014-08-28 00:30 | 11.6 | 18.3 | 17.8
| 2014-08-28 01:00 | 11.2 | 18.3 | 17.8
| 2014-08-28 01:30 | 11 | 18.3 | 17.8
| 2014-08-28 02:00 | 11.1 | 18.3 | 17.8
| 2014-08-28 02:30 | 10.9 | 17.8 | 17.8
| 2014-08-28 03:00 | 10.7 | 17.8 | 17.8
| 2014-08-28 03:30 | 10.4 | 17.8 | 17.8
| 2014-08-28 04:00 | 10.4 | 17.8 | 17.8
| 2014-08-28 04:30 | 10.3 | 17.8 | 17.8
| 2014-08-28 05:00 | 10 | 17.2 | 17.8
| 2014-08-28 05:30 | 9.6 | 17.2 | 17.8
| 2014-08-28 06:00 | 9.7 | 17.2 | 17.8
| 2014-08-28 06:30 | 9.8 | 17.2 | 17.8
| 2014-08-28 07:00 | 9.8 | 17.2 | 17.8
| 2014-08-28 07:30 | 9.9 | 16.7 | 17.8
| 2014-08-28 08:00 | 10.2 | 16.7 | 17.8
| 2014-08-28 08:30 | 11.7 | 16.7 | 17.8
| 2014-08-28 09:00 | 12.4 | 16.7 | 17.8
| 2014-08-28 09:30 | 13.3 | 16.7 | 17.8
| 2014-08-28 10:00 | 14.8 | 16.7 | 17.8
| 2014-08-28 10:30 | 16.7 | 16.7 | 17.8
| 2014-08-28 11:00 | 17.8 | 16.7 | 17.8
| 2014-08-28 11:30 | 19.2 | 16.7 | 17.8
| 2014-08-28 12:00 | 20.6 | 16.7 | 17.8
| 2014-08-28 12:30 | 21.3 | 16.7 | 17.8
| 2014-08-28 13:00 | 22.2 | 16.7 | 17.8
| 2014-08-28 13:30 | 22.9 | 17.2 | 17.8
| 2014-08-28 14:00 | 23.6 | 17.2 | 17.8
| 2014-08-28 14:30 | 23.9 | 17.8 | 17.8
| 2014-08-28 15:00 | 23.4 | 17.8 | 17.8
| 2014-08-28 15:30 | 24.2 | 17.8 | 17.8
| 2014-08-28 16:00 | 24.4 | 18.3 | 17.8
| 2014-08-28 16:30 | 24.5 | 18.3 | 17.8
| 2014-08-28 17:00 | 23.3 | 18.3 | 17.8
| 2014-08-28 17:30 | 22.8 | 18.9 | 17.8
| 2014-08-28 18:00 | 23 | 18.9 | 17.8
| 2014-08-28 18:30 | 22.4 | 18.9 | 17.8
| 2014-08-28 19:00 | 21.8 | 18.9 | 17.8
| 2014-08-28 19:30 | 21.3 | 18.9 | 17.8
| 2014-08-28 20:00 | 21.2 | 19.4 | 17.8
| 2014-08-28 20:30 | 20.3 | 19.4 | 17.8
| 2014-08-28 21:00 | 19.7 | 19.4 | 17.8
| 2014-08-28 21:30 | 18.9 | 19.4 | 17.8
| 2014-08-28 22:00 | 18.1 | 19.4 | 17.8
| 2014-08-28 22:30 | 17.3 | 19.4 | 17.8
| 2014-08-28 23:00 | 16.8 | 19.4 | 17.8
| 2014-08-28 23:30 | 16.7 | 19.4 | 17.8
| 2014-08-29 | 16.8 | 18.9 | 17.8
| 2014-08-29 00:30 | 16.7 | 18.9 | 17.8
| 2014-08-29 01:00 | 16.2 | 18.9 | 17.8
| 2014-08-29 01:30 | 15.6 | 18.9 | 17.8
| 2014-08-29 02:00 | 15.6 | 18.9 | 17.8
| 2014-08-29 02:30 | 15.6 | 18.9 | 17.8
| 2014-08-29 03:00 | 15.8 | 18.9 | 17.8
| 2014-08-29 03:30 | 16.3 | 18.9 | 17.8
| 2014-08-29 04:00 | 16.7 | 18.3 | 17.8
| 2014-08-29 04:30 | 16.6 | 18.3 | 17.8
| 2014-08-29 05:00 | 17 | 18.3 | 17.8
| 2014-08-29 05:30 | 17.6 | 18.3 | 17.8
| 2014-08-29 06:00 | 17.4 | 18.3 | 17.8
| 2014-08-29 06:30 | 17.2 | 18.3 | 17.8
| 2014-08-29 07:00 | 17 | 18.3 | 17.8
| 2014-08-29 07:30 | 16.9 | 18.3 | 17.8
| 2014-08-29 08:00 | 17.2 | 18.3 | 17.8
| 2014-08-29 08:30 | 17.1 | 18.3 | 17.8
| 2014-08-29 09:00 | 17.8 | 18.3 | 17.8
| 2014-08-29 09:30 | 18.9 | 18.3 | 17.8
| 2014-08-29 10:00 | 19.4 | 18.3 | 17.8
| 2014-08-29 10:30 | 19.7 | 18.3 | 17.8
| 2014-08-29 11:00 | 19.8 | 18.3 | 17.8
| 2014-08-29 11:30 | 20.6 | 18.3 | 17.8
| 2014-08-29 12:00 | 21.5 | 18.3 | 17.8
| 2014-08-29 12:30 | 21.8 | 18.3 | 17.8
| 2014-08-29 13:00 | 21.9 | 18.3 | 17.8
| 2014-08-29 13:30 | 23.3 | 18.3 | 17.8
| 2014-08-29 14:00 | 24.1 | 18.9 | 17.8
| 2014-08-29 14:30 | 23.9 | 18.9 | 17.8
| 2014-08-29 15:00 | 24.7 | 18.9 | 17.8
| 2014-08-29 15:30 | 25.1 | 19.4 | 17.8
| 2014-08-29 16:00 | 24.3 | 19.4 | 17.8
| 2014-08-29 16:30 | 24.6 | 19.4 | 17.8
| 2014-08-29 17:00 | 25.2 | 20 | 17.8
| 2014-08-29 17:30 | 24.4 | 20 | 17.8
| 2014-08-29 18:00 | 24.3 | 20 | 17.8
| 2014-08-29 18:30 | 23.9 | 20 | 17.8
| 2014-08-29 19:00 | 22.8 | 20 | 17.8
| 2014-08-29 19:30 | 21.8 | 20 | 17.8
| 2014-08-29 20:00 | 20.7 | 20 | 17.8
| 2014-08-29 20:30 | 19.7 | 20.6 | 17.8
| 2014-08-29 21:00 | 18.8 | 20 | 17.8
| 2014-08-29 21:30 | 18.1 | 20 | 17.8
| 2014-08-29 22:00 | 17.6 | 20 | 17.8
| 2014-08-29 22:30 | 17.6 | 20 | 17.8
| 2014-08-29 23:00 | 17.4 | 20 | 17.8
| 2014-08-29 23:30 | 17.4 | 20 | 17.8
| 2014-08-30 | 17.3 | 20 | 17.8
| 2014-08-30 00:30 | 16.9 | 20 | 17.8
| 2014-08-30 01:00 | 16.7 | 20 | 17.8
| 2014-08-30 01:30 | 16.8 | 19.4 | 17.8
| 2014-08-30 02:00 | 16.8 | 19.4 | 18.3
| 2014-08-30 02:30 | 16.3 | 19.4 | 18.3
| 2014-08-30 03:00 | 15.7 | 19.4 | 18.3
| 2014-08-30 03:30 | 15.1 | 19.4 | 18.3
| 2014-08-30 04:00 | 14.6 | 19.4 | 18.3
| 2014-08-30 04:30 | 14.1 | 19.4 | 18.3
| 2014-08-30 05:00 | 13.8 | 19.4 | 18.3
| 2014-08-30 05:30 | 13.8 | 18.9 | 18.3
| 2014-08-30 06:00 | 13.5 | 18.9 | 18.3
| 2014-08-30 06:30 | 13.2 | 18.9 | 18.3
| 2014-08-30 07:00 | 13 | 18.9 | 18.3
| 2014-08-30 07:30 | 13.6 | 18.9 | 18.3
| 2014-08-30 08:00 | 14.7 | 18.9 | 18.3
| 2014-08-30 08:30 | 15.6 | 18.3 | 18.3
| 2014-08-30 09:00 | 15.9 | 18.3 | 18.3
| 2014-08-30 09:30 | 17.2 | 18.3 | 18.3
| 2014-08-30 10:00 | 18 | 18.3 | 18.3
| 2014-08-30 10:30 | 18.3 | 18.3 | 18.3
| 2014-08-30 11:00 | 19.5 | 18.3 | 18.3
| 2014-08-30 11:30 | 20.8 | 18.3 | 18.3
| 2014-08-30 12:00 | 19.8 | 18.3 | 18.3
| 2014-08-30 12:30 | 21.5 | 18.3 | 18.3
| 2014-08-30 13:00 | 22.1 | 18.3 | 18.3
| 2014-08-30 13:30 | 23.1 | 18.3 | 18.3
| 2014-08-30 14:00 | 21.9 | 18.9 | 18.3
| 2014-08-30 14:30 | 22.8 | 18.9 | 18.3
| 2014-08-30 15:00 | 23 | 18.9 | 18.3
| 2014-08-30 15:30 | 23.9 | 18.9 | 18.3
| 2014-08-30 16:00 | 23.4 | 19.4 | 18.3
| 2014-08-30 16:30 | 24.6 | 19.4 | 18.3
| 2014-08-30 17:00 | 23.2 | 19.4 | 18.3
| 2014-08-30 17:30 | 22.7 | 19.4 | 18.3
| 2014-08-30 18:00 | 22.2 | 19.4 | 18.3
| 2014-08-30 18:30 | 21.8 | 19.4 | 18.3
| 2014-08-30 19:00 | 21.3 | 20 | 18.3
| 2014-08-30 19:30 | 20.4 | 20 | 18.3
| 2014-08-30 20:00 | 19.2 | 20 | 18.3
| 2014-08-30 20:30 | 18.2 | 20 | 18.3
| 2014-08-30 21:00 | 17.9 | 20 | 18.3
| 2014-08-30 21:30 | 17.8 | 20 | 18.3
| 2014-08-30 22:00 | 17.7 | 20 | 18.3
| 2014-08-30 22:30 | 17.8 | 20 | 18.3
| 2014-08-30 23:00 | 17.9 | 19.4 | 18.3
| 2014-08-30 23:30 | 17 | 19.4 | 18.3
| 2014-08-31 | 16.7 | 19.4 | 18.3
| 2014-08-31 00:30 | 16.6 | 19.4 | 18.3
| 2014-08-31 01:00 | 16.7 | 19.4 | 18.3
| 2014-08-31 01:30 | 16.5 | 19.4 | 18.3
| 2014-08-31 02:00 | 16.4 | 19.4 | 18.3
| 2014-08-31 02:30 | 16.4 | 19.4 | 18.3
| 2014-08-31 03:00 | 16.3 | 19.4 | 18.3
| 2014-08-31 03:30 | 16.1 | 19.4 | 18.3
| 2014-08-31 04:00 | 14.6 | 18.9 | 18.3
| 2014-08-31 04:30 | 14.6 | 18.9 | 18.3
| 2014-08-31 05:00 | 14.6 | 18.9 | 18.3
| 2014-08-31 05:30 | 14.6 | 18.9 | 18.3
| 2014-08-31 06:00 | 14.5 | 18.9 | 18.3
| 2014-08-31 06:30 | 14.5 | 18.9 | 18.3
| 2014-08-31 07:00 | 14.5 | 18.9 | 18.3
| 2014-08-31 07:30 | 14.6 | 18.9 | 18.3
| 2014-08-31 08:00 | 14.7 | 18.9 | 18.3
| 2014-08-31 08:30 | 14.9 | 18.3 | 18.3
| 2014-08-31 09:00 | 15.1 | 18.3 | 18.3
| 2014-08-31 09:30 | 15.4 | 18.3 | 18.3
| 2014-08-31 10:00 | 15.8 | 18.3 | 18.3
| 2014-08-31 10:30 | 16.3 | 18.3 | 18.3
| 2014-08-31 11:00 | 16.2 | 18.3 | 18.3
| 2014-08-31 11:30 | 16.6 | 18.3 | 18.3
| 2014-08-31 12:00 | 17.3 | 18.3 | 18.3
| 2014-08-31 12:30 | 18.6 | 18.3 | 18.3
| 2014-08-31 13:00 | 18.1 | 18.3 | 18.3
| 2014-08-31 13:30 | 18.7 | 18.9 | 18.3
| 2014-08-31 14:00 | 19.7 | 18.9 | 18.3
| 2014-08-31 14:30 | 19.6 | 18.9 | 18.3
| 2014-08-31 15:00 | 18.2 | 18.9 | 18.3
| 2014-08-31 15:30 | 16.1 | 18.9 | 18.3
| 2014-08-31 16:00 | 17.2 | 18.9 | 18.3
| 2014-08-31 16:30 | 17.5 | 18.9 | 18.3
| 2014-08-31 17:00 | 17.1 | 19.4 | 18.3
| 2014-08-31 17:30 | 15.4 | 19.4 | 18.3
| 2014-08-31 18:00 | 14.9 | 19.4 | 18.3
| 2014-08-31 18:30 | 15.3 | 19.4 | 18.3
| 2014-08-31 19:00 | 15.3 | 19.4 | 18.3
| 2014-08-31 19:30 | 15.1 | 19.4 | 18.3
| 2014-08-31 20:00 | 14.6 | 19.4 | 18.3
| 2014-08-31 20:30 | 14 | 19.4 | 18.3
| 2014-08-31 21:00 | 13.7 | 18.9 | 18.3
| 2014-08-31 21:30 | 13.4 | 18.9 | 18.3
| 2014-08-31 22:00 | 13.1 | 18.9 | 18.3
| 2014-08-31 22:30 | 12.8 | 18.9 | 18.3
| 2014-08-31 23:00 | 12.7 | 18.9 | 18.3
| 2014-08-31 23:30 | 12.6 | 18.9 | 18.3
| 2014-09-01 | 12.4 | 18.9 | 18.3
| 2014-09-01 00:30 | 12.3 | 18.3 | 18.3
| 2014-09-01 01:00 | 11.9 | 18.3 | 18.3
| 2014-09-01 01:30 | 11.2 | 18.3 | 18.3
| 2014-09-01 02:00 | 10.9 | 18.3 | 18.3
| 2014-09-01 02:30 | 10.1 | 18.3 | 18.3
| 2014-09-01 03:00 | 10.7 | 18.3 | 18.3
| 2014-09-01 03:30 | 10.9 | 18.3 | 18.3
| 2014-09-01 04:00 | 11 | 17.8 | 18.3
| 2014-09-01 04:30 | 10.3 | 17.8 | 18.3
| 2014-09-01 05:00 | 9.8 | 17.8 | 18.3
| 2014-09-01 05:30 | 9.6 | 17.8 | 18.3
| 2014-09-01 06:00 | 9.9 | 17.8 | 18.3
| 2014-09-01 06:30 | 9.8 | 17.2 | 18.3
| 2014-09-01 07:00 | 9.8 | 17.2 | 18.3
| 2014-09-01 07:30 | 10.4 | 17.2 | 18.3
| 2014-09-01 08:00 | 11.3 | 17.2 | 18.3
| 2014-09-01 08:30 | 11.7 | 17.2 | 18.3
| 2014-09-01 09:00 | 12.1 | 17.2 | 18.3
| 2014-09-01 09:30 | 13.1 | 17.2 | 18.3
| 2014-09-01 10:00 | 14.2 | 16.7 | 18.3
| 2014-09-01 10:30 | 15.7 | 16.7 | 18.3
| 2014-09-01 11:00 | 16.1 | 16.7 | 18.3
| 2014-09-01 11:30 | 16.4 | 16.7 | 18.3
| 2014-09-01 12:00 | 16.6 | 16.7 | 18.3
| 2014-09-01 12:30 | 16.7 | 17.2 | 18.3
| 2014-09-01 13:00 | 16.8 | 17.2 | 18.3
| 2014-09-01 13:30 | 17.4 | 17.2 | 18.3
| 2014-09-01 14:00 | 17.3 | 17.2 | 18.3
| 2014-09-01 14:30 | 18.3 | 17.2 | 18.3
| 2014-09-01 15:00 | 17.8 | 17.2 | 18.3
| 2014-09-01 15:30 | 18 | 17.2 | 18.3
| 2014-09-01 16:00 | 18.6 | 17.8 | 18.3
| 2014-09-01 16:30 | 19.1 | 17.8 | 18.3
| 2014-09-01 17:00 | 18.8 | 17.8 | 18.3
| 2014-09-01 17:30 | 18.6 | 17.8 | 18.3
| 2014-09-01 18:00 | 18.8 | 17.8 | 18.3
| 2014-09-01 18:30 | 18.3 | 17.8 | 18.3
| 2014-09-01 19:00 | 18.1 | 17.8 | 18.3
| 2014-09-01 19:30 | 17.7 | 18.3 | 18.3
| 2014-09-01 20:00 | 17.3 | 18.3 | 18.3
| 2014-09-01 20:30 | 16.8 | 18.3 | 18.3
| 2014-09-01 21:00 | 15.7 | 18.3 | 18.3
| 2014-09-01 21:30 | 15.2 | 18.3 | 18.3
| 2014-09-01 22:00 | 14.9 | 18.3 | 18.3
| 2014-09-01 22:30 | 14.7 | 17.8 | 18.3
| 2014-09-01 23:00 | 14.4 | 17.8 | 18.3
| 2014-09-01 23:30 | 14.3 | 17.8 | 18.3
| 2014-09-02 | 14 | 17.8 | 18.3
| 2014-09-02 00:30 | 13.8 | 17.8 | 18.3
| 2014-09-02 01:00 | 13.7 | 17.8 | 18.3
| 2014-09-02 01:30 | 13.6 | 17.8 | 18.3
| 2014-09-02 02:00 | 13.4 | 17.8 | 18.3
| 2014-09-02 02:30 | 13.4 | 17.8 | 18.3
| 2014-09-02 03:00 | 13 | 17.8 | 18.3
| 2014-09-02 03:30 | 12.4 | 17.8 | 18.3
| 2014-09-02 04:00 | 11.8 | 17.2 | 18.3
| 2014-09-02 04:30 | 11.6 | 17.2 | 18.3
| 2014-09-02 05:00 | 11.7 | 17.2 | 18.3
| 2014-09-02 05:30 | 11.8 | 17.2 | 18.3
| 2014-09-02 06:00 | 11.7 | 17.2 | 18.3
| 2014-09-02 06:30 | 11.8 | 17.2 | 18.3
| 2014-09-02 07:00 | 11.8 | 17.2 | 18.3
| 2014-09-02 07:30 | 12.1 | 17.2 | 18.3
| 2014-09-02 08:00 | 12.5 | 17.2 | 18.3
| 2014-09-02 08:30 | 13.1 | 16.7 | 18.3
| 2014-09-02 09:00 | 13.7 | 16.7 | 18.3
| 2014-09-02 09:30 | 14.4 | 16.7 | 18.3
| 2014-09-02 10:00 | 15.2 | 16.7 | 18.3
| 2014-09-02 10:30 | 16.4 | 16.7 | 18.3
| 2014-09-02 11:00 | 17.8 | 16.7 | 18.3
| 2014-09-02 11:30 | 18.4 | 16.7 | 18.3
| 2014-09-02 12:00 | 18.8 | 16.7 | 18.3
| 2014-09-02 12:30 | 19.4 | 17.2 | 18.3
| 2014-09-02 13:00 | 19.9 | 17.2 | 18.3
| 2014-09-02 13:30 | 19.6 | 17.2 | 18.3
| 2014-09-02 14:00 | 20.1 | 17.2 | 18.3
| 2014-09-02 14:30 | 20.1 | 17.8 | 18.3
| 2014-09-02 15:00 | 19.8 | 17.8 | 18.3
| 2014-09-02 15:30 | 19.7 | 17.8 | 18.3
| 2014-09-02 16:00 | 19.4 | 17.8 | 18.3
| 2014-09-02 16:30 | 18.7 | 18.3 | 18.3
| 2014-09-02 17:00 | 18.8 | 18.3 | 18.3
| 2014-09-02 17:30 | 18.8 | 18.3 | 18.3
| 2014-09-02 18:00 | 19.4 | 18.3 | 18.3
| 2014-09-02 18:30 | 20.1 | 18.3 | 18.3
| 2014-09-02 19:00 | 19.7 | 18.3 | 18.3
| 2014-09-02 19:30 | 18.7 | 18.3 | 18.3
| 2014-09-02 20:00 | 17.9 | 18.3 | 18.3
| 2014-09-02 20:30 | 16.8 | 18.3 | 18.3
| 2014-09-02 21:00 | 16.1 | 18.3 | 18.3
| 2014-09-02 21:30 | 15.9 | 18.3 | 18.3
| 2014-09-02 22:00 | 15.7 | 18.3 | 18.3
| 2014-09-02 22:30 | 15.2 | 18.3 | 18.3
| 2014-09-02 23:00 | 14.8 | 18.3 | 18.3
| 2014-09-02 23:30 | 14.7 | 18.3 | 18.3
| 2014-09-03 | 15.2 | 18.3 | 18.3
| 2014-09-03 00:30 | 15.6 | 18.3 | 18.3
| 2014-09-03 01:00 | 15.5 | 18.3 | 18.3
| 2014-09-03 01:30 | 15.3 | 18.3 | 18.3
| 2014-09-03 02:00 | 15.2 | 18.3 | 18.3
| 2014-09-03 02:30 | 14.4 | 17.8 | 18.3
| 2014-09-03 03:00 | 14.1 | 17.8 | 18.3
| 2014-09-03 03:30 | 13.7 | 17.8 | 18.3
| 2014-09-03 04:00 | 13.4 | 17.8 | 18.3
| 2014-09-03 04:30 | 13.2 | 17.8 | 18.3
| 2014-09-03 05:00 | 12.8 | 17.8 | 18.3
| 2014-09-03 05:30 | 12.4 | 17.8 | 18.3
| 2014-09-03 06:00 | 12 | 17.8 | 18.3
| 2014-09-03 06:30 | 11.9 | 17.2 | 18.3
| 2014-09-03 07:00 | 11.8 | 17.2 | 18.3
| 2014-09-03 07:30 | 11.9 | 17.2 | 18.3
| 2014-09-03 08:00 | 12.2 | 17.2 | 18.3
| 2014-09-03 08:30 | 12.8 | 17.2 | 18.3
| 2014-09-03 09:00 | 13.6 | 17.2 | 18.3
| 2014-09-03 09:30 | 15.1 | 17.2 | 18.3
| 2014-09-03 10:00 | 15.6 | 16.7 | 18.3
| 2014-09-03 10:30 | 15.8 | 16.7 | 18.3
| 2014-09-03 11:00 | 16.3 | 16.7 | 18.3
| 2014-09-03 11:30 | 15.7 | 16.7 | 18.3
| 2014-09-03 12:00 | 15.7 | 16.7 | 18.3
| 2014-09-03 12:30 | 16 | 16.7 | 18.3
| 2014-09-03 13:00 | 16.3 | 16.7 | 18.3
| 2014-09-03 13:30 | 16.6 | 17.2 | 18.3
| 2014-09-03 14:00 | 17.1 | 17.2 | 18.3
| 2014-09-03 14:30 | 17.7 | 17.2 | 18.3
| 2014-09-03 15:00 | 18.2 | 17.2 | 18.3
| 2014-09-03 15:30 | 17.8 | 17.2 | 18.3
| 2014-09-03 16:00 | 17.7 | 17.2 | 18.3
| 2014-09-03 16:30 | 18.1 | 17.2 | 18.3
| 2014-09-03 17:00 | 18.4 | 17.8 | 18.3
| 2014-09-03 17:30 | 18.4 | 17.8 | 18.3
| 2014-09-03 18:00 | 18.4 | 17.8 | 18.3
| 2014-09-03 18:30 | 18.7 | 17.8 | 18.3
| 2014-09-03 19:00 | 18.1 | 17.8 | 18.3
| 2014-09-03 19:30 | 17.6 | 17.8 | 18.3
| 2014-09-03 20:00 | 17.1 | 17.8 | 18.3
| 2014-09-03 20:30 | 16.7 | 17.8 | 18.3
| 2014-09-03 21:00 | 16.4 | 17.8 | 18.3
| 2014-09-03 21:30 | 16.3 | 17.8 | 18.3
| 2014-09-03 22:00 | 16 | 17.8 | 18.3
| 2014-09-03 22:30 | 15.8 | 17.8 | 18.3
| 2014-09-03 23:00 | 16.1 | 17.8 | 18.3
| 2014-09-03 23:30 | 16.1 | 17.8 | 18.3
| 2014-09-04 | 15.9 | 17.8 | 18.3
| 2014-09-04 00:30 | 15.8 | 17.8 | 18.3
| 2014-09-04 01:00 | 15.7 | 17.8 | 18.3
| 2014-09-04 01:30 | 15.4 | 17.8 | 18.3
| 2014-09-04 02:00 | 15.5 | 17.8 | 18.3
| 2014-09-04 02:30 | 15.6 | 17.8 | 18.3
| 2014-09-04 03:00 | 15.6 | 17.8 | 18.3
| 2014-09-04 03:30 | 15.5 | 17.8 | 18.3
| 2014-09-04 04:00 | 15.3 | 17.8 | 18.3
| 2014-09-04 04:30 | 15.3 | 17.8 | 18.3
| 2014-09-04 05:00 | 15.2 | 17.2 | 18.3
| 2014-09-04 05:30 | 15.3 | 17.2 | 18.3
| 2014-09-04 06:00 | 15.3 | 17.2 | 18.3
| 2014-09-04 06:30 | 15.3 | 17.2 | 18.3
| 2014-09-04 07:00 | 15.3 | 17.2 | 18.3
| 2014-09-04 07:30 | 15.4 | 17.2 | 18.3
| 2014-09-04 08:00 | 15.8 | 17.2 | 18.3
| 2014-09-04 08:30 | 16.2 | 17.2 | 18.3
| 2014-09-04 09:00 | 16.4 | 17.2 | 18.3
| 2014-09-04 09:30 | 16.7 | 17.2 | 18.3
| 2014-09-04 10:00 | 17.1 | 17.2 | 18.3
| 2014-09-04 10:30 | 17.7 | 17.2 | 18.3
| 2014-09-04 11:00 | 18.6 | 17.2 | 18.3
| 2014-09-04 11:30 | 18.6 | 17.2 | 18.3
| 2014-09-04 12:00 | 18.8 | 17.2 | 18.3
| 2014-09-04 12:30 | 19.4 | 17.2 | 18.3
| 2014-09-04 13:00 | 19.4 | 17.2 | 18.3
| 2014-09-04 13:30 | 19.6 | 17.8 | 18.3
| 2014-09-04 14:00 | 20.2 | 17.8 | 18.3
| 2014-09-04 14:30 | 20.9 | 17.8 | 18.3
| 2014-09-04 15:00 | 20.7 | 17.8 | 18.3
| 2014-09-04 15:30 | 20.6 | 17.8 | 17.8
| 2014-09-04 16:00 | 20.7 | 17.8 | 17.8
| 2014-09-04 16:30 | 20 | 18.3 | 17.8
| 2014-09-04 17:00 | 19.9 | 18.3 | 17.8
| 2014-09-04 17:30 | 20 | 18.3 | 17.8
| 2014-09-04 18:00 | 20 | 18.3 | 17.8
| 2014-09-04 18:30 | 19.9 | 18.3 | 17.8
| 2014-09-04 19:00 | 19.8 | 18.3 | 17.8
| 2014-09-04 19:30 | 19.3 | 18.3 | 17.8
| 2014-09-04 20:00 | 18.8 | 18.3 | 17.8
| 2014-09-04 20:30 | 18.4 | 18.3 | 17.8
| 2014-09-04 21:00 | 17.9 | 18.3 | 17.8
| 2014-09-04 21:30 | 17.4 | 18.3 | 17.8
| 2014-09-04 22:00 | 16.8 | 18.3 | 17.8
| 2014-09-04 22:30 | 16.6 | 18.3 | 17.8
| 2014-09-04 23:00 | 16.4 | 18.3 | 17.8
| 2014-09-04 23:30 | 16.2 | 18.3 | 17.8
| 2014-09-05 | 16.1 | 18.3 | 17.8
| 2014-09-05 00:30 | 15.8 | 18.3 | 17.8
| 2014-09-05 01:00 | 15.6 | 18.3 | 17.8
| 2014-09-05 01:30 | 15.4 | 18.3 | 17.8
| 2014-09-05 02:00 | 15.4 | 18.3 | 17.8
| 2014-09-05 02:30 | 15.4 | 18.3 | 17.8
| 2014-09-05 03:00 | 15.5 | 18.3 | 17.8
| 2014-09-05 03:30 | 15.5 | 18.3 | 17.8
| 2014-09-05 04:00 | 15.4 | 17.8 | 17.8
| 2014-09-05 04:30 | 15.3 | 17.8 | 17.8
| 2014-09-05 05:00 | 15.3 | 17.8 | 17.8
| 2014-09-05 05:30 | 15.2 | 17.8 | 17.8
| 2014-09-05 06:00 | 15 | 17.8 | 17.8
| 2014-09-05 06:30 | 14.8 | 17.8 | 17.8
| 2014-09-05 07:00 | 14.5 | 17.8 | 17.8
| 2014-09-05 07:30 | 15.1 | 17.8 | 17.8
| 2014-09-05 08:00 | 16.2 | 17.8 | 17.8
| 2014-09-05 08:30 | 17.1 | 17.8 | 17.8
| 2014-09-05 09:00 | 18.1 | 17.8 | 17.8
| 2014-09-05 09:30 | 18.9 | 17.8 | 17.8
| 2014-09-05 10:00 | 19.7 | 17.8 | 17.8
| 2014-09-05 10:30 | 20.4 | 17.8 | 17.8
| 2014-09-05 11:00 | 20.8 | 17.8 | 17.8
| 2014-09-05 11:30 | 21.8 | 17.8 | 17.8
| 2014-09-05 12:00 | 22.4 | 17.8 | 17.8
| 2014-09-05 12:30 | 22.9 | 17.8 | 17.8
| 2014-09-05 13:00 | 23.5 | 17.8 | 17.8
| 2014-09-05 13:30 | 24.3 | 18.3 | 17.8
| 2014-09-05 14:00 | 24.7 | 18.3 | 17.8
| 2014-09-05 14:30 | 25.3 | 18.3 | 17.8
| 2014-09-05 15:00 | 25.2 | 18.9 | 17.8
| 2014-09-05 15:30 | 24.6 | 18.9 | 17.8
| 2014-09-05 16:00 | 24.4 | 19.4 | 17.8
| 2014-09-05 16:30 | 24.6 | 19.4 | 17.8
| 2014-09-05 17:00 | 25.9 | 19.4 | 17.8
| 2014-09-05 17:30 | 26.1 | 19.4 | 17.8
| 2014-09-05 18:00 | 26.2 | 20 | 17.8
| 2014-09-05 18:30 | 25.7 | 20 | 17.8
| 2014-09-05 19:00 | 24.4 | 20 | 17.8
| 2014-09-05 19:30 | 22.8 | 20 | 17.8
| 2014-09-05 20:00 | 21.3 | 20 | 17.8
| 2014-09-05 20:30 | 19.9 | 20 | 17.8
| 2014-09-05 21:00 | 19.2 | 20 | 17.8
| 2014-09-05 21:30 | 18.7 | 20 | 17.8
| 2014-09-05 22:00 | 18.2 | 20 | 17.8
| 2014-09-05 22:30 | 17.7 | 20 | 17.8
| 2014-09-05 23:00 | 17.2 | 20 | 17.8
| 2014-09-05 23:30 | 16.8 | 20 | 17.8
| 2014-09-06 | 16.4 | 20 | 17.8
| 2014-09-06 00:30 | 16.3 | 19.4 | 17.8
| 2014-09-06 01:00 | 16 | 19.4 | 17.8
| 2014-09-06 01:30 | 15.7 | 19.4 | 17.8
| 2014-09-06 02:00 | 15.6 | 19.4 | 17.8
| 2014-09-06 02:30 | 15.2 | 19.4 | 17.8
| 2014-09-06 03:00 | 14.8 | 19.4 | 17.8
| 2014-09-06 03:30 | 14.3 | 18.9 | 17.8
| 2014-09-06 04:00 | 14.3 | 18.9 | 17.8
| 2014-09-06 04:30 | 14.1 | 18.9 | 17.8
| 2014-09-06 05:00 | 13.9 | 18.9 | 17.8
| 2014-09-06 05:30 | 13.3 | 18.9 | 17.8
| 2014-09-06 06:00 | 13.3 | 18.9 | 17.8
| 2014-09-06 06:30 | 13.2 | 18.9 | 17.8
| 2014-09-06 07:00 | 13 | 18.3 | 17.8
| 2014-09-06 07:30 | 13.6 | 18.3 | 17.8
| 2014-09-06 08:00 | 14.7 | 18.3 | 17.8
| 2014-09-06 08:30 | 15.1 | 18.3 | 18.3
| 2014-09-06 09:00 | 15.3 | 18.3 | 18.3
| 2014-09-06 09:30 | 15.5 | 18.3 | 18.3
| 2014-09-06 10:00 | 16.1 | 18.3 | 18.3
| 2014-09-06 10:30 | 16.9 | 18.3 | 18.3
| 2014-09-06 11:00 | 17.6 | 18.3 | 18.3
| 2014-09-06 11:30 | 18.6 | 18.3 | 18.3
| 2014-09-06 12:00 | 20.6 | 18.3 | 18.3
| 2014-09-06 12:30 | 22.6 | 18.3 | 18.3
| 2014-09-06 13:00 | 23.8 | 18.3 | 18.3
| 2014-09-06 13:30 | 24.6 | 18.3 | 18.3
| 2014-09-06 14:00 | 25.4 | 18.9 | 18.3
| 2014-09-06 14:30 | 25.9 | 18.9 | 18.3
| 2014-09-06 15:00 | 26.8 | 18.9 | 18.3
| 2014-09-06 15:30 | 26.9 | 19.4 | 18.3
| 2014-09-06 16:00 | 27.3 | 19.4 | 18.3
| 2014-09-06 16:30 | 27.7 | 19.4 | 18.3
| 2014-09-06 17:00 | 27.5 | 20 | 18.3
| 2014-09-06 17:30 | 27.4 | 20 | 18.3
| 2014-09-06 18:00 | 27.4 | 20 | 18.3
| 2014-09-06 18:30 | 26.9 | 20 | 18.3
| 2014-09-06 19:00 | 24.5 | 20.6 | 18.3
| 2014-09-06 19:30 | 22.4 | 20.6 | 18.3
| 2014-09-06 20:00 | 20.8 | 20.6 | 18.3
| 2014-09-06 20:30 | 20.8 | 20.6 | 18.3
| 2014-09-06 21:00 | 19.7 | 20.6 | 18.3
| 2014-09-06 21:30 | 19.1 | 20.6 | 18.3
| 2014-09-06 22:00 | 18.6 | 20.6 | 18.3
| 2014-09-06 22:30 | 18 | 20.6 | 18.3
| 2014-09-06 23:00 | 17.8 | 20.6 | 18.3
| 2014-09-06 23:30 | 17.6 | 20 | 18.3
| 2014-09-07 | 17.6 | 20 | 18.3
| 2014-09-07 00:30 | 17.1 | 20 | 18.3
| 2014-09-07 01:00 | 16.6 | 20 | 18.3
| 2014-09-07 01:30 | 16.4 | 20 | 18.3
| 2014-09-07 02:00 | 16.2 | 20 | 18.3
| 2014-09-07 02:30 | 16.2 | 20 | 18.3
| 2014-09-07 03:00 | 16.1 | 20 | 18.3
| 2014-09-07 03:30 | 15.7 | 20 | 18.3
| 2014-09-07 04:00 | 15.7 | 19.4 | 18.3
| 2014-09-07 04:30 | 15.7 | 19.4 | 18.3
| 2014-09-07 05:00 | 15.7 | 19.4 | 18.3
| 2014-09-07 05:30 | 15.3 | 19.4 | 18.3
| 2014-09-07 06:00 | 15.1 | 19.4 | 18.3
| 2014-09-07 06:30 | 15.1 | 19.4 | 18.3
| 2014-09-07 07:00 | 15.1 | 19.4 | 18.3
| 2014-09-07 07:30 | 15.2 | 19.4 | 18.3
| 2014-09-07 08:00 | 15.6 | 18.9 | 18.3
| 2014-09-07 08:30 | 15.9 | 18.9 | 18.3
| 2014-09-07 09:00 | 16.4 | 18.9 | 18.3
| 2014-09-07 09:30 | 17.4 | 18.9 | 18.3
| 2014-09-07 10:00 | 18.1 | 18.9 | 18.3
| 2014-09-07 10:30 | 19.2 | 18.9 | 18.3
| 2014-09-07 11:00 | 20.5 | 18.9 | 18.3
| 2014-09-07 11:30 | 21.6 | 18.9 | 18.3
| 2014-09-07 12:00 | 21.7 | 18.9 | 18.3
| 2014-09-07 12:30 | 22.4 | 18.9 | 18.3
| 2014-09-07 13:00 | 23.2 | 18.9 | 18.3
| 2014-09-07 13:30 | 23.8 | 19.4 | 18.3
| 2014-09-07 14:00 | 25.1 | 19.4 | 18.3
| 2014-09-07 14:30 | 25.8 | 19.4 | 18.3
| 2014-09-07 15:00 | 24.7 | 19.4 | 18.3
| 2014-09-07 15:30 | 24.3 | 20 | 18.3
| 2014-09-07 16:00 | 24.4 | 20 | 18.3
| 2014-09-07 16:30 | 24.6 | 20 | 18.3
| 2014-09-07 17:00 | 24.8 | 20 | 18.3
| 2014-09-07 17:30 | 24.8 | 20.6 | 18.3
| 2014-09-07 18:00 | 24.4 | 20.6 | 18.3
| 2014-09-07 18:30 | 23.3 | 20.6 | 18.3
| 2014-09-07 19:00 | 22.7 | 20.6 | 18.3
| 2014-09-07 19:30 | 21.7 | 20.6 | 18.3
| 2014-09-07 20:00 | 20.3 | 20.6 | 18.3
| 2014-09-07 20:30 | 19.4 | 20.6 | 18.3
| 2014-09-07 21:00 | 18.3 | 20.6 | 18.3
| 2014-09-07 21:30 | 17.5 | 20.6 | 18.3
| 2014-09-07 22:00 | 16.8 | 20.6 | 18.3
| 2014-09-07 22:30 | 16.6 | 20.6 | 18.3
| 2014-09-07 23:00 | 16.2 | 20.6 | 18.3
| 2014-09-07 23:30 | 15.9 | 20.6 | 18.3
| 2014-09-08 | 15.7 | 20.6 | 18.3
| 2014-09-08 00:30 | 15.6 | 20.6 | 18.3
| 2014-09-08 01:00 | 15.7 | 20 | 18.3
| 2014-09-08 01:30 | 15.9 | 20 | 18.3
| 2014-09-08 02:00 | 15.8 | 20 | 18.3
| 2014-09-08 02:30 | 15.8 | 20 | 18.3
| 2014-09-08 03:00 | 15.8 | 20 | 18.3
| 2014-09-08 03:30 | 15.9 | 20 | 18.3
| 2014-09-08 04:00 | 15.8 | 20 | 18.3
| 2014-09-08 04:30 | 15.8 | 19.4 | 18.3
| 2014-09-08 05:00 | 15.7 | 19.4 | 18.3
| 2014-09-08 05:30 | 15.4 | 19.4 | 18.3
| 2014-09-08 06:00 | 15.4 | 19.4 | 18.3
| 2014-09-08 06:30 | 15.8 | 19.4 | 18.3
| 2014-09-08 07:00 | 15.6 | 19.4 | 18.3
| 2014-09-08 07:30 | 15.5 | 19.4 | 18.3
| 2014-09-08 08:00 | 15.7 | 19.4 | 18.3
| 2014-09-08 08:30 | 16.1 | 19.4 | 18.3
| 2014-09-08 09:00 | 16.7 | 18.9 | 18.3
| 2014-09-08 09:30 | 17.9 | 18.9 | 18.3
| 2014-09-08 10:00 | 18.6 | 18.9 | 18.3
| 2014-09-08 10:30 | 19.2 | 18.9 | 18.3
| 2014-09-08 11:00 | 19.8 | 18.9 | 18.3
| 2014-09-08 11:30 | 21.1 | 18.9 | 18.3
| 2014-09-08 12:00 | 22.4 | 18.9 | 18.3
| 2014-09-08 12:30 | 22.4 | 19.4 | 18.3
| 2014-09-08 13:00 | 23.3 | 19.4 | 18.3
| 2014-09-08 13:30 | 23.4 | 19.4 | 18.3
| 2014-09-08 14:00 | 24.3 | 19.4 | 18.3
| 2014-09-08 14:30 | 24.3 | 20 | 18.3
| 2014-09-08 15:00 | 24.6 | 20 | 18.3
| 2014-09-08 15:30 | 24.8 | 20 | 18.3
| 2014-09-08 16:00 | 25.1 | 20 | 18.3
| 2014-09-08 16:30 | 24.4 | 20.6 | 18.3
| 2014-09-08 17:00 | 24.7 | 20.6 | 18.3
| 2014-09-08 17:30 | 24.3 | 20.6 | 18.3
| 2014-09-08 18:00 | 25.2 | 20.6 | 18.3
| 2014-09-08 18:30 | 24.4 | 21.1 | 18.3
| 2014-09-08 19:00 | 23.2 | 21.1 | 18.3
| 2014-09-08 19:30 | 21.6 | 21.1 | 18.3
| 2014-09-08 20:00 | 19.8 | 21.1 | 18.3
| 2014-09-08 20:30 | 18.6 | 21.1 | 18.3
| 2014-09-08 21:00 | 17.7 | 21.1 | 18.3
| 2014-09-08 21:30 | 16.8 | 21.1 | 18.3
| 2014-09-08 22:00 | 16.2 | 21.1 | 18.3
| 2014-09-08 22:30 | 15.8 | 21.1 | 18.3
| 2014-09-08 23:00 | 15.4 | 20.6 | 18.3
| 2014-09-08 23:30 | 15.1 | 20.6 | 18.3
| 2014-09-09 | 14.7 | 20.6 | 18.3
| 2014-09-09 00:30 | 14.6 | 20.6 | 18.3
| 2014-09-09 01:00 | 14.6 | 20.6 | 18.3
| 2014-09-09 01:30 | 14.3 | 20.6 | 18.3
| 2014-09-09 02:00 | 13.9 | 20 | 18.3
| 2014-09-09 02:30 | 13.7 | 20 | 18.3
| 2014-09-09 03:00 | 13.6 | 20 | 18.3
| 2014-09-09 03:30 | 13.4 | 20 | 18.3
| 2014-09-09 04:00 | 12.9 | 20 | 18.3
| 2014-09-09 04:30 | 12.7 | 20 | 18.3
| 2014-09-09 05:00 | 12.5 | 19.4 | 18.3
| 2014-09-09 05:30 | 11.9 | 19.4 | 18.3
| 2014-09-09 06:00 | 11.8 | 19.4 | 18.3
| 2014-09-09 06:30 | 11.8 | 19.4 | 18.3
| 2014-09-09 07:00 | 11.7 | 19.4 | 18.3
| 2014-09-09 07:30 | 11.9 | 18.9 | 18.3
| 2014-09-09 08:00 | 12.6 | 18.9 | 18.3
| 2014-09-09 08:30 | 13.2 | 18.9 | 18.3
| 2014-09-09 09:00 | 14.3 | 18.9 | 18.3
| 2014-09-09 09:30 | 15.6 | 18.9 | 18.3
| 2014-09-09 10:00 | 16.9 | 18.9 | 18.3
| 2014-09-09 10:30 | 17.2 | 18.9 | 18.3
| 2014-09-09 11:00 | 18 | 18.9 | 18.9
| 2014-09-09 11:30 | 18.4 | 18.9 | 18.9
| 2014-09-09 12:00 | 19.2 | 18.9 | 18.9
| 2014-09-09 12:30 | 19.5 | 18.9 | 18.9
| 2014-09-09 13:00 | 20.9 | 18.9 | 18.9
| 2014-09-09 13:30 | 21.7 | 18.9 | 18.9
| 2014-09-09 14:00 | 21.1 | 18.9 | 18.9
| 2014-09-09 14:30 | 20.9 | 18.9 | 18.9
| 2014-09-09 15:00 | 21.9 | 19.4 | 18.9
| 2014-09-09 15:30 | 22.4 | 19.4 | 18.9
| 2014-09-09 16:00 | 22.3 | 19.4 | 18.9
| 2014-09-09 16:30 | 21.8 | 19.4 | 18.9
| 2014-09-09 17:00 | 22.2 | 20 | 18.9
| 2014-09-09 17:30 | 23 | 20 | 18.9
| 2014-09-09 18:00 | 22.4 | 20 | 18.9
| 2014-09-09 18:30 | 21.9 | 20 | 18.9
| 2014-09-09 19:00 | 20.9 | 20 | 18.9
| 2014-09-09 19:30 | 19.2 | 20 | 18.9
| 2014-09-09 20:00 | 17.2 | 20 | 18.9
| 2014-09-09 20:30 | 15.7 | 20 | 18.9
| 2014-09-09 21:00 | 14.6 | 20 | 18.9
| 2014-09-09 21:30 | 13.7 | 20 | 18.9
| 2014-09-09 22:00 | 13.7 | 20 | 18.9
| 2014-09-09 22:30 | 13.8 | 20 | 18.9
| 2014-09-09 23:00 | 13.6 | 20 | 18.9
| 2014-09-09 23:30 | 13.1 | 20 | 18.9
| 2014-09-10 | 12.5 | 19.4 | 18.9
| 2014-09-10 00:30 | 12.3 | 19.4 | 18.9
| 2014-09-10 01:00 | 12 | 19.4 | 18.9
| 2014-09-10 01:30 | 11.3 | 19.4 | 18.9
| 2014-09-10 02:00 | 11.2 | 19.4 | 18.9
| 2014-09-10 02:30 | 11.6 | 19.4 | 18.9
| 2014-09-10 03:00 | 11.8 | 18.9 | 18.9
| 2014-09-10 03:30 | 11.8 | 18.9 | 18.9
| 2014-09-10 04:00 | 11.7 | 18.9 | 18.9
| 2014-09-10 04:30 | 11.7 | 18.9 | 18.9
| 2014-09-10 05:00 | 11.6 | 18.9 | 18.9
| 2014-09-10 05:30 | 11.4 | 18.9 | 18.9
| 2014-09-10 06:00 | 11.4 | 18.3 | 18.9
| 2014-09-10 06:30 | 11.5 | 18.3 | 18.9
| 2014-09-10 07:00 | 11.6 | 18.3 | 18.9
| 2014-09-10 07:30 | 11.8 | 18.3 | 18.9
| 2014-09-10 08:00 | 12.3 | 18.3 | 18.9
| 2014-09-10 08:30 | 13 | 18.3 | 18.9
| 2014-09-10 09:00 | 13.9 | 18.3 | 18.9
| 2014-09-10 09:30 | 14.7 | 18.3 | 18.9
| 2014-09-10 10:00 | 15.2 | 18.3 | 18.9
| 2014-09-10 10:30 | 16.2 | 18.3 | 18.9
| 2014-09-10 11:00 | 17.3 | 18.3 | 18.9
| 2014-09-10 11:30 | 16.8 | 18.3 | 18.9
| 2014-09-10 12:00 | 17.6 | 18.3 | 18.9
| 2014-09-10 12:30 | 17.2 | 18.3 | 18.9
| 2014-09-10 13:00 | 17.7 | 18.3 | 18.9
| 2014-09-10 13:30 | 19.1 | 18.3 | 18.9
| 2014-09-10 14:00 | 17.9 | 18.3 | 18.9
| 2014-09-10 14:30 | 17.8 | 18.3 | 18.9
| 2014-09-10 15:00 | 18.4 | 18.3 | 18.9
| 2014-09-10 15:30 | 18.7 | 18.3 | 18.9
| 2014-09-10 16:00 | 18.3 | 18.9 | 18.9
| 2014-09-10 16:30 | 17.7 | 18.9 | 18.9
| 2014-09-10 17:00 | 17.4 | 18.9 | 18.9
| 2014-09-10 17:30 | 17.3 | 18.9 | 18.9
| 2014-09-10 18:00 | 17.2 | 18.9 | 18.9
| 2014-09-10 18:30 | 16.8 | 18.9 | 18.9
| 2014-09-10 19:00 | 16.4 | 18.9 | 18.9
| 2014-09-10 19:30 | 15.8 | 18.9 | 18.9
| 2014-09-10 20:00 | 14.3 | 18.9 | 18.9
| 2014-09-10 20:30 | 12.8 | 18.9 | 18.9
| 2014-09-10 21:00 | 11.9 | 18.9 | 18.9
| 2014-09-10 21:30 | 11.1 | 18.9 | 18.9
| 2014-09-10 22:00 | 10.6 | 18.9 | 18.9
| 2014-09-10 22:30 | 10.2 | 18.9 | 18.9
| 2014-09-10 23:00 | 9.9 | 18.9 | 18.9
| 2014-09-10 23:30 | 9.6 | 18.9 | 18.9
| 2014-09-11 | 9.3 | 18.9 | 18.9
| 2014-09-11 00:30 | 8.9 | 18.3 | 18.9
| 2014-09-11 01:00 | 8.8 | 18.3 | 18.9
| 2014-09-11 01:30 | 8.6 | 18.3 | 18.9
| 2014-09-11 02:00 | 8.4 | 18.3 | 18.9
| 2014-09-11 02:30 | 8 | 18.3 | 18.9
| 2014-09-11 03:00 | 7.7 | 18.3 | 18.9
| 2014-09-11 03:30 | 7.4 | 17.8 | 18.9
| 2014-09-11 04:00 | 7.5 | 17.8 | 18.9
| 2014-09-11 04:30 | 7.4 | 17.8 | 18.9
| 2014-09-11 05:00 | 8.2 | 17.8 | 18.9
| 2014-09-11 05:30 | 8.6 | 17.8 | 18.9
| 2014-09-11 06:00 | 8.8 | 17.2 | 18.9
| 2014-09-11 06:30 | 9.1 | 17.2 | 18.9
| 2014-09-11 07:00 | 9.5 | 17.2 | 18.9
| 2014-09-11 07:30 | 9.8 | 17.2 | 18.9
| 2014-09-11 08:00 | 10.3 | 17.2 | 18.9
| 2014-09-11 08:30 | 10.8 | 17.2 | 18.9
| 2014-09-11 09:00 | 11.4 | 17.2 | 18.9
| 2014-09-11 09:30 | 12.3 | 17.2 | 18.9
| 2014-09-11 10:00 | 13.4 | 17.2 | 18.9
| 2014-09-11 10:30 | 14.3 | 16.7 | 18.9
| 2014-09-11 11:00 | 15.5 | 16.7 | 18.9
| 2014-09-11 11:30 | 16.4 | 17.2 | 18.9
| 2014-09-11 12:00 | 15.7 | 17.2 | 18.9
| 2014-09-11 12:30 | 14.7 | 17.2 | 18.9
| 2014-09-11 13:00 | 15.6 | 17.2 | 18.9
| 2014-09-11 13:30 | 15 | 17.2 | 18.9
| 2014-09-11 14:00 | 15.4 | 17.2 | 18.9
| 2014-09-11 14:30 | 16.9 | 17.2 | 18.9
| 2014-09-11 15:00 | 17 | 17.2 | 18.9
| 2014-09-11 15:30 | 16.7 | 17.8 | 18.9
| 2014-09-11 16:00 | 15.9 | 17.8 | 18.9
| 2014-09-11 16:30 | 15.9 | 17.8 | 18.9
| 2014-09-11 17:00 | 17.2 | 17.8 | 18.9
| 2014-09-11 17:30 | 16.3 | 17.8 | 18.9
| 2014-09-11 18:00 | 15.3 | 17.8 | 18.9
| 2014-09-11 18:30 | 15.6 | 18.3 | 18.9
| 2014-09-11 19:00 | 15.2 | 18.3 | 18.9
| 2014-09-11 19:30 | 14.7 | 18.3 | 18.9
| 2014-09-11 20:00 | 14.3 | 18.3 | 18.9
| 2014-09-11 20:30 | 13.5 | 18.3 | 18.9
| 2014-09-11 21:00 | 12.9 | 18.3 | 18.9
| 2014-09-11 21:30 | 12.3 | 18.3 | 18.9
| 2014-09-11 22:00 | 11.7 | 17.8 | 18.9
| 2014-09-11 22:30 | 11.3 | 17.8 | 18.9
| 2014-09-11 23:00 | 11.4 | 17.8 | 18.9
| 2014-09-11 23:30 | 11.6 | 17.8 | 18.9
| 2014-09-12 | 11.8 | 17.8 | 18.3
| 2014-09-12 00:30 | 11.9 | 17.8 | 18.3
| 2014-09-12 01:00 | 12.2 | 17.8 | 18.3
| 2014-09-12 01:30 | 11.9 | 17.2 | 18.3
| 2014-09-12 02:00 | 11.5 | 17.2 | 18.3
| 2014-09-12 02:30 | 11.5 | 17.2 | 18.3
| 2014-09-12 03:00 | 11.2 | 17.2 | 18.3
| 2014-09-12 03:30 | 11 | 17.2 | 18.3
| 2014-09-12 04:00 | 11.1 | 17.2 | 18.3
| 2014-09-12 04:30 | 11.3 | 17.2 | 18.3
| 2014-09-12 05:00 | 11.5 | 17.2 | 18.3
| 2014-09-12 05:30 | 11.7 | 17.2 | 18.3
| 2014-09-12 06:00 | 11.7 | 16.7 | 18.3
| 2014-09-12 06:30 | 11.6 | 16.7 | 18.3
| 2014-09-12 07:00 | 11.6 | 16.7 | 18.3
| 2014-09-12 07:30 | 11.6 | 16.7 | 18.3
| 2014-09-12 08:00 | 11.8 | 16.7 | 18.3
| 2014-09-12 08:30 | 11.9 | 16.7 | 18.3
| 2014-09-12 09:00 | 12.2 | 16.7 | 18.3
| 2014-09-12 09:30 | 12.3 | 16.7 | 18.3
| 2014-09-12 10:00 | 12.6 | 16.7 | 18.3
| 2014-09-12 10:30 | 13.1 | 16.7 | 18.3
| 2014-09-12 11:00 | 13.4 | 16.7 | 18.3
| 2014-09-12 11:30 | 13.7 | 16.7 | 18.3
| 2014-09-12 12:00 | 14 | 16.7 | 18.3
| 2014-09-12 12:30 | 14.5 | 16.7 | 18.3
| 2014-09-12 13:00 | 14.7 | 16.7 | 18.3
| 2014-09-12 13:30 | 14.7 | 16.7 | 18.3
| 2014-09-12 14:00 | 14.4 | 16.7 | 18.3
| 2014-09-12 14:30 | 14.7 | 16.7 | 18.3
| 2014-09-12 15:00 | 14.6 | 16.7 | 18.3
| 2014-09-12 15:30 | 14.5 | 16.7 | 18.3
| 2014-09-12 16:00 | 14.4 | 16.7 | 18.3
| 2014-09-12 16:30 | 14.5 | 16.7 | 18.3
| 2014-09-12 17:00 | 14.5 | 16.7 | 18.3
| 2014-09-12 17:30 | 14.5 | 16.7 | 18.3
| 2014-09-12 18:00 | 14.6 | 16.7 | 18.3
| 2014-09-12 18:30 | 14.7 | 16.7 | 18.3
| 2014-09-12 19:00 | 14.8 | 16.7 | 18.3
| 2014-09-12 19:30 | 14.9 | 16.7 | 18.3
| 2014-09-12 20:00 | 14.8 | 16.7 | 18.3
| 2014-09-12 20:30 | 14.9 | 16.7 | 18.3
| 2014-09-12 21:00 | 15.1 | 16.7 | 18.3
| 2014-09-12 21:30 | 15.5 | 16.7 | 18.3
| 2014-09-12 22:00 | 15.9 | 16.7 | 18.3
| 2014-09-12 22:30 | 16.3 | 16.7 | 18.3
| 2014-09-12 23:00 | 16.4 | 16.7 | 18.3
| 2014-09-12 23:30 | 16.5 | 16.7 | 18.3
| 2014-09-13 | 16.5 | 16.7 | 18.3
| 2014-09-13 00:30 | 16.2 | 16.7 | 18.3
| 2014-09-13 01:00 | 15.9 | 16.7 | 18.3
| 2014-09-13 01:30 | 15.8 | 16.7 | 18.3
| 2014-09-13 02:00 | 15.6 | 16.7 | 18.3
| 2014-09-13 02:30 | 15.2 | 16.7 | 18.3
| 2014-09-13 03:00 | 15.4 | 16.7 | 18.3
| 2014-09-13 03:30 | 15.3 | 16.7 | 18.3
| 2014-09-13 04:00 | 15.2 | 16.7 | 18.3
| 2014-09-13 04:30 | 14.8 | 16.7 | 18.3
| 2014-09-13 05:00 | 15.2 | 16.7 | 18.3
| 2014-09-13 05:30 | 15.3 | 16.7 | 18.3
| 2014-09-13 06:00 | 15 | 16.7 | 18.3
| 2014-09-13 06:30 | 15.1 | 16.7 | 18.3
| 2014-09-13 07:00 | 15.4 | 16.7 | 18.3
| 2014-09-13 07:30 | 15.6 | 16.1 | 18.3
| 2014-09-13 08:00 | 15.8 | 16.1 | 18.3
| 2014-09-13 08:30 | 16.1 | 16.1 | 18.3
| 2014-09-13 09:00 | 16.4 | 16.1 | 18.3
| 2014-09-13 09:30 | 16.8 | 16.1 | 18.3
| 2014-09-13 10:00 | 16.8 | 16.1 | 18.3
| 2014-09-13 10:30 | 17.3 | 16.1 | 18.3
| 2014-09-13 11:00 | 17.7 | 16.7 | 18.3
| 2014-09-13 11:30 | 17.7 | 16.7 | 18.3
| 2014-09-13 12:00 | 18.3 | 16.7 | 18.3
| 2014-09-13 12:30 | 18.1 | 16.7 | 18.3
| 2014-09-13 13:00 | 17.9 | 16.7 | 18.3
| 2014-09-13 13:30 | 17.9 | 16.7 | 18.3
| 2014-09-13 14:00 | 18.3 | 16.7 | 18.3
| 2014-09-13 14:30 | 19.3 | 17.2 | 18.3
| 2014-09-13 15:00 | 18.9 | 17.2 | 18.3
| 2014-09-13 15:30 | 19.6 | 17.2 | 18.3
| 2014-09-13 16:00 | 19.1 | 17.2 | 18.3
| 2014-09-13 16:30 | 18.7 | 17.2 | 18.3
| 2014-09-13 17:00 | 18.4 | 17.2 | 18.3
| 2014-09-13 17:30 | 18.4 | 17.8 | 18.3
| 2014-09-13 18:00 | 18 | 17.8 | 18.3
| 2014-09-13 18:30 | 17.7 | 17.8 | 18.3
| 2014-09-13 19:00 | 17.3 | 17.8 | 18.3
| 2014-09-13 19:30 | 17.1 | 17.8 | 18.3
| 2014-09-13 20:00 | 16.9 | 17.8 | 18.3
| 2014-09-13 20:30 | 16.7 | 17.8 | 18.3
| 2014-09-13 21:00 | 16.4 | 17.8 | 18.3
| 2014-09-13 21:30 | 16.1 | 17.8 | 18.3
| 2014-09-13 22:00 | 16.1 | 17.8 | 18.3
| 2014-09-13 22:30 | 15.9 | 17.8 | 18.3
| 2014-09-13 23:00 | 15.8 | 17.8 | 18.3
| 2014-09-13 23:30 | 15.3 | 17.8 | 18.3
| 2014-09-14 | 14.8 | 17.8 | 18.3
| 2014-09-14 00:30 | 14.6 | 17.8 | 18.3
| 2014-09-14 01:00 | 14.6 | 17.8 | 18.3
| 2014-09-14 01:30 | 14.7 | 17.8 | 18.3
| 2014-09-14 02:00 | 15 | 17.8 | 18.3
| 2014-09-14 02:30 | 15.3 | 17.2 | 18.3
| 2014-09-14 03:00 | 15.4 | 17.2 | 18.3
| 2014-09-14 03:30 | 14.7 | 17.2 | 18.3
| 2014-09-14 04:00 | 14.2 | 17.2 | 18.3
| 2014-09-14 04:30 | 14.2 | 17.2 | 18.3
| 2014-09-14 05:00 | 13.9 | 17.2 | 18.3
| 2014-09-14 05:30 | 14.2 | 17.2 | 18.3
| 2014-09-14 06:00 | 14.5 | 17.2 | 18.3
| 2014-09-14 06:30 | 15 | 17.2 | 18.3
| 2014-09-14 07:00 | 15.2 | 17.2 | 18.3
| 2014-09-14 07:30 | 15.2 | 17.2 | 18.3
| 2014-09-14 08:00 | 15.4 | 17.2 | 18.3
| 2014-09-14 08:30 | 15.7 | 17.2 | 18.3
| 2014-09-14 09:00 | 16.3 | 17.2 | 18.3
| 2014-09-14 09:30 | 16.7 | 17.2 | 18.3
| 2014-09-14 10:00 | 17.1 | 17.2 | 18.3
| 2014-09-14 10:30 | 17.3 | 17.2 | 18.3
| 2014-09-14 11:00 | 17.7 | 17.2 | 18.3
| 2014-09-14 11:30 | 18.1 | 17.2 | 18.3
| 2014-09-14 12:00 | 18.6 | 17.2 | 18.3
| 2014-09-14 12:30 | 18.4 | 17.2 | 18.3
| 2014-09-14 13:00 | 19 | 17.2 | 18.3
| 2014-09-14 13:30 | 19.8 | 17.2 | 18.3
| 2014-09-14 14:00 | 19.7 | 17.2 | 18.3
| 2014-09-14 14:30 | 21.1 | 17.2 | 18.3
| 2014-09-14 15:00 | 21 | 17.8 | 18.3
| 2014-09-14 15:30 | 21.1 | 17.8 | 18.3
| 2014-09-14 16:00 | 21.7 | 17.8 | 17.8
| 2014-09-14 16:30 | 21.6 | 17.8 | 17.8
| 2014-09-14 17:00 | 21 | 18.3 | 17.8
| 2014-09-14 17:30 | 20.8 | 18.3 | 17.8
| 2014-09-14 18:00 | 21.1 | 18.3 | 17.8
| 2014-09-14 18:30 | 20.6 | 18.3 | 17.8
| 2014-09-14 19:00 | 19.6 | 18.3 | 17.8
| 2014-09-14 19:30 | 18.4 | 18.3 | 17.8
| 2014-09-14 20:00 | 17.3 | 18.3 | 17.8
| 2014-09-14 20:30 | 16.2 | 18.3 | 17.8
| 2014-09-14 21:00 | 15.4 | 18.3 | 17.8
| 2014-09-14 21:30 | 15.2 | 18.3 | 17.8
| 2014-09-14 22:00 | 14.9 | 18.3 | 17.8
| 2014-09-14 22:30 | 14.5 | 18.3 | 17.8
| 2014-09-14 23:00 | 14.3 | 18.3 | 17.8
| 2014-09-14 23:30 | 14 | 18.3 | 17.8
| 2014-09-15 | 13.6 | 18.3 | 17.8
| 2014-09-15 00:30 | 13.2 | 18.3 | 17.8
| 2014-09-15 01:00 | 12.6 | 18.3 | 17.8
| 2014-09-15 01:30 | 12.8 | 17.8 | 17.8
| 2014-09-15 02:00 | 13.4 | 17.8 | 17.8
| 2014-09-15 02:30 | 13.7 | 17.8 | 17.8
| 2014-09-15 03:00 | 14 | 17.8 | 17.8
| 2014-09-15 03:30 | 14.1 | 17.8 | 17.8
| 2014-09-15 04:00 | 14.4 | 17.8 | 17.8
| 2014-09-15 04:30 | 14.6 | 17.8 | 17.8
| 2014-09-15 05:00 | 14.6 | 17.2 | 17.8
| 2014-09-15 05:30 | 14.7 | 17.2 | 17.8
| 2014-09-15 06:00 | 14.8 | 17.2 | 17.8
| 2014-09-15 06:30 | 14.9 | 17.2 | 17.8
| 2014-09-15 07:00 | 15 | 17.2 | 17.8
| 2014-09-15 07:30 | 15.2 | 17.2 | 17.8
| 2014-09-15 08:00 | 15.4 | 17.2 | 17.8
| 2014-09-15 08:30 | 15.7 | 17.2 | 17.8
| 2014-09-15 09:00 | 15.9 | 17.2 | 17.8
| 2014-09-15 09:30 | 16.6 | 17.2 | 17.8
| 2014-09-15 10:00 | 17.4 | 17.2 | 17.8
| 2014-09-15 10:30 | 18.2 | 17.2 | 17.8
| 2014-09-15 11:00 | 18.7 | 17.2 | 17.8
| 2014-09-15 11:30 | 19.6 | 17.2 | 17.8
| 2014-09-15 12:00 | 20.4 | 17.2 | 17.8
| 2014-09-15 12:30 | 20.4 | 17.2 | 17.8
| 2014-09-15 13:00 | 20.4 | 17.8 | 17.8
| 2014-09-15 13:30 | 21.4 | 17.8 | 17.8
| 2014-09-15 14:00 | 21.5 | 17.8 | 17.8
| 2014-09-15 14:30 | 21.2 | 17.8 | 17.8
| 2014-09-15 15:00 | 20.8 | 17.8 | 17.8
| 2014-09-15 15:30 | 20.6 | 18.3 | 17.8
| 2014-09-15 16:00 | 20.7 | 18.3 | 17.8
| 2014-09-15 16:30 | 20.8 | 18.3 | 17.8
| 2014-09-15 17:00 | 21 | 18.3 | 17.8
| 2014-09-15 17:30 | 21.1 | 18.3 | 17.8
| 2014-09-15 18:00 | 20.6 | 18.3 | 17.8
| 2014-09-15 18:30 | 20.4 | 18.3 | 17.8
| 2014-09-15 19:00 | 19.8 | 18.3 | 17.8
| 2014-09-15 19:30 | 18.9 | 18.3 | 17.8
| 2014-09-15 20:00 | 18.5 | 18.9 | 17.8
| 2014-09-15 20:30 | 17.7 | 18.9 | 17.8
| 2014-09-15 21:00 | 17 | 18.9 | 17.8
| 2014-09-15 21:30 | 16.6 | 18.9 | 17.8
| 2014-09-15 22:00 | 15.9 | 18.3 | 17.8
| 2014-09-15 22:30 | 15.7 | 18.3 | 17.8
| 2014-09-15 23:00 | 15.8 | 18.3 | 17.8
| 2014-09-15 23:30 | 15.6 | 18.3 | 17.8
| 2014-09-16 | 15.1 | 18.3 | 17.8
| 2014-09-16 00:30 | 15.2 | 18.3 | 17.8
| 2014-09-16 01:00 | 14.8 | 18.3 | 17.8
| 2014-09-16 01:30 | 14.1 | 18.3 | 17.8
| 2014-09-16 02:00 | 13.7 | 18.3 | 17.8
| 2014-09-16 02:30 | 13.6 | 18.3 | 17.8
| 2014-09-16 03:00 | 14 | 17.8 | 17.8
| 2014-09-16 03:30 | 13.1 | 17.8 | 17.8
| 2014-09-16 04:00 | 13.2 | 17.8 | 17.8
| 2014-09-16 04:30 | 13.3 | 17.8 | 17.8
| 2014-09-16 05:00 | 12.9 | 17.8 | 17.8
| 2014-09-16 05:30 | 12.6 | 17.8 | 17.8
| 2014-09-16 06:00 | 12.2 | 17.2 | 17.8
| 2014-09-16 06:30 | 12.4 | 17.2 | 17.8
| 2014-09-16 07:00 | 11.4 | 17.2 | 17.8
| 2014-09-16 07:30 | 11.7 | 17.2 | 17.8
| 2014-09-16 08:00 | 11.7 | 17.2 | 17.8
| 2014-09-16 08:30 | 13.2 | 17.2 | 17.8
| 2014-09-16 09:00 | 14.3 | 17.2 | 17.8
| 2014-09-16 09:30 | 15.2 | 16.7 | 17.8
| 2014-09-16 10:00 | 16.7 | 16.7 | 17.8
| 2014-09-16 10:30 | 17.8 | 16.7 | 17.8
| 2014-09-16 11:00 | 19.3 | 16.7 | 17.8
| 2014-09-16 11:30 | 20.1 | 16.7 | 17.8
| 2014-09-16 12:00 | 21.2 | 16.7 | 17.8
| 2014-09-16 12:30 | 21.8 | 16.7 | 17.8
| 2014-09-16 13:00 | 23.1 | 16.7 | 17.8
| 2014-09-16 13:30 | 23.4 | 17.2 | 17.8
| 2014-09-16 14:00 | 23.5 | 17.2 | 17.8
| 2014-09-16 14:30 | 23.7 | 17.2 | 17.8
| 2014-09-16 15:00 | 24.4 | 17.8 | 17.8
| 2014-09-16 15:30 | 24.1 | 17.8 | 17.8
| 2014-09-16 16:00 | 25.5 | 17.8 | 17.8
| 2014-09-16 16:30 | 26.4 | 18.3 | 17.8
| 2014-09-16 17:00 | 26.2 | 18.3 | 17.8
| 2014-09-16 17:30 | 24.9 | 18.3 | 17.8
| 2014-09-16 18:00 | 25.2 | 18.3 | 17.8
| 2014-09-16 18:30 | 23.8 | 18.3 | 17.8
| 2014-09-16 19:00 | 22.3 | 18.9 | 17.8
| 2014-09-16 19:30 | 20.4 | 18.9 | 17.8
| 2014-09-16 20:00 | 19.2 | 18.9 | 17.8
| 2014-09-16 20:30 | 17.9 | 18.9 | 17.8
| 2014-09-16 21:00 | 17.3 | 18.9 | 17.8
| 2014-09-16 21:30 | 16.9 | 18.9 | 17.8
| 2014-09-16 22:00 | 16.5 | 18.9 | 17.8
| 2014-09-16 22:30 | 16.1 | 18.9 | 17.8
| 2014-09-16 23:00 | 15.6 | 18.3 | 17.8
| 2014-09-16 23:30 | 14.9 | 18.3 | 17.8
| 2014-09-17 | 14.6 | 18.3 | 17.8
| 2014-09-17 00:30 | 14.1 | 18.3 | 17.8
| 2014-09-17 01:00 | 14.2 | 18.3 | 17.8
| 2014-09-17 01:30 | 14 | 18.3 | 17.8
| 2014-09-17 02:00 | 13.5 | 18.3 | 17.8
| 2014-09-17 02:30 | 13.2 | 18.3 | 17.8
| 2014-09-17 03:00 | 12.6 | 17.8 | 17.8
| 2014-09-17 03:30 | 12.2 | 17.8 | 17.8
| 2014-09-17 04:00 | 12.3 | 17.8 | 17.8
| 2014-09-17 04:30 | 12.4 | 17.8 | 17.8
| 2014-09-17 05:00 | 12.6 | 17.8 | 17.8
| 2014-09-17 05:30 | 12.2 | 17.8 | 17.8
| 2014-09-17 06:00 | 11.5 | 17.2 | 17.8
| 2014-09-17 06:30 | 11.5 | 17.2 | 17.8
| 2014-09-17 07:00 | 11.4 | 17.2 | 17.8
| 2014-09-17 07:30 | 11.6 | 17.2 | 17.8
| 2014-09-17 08:00 | 12.2 | 17.2 | 17.8
| 2014-09-17 08:30 | 13.1 | 17.2 | 17.8
| 2014-09-17 09:00 | 13.9 | 17.2 | 17.8
| 2014-09-17 09:30 | 14.7 | 16.7 | 17.8
| 2014-09-17 10:00 | 16.2 | 16.7 | 17.8
| 2014-09-17 10:30 | 17.5 | 16.7 | 17.8
| 2014-09-17 11:00 | 19.3 | 16.7 | 17.8
| 2014-09-17 11:30 | 20.6 | 16.7 | 17.8
| 2014-09-17 12:00 | 22 | 16.7 | 17.8
| 2014-09-17 12:30 | 22.4 | 16.7 | 17.8
| 2014-09-17 13:00 | 23.7 | 16.7 | 17.8
| 2014-09-17 13:30 | 24.4 | 17.2 | 17.8
| 2014-09-17 14:00 | 24.7 | 17.2 | 17.8
| 2014-09-17 14:30 | 25.3 | 17.2 | 17.8
| 2014-09-17 15:00 | 26.4 | 17.8 | 17.8
| 2014-09-17 15:30 | 27 | 17.8 | 17.8
| 2014-09-17 16:00 | 27.2 | 17.8 | 17.8
| 2014-09-17 16:30 | 27.3 | 18.3 | 17.8
| 2014-09-17 17:00 | 27.3 | 18.3 | 17.8
| 2014-09-17 17:30 | 26.9 | 18.3 | 17.8
| 2014-09-17 18:00 | 26 | 18.3 | 17.8
| 2014-09-17 18:30 | 24.8 | 18.3 | 17.8
| 2014-09-17 19:00 | 23.3 | 18.9 | 17.8
| 2014-09-17 19:30 | 21.8 | 18.9 | 17.8
| 2014-09-17 20:00 | 20.4 | 18.9 | 17.8
| 2014-09-17 20:30 | 19.6 | 18.9 | 17.8
| 2014-09-17 21:00 | 19.1 | 18.9 | 17.8
| 2014-09-17 21:30 | 18.6 | 18.9 | 17.8
| 2014-09-17 22:00 | 17.9 | 18.9 | 17.8
| 2014-09-17 22:30 | 17.6 | 18.9 | 17.8
| 2014-09-17 23:00 | 17.2 | 18.9 | 17.8
| 2014-09-17 23:30 | 17 | 18.9 | 17.8
| 2014-09-18 | 16.1 | 18.9 | 17.8
| 2014-09-18 00:30 | 17.4 | 18.9 | 17.8
| 2014-09-18 01:00 | 17.1 | 18.3 | 17.8
| 2014-09-18 01:30 | 16.6 | 18.3 | 17.8
| 2014-09-18 02:00 | 16.2 | 18.3 | 17.8
| 2014-09-18 02:30 | 16.3 | 18.3 | 17.8
| 2014-09-18 03:00 | 16.7 | 18.3 | 17.8
| 2014-09-18 03:30 | 16.8 | 18.3 | 17.8
| 2014-09-18 04:00 | 17.1 | 18.3 | 17.8
| 2014-09-18 04:30 | 17.2 | 18.3 | 17.8
| 2014-09-18 05:00 | 17 | 18.3 | 17.8
| 2014-09-18 05:30 | 16.7 | 18.3 | 17.8
| 2014-09-18 06:00 | 15.5 | 17.8 | 17.8
| 2014-09-18 06:30 | 15.3 | 17.8 | 17.8
| 2014-09-18 07:00 | 15.2 | 17.8 | 17.8
| 2014-09-18 07:30 | 15.2 | 17.8 | 17.8
| 2014-09-18 08:00 | 15.4 | 17.8 | 17.8
| 2014-09-18 08:30 | 15.8 | 17.8 | 17.8
| 2014-09-18 09:00 | 16.7 | 17.8 | 17.8
| 2014-09-18 09:30 | 18 | 17.8 | 17.8
| 2014-09-18 10:00 | 19.6 | 17.8 | 17.8
| 2014-09-18 10:30 | 19.6 | 17.8 | 17.8
| 2014-09-18 11:00 | 19.7 | 17.8 | 17.8
| 2014-09-18 11:30 | 20.1 | 17.8 | 17.8
| 2014-09-18 12:00 | 20.8 | 17.8 | 17.8
| 2014-09-18 12:30 | 21.8 | 17.8 | 17.8
| 2014-09-18 13:00 | 22.1 | 18.3 | 17.8
| 2014-09-18 13:30 | 22.3 | 18.3 | 17.8
| 2014-09-18 14:00 | 22.6 | 18.3 | 17.8
| 2014-09-18 14:30 | 22.8 | 18.3 | 17.8
| 2014-09-18 15:00 | 22.9 | 18.3 | 17.8
| 2014-09-18 15:30 | 23.2 | 18.9 | 17.8
| 2014-09-18 16:00 | 25.1 | 18.9 | 17.8
| 2014-09-18 16:30 | 26.4 | 18.9 | 17.8
| 2014-09-18 17:00 | 25.9 | 18.9 | 17.8
| 2014-09-18 17:30 | 24.5 | 19.4 | 17.8
| 2014-09-18 18:00 | 24.1 | 19.4 | 17.8
| 2014-09-18 18:30 | 23.7 | 19.4 | 17.8
| 2014-09-18 19:00 | 22.7 | 19.4 | 17.8
| 2014-09-18 19:30 | 21.9 | 19.4 | 17.8
| 2014-09-18 20:00 | 20.9 | 19.4 | 17.8
| 2014-09-18 20:30 | 20.4 | 19.4 | 17.8
| 2014-09-18 21:00 | 20 | 19.4 | 17.8
| 2014-09-18 21:30 | 19.9 | 19.4 | 17.8
| 2014-09-18 22:00 | 19.6 | 19.4 | 17.8
| 2014-09-18 22:30 | 19.3 | 19.4 | 17.8
| 2014-09-18 23:00 | 19 | 19.4 | 17.8
| 2014-09-18 23:30 | 18.9 | 19.4 | 17.8
| 2014-09-19 | 18.7 | 19.4 | 17.8
| 2014-09-19 00:30 | 18.6 | 19.4 | 17.8
| 2014-09-19 01:00 | 18.3 | 19.4 | 17.8
| 2014-09-19 01:30 | 18 | 19.4 | 17.8
| 2014-09-19 02:00 | 18.1 | 19.4 | 17.8
| 2014-09-19 02:30 | 17.8 | 19.4 | 17.8
| 2014-09-19 03:00 | 16.9 | 19.4 | 17.8
| 2014-09-19 03:30 | 17 | 19.4 | 17.8
| 2014-09-19 04:00 | 16.1 | 19.4 | 17.8
| 2014-09-19 04:30 | 16.1 | 18.9 | 17.8
| 2014-09-19 05:00 | 15.8 | 18.9 | 17.8
| 2014-09-19 05:30 | 15.1 | 18.9 | 17.8
| 2014-09-19 06:00 | 15.4 | 18.9 | 17.8
| 2014-09-19 06:30 | 15.9 | 18.9 | 17.8
| 2014-09-19 07:00 | 16.2 | 18.9 | 17.8
| 2014-09-19 07:30 | 16.6 | 18.9 | 17.8
| 2014-09-19 08:00 | 16.8 | 18.9 | 17.8
| 2014-09-19 08:30 | 16.8 | 18.9 | 17.8
| 2014-09-19 09:00 | 17.9 | 18.3 | 17.8
| 2014-09-19 09:30 | 18.4 | 18.3 | 17.8
| 2014-09-19 10:00 | 19.2 | 18.3 | 17.8
| 2014-09-19 10:30 | 20.5 | 18.3 | 17.8
| 2014-09-19 11:00 | 21 | 18.3 | 18.3
| 2014-09-19 11:30 | 20.5 | 18.3 | 18.3
| 2014-09-19 12:00 | 20.3 | 18.3 | 18.3
| 2014-09-19 12:30 | 22.2 | 18.3 | 18.3
| 2014-09-19 13:00 | 22.4 | 18.9 | 18.3
| 2014-09-19 13:30 | 23.3 | 18.9 | 18.3
| 2014-09-19 14:00 | 24.5 | 18.9 | 18.3
| 2014-09-19 14:30 | 24.7 | 18.9 | 18.3
| 2014-09-19 15:00 | 24.9 | 18.9 | 18.3
| 2014-09-19 15:30 | 25.1 | 19.4 | 18.3
| 2014-09-19 16:00 | 24.9 | 19.4 | 18.3
| 2014-09-19 16:30 | 25.6 | 19.4 | 18.3
| 2014-09-19 17:00 | 25.4 | 20 | 18.3
| 2014-09-19 17:30 | 24.4 | 20 | 18.3
| 2014-09-19 18:00 | 24.2 | 20 | 18.3
| 2014-09-19 18:30 | 23.9 | 20 | 18.3
| 2014-09-19 19:00 | 22.6 | 20 | 18.3
| 2014-09-19 19:30 | 21.6 | 20 | 18.3
| 2014-09-19 20:00 | 20.6 | 20 | 18.3
| 2014-09-19 20:30 | 19.7 | 20 | 18.3
| 2014-09-19 21:00 | 18.9 | 20 | 18.3
| 2014-09-19 21:30 | 18.5 | 20 | 18.3
| 2014-09-19 22:00 | 18.1 | 20 | 18.3
| 2014-09-19 22:30 | 17.7 | 20 | 18.3
| 2014-09-19 23:00 | 17.2 | 20 | 18.3
| 2014-09-19 23:30 | 16.8 | 20 | 18.3
| 2014-09-20 | 16.4 | 20 | 18.3
| 2014-09-20 00:30 | 16.3 | 20 | 18.3
| 2014-09-20 01:00 | 16.4 | 20 | 18.3
| 2014-09-20 01:30 | 16.6 | 20 | 18.3
| 2014-09-20 02:00 | 16.8 | 19.4 | 18.3
| 2014-09-20 02:30 | 16.8 | 19.4 | 18.3
| 2014-09-20 03:00 | 16.5 | 19.4 | 18.3
| 2014-09-20 03:30 | 16.4 | 19.4 | 18.3
| 2014-09-20 04:00 | 16.2 | 19.4 | 18.3
| 2014-09-20 04:30 | 15.8 | 19.4 | 18.3
| 2014-09-20 05:00 | 15.5 | 19.4 | 18.3
| 2014-09-20 05:30 | 15.5 | 19.4 | 18.3
| 2014-09-20 06:00 | 15.5 | 18.9 | 18.3
| 2014-09-20 06:30 | 15.6 | 18.9 | 18.3
| 2014-09-20 07:00 | 15.8 | 18.9 | 18.3
| 2014-09-20 07:30 | 16.1 | 18.9 | 18.3
| 2014-09-20 08:00 | 16.6 | 18.9 | 18.3
| 2014-09-20 08:30 | 17.3 | 18.9 | 18.3
| 2014-09-20 09:00 | 17.6 | 18.9 | 18.3
| 2014-09-20 09:30 | 18 | 18.9 | 18.3
| 2014-09-20 10:00 | 18.3 | 18.9 | 18.3
| 2014-09-20 10:30 | 18.8 | 18.9 | 18.3
| 2014-09-20 11:00 | 19.5 | 18.9 | 18.3
| 2014-09-20 11:30 | 20.2 | 18.9 | 18.3
| 2014-09-20 12:00 | 20.7 | 18.9 | 18.3
| 2014-09-20 12:30 | 22.2 | 18.9 | 18.3
| 2014-09-20 13:00 | 23.1 | 18.9 | 18.3
| 2014-09-20 13:30 | 24 | 18.9 | 18.3
| 2014-09-20 14:00 | 25 | 18.9 | 18.3
| 2014-09-20 14:30 | 25.3 | 18.9 | 18.3
| 2014-09-20 15:00 | 23.4 | 19.4 | 18.3
| 2014-09-20 15:30 | 22.8 | 19.4 | 18.3
| 2014-09-20 16:00 | 21.4 | 19.4 | 18.3
| 2014-09-20 16:30 | 20.2 | 20 | 18.3
| 2014-09-20 17:00 | 21.6 | 20 | 18.3
| 2014-09-20 17:30 | 23.4 | 20 | 18.3
| 2014-09-20 18:00 | 22.3 | 20 | 18.3
| 2014-09-20 18:30 | 21.9 | 20 | 18.3
| 2014-09-20 19:00 | 21.2 | 20 | 18.3
| 2014-09-20 19:30 | 19.9 | 20 | 18.3
| 2014-09-20 20:00 | 18.8 | 20 | 18.3
| 2014-09-20 20:30 | 17.9 | 20 | 18.3
| 2014-09-20 21:00 | 17.7 | 20 | 18.3
| 2014-09-20 21:30 | 15.6 | 20 | 18.3
| 2014-09-20 22:00 | 15.5 | 20 | 18.3
| 2014-09-20 22:30 | 15.5 | 20 | 18.3
| 2014-09-20 23:00 | 15.4 | 20 | 18.3
| 2014-09-20 23:30 | 15.4 | 19.4 | 18.3
| 2014-09-21 | 15.5 | 19.4 | 18.3
| 2014-09-21 00:30 | 15.4 | 19.4 | 18.3
| 2014-09-21 01:00 | 15.5 | 19.4 | 18.3
| 2014-09-21 01:30 | 15.5 | 19.4 | 18.3
| 2014-09-21 02:00 | 15.3 | 19.4 | 18.3
| 2014-09-21 02:30 | 15.2 | 18.9 | 18.3
| 2014-09-21 03:00 | 15.2 | 18.9 | 18.3
| 2014-09-21 03:30 | 15.2 | 18.9 | 18.3
| 2014-09-21 04:00 | 14.9 | 18.9 | 18.3
| 2014-09-21 04:30 | 14.9 | 18.9 | 18.3
| 2014-09-21 05:00 | 15.1 | 18.9 | 18.3
| 2014-09-21 05:30 | 15.3 | 18.9 | 18.3
| 2014-09-21 06:00 | 15.3 | 18.9 | 18.3
| 2014-09-21 06:30 | 15.3 | 18.9 | 18.3
| 2014-09-21 07:00 | 15.2 | 18.9 | 18.3
| 2014-09-21 07:30 | 15.3 | 18.3 | 18.3
| 2014-09-21 08:00 | 15.7 | 18.3 | 18.3
| 2014-09-21 08:30 | 15.8 | 18.3 | 18.3
| 2014-09-21 09:00 | 15.9 | 18.3 | 18.3
| 2014-09-21 09:30 | 16.1 | 18.3 | 18.3
| 2014-09-21 10:00 | 16.2 | 18.3 | 18.3
| 2014-09-21 10:30 | 16.5 | 18.3 | 18.3
| 2014-09-21 11:00 | 16.5 | 18.3 | 18.3
| 2014-09-21 11:30 | 16.7 | 18.3 | 18.3
| 2014-09-21 12:00 | 17.2 | 18.3 | 18.3
| 2014-09-21 12:30 | 17.5 | 18.3 | 18.3
| 2014-09-21 13:00 | 18.1 | 18.3 | 18.3
| 2014-09-21 13:30 | 18.5 | 18.3 | 18.3
| 2014-09-21 14:00 | 18.4 | 18.3 | 18.3
| 2014-09-21 14:30 | 18.7 | 18.3 | 18.3
| 2014-09-21 15:00 | 17.8 | 18.3 | 18.3
| 2014-09-21 15:30 | 17 | 18.9 | 18.3
| 2014-09-21 16:00 | 16 | 18.9 | 18.3
| 2014-09-21 16:30 | 15.9 | 18.9 | 18.3
| 2014-09-21 17:00 | 15.9 | 18.9 | 18.3
| 2014-09-21 17:30 | 15.9 | 18.9 | 18.3
| 2014-09-21 18:00 | 15.9 | 18.9 | 18.3
| 2014-09-21 18:30 | 15.7 | 18.9 | 18.3
| 2014-09-21 19:00 | 15.3 | 18.9 | 18.3
| 2014-09-21 19:30 | 15.3 | 18.9 | 18.3
| 2014-09-21 20:00 | 15.2 | 18.9 | 18.3
| 2014-09-21 20:30 | 14.8 | 18.9 | 18.3
| 2014-09-21 21:00 | 14.3 | 18.9 | 18.3
| 2014-09-21 21:30 | 13.9 | 18.3 | 18.3
| 2014-09-21 22:00 | 13.1 | 18.3 | 18.3
| 2014-09-21 22:30 | 12.3 | 18.3 | 18.3
| 2014-09-21 23:00 | 12.5 | 18.3 | 18.3
| 2014-09-21 23:30 | 12.5 | 18.3 | 18.3
| 2014-09-22 | 11.8 | 18.3 | 18.3
| 2014-09-22 00:30 | 10.9 | 18.3 | 18.3
| 2014-09-22 01:00 | 10.7 | 18.3 | 18.3
| 2014-09-22 01:30 | 10.9 | 18.3 | 18.3
| 2014-09-22 02:00 | 10.5 | 17.8 | 18.3
| 2014-09-22 02:30 | 9.7 | 17.8 | 18.3
| 2014-09-22 03:00 | 9.1 | 17.8 | 18.3
| 2014-09-22 03:30 | 8.7 | 17.8 | 18.3
| 2014-09-22 04:00 | 8.9 | 17.8 | 18.3
| 2014-09-22 04:30 | 9.2 | 17.2 | 18.3
| 2014-09-22 05:00 | 9.5 | 17.2 | 18.3
| 2014-09-22 05:30 | 9.3 | 17.2 | 18.3
| 2014-09-22 06:00 | 9.6 | 17.2 | 18.3
| 2014-09-22 06:30 | 9.8 | 17.2 | 18.3
| 2014-09-22 07:00 | 10.1 | 16.7 | 18.3
| 2014-09-22 07:30 | 10.3 | 16.7 | 18.3
| 2014-09-22 08:00 | 10.4 | 16.7 | 18.3
| 2014-09-22 08:30 | 10.6 | 16.7 | 18.3
| 2014-09-22 09:00 | 11.2 | 16.7 | 18.3
| 2014-09-22 09:30 | 11.6 | 16.7 | 18.3
| 2014-09-22 10:00 | 12.3 | 16.7 | 18.3
| 2014-09-22 10:30 | 12.6 | 16.7 | 18.3
| 2014-09-22 11:00 | 12.6 | 16.7 | 18.3
| 2014-09-22 11:30 | 13.1 | 16.7 | 18.3
| 2014-09-22 12:00 | 13.7 | 16.7 | 18.3
| 2014-09-22 12:30 | 13.7 | 16.7 | 18.3
| 2014-09-22 13:00 | 13.3 | 16.7 | 18.3
| 2014-09-22 13:30 | 13.9 | 16.7 | 18.3
| 2014-09-22 14:00 | 13.7 | 16.7 | 18.3
| 2014-09-22 14:30 | 14.1 | 16.7 | 18.3
| 2014-09-22 15:00 | 14.7 | 16.7 | 18.3
| 2014-09-22 15:30 | 9.5 | 16.7 | 18.3
| 2014-09-22 16:00 | 10.6 | 16.7 | 18.3
| 2014-09-22 16:30 | 12.3 | 16.7 | 18.3
| 2014-09-22 17:00 | 13.1 | 16.7 | 18.3
| 2014-09-22 17:30 | 13.5 | 16.7 | 18.3
| 2014-09-22 18:00 | 13.2 | 16.7 | 18.3
| 2014-09-22 18:30 | 12.8 | 16.7 | 18.3
| 2014-09-22 19:00 | 12.2 | 16.7 | 18.3
| 2014-09-22 19:30 | 10.8 | 16.7 | 18.3
| 2014-09-22 20:00 | 9.4 | 16.7 | 18.3
| 2014-09-22 20:30 | 8.6 | 16.7 | 18.3
| 2014-09-22 21:00 | 8.1 | 16.7 | 18.3
| 2014-09-22 21:30 | 7.6 | 16.1 | 18.3
| 2014-09-22 22:00 | 7.4 | 16.1 | 18.3
| 2014-09-22 22:30 | 7.1 | 16.1 | 18.3
| 2014-09-22 23:00 | 7 | 16.1 | 18.3
| 2014-09-22 23:30 | 6.8 | 16.1 | 18.3
| 2014-09-23 | 6.5 | 16.1 | 18.3
| 2014-09-23 00:30 | 6.3 | 16.1 | 18.3
| 2014-09-23 01:00 | 6.2 | 15.6 | 18.3
| 2014-09-23 01:30 | 6 | 15.6 | 18.3
| 2014-09-23 02:00 | 5.8 | 15.6 | 18.3
| 2014-09-23 02:30 | 5.7 | 15.6 | 18.3
| 2014-09-23 03:00 | 5.4 | 15.6 | 18.3
| 2014-09-23 03:30 | 5.1 | 15 | 18.3
| 2014-09-23 04:00 | 5.1 | 15 | 18.3
| 2014-09-23 04:30 | 5.2 | 15 | 18.3
| 2014-09-23 05:00 | 5.1 | 15 | 18.3
| 2014-09-23 05:30 | 5.1 | 15 | 18.3
| 2014-09-23 06:00 | 4.9 | 15 | 18.3
| 2014-09-23 06:30 | 4.7 | 14.4 | 18.3
| 2014-09-23 07:00 | 4.4 | 14.4 | 18.3
| 2014-09-23 07:30 | 4.5 | 14.4 | 18.3
| 2014-09-23 08:00 | 4.8 | 14.4 | 18.3
| 2014-09-23 08:30 | 5.4 | 14.4 | 18.3
| 2014-09-23 09:00 | 7.3 | 14.4 | 18.3
| 2014-09-23 09:30 | 8.6 | 13.9 | 18.3
| 2014-09-23 10:00 | 9.2 | 13.9 | 18.3
| 2014-09-23 10:30 | 9.7 | 13.9 | 18.3
| 2014-09-23 11:00 | 11.1 | 13.9 | 18.3
| 2014-09-23 11:30 | 12 | 13.9 | 18.3
| 2014-09-23 12:00 | 13.4 | 13.9 | 18.3
| 2014-09-23 12:30 | 13.2 | 13.9 | 18.3
| 2014-09-23 13:00 | 14.9 | 13.9 | 18.3
| 2014-09-23 13:30 | 15.3 | 13.9 | 18.3
| 2014-09-23 14:00 | 14.4 | 13.9 | 17.8
| 2014-09-23 14:30 | 14.8 | 14.4 | 17.8
| 2014-09-23 15:00 | 16.2 | 14.4 | 17.8
| 2014-09-23 15:30 | 16.9 | 14.4 | 17.8
| 2014-09-23 16:00 | 15.5 | 15 | 17.8
| 2014-09-23 16:30 | 16.1 | 15 | 17.8
| 2014-09-23 17:00 | 16.9 | 15 | 17.8
| 2014-09-23 17:30 | 17.3 | 15 | 17.8
| 2014-09-23 18:00 | 16.2 | 15 | 17.8
| 2014-09-23 18:30 | 14.8 | 15.6 | 17.8
| 2014-09-23 19:00 | 13 | 15.6 | 17.8
| 2014-09-23 19:30 | 11.3 | 15.6 | 17.8
| 2014-09-23 20:00 | 10.1 | 15.6 | 17.8
| 2014-09-23 20:30 | 9.2 | 15.6 | 17.8
| 2014-09-23 21:00 | 8.7 | 15.6 | 17.8
| 2014-09-23 21:30 | 8.1 | 15.6 | 17.8
| 2014-09-23 22:00 | 7.6 | 15 | 17.8
| 2014-09-23 22:30 | 7.7 | 15 | 17.8
| 2014-09-23 23:00 | 7.4 | 15 | 17.8
| 2014-09-23 23:30 | 7.2 | 15 | 17.8
| 2014-09-24 | 6.9 | 15 | 17.8
| 2014-09-24 00:30 | 6.9 | 15 | 17.8
| 2014-09-24 01:00 | 7.3 | 15 | 17.8
| 2014-09-24 01:30 | 7.6 | 15 | 17.8
| 2014-09-24 02:00 | 7.2 | 14.4 | 17.8
| 2014-09-24 02:30 | 6.8 | 14.4 | 17.8
| 2014-09-24 03:00 | 6.5 | 14.4 | 17.8
| 2014-09-24 03:30 | 6.4 | 14.4 | 17.8
| 2014-09-24 04:00 | 6.2 | 14.4 | 17.8
| 2014-09-24 04:30 | 6.1 | 14.4 | 17.8
| 2014-09-24 05:00 | 6 | 13.9 | 17.8
| 2014-09-24 05:30 | 5.9 | 13.9 | 17.8
| 2014-09-24 06:00 | 5.3 | 13.9 | 17.8
| 2014-09-24 06:30 | 5.1 | 13.9 | 17.8
| 2014-09-24 07:00 | 4.9 | 13.9 | 17.8
| 2014-09-24 07:30 | 4.7 | 13.9 | 17.8
| 2014-09-24 08:00 | 5.2 | 13.9 | 17.8
| 2014-09-24 08:30 | 5.8 | 13.9 | 17.8
| 2014-09-24 09:00 | 6.5 | 13.9 | 17.8
| 2014-09-24 09:30 | 7.1 | 13.3 | 17.8
| 2014-09-24 10:00 | 8.1 | 13.3 | 17.8
| 2014-09-24 10:30 | 9.2 | 13.3 | 17.8
| 2014-09-24 11:00 | 10.9 | 13.3 | 17.8
| 2014-09-24 11:30 | 11.3 | 13.3 | 17.8
| 2014-09-24 12:00 | 13.3 | 13.3 | 17.8
| 2014-09-24 12:30 | 13.7 | 13.3 | 17.8
| 2014-09-24 13:00 | 13.6 | 13.9 | 17.8
| 2014-09-24 13:30 | 13.8 | 13.9 | 17.8
| 2014-09-24 14:00 | 14.2 | 13.9 | 17.8
| 2014-09-24 14:30 | 14.8 | 13.9 | 17.8
| 2014-09-24 15:00 | 15 | 13.9 | 17.8
| 2014-09-24 15:30 | 15.7 | 14.4 | 17.8
| 2014-09-24 16:00 | 15.3 | 14.4 | 17.2
| 2014-09-24 16:30 | 15.4 | 14.4 | 17.2
| 2014-09-24 17:00 | 15.1 | 14.4 | 17.2
| 2014-09-24 17:30 | 14.9 | 15 | 17.2
| 2014-09-24 18:00 | 14.4 | 15 | 17.2
| 2014-09-24 18:30 | 14.4 | 15 | 17.2
| 2014-09-24 19:00 | 13.7 | 15 | 17.2
| 2014-09-24 19:30 | 12.8 | 15 | 17.2
| 2014-09-24 20:00 | 12 | 15 | 17.2
| 2014-09-24 20:30 | 11.2 | 15 | 17.2
| 2014-09-24 21:00 | 10.7 | 15 | 17.2
| 2014-09-24 21:30 | 10.7 | 15 | 17.2
| 2014-09-24 22:00 | 11.3 | 15 | 17.2
| 2014-09-24 22:30 | 11.4 | 15 | 17.2
| 2014-09-24 23:00 | 11.4 | 15 | 17.2
| 2014-09-24 23:30 | 11.3 | 15 | 17.2
| 2014-09-25 | 11.2 | 15 | 17.2
| 2014-09-25 00:30 | 11.3 | 15 | 17.2
| 2014-09-25 01:00 | 11.1 | 15 | 17.2
| 2014-09-25 01:30 | 11.2 | 15 | 17.2
| 2014-09-25 02:00 | 10.2 | 15 | 17.2
| 2014-09-25 02:30 | 9.9 | 14.4 | 17.2
| 2014-09-25 03:00 | 10.3 | 14.4 | 17.2
| 2014-09-25 03:30 | 10.3 | 14.4 | 17.2
| 2014-09-25 04:00 | 10.3 | 14.4 | 17.2
| 2014-09-25 04:30 | 10.2 | 14.4 | 17.2
| 2014-09-25 05:00 | 10 | 14.4 | 17.2
| 2014-09-25 05:30 | 10 | 14.4 | 17.2
| 2014-09-25 06:00 | 10.3 | 14.4 | 17.2
| 2014-09-25 06:30 | 10.6 | 14.4 | 17.2
| 2014-09-25 07:00 | 10.8 | 14.4 | 17.2
| 2014-09-25 07:30 | 10.8 | 14.4 | 17.2
| 2014-09-25 08:00 | 11.1 | 14.4 | 17.2
| 2014-09-25 08:30 | 11.3 | 14.4 | 17.2
| 2014-09-25 09:00 | 11.7 | 13.9 | 17.2
| 2014-09-25 09:30 | 12.1 | 13.9 | 17.2
| 2014-09-25 10:00 | 13 | 13.9 | 17.2
| 2014-09-25 10:30 | 13.8 | 13.9 | 17.2
| 2014-09-25 11:00 | 15.2 | 13.9 | 17.2
| 2014-09-25 11:30 | 14.9 | 13.9 | 17.2
| 2014-09-25 12:00 | 15.8 | 14.4 | 17.2
| 2014-09-25 12:30 | 16.4 | 14.4 | 17.2
| 2014-09-25 13:00 | 16.8 | 14.4 | 17.2
| 2014-09-25 13:30 | 16.8 | 14.4 | 17.2
| 2014-09-25 14:00 | 17.3 | 14.4 | 17.2
| 2014-09-25 14:30 | 17.1 | 15 | 17.2
| 2014-09-25 15:00 | 17.4 | 15 | 17.2
| 2014-09-25 15:30 | 18.3 | 15 | 17.2
| 2014-09-25 16:00 | 18.1 | 15 | 17.2
| 2014-09-25 16:30 | 18.1 | 15 | 17.2
| 2014-09-25 17:00 | 18.3 | 15.6 | 17.2
| 2014-09-25 17:30 | 18.6 | 15.6 | 17.2
| 2014-09-25 18:00 | 17.4 | 15.6 | 17.2
| 2014-09-25 18:30 | 17 | 15.6 | 17.2
| 2014-09-25 19:00 | 16.2 | 15.6 | 17.2
| 2014-09-25 19:30 | 15.1 | 15.6 | 17.2
| 2014-09-25 20:00 | 14.1 | 15.6 | 17.2
| 2014-09-25 20:30 | 13.3 | 15.6 | 17.2
| 2014-09-25 21:00 | 12.8 | 15.6 | 17.2
| 2014-09-25 21:30 | 12.4 | 15.6 | 17.2
| 2014-09-25 22:00 | 12 | 15.6 | 16.7
| 2014-09-25 22:30 | 11.9 | 15.6 | 16.7
| 2014-09-25 23:00 | 11.8 | 15.6 | 16.7
| 2014-09-25 23:30 | 11.8 | 15.6 | 16.7
| 2014-09-26 | 11.8 | 15.6 | 16.7
| 2014-09-26 00:30 | 11.8 | 15.6 | 16.7
| 2014-09-26 01:00 | 11.7 | 15.6 | 16.7
| 2014-09-26 01:30 | 11.8 | 15 | 16.7
| 2014-09-26 02:00 | 12.2 | 15 | 16.7
| 2014-09-26 02:30 | 12.2 | 15 | 16.7
| 2014-09-26 03:00 | 12.2 | 15 | 16.7
| 2014-09-26 03:30 | 12.1 | 15 | 16.7
| 2014-09-26 04:00 | 12.4 | 15 | 16.7
| 2014-09-26 04:30 | 12.4 | 15 | 16.7
| 2014-09-26 05:00 | 12.2 | 15 | 16.7
| 2014-09-26 05:30 | 12.3 | 15 | 16.7
| 2014-09-26 06:00 | 12.2 | 15 | 16.7
| 2014-09-26 06:30 | 12.1 | 15 | 16.7
| 2014-09-26 07:00 | 11.7 | 15 | 16.7
| 2014-09-26 07:30 | 10.8 | 15 | 16.7
| 2014-09-26 08:00 | 10.7 | 15 | 16.7
| 2014-09-26 08:30 | 11.4 | 15 | 16.7
| 2014-09-26 09:00 | 12.3 | 15 | 16.7
| 2014-09-26 09:30 | 13.2 | 15 | 16.7
| 2014-09-26 10:00 | 14.2 | 14.4 | 16.7
| 2014-09-26 10:30 | 14.5 | 14.4 | 16.7
| 2014-09-26 11:00 | 16.2 | 14.4 | 16.7
| 2014-09-26 11:30 | 17.3 | 14.4 | 16.7
| 2014-09-26 12:00 | 17.6 | 14.4 | 16.7
| 2014-09-26 12:30 | 18.6 | 14.4 | 16.7
| 2014-09-26 13:00 | 18.3 | 14.4 | 16.7
| 2014-09-26 13:30 | 19.2 | 15 | 16.7
| 2014-09-26 14:00 | 19.7 | 15 | 16.7
| 2014-09-26 14:30 | 19.4 | 15 | 16.7
| 2014-09-26 15:00 | 20.2 | 15 | 16.7
| 2014-09-26 15:30 | 19.8 | 15 | 16.7
| 2014-09-26 16:00 | 19.7 | 15.6 | 16.7
| 2014-09-26 16:30 | 19.2 | 15.6 | 16.7
| 2014-09-26 17:00 | 18.9 | 15.6 | 16.7
| 2014-09-26 17:30 | 18.9 | 16.1 | 16.7
| 2014-09-26 18:00 | 18.7 | 16.1 | 16.7
| 2014-09-26 18:30 | 18.6 | 16.1 | 16.7
| 2014-09-26 19:00 | 17.9 | 16.1 | 16.7
| 2014-09-26 19:30 | 17.2 | 16.1 | 16.7
| 2014-09-26 20:00 | 17.2 | 16.1 | 16.7
| 2014-09-26 20:30 | 16.8 | 16.1 | 16.7
| 2014-09-26 21:00 | 16.4 | 16.1 | 16.7
| 2014-09-26 21:30 | 16.2 | 16.1 | 16.7
| 2014-09-26 22:00 | 15.8 | 16.1 | 16.7
| 2014-09-26 22:30 | 15.6 | 16.1 | 16.7
| 2014-09-26 23:00 | 15.8 | 16.1 | 16.7
| 2014-09-26 23:30 | 15.3 | 16.1 | 16.7
| 2014-09-27 | 14.9 | 16.1 | 16.7
| 2014-09-27 00:30 | 14.7 | 16.1 | 16.7
| 2014-09-27 01:00 | 14.5 | 16.1 | 16.7
| 2014-09-27 01:30 | 14.4 | 16.1 | 16.7
| 2014-09-27 02:00 | 14.3 | 16.1 | 16.7
| 2014-09-27 02:30 | 14.2 | 16.1 | 16.7
| 2014-09-27 03:00 | 14.1 | 16.1 | 16.7
| 2014-09-27 03:30 | 14.1 | 16.1 | 16.7
| 2014-09-27 04:00 | 14.1 | 16.1 | 16.7
| 2014-09-27 04:30 | 14.1 | 16.1 | 16.7
| 2014-09-27 05:00 | 14 | 16.1 | 16.7
| 2014-09-27 05:30 | 13.9 | 16.1 | 16.7
| 2014-09-27 06:00 | 13.9 | 16.1 | 16.7
| 2014-09-27 06:30 | 13.8 | 16.1 | 16.7
| 2014-09-27 07:00 | 13.8 | 16.1 | 16.7
| 2014-09-27 07:30 | 13.8 | 15.6 | 16.7
| 2014-09-27 08:00 | 13.9 | 15.6 | 16.7
| 2014-09-27 08:30 | 14.2 | 15.6 | 16.7
| 2014-09-27 09:00 | 14.6 | 15.6 | 16.7
| 2014-09-27 09:30 | 14.9 | 15.6 | 16.7
| 2014-09-27 10:00 | 15.7 | 15.6 | 16.7
| 2014-09-27 10:30 | 17.1 | 15.6 | 16.7
| 2014-09-27 11:00 | 18.6 | 15.6 | 16.7
| 2014-09-27 11:30 | 18.7 | 15.6 | 16.7
| 2014-09-27 12:00 | 18.8 | 15.6 | 16.7
| 2014-09-27 12:30 | 19.8 | 15.6 | 16.7
| 2014-09-27 13:00 | 19.4 | 16.1 | 16.7
| 2014-09-27 13:30 | 20.2 | 16.1 | 16.7
| 2014-09-27 14:00 | 21.8 | 16.1 | 16.7
| 2014-09-27 14:30 | 20.6 | 16.1 | 16.7
| 2014-09-27 15:00 | 21.3 | 16.1 | 16.7
| 2014-09-27 15:30 | 21.7 | 16.7 | 16.7
| 2014-09-27 16:00 | 21.3 | 16.7 | 16.7
| 2014-09-27 16:30 | 22.2 | 16.7 | 16.7
| 2014-09-27 17:00 | 22.7 | 16.7 | 16.7
| 2014-09-27 17:30 | 22.6 | 16.7 | 16.7
| 2014-09-27 18:00 | 21.5 | 17.2 | 16.7
| 2014-09-27 18:30 | 20.6 | 17.2 | 16.7
| 2014-09-27 19:00 | 18.9 | 17.2 | 16.7
| 2014-09-27 19:30 | 17.1 | 17.2 | 16.7
| 2014-09-27 20:00 | 15.9 | 17.2 | 16.7
| 2014-09-27 20:30 | 15.2 | 17.2 | 16.7
| 2014-09-27 21:00 | 14.7 | 17.2 | 16.7
| 2014-09-27 21:30 | 14.3 | 17.2 | 16.7
| 2014-09-27 22:00 | 13.8 | 17.2 | 16.7
| 2014-09-27 22:30 | 13.2 | 17.2 | 16.7
| 2014-09-27 23:00 | 13.2 | 16.7 | 16.7
| 2014-09-27 23:30 | 13.3 | 16.7 | 16.7
| 2014-09-28 | 13.2 | 16.7 | 16.7
| 2014-09-28 00:30 | 13 | 16.7 | 16.7
| 2014-09-28 01:00 | 12.6 | 16.7 | 16.7
| 2014-09-28 01:30 | 12.2 | 16.7 | 16.7
| 2014-09-28 02:00 | 11.9 | 16.7 | 16.7
| 2014-09-28 02:30 | 11.8 | 16.1 | 16.7
| 2014-09-28 03:00 | 11.7 | 16.1 | 16.7
| 2014-09-28 03:30 | 11.6 | 16.1 | 16.7
| 2014-09-28 04:00 | 11.6 | 16.1 | 16.7
| 2014-09-28 04:30 | 11.1 | 16.1 | 16.7
| 2014-09-28 05:00 | 10.6 | 16.1 | 16.7
| 2014-09-28 05:30 | 10.3 | 16.1 | 16.7
| 2014-09-28 06:00 | 10.3 | 15.6 | 16.7
| 2014-09-28 06:30 | 10.4 | 15.6 | 16.7
| 2014-09-28 07:00 | 10.3 | 15.6 | 16.7
| 2014-09-28 07:30 | 9.4 | 15.6 | 16.7
| 2014-09-28 08:00 | 9.3 | 15.6 | 16.7
| 2014-09-28 08:30 | 9.4 | 15.6 | 16.7
| 2014-09-28 09:00 | 10.8 | 15 | 16.7
| 2014-09-28 09:30 | 12.5 | 15 | 16.7
| 2014-09-28 10:00 | 13.9 | 15 | 16.7
| 2014-09-28 10:30 | 15.8 | 15 | 16.7
| 2014-09-28 11:00 | 17.3 | 15 | 16.7
| 2014-09-28 11:30 | 18.1 | 15 | 16.7
| 2014-09-28 12:00 | 19.2 | 15 | 16.7
| 2014-09-28 12:30 | 19.3 | 15 | 16.7
| 2014-09-28 13:00 | 19.8 | 15 | 16.7
| 2014-09-28 13:30 | 20.9 | 15 | 16.7
| 2014-09-28 14:00 | 21.4 | 15.6 | 16.7
| 2014-09-28 14:30 | 21.4 | 15.6 | 16.7
| 2014-09-28 15:00 | 21.6 | 15.6 | 16.7
| 2014-09-28 15:30 | 21.9 | 16.1 | 16.7
| 2014-09-28 16:00 | 22.2 | 16.1 | 16.7
| 2014-09-28 16:30 | 22.3 | 16.1 | 16.7
| 2014-09-28 17:00 | 22.8 | 16.1 | 16.7
| 2014-09-28 17:30 | 22.8 | 16.7 | 16.7
| 2014-09-28 18:00 | 21.9 | 16.7 | 16.7
| 2014-09-28 18:30 | 21.1 | 16.7 | 16.7
| 2014-09-28 19:00 | 19.8 | 16.7 | 16.7
| 2014-09-28 19:30 | 18.3 | 16.7 | 16.7
| 2014-09-28 20:00 | 17.2 | 16.7 | 16.7
| 2014-09-28 20:30 | 16.5 | 16.7 | 16.7
| 2014-09-28 21:00 | 15.9 | 16.7 | 16.7
| 2014-09-28 21:30 | 15.4 | 16.7 | 16.7
| 2014-09-28 22:00 | 15.1 | 16.7 | 16.7
| 2014-09-28 22:30 | 14.5 | 16.7 | 16.7
| 2014-09-28 23:00 | 13.9 | 16.7 | 16.7
| 2014-09-28 23:30 | 13.7 | 16.7 | 16.7
| 2014-09-29 | 13.4 | 16.7 | 16.7
| 2014-09-29 00:30 | 13.1 | 16.7 | 16.7
| 2014-09-29 01:00 | 12.7 | 16.7 | 16.7
| 2014-09-29 01:30 | 12.4 | 16.7 | 16.7
| 2014-09-29 02:00 | 12.3 | 16.1 | 16.7
| 2014-09-29 02:30 | 11.9 | 16.1 | 16.7
| 2014-09-29 03:00 | 11.8 | 16.1 | 16.7
| 2014-09-29 03:30 | 11.8 | 16.1 | 16.7
| 2014-09-29 04:00 | 11.4 | 16.1 | 16.7
| 2014-09-29 04:30 | 11.4 | 16.1 | 16.7
| 2014-09-29 05:00 | 11.2 | 16.1 | 16.7
| 2014-09-29 05:30 | 11.2 | 16.1 | 16.7
| 2014-09-29 06:00 | 10.8 | 15.6 | 16.7
| 2014-09-29 06:30 | 10.9 | 15.6 | 16.7
| 2014-09-29 07:00 | 11.5 | 15.6 | 16.7
| 2014-09-29 07:30 | 11.2 | 15.6 | 16.7
| 2014-09-29 08:00 | 11.5 | 15.6 | 16.7
| 2014-09-29 08:30 | 13.1 | 15.6 | 16.7
| 2014-09-29 09:00 | 13.4 | 15.6 | 16.7
| 2014-09-29 09:30 | 13.8 | 15.6 | 16.7
| 2014-09-29 10:00 | 14.9 | 15.6 | 16.7
| 2014-09-29 10:30 | 15.5 | 15.6 | 16.7
| 2014-09-29 11:00 | 17.1 | 15.6 | 16.7
| 2014-09-29 11:30 | 19.7 | 15.6 | 16.7
| 2014-09-29 12:00 | 21.3 | 15.6 | 16.7
| 2014-09-29 12:30 | 22 | 15.6 | 16.7
| 2014-09-29 13:00 | 22.8 | 15.6 | 16.7
| 2014-09-29 13:30 | 23.3 | 15.6 | 16.7
| 2014-09-29 14:00 | 24.2 | 16.1 | 16.7
| 2014-09-29 14:30 | 24.3 | 16.1 | 16.7
| 2014-09-29 15:00 | 24.9 | 16.1 | 16.7
| 2014-09-29 15:30 | 24.7 | 16.7 | 16.7
| 2014-09-29 16:00 | 25.4 | 16.7 | 16.7
| 2014-09-29 16:30 | 25.2 | 16.7 | 16.7
| 2014-09-29 17:00 | 24.6 | 16.7 | 16.7
| 2014-09-29 17:30 | 23.7 | 17.2 | 16.7
| 2014-09-29 18:00 | 23 | 17.2 | 16.7
| 2014-09-29 18:30 | 22.1 | 17.2 | 16.7
| 2014-09-29 19:00 | 20.9 | 17.2 | 16.7
| 2014-09-29 19:30 | 20.1 | 17.2 | 16.7
| 2014-09-29 20:00 | 19.4 | 17.8 | 16.7
| 2014-09-29 20:30 | 19 | 17.8 | 16.7
| 2014-09-29 21:00 | 18.6 | 17.8 | 16.7
| 2014-09-29 21:30 | 18.3 | 17.8 | 16.7
| 2014-09-29 22:00 | 18.1 | 17.8 | 16.7
| 2014-09-29 22:30 | 17.8 | 17.8 | 16.7
| 2014-09-29 23:00 | 17.7 | 17.8 | 16.7
| 2014-09-29 23:30 | 17.8 | 17.8 | 16.7
| 2014-09-30 | 17.8 | 17.8 | 16.7
| 2014-09-30 00:30 | 17.6 | 17.8 | 16.7
| 2014-09-30 01:00 | 17.4 | 17.2 | 16.7
| 2014-09-30 01:30 | 17.5 | 17.2 | 16.7
| 2014-09-30 02:00 | 17.8 | 17.2 | 16.7
| 2014-09-30 02:30 | 17.6 | 17.2 | 16.7
| 2014-09-30 03:00 | 17.3 | 17.2 | 16.7
| 2014-09-30 03:30 | 17.3 | 17.2 | 16.7
| 2014-09-30 04:00 | 17.1 | 17.2 | 16.7
| 2014-09-30 04:30 | 16.5 | 17.2 | 16.7
| 2014-09-30 05:00 | 16.1 | 17.2 | 16.7
| 2014-09-30 05:30 | 15.8 | 17.2 | 16.7
| 2014-09-30 06:00 | 15.7 | 17.2 | 16.7
| 2014-09-30 06:30 | 15.6 | 17.2 | 16.7
| 2014-09-30 07:00 | 15.6 | 17.2 | 16.7
| 2014-09-30 07:30 | 15.3 | 17.2 | 16.7
| 2014-09-30 08:00 | 15.3 | 17.2 | 16.7
| 2014-09-30 08:30 | 15.6 | 17.2 | 16.7
| 2014-09-30 09:00 | 16.4 | 17.2 | 16.7
| 2014-09-30 09:30 | 17.3 | 17.2 | 16.7
| 2014-09-30 10:00 | 17.9 | 17.2 | 16.7
| 2014-09-30 10:30 | 18.1 | 17.2 | 16.7
| 2014-09-30 11:00 | 18.5 | 17.2 | 16.7
| 2014-09-30 11:30 | 19.1 | 17.2 | 16.7
| 2014-09-30 12:00 | 19.2 | 17.2 | 16.7
| 2014-09-30 12:30 | 19.4 | 17.2 | 16.7
| 2014-09-30 13:00 | 19.6 | 17.2 | 16.7
| 2014-09-30 13:30 | 19.8 | 17.2 | 16.7
| 2014-09-30 14:00 | 20.4 | 17.2 | 16.7
| 2014-09-30 14:30 | 20.6 | 17.2 | 16.7
| 2014-09-30 15:00 | 20.8 | 17.2 | 16.7
| 2014-09-30 15:30 | 21.3 | 17.8 | 16.7
| 2014-09-30 16:00 | 21.3 | 17.8 | 16.7
| 2014-09-30 16:30 | 21.2 | 17.8 | 16.7
| 2014-09-30 17:00 | 21.7 | 17.8 | 16.7
| 2014-09-30 17:30 | 21.3 | 17.8 | 16.7
| 2014-09-30 18:00 | 20.5 | 18.3 | 16.7
| 2014-09-30 18:30 | 19.3 | 18.3 | 16.7
| 2014-09-30 19:00 | 18.6 | 18.3 | 16.7
| 2014-09-30 19:30 | 17.6 | 18.3 | 16.7
| 2014-09-30 20:00 | 16.9 | 18.3 | 16.7
| 2014-09-30 20:30 | 16.6 | 18.3 | 16.7
| 2014-09-30 21:00 | 16 | 18.3 | 16.7
| 2014-09-30 21:30 | 15.6 | 18.3 | 16.7
| 2014-09-30 22:00 | 15.2 | 18.3 | 16.7
| 2014-09-30 22:30 | 14.7 | 17.8 | 16.7
| 2014-09-30 23:00 | 14.2 | 17.8 | 16.7
| 2014-09-30 23:30 | 13.7 | 17.8 | 16.7
| 2014-10-01 | 13.4 | 17.8 | 16.7
| 2014-10-01 00:30 | 13.7 | 17.8 | 16.7
| 2014-10-01 01:00 | 13.8 | 17.8 | 16.7
| 2014-10-01 01:30 | 13.7 | 17.8 | 16.7
| 2014-10-01 02:00 | 13.4 | 17.8 | 16.7
| 2014-10-01 02:30 | 12.8 | 17.2 | 16.7
| 2014-10-01 03:00 | 12.5 | 17.2 | 16.7
| 2014-10-01 03:30 | 12.2 | 17.2 | 16.7
| 2014-10-01 04:00 | 12.1 | 17.2 | 16.7
| 2014-10-01 04:30 | 11.8 | 17.2 | 16.7
| 2014-10-01 05:00 | 11.7 | 17.2 | 16.7
| 2014-10-01 05:30 | 11.9 | 17.2 | 16.7
| 2014-10-01 06:00 | 11.8 | 16.7 | 16.7
| 2014-10-01 06:30 | 12.2 | 16.7 | 16.7
| 2014-10-01 07:00 | 12.2 | 16.7 | 16.7
| 2014-10-01 07:30 | 12.2 | 16.7 | 16.7
| 2014-10-01 08:00 | 12.4 | 16.7 | 16.7
| 2014-10-01 08:30 | 12.9 | 16.7 | 16.7
| 2014-10-01 09:00 | 13.4 | 16.7 | 16.7
| 2014-10-01 09:30 | 14.1 | 16.7 | 16.7
| 2014-10-01 10:00 | 14.6 | 16.1 | 16.7
| 2014-10-01 10:30 | 15.1 | 16.1 | 16.7
| 2014-10-01 11:00 | 16.6 | 16.1 | 16.7
| 2014-10-01 11:30 | 17.3 | 16.1 | 16.7
| 2014-10-01 12:00 | 18.5 | 16.1 | 16.7
| 2014-10-01 12:30 | 19.9 | 16.7 | 16.7
| 2014-10-01 13:00 | 21.2 | 16.7 | 16.7
| 2014-10-01 13:30 | 21.4 | 16.7 | 16.7
| 2014-10-01 14:00 | 21.6 | 16.7 | 16.7
| 2014-10-01 14:30 | 22 | 16.7 | 16.7
| 2014-10-01 15:00 | 22.4 | 17.2 | 16.7
| 2014-10-01 15:30 | 22.2 | 17.2 | 16.7
| 2014-10-01 16:00 | 21.3 | 17.2 | 16.7
| 2014-10-01 16:30 | 20.9 | 17.2 | 16.7
| 2014-10-01 17:00 | 20.9 | 17.8 | 16.7
| 2014-10-01 17:30 | 20.6 | 17.8 | 16.7
| 2014-10-01 18:00 | 20.2 | 17.8 | 16.7
| 2014-10-01 18:30 | 20.6 | 17.8 | 16.7
| 2014-10-01 19:00 | 19.3 | 17.8 | 16.7
| 2014-10-01 19:30 | 17.7 | 17.8 | 16.7
| 2014-10-01 20:00 | 16.4 | 17.8 | 16.7
| 2014-10-01 20:30 | 15.8 | 17.8 | 16.7
| 2014-10-01 21:00 | 15.2 | 17.8 | 16.7
| 2014-10-01 21:30 | 14.7 | 17.8 | 16.7
| 2014-10-01 22:00 | 14.1 | 17.8 | 16.7
| 2014-10-01 22:30 | 13.8 | 17.8 | 16.7
| 2014-10-01 23:00 | 13.3 | 17.8 | 16.7
| 2014-10-01 23:30 | 12.7 | 17.8 | 16.7
| 2014-10-02 | 12.3 | 17.8 | 16.7
| 2014-10-02 00:30 | 12.5 | 17.2 | 16.7
| 2014-10-02 01:00 | 12.1 | 17.2 | 16.7
| 2014-10-02 01:30 | 11.6 | 17.2 | 16.7
| 2014-10-02 02:00 | 11.3 | 17.2 | 16.7
| 2014-10-02 02:30 | 11.2 | 17.2 | 16.7
| 2014-10-02 03:00 | 10.7 | 17.2 | 16.7
| 2014-10-02 03:30 | 10.4 | 17.2 | 16.7
| 2014-10-02 04:00 | 10.3 | 16.7 | 16.7
| 2014-10-02 04:30 | 10.5 | 16.7 | 16.7
| 2014-10-02 05:00 | 10.3 | 16.7 | 16.7
| 2014-10-02 05:30 | 9.9 | 16.7 | 16.7
| 2014-10-02 06:00 | 9.7 | 16.7 | 17.2
| 2014-10-02 06:30 | 10.1 | 16.7 | 17.2
| 2014-10-02 07:00 | 10.3 | 16.1 | 17.2
| 2014-10-02 07:30 | 10.4 | 16.1 | 17.2
| 2014-10-02 08:00 | 11.3 | 16.1 | 17.2
| 2014-10-02 08:30 | 11.8 | 16.1 | 17.2
| 2014-10-02 09:00 | 12.6 | 16.1 | 17.2
| 2014-10-02 09:30 | 13.2 | 16.1 | 17.2
| 2014-10-02 10:00 | 14 | 16.1 | 17.2
| 2014-10-02 10:30 | 15.1 | 16.1 | 17.2
| 2014-10-02 11:00 | 16.3 | 16.1 | 17.2
| 2014-10-02 11:30 | 17.4 | 16.1 | 17.2
| 2014-10-02 12:00 | 18.4 | 16.1 | 17.2
| 2014-10-02 12:30 | 19.7 | 16.1 | 17.2
| 2014-10-02 13:00 | 20.7 | 16.1 | 17.2
| 2014-10-02 13:30 | 21.4 | 16.1 | 17.2
| 2014-10-02 14:00 | 21.8 | 16.1 | 17.2
| 2014-10-02 14:30 | 22.3 | 16.1 | 17.2
| 2014-10-02 15:00 | 22 | 16.1 | 17.2
| 2014-10-02 15:30 | 22.7 | 16.7 | 17.2
| 2014-10-02 16:00 | 22.7 | 16.7 | 17.2
| 2014-10-02 16:30 | 22.9 | 16.7 | 17.2
| 2014-10-02 17:00 | 23.1 | 16.7 | 17.2
| 2014-10-02 17:30 | 22.2 | 17.2 | 17.2
| 2014-10-02 18:00 | 21.3 | 17.2 | 17.2
| 2014-10-02 18:30 | 19.7 | 17.2 | 17.2
| 2014-10-02 19:00 | 17.5 | 17.2 | 17.2
| 2014-10-02 19:30 | 16.1 | 17.2 | 17.2
| 2014-10-02 20:00 | 15.4 | 17.2 | 17.2
| 2014-10-02 20:30 | 14.9 | 17.2 | 17.2
| 2014-10-02 21:00 | 14.4 | 17.2 | 17.2
| 2014-10-02 21:30 | 13.8 | 17.2 | 17.2
| 2014-10-02 22:00 | 13.4 | 17.2 | 17.2
| 2014-10-02 22:30 | 12.8 | 17.2 | 17.2
| 2014-10-02 23:00 | 12.4 | 17.2 | 17.2
| 2014-10-02 23:30 | 12.3 | 17.2 | 17.2
| 2014-10-03 | 12.1 | 16.7 | 17.2
| 2014-10-03 00:30 | 11.7 | 16.7 | 17.2
| 2014-10-03 01:00 | 11.8 | 16.7 | 17.2
| 2014-10-03 01:30 | 11.6 | 16.7 | 17.2
| 2014-10-03 02:00 | 11.1 | 16.7 | 17.2
| 2014-10-03 02:30 | 10.7 | 16.7 | 17.2
| 2014-10-03 03:00 | 10.6 | 16.7 | 17.2
| 2014-10-03 03:30 | 11 | 16.1 | 17.2
| 2014-10-03 04:00 | 10.5 | 16.1 | 17.2
| 2014-10-03 04:30 | 10.1 | 16.1 | 17.2
| 2014-10-03 05:00 | 10.6 | 16.1 | 17.2
| 2014-10-03 05:30 | 10.7 | 16.1 | 17.2
| 2014-10-03 06:00 | 10.6 | 16.1 | 17.2
| 2014-10-03 06:30 | 10.9 | 16.1 | 17.2
| 2014-10-03 07:00 | 11 | 16.1 | 17.2
| 2014-10-03 07:30 | 10.9 | 15.6 | 17.2
| 2014-10-03 08:00 | 10.3 | 15.6 | 17.2
| 2014-10-03 08:30 | 10.2 | 15.6 | 17.2
| 2014-10-03 09:00 | 10.9 | 15.6 | 17.2
| 2014-10-03 09:30 | 12.2 | 15.6 | 17.2
| 2014-10-03 10:00 | 13.5 | 15.6 | 17.2
| 2014-10-03 10:30 | 15.1 | 15.6 | 17.2
| 2014-10-03 11:00 | 17.7 | 15.6 | 17.2
| 2014-10-03 11:30 | 19.7 | 15.6 | 17.2
| 2014-10-03 12:00 | 20.8 | 15.6 | 17.2
| 2014-10-03 12:30 | 21 | 15.6 | 17.2
| 2014-10-03 13:00 | 21.1 | 15.6 | 17.2
| 2014-10-03 13:30 | 21.8 | 15.6 | 17.2
| 2014-10-03 14:00 | 22.4 | 15.6 | 17.2
| 2014-10-03 14:30 | 22.9 | 15.6 | 17.2
| 2014-10-03 15:00 | 23.2 | 16.1 | 17.2
| 2014-10-03 15:30 | 23.6 | 16.1 | 17.2
| 2014-10-03 16:00 | 23.6 | 16.1 | 17.2
| 2014-10-03 16:30 | 23.6 | 16.1 | 17.2
| 2014-10-03 17:00 | 22.9 | 16.7 | 17.2
| 2014-10-03 17:30 | 22.4 | 16.7 | 17.2
| 2014-10-03 18:00 | 20.8 | 16.7 | 17.2
| 2014-10-03 18:30 | 19.2 | 16.7 | 17.2
| 2014-10-03 19:00 | 17.3 | 16.7 | 17.2
| 2014-10-03 19:30 | 15.7 | 16.7 | 17.2
| 2014-10-03 20:00 | 14.8 | 16.7 | 17.2
| 2014-10-03 20:30 | 13.8 | 16.7 | 17.2
| 2014-10-03 21:00 | 13.2 | 16.7 | 17.2
| 2014-10-03 21:30 | 12.7 | 16.7 | 17.2
| 2014-10-03 22:00 | 12.4 | 16.7 | 17.2
| 2014-10-03 22:30 | 11.8 | 16.7 | 17.2
| 2014-10-03 23:00 | 11.4 | 16.7 | 17.2
| 2014-10-03 23:30 | 11.3 | 16.7 | 17.2
| 2014-10-04 | 11.2 | 16.7 | 17.2
| 2014-10-04 00:30 | 10.9 | 16.7 | 17.2
| 2014-10-04 01:00 | 10.3 | 16.1 | 17.2
| 2014-10-04 01:30 | 10.1 | 16.1 | 17.2
| 2014-10-04 02:00 | 10.2 | 16.1 | 16.7
| 2014-10-04 02:30 | 10.1 | 16.1 | 16.7
| 2014-10-04 03:00 | 9.9 | 16.1 | 16.7
| 2014-10-04 03:30 | 9.8 | 16.1 | 16.7
| 2014-10-04 04:00 | 10.2 | 16.1 | 16.7
| 2014-10-04 04:30 | 10.3 | 16.1 | 16.7
| 2014-10-04 05:00 | 10.4 | 15.6 | 16.7
| 2014-10-04 05:30 | 10.3 | 15.6 | 16.7
| 2014-10-04 06:00 | 10.1 | 15.6 | 16.7
| 2014-10-04 06:30 | 9.9 | 15.6 | 16.7
| 2014-10-04 07:00 | 9.7 | 15.6 | 16.7
| 2014-10-04 07:30 | 9.4 | 15.6 | 16.7
| 2014-10-04 08:00 | 9.5 | 15.6 | 16.7
| 2014-10-04 08:30 | 9.2 | 15 | 16.7
| 2014-10-04 09:00 | 10.4 | 15 | 16.7
| 2014-10-04 09:30 | 11.4 | 15 | 16.7
| 2014-10-04 10:00 | 12.4 | 15 | 16.7
| 2014-10-04 10:30 | 13.8 | 15 | 16.7
| 2014-10-04 11:00 | 15.8 | 15 | 16.7
| 2014-10-04 11:30 | 18.1 | 15 | 16.7
| 2014-10-04 12:00 | 19.3 | 15 | 16.7
| 2014-10-04 12:30 | 20 | 15 | 16.7
| 2014-10-04 13:00 | 20.9 | 15 | 16.7
| 2014-10-04 13:30 | 21.1 | 15 | 16.7
| 2014-10-04 14:00 | 21.8 | 15 | 16.7
| 2014-10-04 14:30 | 22.2 | 15 | 16.7
| 2014-10-04 15:00 | 22.6 | 15.6 | 16.7
| 2014-10-04 15:30 | 22.8 | 15.6 | 16.7
| 2014-10-04 16:00 | 23 | 15.6 | 16.7
| 2014-10-04 16:30 | 22.8 | 15.6 | 16.7
| 2014-10-04 17:00 | 22.3 | 16.1 | 16.7
| 2014-10-04 17:30 | 21.1 | 16.1 | 16.7
| 2014-10-04 18:00 | 20.3 | 16.1 | 16.7
| 2014-10-04 18:30 | 19.1 | 16.1 | 16.7
| 2014-10-04 19:00 | 17.1 | 16.1 | 16.7
| 2014-10-04 19:30 | 15.6 | 16.1 | 16.7
| 2014-10-04 20:00 | 14.1 | 16.1 | 16.7
| 2014-10-04 20:30 | 13.3 | 16.1 | 16.7
| 2014-10-04 21:00 | 12.9 | 16.1 | 16.7
| 2014-10-04 21:30 | 12.4 | 16.1 | 16.7
| 2014-10-04 22:00 | 11.9 | 16.1 | 16.7
| 2014-10-04 22:30 | 11.6 | 16.1 | 16.7
| 2014-10-04 23:00 | 10.7 | 16.1 | 16.7
| 2014-10-04 23:30 | 10.6 | 16.1 | 16.7
| 2014-10-05 | 10.3 | 16.1 | 16.7
| 2014-10-05 00:30 | 9.7 | 16.1 | 16.7
| 2014-10-05 01:00 | 9.6 | 16.1 | 16.7
| 2014-10-05 01:30 | 9.1 | 16.1 | 16.7
| 2014-10-05 02:00 | 8.7 | 15.6 | 16.7
| 2014-10-05 02:30 | 8.7 | 15.6 | 16.7
| 2014-10-05 03:00 | 8.6 | 15.6 | 16.7
| 2014-10-05 03:30 | 8.7 | 15.6 | 16.7
| 2014-10-05 04:00 | 9 | 15.6 | 16.7
| 2014-10-05 04:30 | 8.9 | 15.6 | 16.7
| 2014-10-05 05:00 | 8.8 | 15.6 | 16.7
| 2014-10-05 05:30 | 9 | 15 | 16.7
| 2014-10-05 06:00 | 9.2 | 15 | 16.7
| 2014-10-05 06:30 | 9.3 | 15 | 16.7
| 2014-10-05 07:00 | 9.3 | 15 | 16.7
| 2014-10-05 07:30 | 9.2 | 15 | 16.7
| 2014-10-05 08:00 | 9.2 | 15 | 16.7
| 2014-10-05 08:30 | 9.9 | 15 | 16.7
| 2014-10-05 09:00 | 10.6 | 15 | 16.7
| 2014-10-05 09:30 | 11.2 | 15 | 16.7
| 2014-10-05 10:00 | 11.9 | 15 | 16.7
| 2014-10-05 10:30 | 12.9 | 15 | 16.7
| 2014-10-05 11:00 | 14.3 | 15 | 16.7
| 2014-10-05 11:30 | 14.6 | 15 | 16.7
| 2014-10-05 12:00 | 15.5 | 15 | 16.7
| 2014-10-05 12:30 | 14.9 | 15 | 16.7
| 2014-10-05 13:00 | 14.8 | 15 | 16.7
| 2014-10-05 13:30 | 15.6 | 15 | 16.7
| 2014-10-05 14:00 | 16.3 | 15 | 16.7
| 2014-10-05 14:30 | 15.3 | 15 | 16.7
| 2014-10-05 15:00 | 15.5 | 15.6 | 16.7
| 2014-10-05 15:30 | 15.6 | 15.6 | 16.7
| 2014-10-05 16:00 | 16.1 | 15.6 | 16.7
| 2014-10-05 16:30 | 15.8 | 15.6 | 16.7
| 2014-10-05 17:00 | 15.2 | 15.6 | 16.7
| 2014-10-05 17:30 | 14.7 | 15.6 | 16.7
| 2014-10-05 18:00 | 14.1 | 16.1 | 16.7
| 2014-10-05 18:30 | 13.7 | 16.1 | 16.7
| 2014-10-05 19:00 | 13 | 16.1 | 16.7
| 2014-10-05 19:30 | 12.5 | 16.1 | 16.7
| 2014-10-05 20:00 | 12.2 | 16.1 | 16.7
| 2014-10-05 20:30 | 12.1 | 16.1 | 16.7
| 2014-10-05 21:00 | 12.4 | 16.1 | 16.7
| 2014-10-05 21:30 | 12.3 | 16.1 | 16.7
| 2014-10-05 22:00 | 11.9 | 16.1 | 16.7
| 2014-10-05 22:30 | 12 | 15.6 | 16.7
| 2014-10-05 23:00 | 12.4 | 15.6 | 16.7
| 2014-10-05 23:30 | 12.4 | 15.6 | 16.7
| 2014-10-06 | 12.4 | 15.6 | 16.7
| 2014-10-06 00:30 | 12.4 | 15.6 | 16.7
| 2014-10-06 01:00 | 12.3 | 15.6 | 16.7
| 2014-10-06 01:30 | 12.2 | 15.6 | 16.7
| 2014-10-06 02:00 | 12.2 | 15.6 | 16.7
| 2014-10-06 02:30 | 11.5 | 15.6 | 16.7
| 2014-10-06 03:00 | 10.6 | 15.6 | 16.7
| 2014-10-06 03:30 | 10.1 | 15.6 | 16.7
| 2014-10-06 04:00 | 10.1 | 15.6 | 16.7
| 2014-10-06 04:30 | 10.7 | 15.6 | 16.7
| 2014-10-06 05:00 | 10.9 | 15.6 | 16.7
| 2014-10-06 05:30 | 11.2 | 15 | 16.7
| 2014-10-06 06:00 | 11.6 | 15 | 16.7
| 2014-10-06 06:30 | 11.7 | 15 | 16.7
| 2014-10-06 07:00 | 11.8 | 15 | 16.7
| 2014-10-06 07:30 | 11.9 | 15 | 16.7
| 2014-10-06 08:00 | 12 | 15 | 16.7
| 2014-10-06 08:30 | 12.3 | 15 | 16.7
| 2014-10-06 09:00 | 12.8 | 15 | 16.7
| 2014-10-06 09:30 | 13.5 | 15 | 16.7
| 2014-10-06 10:00 | 13.9 | 15 | 16.7
| 2014-10-06 10:30 | 14 | 15 | 16.7
| 2014-10-06 11:00 | 14.6 | 15 | 16.7
| 2014-10-06 11:30 | 15.3 | 15 | 16.7
| 2014-10-06 12:00 | 15.7 | 15 | 16.7
| 2014-10-06 12:30 | 15.9 | 15 | 16.7
| 2014-10-06 13:00 | 16.8 | 15 | 16.7
| 2014-10-06 13:30 | 17.1 | 15 | 16.7
| 2014-10-06 14:00 | 18.2 | 15.6 | 16.7
| 2014-10-06 14:30 | 18.4 | 15.6 | 16.7
| 2014-10-06 15:00 | 18.3 | 15.6 | 16.7
| 2014-10-06 15:30 | 18.4 | 15.6 | 16.7
| 2014-10-06 16:00 | 18.8 | 15.6 | 16.7
| 2014-10-06 16:30 | 19 | 16.1 | 16.7
| 2014-10-06 17:00 | 18.7 | 16.1 | 16.7
| 2014-10-06 17:30 | 18.8 | 16.1 | 16.7
| 2014-10-06 18:00 | 17.2 | 16.1 | 16.7
| 2014-10-06 18:30 | 15.9 | 16.1 | 16.7
| 2014-10-06 19:00 | 14.7 | 16.1 | 16.7
| 2014-10-06 19:30 | 13.7 | 16.1 | 16.7
| 2014-10-06 20:00 | 13 | 16.1 | 16.7
| 2014-10-06 20:30 | 12.6 | 16.1 | 16.7
| 2014-10-06 21:00 | 12.2 | 16.1 | 16.7
| 2014-10-06 21:30 | 11.7 | 16.1 | 16.7
| 2014-10-06 22:00 | 11.3 | 16.1 | 16.7
| 2014-10-06 22:30 | 11.1 | 16.1 | 16.7
| 2014-10-06 23:00 | 10.8 | 16.1 | 16.7
| 2014-10-06 23:30 | 10.8 | 16.1 | 16.7
| 2014-10-07 | 10.6 | 15.6 | 16.7
| 2014-10-07 00:30 | 10.2 | 15.6 | 16.7
| 2014-10-07 01:00 | 9.8 | 15.6 | 16.7
| 2014-10-07 01:30 | 9.7 | 15.6 | 16.7
| 2014-10-07 02:00 | 9.7 | 15.6 | 16.7
| 2014-10-07 02:30 | 9.8 | 15.6 | 16.7
| 2014-10-07 03:00 | 9.9 | 15.6 | 16.7
| 2014-10-07 03:30 | 10.3 | 15 | 16.7
| 2014-10-07 04:00 | 10.8 | 15 | 16.7
| 2014-10-07 04:30 | 11 | 15 | 16.7
| 2014-10-07 05:00 | 11.2 | 15 | 16.7
| 2014-10-07 05:30 | 11.5 | 15 | 16.7
| 2014-10-07 06:00 | 12.3 | 15 | 16.7
| 2014-10-07 06:30 | 13.1 | 15 | 16.7
| 2014-10-07 07:00 | 13.4 | 15 | 16.7
| 2014-10-07 07:30 | 13.8 | 15 | 16.7
| 2014-10-07 08:00 | 14.1 | 15 | 16.7
| 2014-10-07 08:30 | 14 | 15 | 16.7
| 2014-10-07 09:00 | 14.2 | 15 | 16.7
| 2014-10-07 09:30 | 14.9 | 15 | 16.7
| 2014-10-07 10:00 | 14.9 | 15 | 16.7
| 2014-10-07 10:30 | 15 | 15 | 16.7
| 2014-10-07 11:00 | 16.3 | 15 | 16.7
| 2014-10-07 11:30 | 15.2 | 15 | 16.7
| 2014-10-07 12:00 | 14.6 | 15 | 16.7
| 2014-10-07 12:30 | 14.7 | 15 | 16.7
| 2014-10-07 13:00 | 15 | 15 | 16.7
| 2014-10-07 13:30 | 15.6 | 15 | 16.7
| 2014-10-07 14:00 | 15.8 | 15 | 16.7
| 2014-10-07 14:30 | 15.9 | 15 | 16.7
| 2014-10-07 15:00 | 16.2 | 15 | 16.7
| 2014-10-07 15:30 | 15.8 | 15 | 16.7
| 2014-10-07 16:00 | 16.1 | 15 | 16.7
| 2014-10-07 16:30 | 16.2 | 15.6 | 16.7
| 2014-10-07 17:00 | 15.8 | 15.6 | 16.7
| 2014-10-07 17:30 | 16 | 15.6 | 16.7
| 2014-10-07 18:00 | 15.7 | 15.6 | 16.7
| 2014-10-07 18:30 | 15.7 | 15.6 | 16.7
| 2014-10-07 19:00 | 15.5 | 15.6 | 16.7
| 2014-10-07 19:30 | 15.2 | 15.6 | 16.7
| 2014-10-07 20:00 | 15.1 | 15.6 | 16.7
| 2014-10-07 20:30 | 15 | 15.6 | 16.7
| 2014-10-07 21:00 | 14.4 | 15.6 | 16.7
| 2014-10-07 21:30 | 13.3 | 15.6 | 16.7
| 2014-10-07 22:00 | 13.3 | 15.6 | 16.7
| 2014-10-07 22:30 | 13.2 | 15.6 | 16.7
| 2014-10-07 23:00 | 13.1 | 15.6 | 16.7
| 2014-10-07 23:30 | 12.8 | 15.6 | 16.7
| 2014-10-08 | 12.6 | 15.6 | 16.7
| 2014-10-08 00:30 | 12.3 | 15.6 | 16.7
| 2014-10-08 01:00 | 12.1 | 15.6 | 16.7
| 2014-10-08 01:30 | 12 | 15.6 | 16.7
| 2014-10-08 02:00 | 12.2 | 15 | 16.7
| 2014-10-08 02:30 | 12.2 | 15 | 16.7
| 2014-10-08 03:00 | 11.8 | 15 | 16.7
| 2014-10-08 03:30 | 11.8 | 15 | 16.7
| 2014-10-08 04:00 | 11.8 | 15 | 16.7
| 2014-10-08 04:30 | 11.8 | 15 | 16.7
| 2014-10-08 05:00 | 11.9 | 15 | 16.7
| 2014-10-08 05:30 | 12 | 15 | 16.7
| 2014-10-08 06:00 | 11.8 | 15 | 16.7
| 2014-10-08 06:30 | 11.6 | 15 | 16.7
| 2014-10-08 07:00 | 11.3 | 15 | 16.7
| 2014-10-08 07:30 | 11.2 | 15 | 16.7
| 2014-10-08 08:00 | 10.8 | 15 | 16.7
| 2014-10-08 08:30 | 11.4 | 15 | 16.7
| 2014-10-08 09:00 | 12.1 | 14.4 | 16.7
| 2014-10-08 09:30 | 12.5 | 14.4 | 16.7
| 2014-10-08 10:00 | 13 | 14.4 | 16.7
| 2014-10-08 10:30 | 13.3 | 14.4 | 16.7
| 2014-10-08 11:00 | 13.8 | 14.4 | 16.7
| 2014-10-08 11:30 | 14.1 | 14.4 | 16.7
| 2014-10-08 12:00 | 14.3 | 14.4 | 16.7
| 2014-10-08 12:30 | 14.6 | 14.4 | 16.7
| 2014-10-08 13:00 | 14.5 | 14.4 | 16.7
| 2014-10-08 13:30 | 14.9 | 14.4 | 16.7
| 2014-10-08 14:00 | 15.2 | 14.4 | 16.7
| 2014-10-08 14:30 | 16.1 | 15 | 16.7
| 2014-10-08 15:00 | 17.1 | 15 | 16.7
| 2014-10-08 15:30 | 17.9 | 15 | 16.7
| 2014-10-08 16:00 | 18.6 | 15 | 16.7
| 2014-10-08 16:30 | 18.5 | 15 | 16.7
| 2014-10-08 17:00 | 18.6 | 15 | 16.1
| 2014-10-08 17:30 | 18.5 | 15 | 16.1
| 2014-10-08 18:00 | 18.3 | 15 | 16.1
| 2014-10-08 18:30 | 16.9 | 15 | 16.1
| 2014-10-08 19:00 | 16.6 | 15.6 | 16.1
| 2014-10-08 19:30 | 16.3 | 15.6 | 16.1
| 2014-10-08 20:00 | 15.9 | 15.6 | 16.1
| 2014-10-08 20:30 | 15.4 | 15.6 | 16.1
| 2014-10-08 21:00 | 15.1 | 15.6 | 16.1
| 2014-10-08 21:30 | 14.9 | 15.6 | 16.1
| 2014-10-08 22:00 | 14.7 | 15.6 | 16.1
| 2014-10-08 22:30 | 14.8 | 15.6 | 16.1
| 2014-10-08 23:00 | 15 | 15.6 | 16.1
| 2014-10-08 23:30 | 15.5 | 15.6 | 16.1
| 2014-10-09 | 15.8 | 15.6 | 16.1
| 2014-10-09 00:30 | 15.8 | 15.6 | 16.1
| 2014-10-09 01:00 | 16.3 | 15.6 | 16.1
| 2014-10-09 01:30 | 16.9 | 15.6 | 16.1
| 2014-10-09 02:00 | 17.4 | 15.6 | 16.1
| 2014-10-09 02:30 | 17.4 | 15 | 16.1
| 2014-10-09 03:00 | 18.3 | 15 | 16.1
| 2014-10-09 03:30 | 18.8 | 15 | 16.1
| 2014-10-09 04:00 | 19.3 | 15 | 16.1
| 2014-10-09 04:30 | 18.3 | 15 | 16.1
| 2014-10-09 05:00 | 17.3 | 15 | 16.1
| 2014-10-09 05:30 | 16.7 | 15.6 | 16.1
| 2014-10-09 06:00 | 17.6 | 15.6 | 16.1
| 2014-10-09 06:30 | 18.1 | 15.6 | 16.1
| 2014-10-09 07:00 | 17.6 | 15.6 | 16.1
| 2014-10-09 07:30 | 17 | 15.6 | 16.1
| 2014-10-09 08:00 | 16.4 | 15.6 | 16.1
| 2014-10-09 08:30 | 16.3 | 15.6 | 16.1
| 2014-10-09 09:00 | 16.4 | 15.6 | 16.1
| 2014-10-09 09:30 | 16.7 | 15.6 | 16.1
| 2014-10-09 10:00 | 17.3 | 15.6 | 16.1
| 2014-10-09 10:30 | 17.3 | 15.6 | 16.1
| 2014-10-09 11:00 | 17.7 | 15.6 | 16.1
| 2014-10-09 11:30 | 17.7 | 15.6 | 16.1
| 2014-10-09 12:00 | 18 | 15.6 | 16.1
| 2014-10-09 12:30 | 18.3 | 15.6 | 16.1
| 2014-10-09 13:00 | 18.2 | 15.6 | 16.1
| 2014-10-09 13:30 | 18.8 | 15.6 | 16.1
| 2014-10-09 14:00 | 19.2 | 15.6 | 16.1
| 2014-10-09 14:30 | 19.5 | 15.6 | 16.1
| 2014-10-09 15:00 | 19.3 | 15.6 | 16.1
| 2014-10-09 15:30 | 18.9 | 15.6 | 16.1
| 2014-10-09 16:00 | 19.9 | 15.6 | 16.1
| 2014-10-09 16:30 | 18.7 | 16.1 | 16.1
| 2014-10-09 17:00 | 17.1 | 16.1 | 16.1
| 2014-10-09 17:30 | 16.4 | 16.1 | 16.1
| 2014-10-09 18:00 | 16.1 | 16.1 | 16.1
| 2014-10-09 18:30 | 15.7 | 16.1 | 16.1
| 2014-10-09 19:00 | 15.4 | 16.1 | 16.1
| 2014-10-09 19:30 | 15.4 | 16.1 | 16.1
| 2014-10-09 20:00 | 15.3 | 16.1 | 16.1
| 2014-10-09 20:30 | 15.3 | 16.1 | 16.1
| 2014-10-09 21:00 | 15.2 | 16.1 | 16.1
| 2014-10-09 21:30 | 15.2 | 16.1 | 16.1
| 2014-10-09 22:00 | 15 | 16.1 | 16.1
| 2014-10-09 22:30 | 14.9 | 16.1 | 16.1
| 2014-10-09 23:00 | 14.7 | 16.1 | 16.1
| 2014-10-09 23:30 | 14.1 | 16.1 | 16.1
| 2014-10-10 | 13.6 | 16.1 | 16.1
| 2014-10-10 00:30 | 13.7 | 16.1 | 16.1
| 2014-10-10 01:00 | 13.4 | 16.1 | 16.1
| 2014-10-10 01:30 | 12.9 | 16.1 | 16.1
| 2014-10-10 02:00 | 12.8 | 15.6 | 16.1
| 2014-10-10 02:30 | 12.5 | 15.6 | 16.1
| 2014-10-10 03:00 | 12.6 | 15.6 | 16.1
| 2014-10-10 03:30 | 12.5 | 15.6 | 16.1
| 2014-10-10 04:00 | 12.7 | 15.6 | 16.1
| 2014-10-10 04:30 | 13.1 | 15.6 | 16.1
| 2014-10-10 05:00 | 12.8 | 15.6 | 16.1
| 2014-10-10 05:30 | 12.8 | 15.6 | 16.1
| 2014-10-10 06:00 | 13.2 | 15.6 | 16.1
| 2014-10-10 06:30 | 13.5 | 15.6 | 16.1
| 2014-10-10 07:00 | 13.4 | 15 | 16.1
| 2014-10-10 07:30 | 13.8 | 15 | 16.1
| 2014-10-10 08:00 | 13.8 | 15 | 16.1
| 2014-10-10 08:30 | 13.9 | 15 | 16.1
| 2014-10-10 09:00 | 13.9 | 15 | 16.1
| 2014-10-10 09:30 | 14.3 | 15 | 16.1
| 2014-10-10 10:00 | 15 | 15 | 16.1
| 2014-10-10 10:30 | 15.5 | 15 | 16.1
| 2014-10-10 11:00 | 15.9 | 15 | 16.1
| 2014-10-10 11:30 | 16.3 | 15 | 16.1
| 2014-10-10 12:00 | 17.2 | 15 | 16.1
| 2014-10-10 12:30 | 17.3 | 15 | 16.1
| 2014-10-10 13:00 | 18.1 | 15 | 16.1
| 2014-10-10 13:30 | 18.6 | 15.6 | 16.1
| 2014-10-10 14:00 | 19 | 15.6 | 16.1
| 2014-10-10 14:30 | 19.2 | 15.6 | 16.1
| 2014-10-10 15:00 | 19.1 | 15.6 | 16.1
| 2014-10-10 15:30 | 18.9 | 15.6 | 16.1
| 2014-10-10 16:00 | 18.4 | 16.1 | 16.1
| 2014-10-10 16:30 | 18 | 16.1 | 16.1
| 2014-10-10 17:00 | 18.3 | 16.1 | 16.1
| 2014-10-10 17:30 | 17.7 | 16.1 | 16.1
| 2014-10-10 18:00 | 17.3 | 16.1 | 16.1
| 2014-10-10 18:30 | 16.8 | 16.1 | 16.1
| 2014-10-10 19:00 | 16.5 | 16.1 | 16.1
| 2014-10-10 19:30 | 16.2 | 16.1 | 16.1
| 2014-10-10 20:00 | 15.8 | 16.1 | 16.1
| 2014-10-10 20:30 | 15.6 | 16.1 | 16.1
| 2014-10-10 21:00 | 15.2 | 16.1 | 16.1
| 2014-10-10 21:30 | 14.9 | 16.1 | 16.1
| 2014-10-10 22:00 | 14.8 | 16.1 | 16.1
| 2014-10-10 22:30 | 14.8 | 16.1 | 16.1
| 2014-10-10 23:00 | 14.7 | 16.1 | 16.1
| 2014-10-10 23:30 | 14.7 | 16.1 | 16.1
| 2014-10-11 | 14.7 | 16.1 | 16.1
| 2014-10-11 00:30 | 14.7 | 16.1 | 16.1
| 2014-10-11 01:00 | 14.7 | 16.1 | 16.1
| 2014-10-11 01:30 | 14.7 | 16.1 | 16.1
| 2014-10-11 02:00 | 14.7 | 16.1 | 16.1
| 2014-10-11 02:30 | 14.7 | 16.1 | 16.1
| 2014-10-11 03:00 | 14.7 | 16.1 | 16.1
| 2014-10-11 03:30 | 14.7 | 16.1 | 16.1
| 2014-10-11 04:00 | 14.8 | 16.1 | 16.1
| 2014-10-11 04:30 | 14.8 | 16.1 | 16.1
| 2014-10-11 05:00 | 14.7 | 16.1 | 16.1
| 2014-10-11 05:30 | 14.7 | 16.1 | 16.1
| 2014-10-11 06:00 | 14.7 | 16.1 | 16.1
| 2014-10-11 06:30 | 14.7 | 16.1 | 16.1
| 2014-10-11 07:00 | 14.7 | 16.1 | 16.1
| 2014-10-11 07:30 | 14.7 | 15.6 | 16.1
| 2014-10-11 08:00 | 14.7 | 15.6 | 16.1
| 2014-10-11 08:30 | 14.8 | 15.6 | 16.1
| 2014-10-11 09:00 | 14.8 | 15.6 | 16.1
| 2014-10-11 09:30 | 14.9 | 15.6 | 16.1
| 2014-10-11 10:00 | 15.1 | 15.6 | 16.1
| 2014-10-11 10:30 | 15.1 | 15.6 | 16.1
| 2014-10-11 11:00 | 15.2 | 15.6 | 16.1
| 2014-10-11 11:30 | 15.4 | 15.6 | 16.1
| 2014-10-11 12:00 | 15.6 | 15.6 | 16.1
| 2014-10-11 12:30 | 15.7 | 15.6 | 16.1
| 2014-10-11 13:00 | 16.3 | 16.1 | 16.1
| 2014-10-11 13:30 | 16.9 | 16.1 | 16.1
| 2014-10-11 14:00 | 16.9 | 16.1 | 16.1
| 2014-10-11 14:30 | 16.7 | 16.1 | 16.1
| 2014-10-11 15:00 | 17.1 | 16.1 | 16.1
| 2014-10-11 15:30 | 17.3 | 16.1 | 16.1
| 2014-10-11 16:00 | 17.4 | 16.1 | 16.1
| 2014-10-11 16:30 | 17.8 | 16.1 | 16.1
| 2014-10-11 17:00 | 18.7 | 16.1 | 16.1
| 2014-10-11 17:30 | 17.7 | 16.1 | 16.1
| 2014-10-11 18:00 | 16.9 | 16.7 | 16.1
| 2014-10-11 18:30 | 16.4 | 16.7 | 16.1
| 2014-10-11 19:00 | 15.6 | 16.7 | 16.1
| 2014-10-11 19:30 | 15.2 | 16.7 | 16.1
| 2014-10-11 20:00 | 14.6 | 16.7 | 16.1
| 2014-10-11 20:30 | 14.1 | 16.7 | 16.1
| 2014-10-11 21:00 | 14.7 | 16.7 | 16.1
| 2014-10-11 21:30 | 14.3 | 16.1 | 16.1
| 2014-10-11 22:00 | 14.3 | 16.1 | 16.1
| 2014-10-11 22:30 | 14.2 | 16.1 | 16.1
| 2014-10-11 23:00 | 13.4 | 16.1 | 16.1
| 2014-10-11 23:30 | 12.9 | 16.1 | 16.1
| 2014-10-12 | 12.5 | 16.1 | 16.1
| 2014-10-12 00:30 | 12.1 | 16.1 | 16.1
| 2014-10-12 01:00 | 11.7 | 16.1 | 16.1
| 2014-10-12 01:30 | 11.4 | 16.1 | 16.1
| 2014-10-12 02:00 | 10.9 | 16.1 | 16.1
| 2014-10-12 02:30 | 10.7 | 15.6 | 16.1
| 2014-10-12 03:00 | 10.3 | 15.6 | 16.1
| 2014-10-12 03:30 | 9.9 | 15.6 | 16.1
| 2014-10-12 04:00 | 9.5 | 15.6 | 16.1
| 2014-10-12 04:30 | 9.2 | 15.6 | 16.1
| 2014-10-12 05:00 | 9.2 | 15.6 | 16.1
| 2014-10-12 05:30 | 8.5 | 15.6 | 16.1
| 2014-10-12 06:00 | 8.4 | 15 | 16.1
| 2014-10-12 06:30 | 8.1 | 15 | 16.1
| 2014-10-12 07:00 | 7.8 | 15 | 16.1
| 2014-10-12 07:30 | 7.6 | 15 | 16.1
| 2014-10-12 08:00 | 7.4 | 15 | 16.1
| 2014-10-12 08:30 | 7.4 | 15 | 16.1
| 2014-10-12 09:00 | 8.9 | 14.4 | 16.1
| 2014-10-12 09:30 | 10.3 | 14.4 | 16.1
| 2014-10-12 10:00 | 11.9 | 14.4 | 16.1
| 2014-10-12 10:30 | 12.5 | 14.4 | 16.1
| 2014-10-12 11:00 | 12.9 | 14.4 | 16.1
| 2014-10-12 11:30 | 13.1 | 14.4 | 16.1
| 2014-10-12 12:00 | 13.8 | 14.4 | 16.1
| 2014-10-12 12:30 | 14.7 | 14.4 | 16.1
| 2014-10-12 13:00 | 15.3 | 14.4 | 16.1
| 2014-10-12 13:30 | 15.9 | 14.4 | 16.1
| 2014-10-12 14:00 | 17.4 | 14.4 | 16.1
| 2014-10-12 14:30 | 17.8 | 14.4 | 16.1
| 2014-10-12 15:00 | 18.4 | 15 | 16.1
| 2014-10-12 15:30 | 18.9 | 15 | 16.1
| 2014-10-12 16:00 | 18.2 | 15 | 16.1
| 2014-10-12 16:30 | 17.6 | 15 | 16.1
| 2014-10-12 17:00 | 17.1 | 15 | 16.1
| 2014-10-12 17:30 | 16.4 | 15 | 16.1
| 2014-10-12 18:00 | 15.8 | 15 | 16.1
| 2014-10-12 18:30 | 15.2 | 15.6 | 16.1
| 2014-10-12 19:00 | 14.7 | 15.6 | 16.1
| 2014-10-12 19:30 | 14.6 | 15.6 | 16.1
| 2014-10-12 20:00 | 14.5 | 15.6 | 16.1
| 2014-10-12 20:30 | 14.4 | 15.6 | 16.1
| 2014-10-12 21:00 | 14.3 | 15.6 | 16.1
| 2014-10-12 21:30 | 14.3 | 15.6 | 16.1
| 2014-10-12 22:00 | 14.3 | 15.6 | 16.1
| 2014-10-12 22:30 | 14.3 | 15.6 | 16.1
| 2014-10-12 23:00 | 14.4 | 15.6 | 16.1
| 2014-10-12 23:30 | 14.3 | 15.6 | 16.1
| 2014-10-13 | 14.3 | 15.6 | 16.1
| 2014-10-13 00:30 | 14.1 | 15.6 | 16.1
| 2014-10-13 01:00 | 14.1 | 15.6 | 16.1
| 2014-10-13 01:30 | 14.1 | 15.6 | 16.1
| 2014-10-13 02:00 | 13.7 | 15.6 | 16.1
| 2014-10-13 02:30 | 13.4 | 15.6 | 16.1
| 2014-10-13 03:00 | 13 | 15.6 | 16.1
| 2014-10-13 03:30 | 13.1 | 15.6 | 16.1
| 2014-10-13 04:00 | 12.9 | 15.6 | 16.1
| 2014-10-13 04:30 | 13.2 | 15 | 16.1
| 2014-10-13 05:00 | 12.8 | 15 | 16.1
| 2014-10-13 05:30 | 12.8 | 15 | 16.1
| 2014-10-13 06:00 | 12.6 | 15 | 16.1
| 2014-10-13 06:30 | 12.8 | 15 | 16.1
| 2014-10-13 07:00 | 12.9 | 15 | 16.1
| 2014-10-13 07:30 | 12.9 | 15 | 16.1
| 2014-10-13 08:00 | 13.6 | 15 | 16.1
| 2014-10-13 08:30 | 14.1 | 15 | 16.1
| 2014-10-13 09:00 | 14.6 | 15 | 16.1
| 2014-10-13 09:30 | 15.1 | 15 | 16.1
| 2014-10-13 10:00 | 15.5 | 15 | 16.1
| 2014-10-13 10:30 | 15.9 | 15 | 16.1
| 2014-10-13 11:00 | 15.7 | 15 | 16.1
| 2014-10-13 11:30 | 16.1 | 15 | 16.1
| 2014-10-13 12:00 | 17.4 | 15 | 16.1
| 2014-10-13 12:30 | 17.3 | 15 | 16.1
| 2014-10-13 13:00 | 17.3 | 15 | 16.1
| 2014-10-13 13:30 | 17.6 | 15 | 16.1
| 2014-10-13 14:00 | 17.7 | 15 | 16.1
| 2014-10-13 14:30 | 17.9 | 15.6 | 16.1
| 2014-10-13 15:00 | 17.7 | 15.6 | 16.1
| 2014-10-13 15:30 | 18.2 | 15.6 | 16.1
| 2014-10-13 16:00 | 18.2 | 15.6 | 16.1
| 2014-10-13 16:30 | 18.1 | 15.6 | 16.1
| 2014-10-13 17:00 | 18.1 | 15.6 | 16.1
| 2014-10-13 17:30 | 17.8 | 16.1 | 16.1
| 2014-10-13 18:00 | 17.3 | 16.1 | 16.1
| 2014-10-13 18:30 | 16.5 | 16.1 | 16.1
| 2014-10-13 19:00 | 15.7 | 16.1 | 16.1
| 2014-10-13 19:30 | 14.7 | 16.1 | 16.1
| 2014-10-13 20:00 | 14.1 | 16.1 | 16.1
| 2014-10-13 20:30 | 13.6 | 16.1 | 16.1
| 2014-10-13 21:00 | 13.2 | 16.1 | 16.1
| 2014-10-13 21:30 | 12.8 | 16.1 | 16.1
| 2014-10-13 22:00 | 12.6 | 16.1 | 16.1
| 2014-10-13 22:30 | 12.2 | 16.1 | 16.1
| 2014-10-13 23:00 | 11.8 | 15.6 | 16.1
| 2014-10-13 23:30 | 11.8 | 15.6 | 16.1
| 2014-10-14 | 11.8 | 15.6 | 16.1
| 2014-10-14 00:30 | 11.9 | 15.6 | 16.1
| 2014-10-14 01:00 | 11.9 | 15.6 | 16.1
| 2014-10-14 01:30 | 11.9 | 15.6 | 16.1
| 2014-10-14 02:00 | 11.9 | 15.6 | 16.1
| 2014-10-14 02:30 | 12.2 | 15.6 | 16.1
| 2014-10-14 03:00 | 12.8 | 15 | 16.1
| 2014-10-14 03:30 | 12.6 | 15 | 16.1
| 2014-10-14 04:00 | 12.2 | 15 | 16.1
| 2014-10-14 04:30 | 11.8 | 15 | 16.1
| 2014-10-14 05:00 | 12.5 | 15 | 16.1
| 2014-10-14 05:30 | 12 | 15 | 16.1
| 2014-10-14 06:00 | 11.4 | 15 | 16.1
| 2014-10-14 06:30 | 11.2 | 15 | 16.1
| 2014-10-14 07:00 | 11.6 | 15 | 16.1
| 2014-10-14 07:30 | 11.2 | 15 | 16.1
| 2014-10-14 08:00 | 11.1 | 15 | 16.1
| 2014-10-14 08:30 | 11.3 | 15 | 16.1
| 2014-10-14 09:00 | 12.1 | 14.4 | 16.1
| 2014-10-14 09:30 | 12.7 | 14.4 | 16.1
| 2014-10-14 10:00 | 13.3 | 14.4 | 16.1
| 2014-10-14 10:30 | 14.2 | 14.4 | 16.1
| 2014-10-14 11:00 | 14.8 | 14.4 | 16.1
| 2014-10-14 11:30 | 15.5 | 14.4 | 16.1
| 2014-10-14 12:00 | 16.2 | 14.4 | 16.1
| 2014-10-14 12:30 | 17.1 | 14.4 | 16.1
| 2014-10-14 13:00 | 17.9 | 14.4 | 16.1
| 2014-10-14 13:30 | 18.6 | 15 | 16.1
| 2014-10-14 14:00 | 19.8 | 15 | 16.1
| 2014-10-14 14:30 | 20.1 | 15 | 16.1
| 2014-10-14 15:00 | 19.6 | 15 | 16.1
| 2014-10-14 15:30 | 20.6 | 15 | 16.1
| 2014-10-14 16:00 | 20.6 | 15 | 16.1
| 2014-10-14 16:30 | 20 | 15.6 | 16.1
| 2014-10-14 17:00 | 18.9 | 15.6 | 16.1
| 2014-10-14 17:30 | 18.1 | 15.6 | 16.1
| 2014-10-14 18:00 | 17.8 | 15.6 | 16.1
| 2014-10-14 18:30 | 17.1 | 15.6 | 16.1
| 2014-10-14 19:00 | 15.8 | 15.6 | 16.1
| 2014-10-14 19:30 | 14.8 | 15.6 | 16.1
| 2014-10-14 20:00 | 14.4 | 15.6 | 16.1
| 2014-10-14 20:30 | 13.8 | 15.6 | 16.1
| 2014-10-14 21:00 | 13.4 | 15.6 | 16.1
| 2014-10-14 21:30 | 13.2 | 15.6 | 16.1
| 2014-10-14 22:00 | 13.2 | 15.6 | 16.1
| 2014-10-14 22:30 | 12.7 | 15.6 | 16.1
| 2014-10-14 23:00 | 12.4 | 15.6 | 16.1
| 2014-10-14 23:30 | 12.3 | 15.6 | 16.1
| 2014-10-15 | 11.8 | 15.6 | 16.1
| 2014-10-15 00:30 | 12.1 | 15.6 | 16.1
| 2014-10-15 01:00 | 12.3 | 15.6 | 16.1
| 2014-10-15 01:30 | 12.7 | 15.6 | 16.1
| 2014-10-15 02:00 | 12.8 | 15.6 | 16.1
| 2014-10-15 02:30 | 12.6 | 15 | 16.1
| 2014-10-15 03:00 | 12.4 | 15 | 16.1
| 2014-10-15 03:30 | 12.6 | 15 | 16.1
| 2014-10-15 04:00 | 12.8 | 15 | 16.1
| 2014-10-15 04:30 | 12.7 | 15 | 16.1
| 2014-10-15 05:00 | 12.7 | 15 | 16.1
| 2014-10-15 05:30 | 12.6 | 15 | 16.1
| 2014-10-15 06:00 | 12.4 | 15 | 16.1
| 2014-10-15 06:30 | 12.2 | 15 | 16.1
| 2014-10-15 07:00 | 12.2 | 15 | 16.1
| 2014-10-15 07:30 | 11.7 | 15 | 16.1
| 2014-10-15 08:00 | 11.7 | 15 | 16.1
| 2014-10-15 08:30 | 11.7 | 15 | 16.1
| 2014-10-15 09:00 | 12.3 | 15 | 16.1
| 2014-10-15 09:30 | 12.7 | 15 | 16.1
| 2014-10-15 10:00 | 13.1 | 15 | 16.1
| 2014-10-15 10:30 | 13.3 | 15 | 16.1
| 2014-10-15 11:00 | 14.1 | 15 | 16.1
| 2014-10-15 11:30 | 15 | 15 | 16.1
| 2014-10-15 12:00 | 15.6 | 15 | 16.1
| 2014-10-15 12:30 | 16.8 | 15 | 16.1
| 2014-10-15 13:00 | 17.8 | 15 | 16.1
| 2014-10-15 13:30 | 17.5 | 15 | 16.1
| 2014-10-15 14:00 | 17.2 | 15 | 16.1
| 2014-10-15 14:30 | 17.7 | 15 | 16.1
| 2014-10-15 15:00 | 18.4 | 15 | 16.1
| 2014-10-15 15:30 | 19.5 | 15 | 16.1
| 2014-10-15 16:00 | 18.8 | 15.6 | 16.1
| 2014-10-15 16:30 | 18.3 | 15.6 | 16.1
| 2014-10-15 17:00 | 17.9 | 15.6 | 16.1
| 2014-10-15 17:30 | 17.3 | 15.6 | 16.1
| 2014-10-15 18:00 | 16.7 | 15.6 | 16.1
| 2014-10-15 18:30 | 16.1 | 15.6 | 16.1
| 2014-10-15 19:00 | 15.3 | 15.6 | 16.1
| 2014-10-15 19:30 | 14.8 | 15.6 | 16.1
| 2014-10-15 20:00 | 14.4 | 16.1 | 16.1
| 2014-10-15 20:30 | 14.1 | 15.6 | 16.1
| 2014-10-15 21:00 | 14.1 | 15.6 | 16.1
| 2014-10-15 21:30 | 13.9 | 15.6 | 16.1
| 2014-10-15 22:00 | 13.9 | 15.6 | 16.1
| 2014-10-15 22:30 | 13.8 | 15.6 | 16.1
| 2014-10-15 23:00 | 13.8 | 15.6 | 16.1
| 2014-10-15 23:30 | 13.8 | 15.6 | 16.1
| 2014-10-16 | 13.8 | 15.6 | 16.1
| 2014-10-16 00:30 | 13.7 | 15.6 | 16.1
| 2014-10-16 01:00 | 13.7 | 15.6 | 16.1
| 2014-10-16 01:30 | 13.6 | 15.6 | 16.1
| 2014-10-16 02:00 | 13.5 | 15.6 | 16.1
| 2014-10-16 02:30 | 13.4 | 15.6 | 16.1
| 2014-10-16 03:00 | 13.6 | 15.6 | 16.1
| 2014-10-16 03:30 | 13.4 | 15.6 | 16.1
| 2014-10-16 04:00 | 13.8 | 15.6 | 16.1
| 2014-10-16 04:30 | 13.8 | 15.6 | 16.1
| 2014-10-16 05:00 | 13.8 | 15.6 | 16.1
| 2014-10-16 05:30 | 13.7 | 15.6 | 16.1
| 2014-10-16 06:00 | 13.7 | 15 | 16.1
| 2014-10-16 06:30 | 13.8 | 15 | 16.1
| 2014-10-16 07:00 | 13.8 | 15 | 16.1
| 2014-10-16 07:30 | 13.9 | 15 | 16.1
| 2014-10-16 08:00 | 14 | 15 | 16.1
| 2014-10-16 08:30 | 14.1 | 15 | 16.1
| 2014-10-16 09:00 | 14.4 | 15 | 16.1
| 2014-10-16 09:30 | 14.6 | 15 | 16.1
| 2014-10-16 10:00 | 15.4 | 15 | 16.1
| 2014-10-16 10:30 | 15.5 | 15 | 16.1
| 2014-10-16 11:00 | 16.6 | 15 | 16.1
| 2014-10-16 11:30 | 16.7 | 15 | 16.1
| 2014-10-16 12:00 | 16.1 | 15 | 16.1
| 2014-10-16 12:30 | 16.6 | 15 | 16.1
| 2014-10-16 13:00 | 17.4 | 15 | 16.1
| 2014-10-16 13:30 | 17.3 | 15 | 16.1
| 2014-10-16 14:00 | 17.9 | 15.6 | 16.1
| 2014-10-16 14:30 | 18.1 | 15.6 | 16.1
| 2014-10-16 15:00 | 19.1 | 15.6 | 16.1
| 2014-10-16 15:30 | 18.9 | 15.6 | 16.1
| 2014-10-16 16:00 | 18.4 | 15.6 | 16.1
| 2014-10-16 16:30 | 18.2 | 15.6 | 16.1
| 2014-10-16 17:00 | 17.6 | 15.6 | 16.1
| 2014-10-16 17:30 | 17 | 15.6 | 16.1
| 2014-10-16 18:00 | 16.4 | 16.1 | 16.1
| 2014-10-16 18:30 | 15.7 | 16.1 | 16.1
| 2014-10-16 19:00 | 15.3 | 16.1 | 16.1
| 2014-10-16 19:30 | 15.1 | 16.1 | 16.1
| 2014-10-16 20:00 | 15.6 | 16.1 | 16.1
| 2014-10-16 20:30 | 15 | 16.1 | 16.1
| 2014-10-16 21:00 | 15 | 16.1 | 16.1
| 2014-10-16 21:30 | 14.9 | 15.6 | 16.1
| 2014-10-16 22:00 | 14.7 | 15.6 | 16.1
| 2014-10-16 22:30 | 14.7 | 15.6 | 16.1
| 2014-10-16 23:00 | 14.8 | 15.6 | 16.1
| 2014-10-16 23:30 | 14.7 | 15.6 | 16.1
| 2014-10-17 | 14.6 | 15.6 | 16.1
| 2014-10-17 00:30 | 14.8 | 15.6 | 16.1
| 2014-10-17 01:00 | 14.8 | 15.6 | 16.1
| 2014-10-17 01:30 | 14.7 | 15.6 | 16.1
| 2014-10-17 02:00 | 14.4 | 15.6 | 16.1
| 2014-10-17 02:30 | 14.3 | 15.6 | 16.1
| 2014-10-17 03:00 | 14.8 | 15.6 | 16.1
| 2014-10-17 03:30 | 14.7 | 15.6 | 16.1
| 2014-10-17 04:00 | 14.4 | 15.6 | 16.1
| 2014-10-17 04:30 | 14.6 | 15.6 | 16.1
| 2014-10-17 05:00 | 14.3 | 15.6 | 16.1
| 2014-10-17 05:30 | 13.8 | 15.6 | 16.1
| 2014-10-17 06:00 | 13.6 | 15.6 | 16.1
| 2014-10-17 06:30 | 13.6 | 15.6 | 16.1
| 2014-10-17 07:00 | 13 | 15 | 16.1
| 2014-10-17 07:30 | 12.8 | 15 | 16.1
| 2014-10-17 08:00 | 13 | 15 | 16.1
| 2014-10-17 08:30 | 12.9 | 15 | 16.1
| 2014-10-17 09:00 | 12.9 | 15 | 16.1
| 2014-10-17 09:30 | 13.1 | 15 | 16.1
| 2014-10-17 10:00 | 13.7 | 15 | 16.1
| 2014-10-17 10:30 | 14.7 | 15 | 16.1
| 2014-10-17 11:00 | 14.8 | 15 | 16.1
| 2014-10-17 11:30 | 14.8 | 15 | 16.1
| 2014-10-17 12:00 | 15.2 | 15 | 16.1
| 2014-10-17 12:30 | 15.3 | 15 | 16.1
| 2014-10-17 13:00 | 15.6 | 15 | 16.1
| 2014-10-17 13:30 | 15.6 | 15 | 16.1
| 2014-10-17 14:00 | 15.7 | 15 | 16.1
| 2014-10-17 14:30 | 15.7 | 15 | 16.1
| 2014-10-17 15:00 | 15.8 | 15.6 | 16.1
| 2014-10-17 15:30 | 16.5 | 15.6 | 16.1
| 2014-10-17 16:00 | 16.8 | 15.6 | 16.1
| 2014-10-17 16:30 | 16.6 | 15.6 | 16.1
| 2014-10-17 17:00 | 15.5 | 15.6 | 16.1
| 2014-10-17 17:30 | 15.8 | 15.6 | 16.1
| 2014-10-17 18:00 | 15.7 | 15.6 | 16.1
| 2014-10-17 18:30 | 15.3 | 15.6 | 16.1
| 2014-10-17 19:00 | 15.1 | 15.6 | 16.1
| 2014-10-17 19:30 | 14.7 | 15.6 | 16.1
| 2014-10-17 20:00 | 14.4 | 15.6 | 16.1
| 2014-10-17 20:30 | 14.3 | 15.6 | 16.1
| 2014-10-17 21:00 | 14.1 | 15.6 | 16.1
| 2014-10-17 21:30 | 13.7 | 15.6 | 16.1
| 2014-10-17 22:00 | 13 | 15.6 | 16.1
| 2014-10-17 22:30 | 12.1 | 15.6 | 16.1
| 2014-10-17 23:00 | 11.7 | 15.6 | 16.1
| 2014-10-17 23:30 | 11.5 | 15.6 | 16.1
| 2014-10-18 | 11 | 15.6 | 16.1
| 2014-10-18 00:30 | 10.7 | 15.6 | 16.1
| 2014-10-18 01:00 | 10.6 | 15 | 16.1
| 2014-10-18 01:30 | 10.4 | 15 | 16.1
| 2014-10-18 02:00 | 10.1 | 15 | 16.1
| 2014-10-18 02:30 | 9.7 | 15 | 16.1
| 2014-10-18 03:00 | 9.1 | 15 | 16.1
| 2014-10-18 03:30 | 8.8 | 15 | 16.1
| 2014-10-18 04:00 | 8.8 | 15 | 16.1
| 2014-10-18 04:30 | 8.8 | 15 | 16.1
| 2014-10-18 05:00 | 8.2 | 14.4 | 16.1
| 2014-10-18 05:30 | 7.6 | 14.4 | 16.1
| 2014-10-18 06:00 | 7.8 | 14.4 | 16.1
| 2014-10-18 06:30 | 7.6 | 14.4 | 16.1
| 2014-10-18 07:00 | 7.2 | 14.4 | 16.1
| 2014-10-18 07:30 | 7.2 | 14.4 | 16.1
| 2014-10-18 08:00 | 7.1 | 13.9 | 16.1
| 2014-10-18 08:30 | 6.9 | 13.9 | 16.1
| 2014-10-18 09:00 | 8.1 | 13.9 | 16.1
| 2014-10-18 09:30 | 8.7 | 13.9 | 16.1
| 2014-10-18 10:00 | 9.6 | 13.9 | 16.1
| 2014-10-18 10:30 | 10.3 | 13.9 | 16.1
| 2014-10-18 11:00 | 10.9 | 13.9 | 16.1
| 2014-10-18 11:30 | 11.3 | 13.9 | 16.1
| 2014-10-18 12:00 | 12 | 13.9 | 16.1
| 2014-10-18 12:30 | 13.2 | 13.9 | 16.1
| 2014-10-18 13:00 | 14.5 | 13.9 | 16.1
| 2014-10-18 13:30 | 15.9 | 13.9 | 16.1
| 2014-10-18 14:00 | 16.7 | 13.9 | 16.1
| 2014-10-18 14:30 | 17.8 | 13.9 | 16.1
| 2014-10-18 15:00 | 18.8 | 13.9 | 16.1
| 2014-10-18 15:30 | 19.3 | 14.4 | 16.1
| 2014-10-18 16:00 | 20.1 | 14.4 | 16.1
| 2014-10-18 16:30 | 20.8 | 14.4 | 16.1
| 2014-10-18 17:00 | 20.3 | 14.4 | 16.1
| 2014-10-18 17:30 | 19.7 | 14.4 | 16.1
| 2014-10-18 18:00 | 18.8 | 14.4 | 16.1
| 2014-10-18 18:30 | 17.3 | 15 | 16.1
| 2014-10-18 19:00 | 15.9 | 15 | 16.1
| 2014-10-18 19:30 | 15.1 | 15 | 16.1
| 2014-10-18 20:00 | 14.3 | 15 | 16.1
| 2014-10-18 20:30 | 14.1 | 15 | 16.1
| 2014-10-18 21:00 | 13.4 | 15 | 16.1
| 2014-10-18 21:30 | 12.7 | 15 | 16.1
| 2014-10-18 22:00 | 12.3 | 15 | 16.1
| 2014-10-18 22:30 | 11.9 | 15 | 16.1
| 2014-10-18 23:00 | 11.5 | 14.4 | 16.1
| 2014-10-18 23:30 | 11.1 | 14.4 | 16.1
| 2014-10-19 | 10.7 | 14.4 | 16.1
| 2014-10-19 00:30 | 10.9 | 14.4 | 16.1
| 2014-10-19 01:00 | 10.5 | 14.4 | 16.1
| 2014-10-19 01:30 | 10.2 | 14.4 | 16.1
| 2014-10-19 02:00 | 9.6 | 14.4 | 16.1
| 2014-10-19 02:30 | 9.7 | 14.4 | 16.1
| 2014-10-19 03:00 | 10.4 | 14.4 | 16.1
| 2014-10-19 03:30 | 10.8 | 14.4 | 16.1
| 2014-10-19 04:00 | 11.1 | 13.9 | 15.6
| 2014-10-19 04:30 | 11.3 | 13.9 | 15.6
| 2014-10-19 05:00 | 11.6 | 13.9 | 15.6
| 2014-10-19 05:30 | 11.7 | 13.9 | 15.6
| 2014-10-19 06:00 | 11.8 | 13.9 | 15.6
| 2014-10-19 06:30 | 11.6 | 13.9 | 15.6
| 2014-10-19 07:00 | 11.5 | 13.9 | 15.6
| 2014-10-19 07:30 | 11.3 | 13.9 | 15.6
| 2014-10-19 08:00 | 11.3 | 13.9 | 15.6
| 2014-10-19 08:30 | 11.1 | 13.9 | 15.6
| 2014-10-19 09:00 | 11.4 | 13.9 | 15.6
| 2014-10-19 09:30 | 12.2 | 13.9 | 15.6
| 2014-10-19 10:00 | 13.5 | 13.9 | 15.6
| 2014-10-19 10:30 | 15.7 | 13.9 | 15.6
| 2014-10-19 11:00 | 17.5 | 13.9 | 15.6
| 2014-10-19 11:30 | 18.6 | 13.9 | 15.6
| 2014-10-19 12:00 | 19.7 | 13.9 | 15.6
| 2014-10-19 12:30 | 20.3 | 13.9 | 15.6
| 2014-10-19 13:00 | 21.2 | 13.9 | 15.6
| 2014-10-19 13:30 | 22 | 14.4 | 15.6
| 2014-10-19 14:00 | 22.3 | 14.4 | 15.6
| 2014-10-19 14:30 | 22.9 | 14.4 | 15.6
| 2014-10-19 15:00 | 23.6 | 14.4 | 15.6
| 2014-10-19 15:30 | 22.6 | 14.4 | 15.6
| 2014-10-19 16:00 | 23.6 | 15 | 15.6
| 2014-10-19 16:30 | 23.6 | 15 | 15.6
| 2014-10-19 17:00 | 22.7 | 15 | 15.6
| 2014-10-19 17:30 | 21.6 | 15 | 15.6
| 2014-10-19 18:00 | 20 | 15 | 15.6
| 2014-10-19 18:30 | 18.8 | 15.6 | 15.6
| 2014-10-19 19:00 | 18.5 | 15.6 | 15.6
| 2014-10-19 19:30 | 18.2 | 15.6 | 15.6
| 2014-10-19 20:00 | 18 | 15.6 | 15.6
| 2014-10-19 20:30 | 18.4 | 15.6 | 15.6
| 2014-10-19 21:00 | 18.5 | 15.6 | 15.6
| 2014-10-19 21:30 | 18 | 15.6 | 15.6
| 2014-10-19 22:00 | 17.2 | 15.6 | 15.6
| 2014-10-19 22:30 | 16.6 | 15.6 | 15.6
| 2014-10-19 23:00 | 16.7 | 15.6 | 15.6
| 2014-10-19 23:30 | 18 | 15.6 | 15.6
| 2014-10-20 | 17.8 | 15.6 | 15.6
| 2014-10-20 00:30 | 17.6 | 15.6 | 15.6
| 2014-10-20 01:00 | 17.9 | 15.6 | 15.6
| 2014-10-20 01:30 | 18.3 | 15 | 15.6
| 2014-10-20 02:00 | 18.3 | 15 | 15.6
| 2014-10-20 02:30 | 17.8 | 15 | 15.6
| 2014-10-20 03:00 | 17.6 | 15 | 15.6
| 2014-10-20 03:30 | 17.7 | 15 | 15.6
| 2014-10-20 04:00 | 17.6 | 15 | 15.6
| 2014-10-20 04:30 | 17.4 | 15 | 15.6
| 2014-10-20 05:00 | 16.9 | 15 | 15.6
| 2014-10-20 05:30 | 16.3 | 15 | 15.6
| 2014-10-20 06:00 | 15.8 | 15 | 15.6
| 2014-10-20 06:30 | 15.6 | 15 | 15.6
| 2014-10-20 07:00 | 15.4 | 15 | 15.6
| 2014-10-20 07:30 | 15.5 | 15 | 15.6
| 2014-10-20 08:00 | 15.4 | 15 | 15.6
| 2014-10-20 08:30 | 15.7 | 15 | 15.6
| 2014-10-20 09:00 | 16.4 | 15 | 15.6
| 2014-10-20 09:30 | 16.7 | 15 | 15.6
| 2014-10-20 10:00 | 16.9 | 15 | 15.6
| 2014-10-20 10:30 | 17.5 | 15 | 15.6
| 2014-10-20 11:00 | 17.9 | 15 | 15.6
| 2014-10-20 11:30 | 18.2 | 15 | 15.6
| 2014-10-20 12:00 | 18.6 | 15 | 15.6
| 2014-10-20 12:30 | 19.2 | 15.6 | 15.6
| 2014-10-20 13:00 | 19.1 | 15.6 | 15.6
| 2014-10-20 13:30 | 19.3 | 15.6 | 15.6
| 2014-10-20 14:00 | 19.2 | 15.6 | 15.6
| 2014-10-20 14:30 | 18.9 | 15.6 | 15.6
| 2014-10-20 15:00 | 18.7 | 15.6 | 15.6
| 2014-10-20 15:30 | 18.6 | 15.6 | 15.6
| 2014-10-20 16:00 | 18.4 | 15.6 | 15.6
| 2014-10-20 16:30 | 18.2 | 16.1 | 15.6
| 2014-10-20 17:00 | 17.8 | 16.1 | 15.6
| 2014-10-20 17:30 | 17.5 | 16.1 | 15.6
| 2014-10-20 18:00 | 17 | 16.1 | 15.6
| 2014-10-20 18:30 | 15.9 | 16.1 | 15.6
| 2014-10-20 19:00 | 15.1 | 16.1 | 15.6
| 2014-10-20 19:30 | 14.4 | 16.1 | 15.6
| 2014-10-20 20:00 | 13.9 | 16.1 | 15.6
| 2014-10-20 20:30 | 13.3 | 16.1 | 15.6
| 2014-10-20 21:00 | 12.7 | 16.1 | 15.6
| 2014-10-20 21:30 | 12.1 | 16.1 | 15.6
| 2014-10-20 22:00 | 11.6 | 15.6 | 15.6
| 2014-10-20 22:30 | 11.1 | 15.6 | 15.6
| 2014-10-20 23:00 | 10.7 | 15.6 | 15.6
| 2014-10-20 23:30 | 10.4 | 15.6 | 15.6
| 2014-10-21 | 10 | 15.6 | 15.6
| 2014-10-21 00:30 | 9.8 | 15.6 | 15.6
| 2014-10-21 01:00 | 9.4 | 15.6 | 15.6
| 2014-10-21 01:30 | 9.4 | 15 | 15.6
| 2014-10-21 02:00 | 9.1 | 15 | 15.6
| 2014-10-21 02:30 | 9 | 15 | 15.6
| 2014-10-21 03:00 | 8.8 | 15 | 15.6
| 2014-10-21 03:30 | 9.1 | 15 | 15.6
| 2014-10-21 04:00 | 8.7 | 15 | 15.6
| 2014-10-21 04:30 | 8.5 | 14.4 | 15.6
| 2014-10-21 05:00 | 8.4 | 14.4 | 15.6
| 2014-10-21 05:30 | 8.8 | 14.4 | 15.6
| 2014-10-21 06:00 | 8.7 | 14.4 | 15.6
| 2014-10-21 06:30 | 9.2 | 14.4 | 15.6
| 2014-10-21 07:00 | 9 | 14.4 | 15.6
| 2014-10-21 07:30 | 9.3 | 13.9 | 15.6
| 2014-10-21 08:00 | 9.1 | 13.9 | 15.6
| 2014-10-21 08:30 | 9.2 | 13.9 | 15.6
| 2014-10-21 09:00 | 9.7 | 13.9 | 15.6
| 2014-10-21 09:30 | 10.9 | 13.9 | 15.6
| 2014-10-21 10:00 | 11.7 | 13.9 | 15.6
| 2014-10-21 10:30 | 12.5 | 13.9 | 15.6
| 2014-10-21 11:00 | 12.9 | 13.9 | 15.6
| 2014-10-21 11:30 | 13.2 | 13.9 | 15.6
| 2014-10-21 12:00 | 13.8 | 13.9 | 15.6
| 2014-10-21 12:30 | 13.9 | 13.9 | 15.6
| 2014-10-21 13:00 | 14.5 | 13.9 | 15.6
| 2014-10-21 13:30 | 14.5 | 13.9 | 15.6
| 2014-10-21 14:00 | 15 | 13.9 | 15.6
| 2014-10-21 14:30 | 14.3 | 13.9 | 15.6
| 2014-10-21 15:00 | 14.8 | 13.9 | 15.6
| 2014-10-21 15:30 | 14.9 | 13.9 | 15.6
| 2014-10-21 16:00 | 14.8 | 13.9 | 15.6
| 2014-10-21 16:30 | 14.4 | 13.9 | 15.6
| 2014-10-21 17:00 | 14 | 13.9 | 15.6
| 2014-10-21 17:30 | 13.9 | 13.9 | 15.6
| 2014-10-21 18:00 | 13.3 | 13.9 | 15.6
| 2014-10-21 18:30 | 12.3 | 13.9 | 15.6
| 2014-10-21 19:00 | 10.8 | 13.9 | 15.6
| 2014-10-21 19:30 | 10.8 | 13.9 | 15.6
| 2014-10-21 20:00 | 10.4 | 13.9 | 15.6
| 2014-10-21 20:30 | 10.1 | 13.9 | 15.6
| 2014-10-21 21:00 | 9.9 | 13.9 | 15.6
| 2014-10-21 21:30 | 8.9 | 13.9 | 15.6
| 2014-10-21 22:00 | 8.4 | 13.9 | 15.6
| 2014-10-21 22:30 | 8.3 | 13.9 | 15.6
| 2014-10-21 23:00 | 7.8 | 13.9 | 15.6
| 2014-10-21 23:30 | 7.8 | 13.9 | 15.6
| 2014-10-22 | 7.8 | 13.9 | 15.6
| 2014-10-22 00:30 | 8.1 | 13.9 | 15.6
| 2014-10-22 01:00 | 8.1 | 13.3 | 15.6
| 2014-10-22 01:30 | 8 | 13.3 | 15.6
| 2014-10-22 02:00 | 8.1 | 13.3 | 15.6
| 2014-10-22 02:30 | 7.8 | 13.3 | 15.6
| 2014-10-22 03:00 | 8.2 | 13.3 | 15.6
| 2014-10-22 03:30 | 8.2 | 13.3 | 15.6
| 2014-10-22 04:00 | 8.3 | 13.3 | 15.6
| 2014-10-22 04:30 | 8.4 | 12.8 | 15.6
| 2014-10-22 05:00 | 8.3 | 12.8 | 15.6
| 2014-10-22 05:30 | 7.3 | 12.8 | 15.6
| 2014-10-22 06:00 | 6.8 | 12.8 | 15.6
| 2014-10-22 06:30 | 6.7 | 12.8 | 15.6
| 2014-10-22 07:00 | 6.1 | 12.8 | 15.6
| 2014-10-22 07:30 | 6.4 | 12.8 | 15.6
| 2014-10-22 08:00 | 7.1 | 12.8 | 15.6
| 2014-10-22 08:30 | 7.5 | 12.8 | 15.6
| 2014-10-22 09:00 | 7.7 | 12.8 | 15.6
| 2014-10-22 09:30 | 7.9 | 12.2 | 15.6
| 2014-10-22 10:00 | 7.8 | 12.2 | 15.6
| 2014-10-22 10:30 | 7.6 | 12.2 | 15.6
| 2014-10-22 11:00 | 7.1 | 12.2 | 15.6
| 2014-10-22 11:30 | 7.1 | 12.2 | 15.6
| 2014-10-22 12:00 | 7.4 | 12.2 | 15.6
| 2014-10-22 12:30 | 7.8 | 12.2 | 15.6
| 2014-10-22 13:00 | 7.9 | 12.2 | 15.6
| 2014-10-22 13:30 | 8.3 | 12.2 | 15.6
| 2014-10-22 14:00 | 9.1 | 12.2 | 15.6
| 2014-10-22 14:30 | 9.3 | 12.2 | 15.6
| 2014-10-22 15:00 | 9.4 | 12.2 | 15.6
| 2014-10-22 15:30 | 9.3 | 12.2 | 15.6
| 2014-10-22 16:00 | 10.1 | 12.2 | 15.6
| 2014-10-22 16:30 | 10 | 12.2 | 15.6
| 2014-10-22 17:00 | 10.1 | 12.2 | 15.6
| 2014-10-22 17:30 | 9.9 | 12.2 | 15.6
| 2014-10-22 18:00 | 9.7 | 12.2 | 15.6
| 2014-10-22 18:30 | 9.6 | 12.2 | 15.6
| 2014-10-22 19:00 | 9.5 | 12.2 | 15.6
| 2014-10-22 19:30 | 9.4 | 12.2 | 15.6
| 2014-10-22 20:00 | 9.4 | 12.2 | 15.6
| 2014-10-22 20:30 | 9.3 | 12.2 | 15.6
| 2014-10-22 21:00 | 9.3 | 12.2 | 15.6
| 2014-10-22 21:30 | 9.4 | 12.2 | 15.6
| 2014-10-22 22:00 | 9.3 | 12.2 | 15.6
| 2014-10-22 22:30 | 9.5 | 11.7 | 15.6
| 2014-10-22 23:00 | 9.6 | 11.7 | 15.6
| 2014-10-22 23:30 | 9.4 | 11.7 | 15.6
| 2014-10-23 | 9.4 | 11.7 | 15.6
| 2014-10-23 00:30 | 9.3 | 11.7 | 15.6
| 2014-10-23 01:00 | 9.2 | 11.7 | 15.6
| 2014-10-23 01:30 | 9.1 | 11.7 | 15.6
| 2014-10-23 02:00 | 8.9 | 11.7 | 15.6
| 2014-10-23 02:30 | 8.8 | 11.7 | 15.6
| 2014-10-23 03:00 | 8.8 | 11.7 | 15.6
| 2014-10-23 03:30 | 8.8 | 11.7 | 15.6
| 2014-10-23 04:00 | 8.9 | 11.7 | 15.6
| 2014-10-23 04:30 | 8.9 | 11.7 | 15.6
| 2014-10-23 05:00 | 8.9 | 11.7 | 15.6
| 2014-10-23 05:30 | 8.9 | 11.7 | 15
| 2014-10-23 06:00 | 8.8 | 11.7 | 15
| 2014-10-23 06:30 | 8.7 | 11.7 | 15
| 2014-10-23 07:00 | 8.6 | 11.7 | 15
| 2014-10-23 07:30 | 8.4 | 11.7 | 15
| 2014-10-23 08:00 | 8.2 | 11.7 | 15
| 2014-10-23 08:30 | 7.9 | 11.7 | 15
| 2014-10-23 09:00 | 8.3 | 11.7 | 15
| 2014-10-23 09:30 | 9.2 | 11.7 | 15
| 2014-10-23 10:00 | 9.6 | 11.7 | 15
| 2014-10-23 10:30 | 9.8 | 11.7 | 15
| 2014-10-23 11:00 | 9.9 | 11.7 | 15
| 2014-10-23 11:30 | 10.1 | 11.7 | 15
| 2014-10-23 12:00 | 10.1 | 11.7 | 15
| 2014-10-23 12:30 | 10.1 | 11.7 | 15
| 2014-10-23 13:00 | 10.3 | 11.7 | 15
| 2014-10-23 13:30 | 10.8 | 11.7 | 15
| 2014-10-23 14:00 | 11.8 | 11.7 | 15
| 2014-10-23 14:30 | 11.8 | 11.7 | 15
| 2014-10-23 15:00 | 12.7 | 11.7 | 15
| 2014-10-23 15:30 | 13.2 | 11.7 | 15
| 2014-10-23 16:00 | 13.7 | 11.7 | 15
| 2014-10-23 16:30 | 13.3 | 11.7 | 15
| 2014-10-23 17:00 | 13 | 12.2 | 15
| 2014-10-23 17:30 | 11.8 | 12.2 | 15
| 2014-10-23 18:00 | 11.1 | 12.2 | 15
| 2014-10-23 18:30 | 9.9 | 12.2 | 15
| 2014-10-23 19:00 | 9.2 | 12.2 | 15
| 2014-10-23 19:30 | 8.5 | 12.2 | 15
| 2014-10-23 20:00 | 8 | 12.2 | 15
| 2014-10-23 20:30 | 7.4 | 12.2 | 15
| 2014-10-23 21:00 | 7.2 | 12.2 | 15
| 2014-10-23 21:30 | 6.9 | 12.2 | 15
| 2014-10-23 22:00 | 6.5 | 12.2 | 15
| 2014-10-23 22:30 | 6.2 | 12.2 | 15
| 2014-10-23 23:00 | 6.1 | 11.7 | 15
| 2014-10-23 23:30 | 5.6 | 11.7 | 15
| 2014-10-24 | 5.4 | 11.7 | 15
| 2014-10-24 00:30 | 5.3 | 11.7 | 15
| 2014-10-24 01:00 | 5.2 | 11.7 | 15
| 2014-10-24 01:30 | 4.7 | 11.7 | 15
| 2014-10-24 02:00 | 4.7 | 11.7 | 15
| 2014-10-24 02:30 | 4.7 | 11.7 | 15
| 2014-10-24 03:00 | 4.6 | 11.1 | 15
| 2014-10-24 03:30 | 4.4 | 11.1 | 15
| 2014-10-24 04:00 | 4.2 | 11.1 | 15
| 2014-10-24 04:30 | 4.2 | 11.1 | 15
| 2014-10-24 05:00 | 4.2 | 11.1 | 15
| 2014-10-24 05:30 | 4 | 11.1 | 15
| 2014-10-24 06:00 | 3.8 | 11.1 | 15
| 2014-10-24 06:30 | 3.5 | 11.1 | 15
| 2014-10-24 07:00 | 3.2 | 10.6 | 15
| 2014-10-24 07:30 | 3.8 | 10.6 | 15
| 2014-10-24 08:00 | 4.5 | 10.6 | 15
| 2014-10-24 08:30 | 4.7 | 10.6 | 15
| 2014-10-24 09:00 | 4.6 | 10.6 | 15
| 2014-10-24 09:30 | 5 | 10.6 | 15
| 2014-10-24 10:00 | 5.7 | 10.6 | 15
| 2014-10-24 10:30 | 6 | 10.6 | 15
| 2014-10-24 11:00 | 6.4 | 10.6 | 15
| 2014-10-24 11:30 | 7.2 | 10.6 | 15
| 2014-10-24 12:00 | 7.8 | 10.6 | 15
| 2014-10-24 12:30 | 8.5 | 10.6 | 15
| 2014-10-24 13:00 | 8.7 | 10.6 | 15
| 2014-10-24 13:30 | 8.5 | 10.6 | 15
| 2014-10-24 14:00 | 9.4 | 10.6 | 15
| 2014-10-24 14:30 | 11 | 10.6 | 15
| 2014-10-24 15:00 | 11.9 | 11.1 | 15
| 2014-10-24 15:30 | 12.5 | 11.1 | 14.4
| 2014-10-24 16:00 | 12.6 | 11.1 | 14.4
| 2014-10-24 16:30 | 12.6 | 11.1 | 14.4
| 2014-10-24 17:00 | 12.5 | 11.1 | 14.4
| 2014-10-24 17:30 | 12.3 | 11.1 | 14.4
| 2014-10-24 18:00 | 11.6 | 11.1 | 14.4
| 2014-10-24 18:30 | 10.4 | 11.1 | 14.4
| 2014-10-24 19:00 | 9.7 | 11.1 | 14.4
| 2014-10-24 19:30 | 9.1 | 11.1 | 14.4
| 2014-10-24 20:00 | 8.5 | 11.1 | 14.4
| 2014-10-24 20:30 | 8.3 | 11.1 | 14.4
| 2014-10-24 21:00 | 8.1 | 11.1 | 14.4
| 2014-10-24 21:30 | 8.1 | 11.1 | 14.4
| 2014-10-24 22:00 | 8.2 | 11.1 | 14.4
| 2014-10-24 22:30 | 8.3 | 11.1 | 14.4
| 2014-10-24 23:00 | 8.1 | 11.1 | 14.4
| 2014-10-24 23:30 | 8.3 | 11.1 | 14.4
| 2014-10-25 | 8.6 | 11.1 | 14.4
| 2014-10-25 00:30 | 8.6 | 11.1 | 14.4
| 2014-10-25 01:00 | 8.4 | 11.1 | 14.4
| 2014-10-25 01:30 | 8.3 | 11.1 | 14.4
| 2014-10-25 02:00 | 8.3 | 11.1 | 14.4
| 2014-10-25 02:30 | 8.2 | 11.1 | 14.4
| 2014-10-25 03:00 | 8.3 | 11.1 | 14.4
| 2014-10-25 03:30 | 8.3 | 11.1 | 14.4
| 2014-10-25 04:00 | 8.4 | 11.1 | 14.4
| 2014-10-25 04:30 | 8.4 | 11.1 | 14.4
| 2014-10-25 05:00 | 8.4 | 11.1 | 14.4
| 2014-10-25 05:30 | 8.4 | 11.1 | 14.4
| 2014-10-25 06:00 | 8.4 | 11.1 | 14.4
| 2014-10-25 06:30 | 8.4 | 11.1 | 14.4
| 2014-10-25 07:00 | 8.4 | 11.1 | 14.4
| 2014-10-25 07:30 | 8.4 | 11.1 | 14.4
| 2014-10-25 08:00 | 8.3 | 11.1 | 14.4
| 2014-10-25 08:30 | 8.3 | 11.1 | 14.4
| 2014-10-25 09:00 | 8.6 | 11.1 | 14.4
| 2014-10-25 09:30 | 8.9 | 11.1 | 14.4
| 2014-10-25 10:00 | 9.1 | 11.1 | 14.4
| 2014-10-25 10:30 | 9.8 | 11.1 | 14.4
| 2014-10-25 11:00 | 10.3 | 11.1 | 14.4
| 2014-10-25 11:30 | 11 | 11.1 | 14.4
| 2014-10-25 12:00 | 11.3 | 11.1 | 14.4
| 2014-10-25 12:30 | 12.2 | 11.1 | 14.4
| 2014-10-25 13:00 | 12.9 | 11.1 | 14.4
| 2014-10-25 13:30 | 13.2 | 11.1 | 14.4
| 2014-10-25 14:00 | 13.2 | 11.1 | 14.4
| 2014-10-25 14:30 | 13.5 | 11.7 | 14.4
| 2014-10-25 15:00 | 13.6 | 11.7 | 14.4
| 2014-10-25 15:30 | 13.6 | 11.7 | 14.4
| 2014-10-25 16:00 | 13.4 | 11.7 | 14.4
| 2014-10-25 16:30 | 13.4 | 11.7 | 14.4
| 2014-10-25 17:00 | 13.4 | 11.7 | 14.4
| 2014-10-25 17:30 | 13.4 | 12.2 | 14.4
| 2014-10-25 18:00 | 13.2 | 12.2 | 14.4
| 2014-10-25 18:30 | 12.9 | 12.2 | 14.4
| 2014-10-25 19:00 | 12.6 | 12.2 | 14.4
| 2014-10-25 19:30 | 12.4 | 12.2 | 14.4
| 2014-10-25 20:00 | 12.2 | 12.2 | 14.4
| 2014-10-25 20:30 | 11.8 | 12.2 | 14.4
| 2014-10-25 21:00 | 11.7 | 12.2 | 14.4
| 2014-10-25 21:30 | 11.6 | 12.2 | 14.4
| 2014-10-25 22:00 | 11.6 | 12.2 | 14.4
| 2014-10-25 22:30 | 11.6 | 12.2 | 14.4
| 2014-10-25 23:00 | 11.7 | 12.2 | 14.4
| 2014-10-25 23:30 | 11.6 | 12.2 | 14.4
| 2014-10-26 | 11.7 | 12.2 | 14.4
| 2014-10-26 00:30 | 11.6 | 12.2 | 14.4
| 2014-10-26 01:00 | 11.7 | 12.2 | 14.4
| 2014-10-26 01:30 | 11.7 | 12.2 | 13.9
| 2014-10-26 02:00 | 11.6 | 12.2 | 13.9
| 2014-10-26 02:30 | 11.6 | 12.2 | 13.9
| 2014-10-26 03:00 | 11.6 | 12.2 | 13.9
| 2014-10-26 03:30 | 11.6 | 12.2 | 13.9
| 2014-10-26 04:00 | 11.6 | 12.2 | 13.9
| 2014-10-26 04:30 | 11.6 | 12.2 | 13.9
| 2014-10-26 05:00 | 11.6 | 12.2 | 13.9
| 2014-10-26 05:30 | 11.6 | 12.2 | 13.9
| 2014-10-26 06:00 | 11.6 | 12.2 | 13.9
| 2014-10-26 06:30 | 11.5 | 12.2 | 13.9
| 2014-10-26 07:00 | 11.4 | 12.2 | 13.9
| 2014-10-26 07:30 | 11.2 | 12.2 | 13.9
| 2014-10-26 08:00 | 11.5 | 12.2 | 13.9
| 2014-10-26 08:30 | 11.8 | 12.2 | 13.9
| 2014-10-26 09:00 | 12.2 | 12.2 | 13.9
| 2014-10-26 09:30 | 13 | 12.2 | 13.9
| 2014-10-26 10:00 | 13.8 | 12.2 | 13.9
| 2014-10-26 10:30 | 14 | 12.2 | 13.9
| 2014-10-26 11:00 | 14.4 | 12.2 | 13.9
| 2014-10-26 11:30 | 15.6 | 12.2 | 13.9
| 2014-10-26 12:00 | 15.4 | 12.2 | 13.9
| 2014-10-26 12:30 | 15.6 | 12.2 | 13.9
| 2014-10-26 13:00 | 15.9 | 12.8 | 13.9
| 2014-10-26 13:30 | 15.9 | 12.8 | 13.9
| 2014-10-26 14:00 | 16.1 | 12.8 | 13.9
| 2014-10-26 14:30 | 15.9 | 12.8 | 13.9
| 2014-10-26 15:00 | 15.9 | 12.8 | 13.9
| 2014-10-26 15:30 | 16.2 | 12.8 | 13.9
| 2014-10-26 16:00 | 16.2 | 13.3 | 13.9
| 2014-10-26 16:30 | 15.7 | 13.3 | 13.9
| 2014-10-26 17:00 | 15 | 13.3 | 13.9
| 2014-10-26 17:30 | 13.2 | 13.3 | 13.9
| 2014-10-26 18:00 | 12.1 | 13.3 | 13.9
| 2014-10-26 18:30 | 11.3 | 13.3 | 13.9
| 2014-10-26 19:00 | 10.7 | 13.3 | 13.9
| 2014-10-26 19:30 | 10.4 | 13.3 | 13.9
| 2014-10-26 20:00 | 9.9 | 13.3 | 13.9
| 2014-10-26 20:30 | 9.8 | 13.3 | 13.9
| 2014-10-26 21:00 | 9.7 | 13.3 | 13.9
| 2014-10-26 21:30 | 9.6 | 12.8 | 13.9
| 2014-10-26 22:00 | 9.4 | 12.8 | 13.9
| 2014-10-26 22:30 | 9.6 | 12.8 | 13.9
| 2014-10-26 23:00 | 9.5 | 12.8 | 13.9
| 2014-10-26 23:30 | 9.1 | 12.8 | 13.9
| 2014-10-27 | 8.9 | 12.8 | 13.9
| 2014-10-27 00:30 | 8.6 | 12.8 | 13.9
| 2014-10-27 01:00 | 7.9 | 12.8 | 13.9
| 2014-10-27 01:30 | 7.5 | 12.2 | 13.9
| 2014-10-27 02:00 | 7.2 | 12.2 | 13.9
| 2014-10-27 02:30 | 7 | 12.2 | 13.9
| 2014-10-27 03:00 | 6.7 | 12.2 | 13.9
| 2014-10-27 03:30 | 6.4 | 12.2 | 13.9
| 2014-10-27 04:00 | 6.3 | 12.2 | 13.9
| 2014-10-27 04:30 | 6.3 | 12.2 | 13.9
| 2014-10-27 05:00 | 5.7 | 11.7 | 13.9
| 2014-10-27 05:30 | 5 | 11.7 | 13.9
| 2014-10-27 06:00 | 4.7 | 11.7 | 13.9
| 2014-10-27 06:30 | 4.9 | 11.7 | 13.9
| 2014-10-27 07:00 | 4.7 | 11.7 | 13.9
| 2014-10-27 07:30 | 4.5 | 11.7 | 13.9
| 2014-10-27 08:00 | 4.3 | 11.7 | 13.9
| 2014-10-27 08:30 | 5.2 | 11.7 | 13.9
| 2014-10-27 09:00 | 7.2 | 11.7 | 13.9
| 2014-10-27 09:30 | 8.2 | 11.1 | 13.9
| 2014-10-27 10:00 | 9.3 | 11.1 | 13.9
| 2014-10-27 10:30 | 10.6 | 11.1 | 13.9
| 2014-10-27 11:00 | 11.4 | 11.1 | 13.9
| 2014-10-27 11:30 | 12.2 | 11.1 | 13.9
| 2014-10-27 12:00 | 13.3 | 11.1 | 13.9
| 2014-10-27 12:30 | 13.9 | 11.1 | 13.9
| 2014-10-27 13:00 | 13.9 | 11.1 | 13.9
| 2014-10-27 13:30 | 13.8 | 11.1 | 13.9
| 2014-10-27 14:00 | 14 | 11.7 | 13.9
| 2014-10-27 14:30 | 14.4 | 11.7 | 13.9
| 2014-10-27 15:00 | 14.3 | 11.7 | 13.9
| 2014-10-27 15:30 | 14 | 11.7 | 13.9
| 2014-10-27 16:00 | 13.2 | 11.7 | 13.9
| 2014-10-27 16:30 | 11.6 | 11.7 | 13.9
| 2014-10-27 17:00 | 10.2 | 11.7 | 13.9
| 2014-10-27 17:30 | 9.1 | 11.7 | 13.9
| 2014-10-27 18:00 | 8.3 | 11.7 | 13.9
| 2014-10-27 18:30 | 7.8 | 11.7 | 13.9
| 2014-10-27 19:00 | 7.4 | 11.7 | 13.9
| 2014-10-27 19:30 | 7.3 | 11.7 | 13.9
| 2014-10-27 20:00 | 7.1 | 11.7 | 13.9
| 2014-10-27 20:30 | 6.9 | 11.7 | 13.9
| 2014-10-27 21:00 | 6.6 | 11.7 | 13.9
| 2014-10-27 21:30 | 6.4 | 11.7 | 13.9
| 2014-10-27 22:00 | 5.9 | 11.7 | 13.9
| 2014-10-27 22:30 | 5.3 | 11.7 | 13.9
| 2014-10-27 23:00 | 5.4 | 11.1 | 13.9
| 2014-10-27 23:30 | 5.1 | 11.1 | 13.9
| 2014-10-28 | 4.8 | 11.1 | 13.9
| 2014-10-28 00:30 | 4.4 | 11.1 | 13.9
| 2014-10-28 01:00 | 4.3 | 11.1 | 13.9
| 2014-10-28 01:30 | 4.2 | 11.1 | 13.9
| 2014-10-28 02:00 | 3.8 | 11.1 | 13.9
| 2014-10-28 02:30 | 4.1 | 10.6 | 13.9
| 2014-10-28 03:00 | 4.8 | 10.6 | 13.9
| 2014-10-28 03:30 | 5.4 | 10.6 | 13.9
| 2014-10-28 04:00 | 5.7 | 10.6 | 13.9
| 2014-10-28 04:30 | 5.8 | 10.6 | 13.9
| 2014-10-28 05:00 | 5.9 | 10.6 | 13.9
| 2014-10-28 05:30 | 5.9 | 10.6 | 13.9
| 2014-10-28 06:00 | 5.8 | 10.6 | 13.9
| 2014-10-28 06:30 | 5.8 | 10.6 | 13.9
| 2014-10-28 07:00 | 6 | 10.6 | 13.9
| 2014-10-28 07:30 | 6.1 | 10.6 | 13.9
| 2014-10-28 08:00 | 6.2 | 10.6 | 13.9
| 2014-10-28 08:30 | 6.4 | 10.6 | 13.9
| 2014-10-28 09:00 | 6.7 | 10.6 | 13.9
| 2014-10-28 09:30 | 6.8 | 10.6 | 13.9
| 2014-10-28 10:00 | 7.1 | 10.6 | 13.9
| 2014-10-28 10:30 | 7.1 | 10.6 | 13.9
| 2014-10-28 11:00 | 7.2 | 10.6 | 13.9
| 2014-10-28 11:30 | 7.4 | 10.6 | 13.9
| 2014-10-28 12:00 | 7.5 | 10.6 | 13.9
| 2014-10-28 12:30 | 7.6 | 10.6 | 13.9
| 2014-10-28 13:00 | 7.9 | 10.6 | 13.9
| 2014-10-28 13:30 | 8.2 | 10.6 | 13.9
| 2014-10-28 14:00 | 8.3 | 10.6 | 13.9
| 2014-10-28 14:30 | 8.3 | 10.6 | 13.9
| 2014-10-28 15:00 | 8.3 | 10.6 | 13.9
| 2014-10-28 15:30 | 8.2 | 10.6 | 13.9
| 2014-10-28 16:00 | 8.1 | 10.6 | 13.9
| 2014-10-28 16:30 | 8 | 10.6 | 13.9
| 2014-10-28 17:00 | 7.9 | 10.6 | 13.9
| 2014-10-28 17:30 | 7.6 | 10.6 | 13.9
| 2014-10-28 18:00 | 7.6 | 10.6 | 13.9
| 2014-10-28 18:30 | 7.5 | 10.6 | 13.9
| 2014-10-28 19:00 | 7.4 | 10.6 | 13.9
| 2014-10-28 19:30 | 7.4 | 10.6 | 13.9
| 2014-10-28 20:00 | 7.3 | 10.6 | 13.9
| 2014-10-28 20:30 | 7.2 | 10.6 | 13.9
| 2014-10-28 21:00 | 7.2 | 10.6 | 13.9
| 2014-10-28 21:30 | 7.1 | 10.6 | 13.9
| 2014-10-28 22:00 | 6.9 | 10.6 | 13.9
| 2014-10-28 22:30 | 7 | 10.6 | 13.9
| 2014-10-28 23:00 | 6.9 | 10.6 | 13.9
| 2014-10-28 23:30 | 6.9 | 10.6 | 13.9
| 2014-10-29 | 6.9 | 10.6 | 13.9
| 2014-10-29 00:30 | 6.9 | 10.6 | 13.9
| 2014-10-29 01:00 | 7 | 10.6 | 13.9
| 2014-10-29 01:30 | 6.9 | 10.6 | 13.9
| 2014-10-29 02:00 | 6.9 | 10.6 | 13.9
| 2014-10-29 02:30 | 6.9 | 10.6 | 13.9
| 2014-10-29 03:00 | 7 | 10.6 | 13.9
| 2014-10-29 03:30 | 7 | 10.6 | 13.9
| 2014-10-29 04:00 | 7.1 | 10.6 | 13.9
| 2014-10-29 04:30 | 7 | 10.6 | 13.9
| 2014-10-29 05:00 | 7 | 10.6 | 13.9
| 2014-10-29 05:30 | 6.9 | 10.6 | 13.9
| 2014-10-29 06:00 | 6.9 | 10.6 | 13.9
| 2014-10-29 06:30 | 6.9 | 10.6 | 13.9
| 2014-10-29 07:00 | 7 | 10.6 | 13.9
| 2014-10-29 07:30 | 7 | 10.6 | 13.9
| 2014-10-29 08:00 | 7.3 | 10.6 | 13.9
| 2014-10-29 08:30 | 7.7 | 10.6 | 13.9
| 2014-10-29 09:00 | 8.1 | 10.6 | 13.9
| 2014-10-29 09:30 | 8.5 | 10.6 | 13.9
| 2014-10-29 10:00 | 8.8 | 10.6 | 13.9
| 2014-10-29 10:30 | 9.2 | 10.6 | 13.9
| 2014-10-29 11:00 | 9.6 | 10.6 | 13.9
| 2014-10-29 11:30 | 10.1 | 10.6 | 13.9
| 2014-10-29 12:00 | 10.2 | 10.6 | 13.9
| 2014-10-29 12:30 | 10.6 | 10.6 | 13.9
| 2014-10-29 13:00 | 10.7 | 10.6 | 13.9
| 2014-10-29 13:30 | 10.7 | 10.6 | 13.9
| 2014-10-29 14:00 | 11.6 | 10.6 | 13.9
| 2014-10-29 14:30 | 11.9 | 11.1 | 13.9
| 2014-10-29 15:00 | 11.7 | 11.1 | 13.9
| 2014-10-29 15:30 | 11.8 | 11.1 | 13.9
| 2014-10-29 16:00 | 11.4 | 11.1 | 13.9
| 2014-10-29 16:30 | 10.7 | 11.1 | 13.9
| 2014-10-29 17:00 | 10.3 | 11.1 | 13.3
| 2014-10-29 17:30 | 9.8 | 11.1 | 13.3
| 2014-10-29 18:00 | 9.4 | 11.1 | 13.3
| 2014-10-29 18:30 | 9.3 | 11.1 | 13.3
| 2014-10-29 19:00 | 9.4 | 11.1 | 13.3
| 2014-10-29 19:30 | 9.4 | 11.1 | 13.3
| 2014-10-29 20:00 | 9.5 | 11.1 | 13.3
| 2014-10-29 20:30 | 9.4 | 11.1 | 13.3
| 2014-10-29 21:00 | 9.2 | 11.1 | 13.3
| 2014-10-29 21:30 | 9.2 | 11.1 | 13.3
| 2014-10-29 22:00 | 9.3 | 11.1 | 13.3
| 2014-10-29 22:30 | 9.3 | 11.1 | 13.3
| 2014-10-29 23:00 | 9.3 | 11.1 | 13.3
| 2014-10-29 23:30 | 9.2 | 11.1 | 13.3
| 2014-10-30 | 9.2 | 11.1 | 13.3
| 2014-10-30 00:30 | 9.2 | 11.1 | 13.3
| 2014-10-30 01:00 | 9.1 | 11.1 | 13.3
| 2014-10-30 01:30 | 9.2 | 11.1 | 13.3
| 2014-10-30 02:00 | 9.2 | 11.1 | 13.3
| 2014-10-30 02:30 | 9.2 | 11.1 | 13.3
| 2014-10-30 03:00 | 9.3 | 11.1 | 13.3
| 2014-10-30 03:30 | 9.5 | 11.1 | 13.3
| 2014-10-30 04:00 | 9.6 | 11.1 | 13.3
| 2014-10-30 04:30 | 9.6 | 11.1 | 13.3
| 2014-10-30 05:00 | 9.6 | 11.1 | 13.3
| 2014-10-30 05:30 | 9.6 | 11.1 | 13.3
| 2014-10-30 06:00 | 9.7 | 11.1 | 13.3
| 2014-10-30 06:30 | 9.8 | 11.1 | 13.3
| 2014-10-30 07:00 | 9.9 | 11.1 | 13.3
| 2014-10-30 07:30 | 9.9 | 11.1 | 13.3
| 2014-10-30 08:00 | 10.1 | 11.1 | 13.3
| 2014-10-30 08:30 | 10.3 | 11.1 | 13.3
| 2014-10-30 09:00 | 10.9 | 11.1 | 13.3
| 2014-10-30 09:30 | 11 | 11.1 | 13.3
| 2014-10-30 10:00 | 11.3 | 11.1 | 13.3
| 2014-10-30 10:30 | 11.5 | 11.1 | 13.3
| 2014-10-30 11:00 | 11.8 | 11.1 | 13.3
| 2014-10-30 11:30 | 11.9 | 11.1 | 13.3
| 2014-10-30 12:00 | 12.3 | 11.1 | 13.3
| 2014-10-30 12:30 | 12.8 | 11.1 | 13.3
| 2014-10-30 13:00 | 13 | 11.1 | 13.3
| 2014-10-30 13:30 | 13.3 | 11.1 | 13.3
| 2014-10-30 14:00 | 13.9 | 11.7 | 13.3
| 2014-10-30 14:30 | 13.9 | 11.7 | 13.3
| 2014-10-30 15:00 | 14 | 11.7 | 13.3
| 2014-10-30 15:30 | 14.1 | 11.7 | 13.3
| 2014-10-30 16:00 | 13.9 | 11.7 | 13.3
| 2014-10-30 16:30 | 13.8 | 11.7 | 13.3
| 2014-10-30 17:00 | 13.6 | 11.7 | 13.3
| 2014-10-30 17:30 | 13.2 | 11.7 | 13.3
| 2014-10-30 18:00 | 12.9 | 12.2 | 13.3
| 2014-10-30 18:30 | 12.8 | 12.2 | 13.3
| 2014-10-30 19:00 | 12.3 | 12.2 | 13.3
| 2014-10-30 19:30 | 11.8 | 12.2 | 13.3
| 2014-10-30 20:00 | 11.1 | 12.2 | 13.3
| 2014-10-30 20:30 | 10.6 | 12.2 | 13.3
| 2014-10-30 21:00 | 10.3 | 12.2 | 13.3
| 2014-10-30 21:30 | 10.1 | 12.2 | 13.3
| 2014-10-30 22:00 | 10 | 12.2 | 13.3
| 2014-10-30 22:30 | 9.8 | 11.7 | 13.3
| 2014-10-30 23:00 | 9.8 | 11.7 | 13.3
| 2014-10-30 23:30 | 10.1 | 11.7 | 13.3
| 2014-10-31 | 10.1 | 11.7 | 13.3
| 2014-10-31 00:30 | 10.1 | 11.7 | 13.3
| 2014-10-31 01:00 | 9.8 | 11.7 | 13.3
| 2014-10-31 01:30 | 9.7 | 11.7 | 13.3
| 2014-10-31 02:00 | 9.6 | 11.7 | 13.3
| 2014-10-31 02:30 | 9.6 | 11.7 | 13.3
| 2014-10-31 03:00 | 9.6 | 11.7 | 13.3
| 2014-10-31 03:30 | 9.3 | 11.7 | 13.3
| 2014-10-31 04:00 | 9.1 | 11.7 | 13.3
| 2014-10-31 04:30 | 8.4 | 11.7 | 13.3
| 2014-10-31 05:00 | 8 | 11.7 | 13.3
| 2014-10-31 05:30 | 8 | 11.7 | 13.3
| 2014-10-31 06:00 | 8.4 | 11.7 | 13.3
| 2014-10-31 06:30 | 8.7 | 11.7 | 13.3
| 2014-10-31 07:00 | 9.1 | 11.1 | 13.3
| 2014-10-31 07:30 | 9.3 | 11.1 | 13.3
| 2014-10-31 08:00 | 9.7 | 11.1 | 13.3
| 2014-10-31 08:30 | 9.8 | 11.1 | 13.3
| 2014-10-31 09:00 | 10.7 | 11.1 | 13.3
| 2014-10-31 09:30 | 10.8 | 11.1 | 13.3
| 2014-10-31 10:00 | 10.9 | 11.1 | 13.3
| 2014-10-31 10:30 | 11.1 | 11.1 | 13.3
| 2014-10-31 11:00 | 11.4 | 11.1 | 13.3
| 2014-10-31 11:30 | 11.7 | 11.1 | 13.3
| 2014-10-31 12:00 | 11.9 | 11.7 | 13.3
| 2014-10-31 12:30 | 12.7 | 11.7 | 13.3
| 2014-10-31 13:00 | 13.4 | 11.7 | 13.3
| 2014-10-31 13:30 | 14 | 11.7 | 13.3
| 2014-10-31 14:00 | 14.3 | 11.7 | 13.3
| 2014-10-31 14:30 | 15.7 | 11.7 | 13.3
| 2014-10-31 15:00 | 15.3 | 11.7 | 13.3
| 2014-10-31 15:30 | 14.7 | 12.2 | 13.3
| 2014-10-31 16:00 | 14.5 | 12.2 | 13.3
| 2014-10-31 16:30 | 14.2 | 12.2 | 13.3
| 2014-10-31 17:00 | 13.7 | 12.2 | 13.3
| 2014-10-31 17:30 | 12.9 | 12.2 | 13.3
| 2014-10-31 18:00 | 12.1 | 12.2 | 13.3
| 2014-10-31 18:30 | 11.6 | 12.2 | 13.3
| 2014-10-31 19:00 | 10.9 | 12.2 | 13.3
| 2014-10-31 19:30 | 10.4 | 12.2 | 13.3
| 2014-10-31 20:00 | 10.2 | 12.2 | 13.3
| 2014-10-31 20:30 | 10.4 | 12.2 | 13.3
| 2014-10-31 21:00 | 10.2 | 12.2 | 13.3
| 2014-10-31 21:30 | 9.7 | 12.2 | 13.3
| 2014-10-31 22:00 | 9.3 | 12.2 | 13.3
| 2014-10-31 22:30 | 8.8 | 12.2 | 13.3
| 2014-10-31 23:00 | 8.4 | 12.2 | 13.3
| 2014-10-31 23:30 | 8.2 | 12.2 | 13.3
| 2014-11-01 | 8.4 | 11.7 | 13.3
| 2014-11-01 00:30 | 8.1 | 11.7 | 13.3
| 2014-11-01 01:00 | 7.8 | 11.7 | 13.3
| 2014-11-01 01:30 | 7.5 | 11.7 | 13.3
| 2014-11-01 02:00 | 7.6 | 11.7 | 13.3
| 2014-11-01 02:30 | 8.1 | 11.7 | 13.3
| 2014-11-01 03:00 | 8.3 | 11.7 | 13.3
| 2014-11-01 03:30 | 8.5 | 11.7 | 13.3
| 2014-11-01 04:00 | 8.6 | 11.7 | 13.3
| 2014-11-01 04:30 | 8.5 | 11.7 | 13.3
| 2014-11-01 05:00 | 8.3 | 11.7 | 13.3
| 2014-11-01 05:30 | 8.3 | 11.7 | 13.3
| 2014-11-01 06:00 | 8.2 | 11.7 | 13.3
| 2014-11-01 06:30 | 8.3 | 11.7 | 13.3
| 2014-11-01 07:00 | 8.3 | 11.1 | 13.3
| 2014-11-01 07:30 | 8.3 | 11.1 | 13.3
| 2014-11-01 08:00 | 8.4 | 11.1 | 13.3
| 2014-11-01 08:30 | 8.6 | 11.1 | 13.3
| 2014-11-01 09:00 | 8.8 | 11.1 | 13.3
| 2014-11-01 09:30 | 9.1 | 11.1 | 13.3
| 2014-11-01 10:00 | 9.3 | 11.1 | 13.3
| 2014-11-01 10:30 | 9.4 | 11.1 | 13.3
| 2014-11-01 11:00 | 9.7 | 11.1 | 13.3
| 2014-11-01 11:30 | 9.9 | 11.1 | 13.3
| 2014-11-01 12:00 | 10.2 | 11.1 | 13.3
| 2014-11-01 12:30 | 10.4 | 11.7 | 13.3
| 2014-11-01 13:00 | 10.6 | 11.7 | 13.3
| 2014-11-01 13:30 | 10.8 | 11.7 | 13.3
| 2014-11-01 14:00 | 11 | 11.7 | 13.3
| 2014-11-01 14:30 | 11.1 | 11.7 | 13.3
| 2014-11-01 15:00 | 11.3 | 11.7 | 13.3
| 2014-11-01 15:30 | 11.3 | 11.7 | 13.3
| 2014-11-01 16:00 | 11.2 | 11.7 | 13.3
| 2014-11-01 16:30 | 11 | 11.7 | 13.3
| 2014-11-01 17:00 | 10.9 | 11.7 | 13.3
| 2014-11-01 17:30 | 10.9 | 11.7 | 13.3
| 2014-11-01 18:00 | 10.9 | 11.7 | 13.3
| 2014-11-01 18:30 | 10.8 | 11.7 | 13.3
| 2014-11-01 19:00 | 10.7 | 12.2 | 13.3
| 2014-11-01 19:30 | 10.6 | 12.2 | 13.3
| 2014-11-01 20:00 | 10.4 | 12.2 | 13.3
| 2014-11-01 20:30 | 10.3 | 12.2 | 13.3
| 2014-11-01 21:00 | 10.2 | 12.2 | 13.3
| 2014-11-01 21:30 | 10.2 | 12.2 | 13.3
| 2014-11-01 22:00 | 10.3 | 12.2 | 13.3
| 2014-11-01 22:30 | 10.2 | 11.7 | 13.3
| 2014-11-01 23:00 | 9.9 | 11.7 | 13.3
| 2014-11-01 23:30 | 9.9 | 11.7 | 13.3
| 2014-11-02 | 9.8 | 11.7 | 13.3
| 2014-11-02 00:30 | 9.8 | 11.7 | 13.3
| 2014-11-02 01:00 | 9.8 | 11.7 | 13.3
| 2014-11-02 01:30 | 9.7 | 11.7 | 13.3
| 2014-11-02 02:00 | 9.4 | 11.7 | 13.3
| 2014-11-02 02:30 | 9.3 | 11.7 | 13.3
| 2014-11-02 03:00 | 9.3 | 11.7 | 13.3
| 2014-11-02 03:30 | 9.2 | 11.7 | 13.3
| 2014-11-02 04:00 | 9.1 | 11.7 | 13.3
| 2014-11-02 04:30 | 8.8 | 11.7 | 13.3
| 2014-11-02 05:00 | 8.7 | 11.7 | 13.3
| 2014-11-02 05:30 | 8.4 | 11.7 | 13.3
| 2014-11-02 06:00 | 8.2 | 11.7 | 13.3
| 2014-11-02 06:30 | 8 | 11.7 | 13.3
| 2014-11-02 07:00 | 8.2 | 11.7 | 13.3
| 2014-11-02 07:30 | 8.3 | 11.7 | 13.3
| 2014-11-02 08:00 | 8.3 | 11.7 | 13.3
| 2014-11-02 08:30 | 8.7 | 11.7 | 13.3
| 2014-11-02 09:00 | 8.8 | 11.7 | 13.3
| 2014-11-02 09:30 | 9.1 | 11.7 | 13.3
| 2014-11-02 10:00 | 9.3 | 11.7 | 13.3
| 2014-11-02 10:30 | 9.6 | 11.7 | 13.3
| 2014-11-02 11:00 | 9.8 | 11.7 | 13.3
| 2014-11-02 11:30 | 9.9 | 11.7 | 13.3
| 2014-11-02 12:00 | 10.9 | 11.7 | 13.3
| 2014-11-02 12:30 | 11.6 | 11.7 | 13.3
| 2014-11-02 13:00 | 11.4 | 11.7 | 13.3
| 2014-11-02 13:30 | 11.5 | 11.7 | 13.3
| 2014-11-02 14:00 | 13 | 11.7 | 13.3
| 2014-11-02 14:30 | 14.1 | 11.7 | 13.3
| 2014-11-02 15:00 | 13.9 | 12.2 | 13.3
| 2014-11-02 15:30 | 13.5 | 12.2 | 13.3
| 2014-11-02 16:00 | 12.8 | 12.2 | 13.3
| 2014-11-02 16:30 | 12.7 | 12.2 | 13.3
| 2014-11-02 17:00 | 12.3 | 12.2 | 13.3
| 2014-11-02 17:30 | 11.7 | 12.2 | 13.3
| 2014-11-02 18:00 | 11.3 | 12.2 | 13.3
| 2014-11-02 18:30 | 11.1 | 12.2 | 13.3
| 2014-11-02 19:00 | 11.2 | 12.2 | 13.3
| 2014-11-02 19:30 | 11.1 | 12.2 | 13.3
| 2014-11-02 20:00 | 10.9 | 12.2 | 13.3
| 2014-11-02 20:30 | 10.3 | 12.2 | 13.3
| 2014-11-02 21:00 | 10.1 | 12.2 | 13.3
| 2014-11-02 21:30 | 10 | 12.2 | 13.3
| 2014-11-02 22:00 | 10.2 | 12.2 | 13.3
| 2014-11-02 22:30 | 10.3 | 12.2 | 13.3
| 2014-11-02 23:00 | 10.4 | 12.2 | 13.3
| 2014-11-02 23:30 | 10.8 | 12.2 | 13.3
| 2014-11-03 | 11.1 | 11.7 | 13.3
| 2014-11-03 00:30 | 11.2 | 11.7 | 13.3
| 2014-11-03 01:00 | 12.8 | 11.7 | 13.3
| 2014-11-03 01:30 | 14.1 | 11.7 | 13.3
| 2014-11-03 02:00 | 13.3 | 11.7 | 13.3
| 2014-11-03 02:30 | 13.4 | 11.7 | 13.3
| 2014-11-03 03:00 | 13.7 | 11.7 | 13.3
| 2014-11-03 03:30 | 13.5 | 11.7 | 13.3
| 2014-11-03 04:00 | 13.6 | 11.7 | 13.3
| 2014-11-03 04:30 | 13.4 | 11.7 | 13.3
| 2014-11-03 05:00 | 13.4 | 11.7 | 13.3
| 2014-11-03 05:30 | 13.2 | 11.7 | 13.3
| 2014-11-03 06:00 | 13.2 | 11.7 | 13.3
| 2014-11-03 06:30 | 12.9 | 11.7 | 13.3
| 2014-11-03 07:00 | 12.5 | 11.7 | 13.3
| 2014-11-03 07:30 | 12.7 | 11.7 | 13.3
| 2014-11-03 08:00 | 13.1 | 11.7 | 13.3
| 2014-11-03 08:30 | 13.1 | 11.7 | 13.3
| 2014-11-03 09:00 | 13.4 | 11.7 | 13.3
| 2014-11-03 09:30 | 13.3 | 11.7 | 13.3
| 2014-11-03 10:00 | 13.6 | 11.7 | 13.3
| 2014-11-03 10:30 | 13.6 | 11.7 | 13.3
| 2014-11-03 11:00 | 13.6 | 11.7 | 13.3
| 2014-11-03 11:30 | 13.8 | 11.7 | 13.3
| 2014-11-03 12:00 | 13.7 | 11.7 | 13.3
| 2014-11-03 12:30 | 13.6 | 11.7 | 13.3
| 2014-11-03 13:00 | 14.2 | 11.7 | 13.3
| 2014-11-03 13:30 | 14.3 | 12.2 | 13.3
| 2014-11-03 14:00 | 14.8 | 12.2 | 13.3
| 2014-11-03 14:30 | 14.8 | 12.2 | 13.3
| 2014-11-03 15:00 | 14.6 | 12.2 | 13.3
| 2014-11-03 15:30 | 14.2 | 12.2 | 13.3
| 2014-11-03 16:00 | 13.8 | 12.2 | 13.3
| 2014-11-03 16:30 | 14.1 | 12.2 | 13.3
| 2014-11-03 17:00 | 13.7 | 12.2 | 13.3
| 2014-11-03 17:30 | 13.5 | 12.2 | 13.3
| 2014-11-03 18:00 | 13.4 | 12.2 | 13.3
| 2014-11-03 18:30 | 13 | 12.2 | 13.3
| 2014-11-03 19:00 | 12.8 | 12.2 | 13.3
| 2014-11-03 19:30 | 12.3 | 12.2 | 13.3
| 2014-11-03 20:00 | 11.9 | 12.2 | 13.3
| 2014-11-03 20:30 | 11.8 | 12.2 | 13.3
| 2014-11-03 21:00 | 11.6 | 12.2 | 13.3
| 2014-11-03 21:30 | 11.5 | 12.2 | 13.3
| 2014-11-03 22:00 | 11.4 | 12.2 | 13.3
| 2014-11-03 22:30 | 11.3 | 12.2 | 13.3
| 2014-11-03 23:00 | 12.4 | 12.2 | 13.3
| 2014-11-03 23:30 | 12.1 | 12.2 | 13.3
| 2014-11-04 | 11.8 | 12.2 | 13.3
| 2014-11-04 00:30 | 11.5 | 12.2 | 13.3
| 2014-11-04 01:00 | 11.3 | 12.2 | 13.3
| 2014-11-04 01:30 | 11.3 | 12.2 | 13.3
| 2014-11-04 02:00 | 11.5 | 12.2 | 13.3
| 2014-11-04 02:30 | 11.4 | 12.2 | 13.3
| 2014-11-04 03:00 | 11.2 | 12.2 | 13.3
| 2014-11-04 03:30 | 11.3 | 12.2 | 13.3
| 2014-11-04 04:00 | 11.3 | 12.2 | 13.3
| 2014-11-04 04:30 | 12.1 | 12.2 | 13.3
| 2014-11-04 05:00 | 11.8 | 12.2 | 13.3
| 2014-11-04 05:30 | 11.7 | 12.2 | 13.3
| 2014-11-04 06:00 | 11.7 | 12.2 | 13.3
| 2014-11-04 06:30 | 12.2 | 12.2 | 13.3
| 2014-11-04 07:00 | 12.6 | 12.2 | 13.3
| 2014-11-04 07:30 | 13.1 | 12.2 | 13.3
| 2014-11-04 08:00 | 13 | 12.2 | 13.3
| 2014-11-04 08:30 | 13.2 | 12.2 | 13.3
| 2014-11-04 09:00 | 13.2 | 12.2 | 13.3
| 2014-11-04 09:30 | 13.3 | 12.2 | 13.3
| 2014-11-04 10:00 | 13.7 | 12.2 | 13.3
| 2014-11-04 10:30 | 13.8 | 12.2 | 13.3
| 2014-11-04 11:00 | 13.9 | 12.2 | 13.3
| 2014-11-04 11:30 | 14.2 | 12.2 | 13.3
| 2014-11-04 12:00 | 14.1 | 12.2 | 13.3
| 2014-11-04 12:30 | 13.8 | 12.2 | 13.3
| 2014-11-04 13:00 | 14.1 | 12.2 | 13.3
| 2014-11-04 13:30 | 14.8 | 12.2 | 13.3
| 2014-11-04 14:00 | 14.7 | 12.2 | 13.3
| 2014-11-04 14:30 | 14.8 | 12.2 | 13.3
| 2014-11-04 15:00 | 14.8 | 12.2 | 13.3
| 2014-11-04 15:30 | 14.7 | 12.2 | 13.3
| 2014-11-04 16:00 | 14.6 | 12.2 | 13.3
| 2014-11-04 16:30 | 13.8 | 12.2 | 13.3
| 2014-11-04 17:00 | 13.1 | 12.8 | 13.3
| 2014-11-04 17:30 | 12.6 | 12.8 | 13.3
| 2014-11-04 18:00 | 11.7 | 12.8 | 13.3
| 2014-11-04 18:30 | 10.9 | 12.8 | 13.3
| 2014-11-04 19:00 | 10.4 | 12.8 | 13.3
| 2014-11-04 19:30 | 10.8 | 12.8 | 13.3
| 2014-11-04 20:00 | 11 | 12.8 | 13.3
| 2014-11-04 20:30 | 11.4 | 12.2 | 13.3
| 2014-11-04 21:00 | 11.8 | 12.2 | 13.3
| 2014-11-04 21:30 | 11.6 | 12.2 | 13.3
| 2014-11-04 22:00 | 11.1 | 12.2 | 13.3
| 2014-11-04 22:30 | 10.6 | 12.2 | 13.3
| 2014-11-04 23:00 | 10.2 | 12.2 | 13.3
| 2014-11-04 23:30 | 9.8 | 12.2 | 13.3
| 2014-11-05 | 9.7 | 12.2 | 13.3
| 2014-11-05 00:30 | 9.7 | 12.2 | 13.3
| 2014-11-05 01:00 | 9.4 | 12.2 | 13.3
| 2014-11-05 01:30 | 9.1 | 12.2 | 13.3
| 2014-11-05 02:00 | 8.9 | 12.2 | 13.3
| 2014-11-05 02:30 | 8.8 | 12.2 | 13.3
| 2014-11-05 03:00 | 8.8 | 12.2 | 13.3
| 2014-11-05 03:30 | 8.7 | 12.2 | 13.3
| 2014-11-05 04:00 | 8.7 | 12.2 | 13.3
| 2014-11-05 04:30 | 8.7 | 12.2 | 13.3
| 2014-11-05 05:00 | 8.7 | 12.2 | 13.3
| 2014-11-05 05:30 | 8.7 | 12.2 | 13.3
| 2014-11-05 06:00 | 8.7 | 11.7 | 13.3
| 2014-11-05 06:30 | 8.6 | 11.7 | 13.3
| 2014-11-05 07:00 | 8.6 | 11.7 | 13.3
| 2014-11-05 07:30 | 8.5 | 11.7 | 13.3
| 2014-11-05 08:00 | 8.4 | 11.7 | 13.3
| 2014-11-05 08:30 | 8.4 | 11.7 | 13.3
| 2014-11-05 09:00 | 8.4 | 11.7 | 13.3
| 2014-11-05 09:30 | 8.6 | 11.7 | 13.3
| 2014-11-05 10:00 | 8.9 | 11.7 | 13.3
| 2014-11-05 10:30 | 9.4 | 11.7 | 13.3
| 2014-11-05 11:00 | 9.8 | 11.7 | 13.3
| 2014-11-05 11:30 | 10 | 11.7 | 13.3
| 2014-11-05 12:00 | 10.3 | 11.7 | 13.3
| 2014-11-05 12:30 | 10.5 | 11.7 | 13.3
| 2014-11-05 13:00 | 10.5 | 11.7 | 13.3
| 2014-11-05 13:30 | 10.4 | 11.7 | 13.3
| 2014-11-05 14:00 | 10.4 | 11.7 | 13.3
| 2014-11-05 14:30 | 10.3 | 11.7 | 13.3
| 2014-11-05 15:00 | 10 | 11.7 | 13.3
| 2014-11-05 15:30 | 9.9 | 12.2 | 13.3
| 2014-11-05 16:00 | 9.6 | 12.2 | 13.3
| 2014-11-05 16:30 | 9.4 | 12.2 | 13.3
| 2014-11-05 17:00 | 9.2 | 12.2 | 13.3
| 2014-11-05 17:30 | 8.8 | 12.2 | 13.3
| 2014-11-05 18:00 | 8.8 | 12.2 | 13.3
| 2014-11-05 18:30 | 8.8 | 12.2 | 13.3
| 2014-11-05 19:00 | 8.8 | 12.2 | 13.3
| 2014-11-05 19:30 | 8.6 | 12.2 | 13.3
| 2014-11-05 20:00 | 8.5 | 11.7 | 13.3
| 2014-11-05 20:30 | 8.3 | 11.7 | 13.3
| 2014-11-05 21:00 | 8.2 | 11.7 | 13.3
| 2014-11-05 21:30 | 8.2 | 11.7 | 13.3
| 2014-11-05 22:00 | 8.1 | 11.7 | 13.3
| 2014-11-05 22:30 | 8.1 | 11.7 | 13.3
| 2014-11-05 23:00 | 8.1 | 11.7 | 13.3
| 2014-11-05 23:30 | 7.9 | 11.7 | 13.3
| 2014-11-06 | 7.9 | 11.7 | 13.3
| 2014-11-06 00:30 | 7.8 | 11.7 | 13.3
| 2014-11-06 01:00 | 7.7 | 11.7 | 13.3
| 2014-11-06 01:30 | 7.5 | 11.7 | 13.3
| 2014-11-06 02:00 | 7.3 | 11.7 | 13.3
| 2014-11-06 02:30 | 7.2 | 11.7 | 13.3
| 2014-11-06 03:00 | 7 | 11.7 | 13.3
| 2014-11-06 03:30 | 6.8 | 11.7 | 13.3
| 2014-11-06 04:00 | 6.9 | 11.1 | 13.3
| 2014-11-06 04:30 | 6.8 | 11.1 | 13.3
| 2014-11-06 05:00 | 6.4 | 11.1 | 13.3
| 2014-11-06 05:30 | 5.9 | 11.1 | 13.3
| 2014-11-06 06:00 | 6.2 | 11.1 | 13.3
| 2014-11-06 06:30 | 6.2 | 11.1 | 13.3
| 2014-11-06 07:00 | 6.1 | 11.1 | 13.3
| 2014-11-06 07:30 | 5.3 | 11.1 | 13.3
| 2014-11-06 08:00 | 5.8 | 11.1 | 13.3
| 2014-11-06 08:30 | 6.2 | 11.1 | 13.3
| 2014-11-06 09:00 | 6.6 | 11.1 | 13.3
| 2014-11-06 09:30 | 7.2 | 10.6 | 13.3
| 2014-11-06 10:00 | 7.6 | 10.6 | 13.3
| 2014-11-06 10:30 | 7.7 | 10.6 | 13.3
| 2014-11-06 11:00 | 8.1 | 10.6 | 13.3
| 2014-11-06 11:30 | 8.3 | 10.6 | 13.3
| 2014-11-06 12:00 | 8.9 | 10.6 | 13.3
| 2014-11-06 12:30 | 9 | 10.6 | 13.3
| 2014-11-06 13:00 | 9.4 | 10.6 | 13.3
| 2014-11-06 13:30 | 10.6 | 10.6 | 13.3
| 2014-11-06 14:00 | 10.2 | 10.6 | 13.3
| 2014-11-06 14:30 | 9.8 | 10.6 | 13.3
| 2014-11-06 15:00 | 9.3 | 11.1 | 13.3
| 2014-11-06 15:30 | 9.8 | 11.1 | 13.3
| 2014-11-06 16:00 | 8.7 | 11.1 | 13.3
| 2014-11-06 16:30 | 8.3 | 11.1 | 13.3
| 2014-11-06 17:00 | 7.6 | 11.1 | 13.3
| 2014-11-06 17:30 | 7.5 | 11.1 | 13.3
| 2014-11-06 18:00 | 7.9 | 11.1 | 13.3
| 2014-11-06 18:30 | 7.1 | 11.1 | 13.3
| 2014-11-06 19:00 | 6.9 | 11.1 | 13.3
| 2014-11-06 19:30 | 6.9 | 11.1 | 13.3
| 2014-11-06 20:00 | 6.8 | 11.1 | 13.3
| 2014-11-06 20:30 | 6.7 | 11.1 | 13.3
| 2014-11-06 21:00 | 6.2 | 11.1 | 13.3
| 2014-11-06 21:30 | 5.9 | 10.6 | 13.3
| 2014-11-06 22:00 | 5.6 | 10.6 | 13.3
| 2014-11-06 22:30 | 4.9 | 10.6 | 13.3
| 2014-11-06 23:00 | 4.1 | 10.6 | 13.3
| 2014-11-06 23:30 | 3.3 | 10.6 | 13.3
| 2014-11-07 | 2.9 | 10.6 | 13.3
| 2014-11-07 00:30 | 2.6 | 10.6 | 13.3
| 2014-11-07 01:00 | 2.1 | 10.6 | 13.3
| 2014-11-07 01:30 | 1.8 | 10.6 | 13.3
| 2014-11-07 02:00 | 1.4 | 10 | 13.3
| 2014-11-07 02:30 | 0.8 | 10 | 13.3
| 2014-11-07 03:00 | 0.5 | 10 | 13.3
| 2014-11-07 03:30 | 0.6 | 10 | 13.3
| 2014-11-07 04:00 | 0.2 | 10 | 13.3
| 2014-11-07 04:30 | 1.5 | 10 | 13.3
| 2014-11-07 05:00 | 2.6 | 9.4 | 13.3
| 2014-11-07 05:30 | 3.2 | 9.4 | 13.3
| 2014-11-07 06:00 | 3.4 | 9.4 | 13.3
| 2014-11-07 06:30 | 3.7 | 9.4 | 13.3
| 2014-11-07 07:00 | 4.4 | 9.4 | 13.3
| 2014-11-07 07:30 | 4.6 | 9.4 | 13.3
| 2014-11-07 08:00 | 4.7 | 9.4 | 13.3
| 2014-11-07 08:30 | 4.9 | 9.4 | 13.3
| 2014-11-07 09:00 | 5 | 9.4 | 13.3
| 2014-11-07 09:30 | 5.6 | 9.4 | 13.3
| 2014-11-07 10:00 | 6.2 | 9.4 | 13.3
| 2014-11-07 10:30 | 7.1 | 9.4 | 13.3
| 2014-11-07 11:00 | 7.3 | 9.4 | 13.3
| 2014-11-07 11:30 | 7.4 | 9.4 | 13.3
| 2014-11-07 12:00 | 7.3 | 9.4 | 13.3
| 2014-11-07 12:30 | 8.2 | 9.4 | 13.3
| 2014-11-07 13:00 | 8.6 | 9.4 | 13.3
| 2014-11-07 13:30 | 8.1 | 9.4 | 13.3
| 2014-11-07 14:00 | 8.2 | 9.4 | 13.3
| 2014-11-07 14:30 | 8.2 | 9.4 | 13.3
| 2014-11-07 15:00 | 8.4 | 9.4 | 13.3
| 2014-11-07 15:30 | 8.4 | 9.4 | 13.3
| 2014-11-07 16:00 | 8.3 | 9.4 | 13.3
| 2014-11-07 16:30 | 8.3 | 10 | 13.3
| 2014-11-07 17:00 | 8.3 | 10 | 13.3
| 2014-11-07 17:30 | 7.9 | 10 | 13.3
| 2014-11-07 18:00 | 8.1 | 10 | 12.8
| 2014-11-07 18:30 | 8.3 | 10 | 12.8
| 2014-11-07 19:00 | 8.3 | 10 | 12.8
| 2014-11-07 19:30 | 8.4 | 10 | 12.8
| 2014-11-07 20:00 | 7.9 | 10 | 12.8
| 2014-11-07 20:30 | 8.1 | 10 | 12.8
| 2014-11-07 21:00 | 8.4 | 10 | 12.8
| 2014-11-07 21:30 | 8.4 | 10 | 12.8
| 2014-11-07 22:00 | 8.4 | 10 | 12.8
| 2014-11-07 22:30 | 8.2 | 10 | 12.8
| 2014-11-07 23:00 | 8.2 | 10 | 12.8
| 2014-11-07 23:30 | 8.2 | 9.4 | 12.8
| 2014-11-08 | 8.4 | 9.4 | 12.8
| 2014-11-08 00:30 | 7.8 | 9.4 | 12.8
| 2014-11-08 01:00 | 7.2 | 9.4 | 12.8
| 2014-11-08 01:30 | 7.7 | 9.4 | 12.8
| 2014-11-08 02:00 | 8.3 | 9.4 | 12.8
| 2014-11-08 02:30 | 8 | 9.4 | 12.8
| 2014-11-08 03:00 | 7.6 | 9.4 | 12.8
| 2014-11-08 03:30 | 7.5 | 9.4 | 12.8
| 2014-11-08 04:00 | 7.4 | 9.4 | 12.8
| 2014-11-08 04:30 | 7.4 | 9.4 | 12.8
| 2014-11-08 05:00 | 7.6 | 9.4 | 12.8
| 2014-11-08 05:30 | 7.9 | 9.4 | 12.8
| 2014-11-08 06:00 | 8.2 | 9.4 | 12.8
| 2014-11-08 06:30 | 7.9 | 9.4 | 12.8
| 2014-11-08 07:00 | 7.4 | 9.4 | 12.8
| 2014-11-08 07:30 | 7.6 | 9.4 | 12.8
| 2014-11-08 08:00 | 7.9 | 9.4 | 12.8
| 2014-11-08 08:30 | 8.7 | 9.4 | 12.8
| 2014-11-08 09:00 | 9.5 | 9.4 | 12.8
| 2014-11-08 09:30 | 9.6 | 8.9 | 12.8
| 2014-11-08 10:00 | 11.3 | 8.9 | 12.8
| 2014-11-08 10:30 | 11.1 | 8.9 | 12.8
| 2014-11-08 11:00 | 11.4 | 8.9 | 12.8
| 2014-11-08 11:30 | 12.1 | 9.4 | 12.8
| 2014-11-08 12:00 | 13.1 | 9.4 | 12.8
| 2014-11-08 12:30 | 13.3 | 9.4 | 12.8
| 2014-11-08 13:00 | 13.4 | 9.4 | 12.8
| 2014-11-08 13:30 | 14.3 | 9.4 | 12.8
| 2014-11-08 14:00 | 13.8 | 9.4 | 12.8
| 2014-11-08 14:30 | 14.4 | 9.4 | 12.8
| 2014-11-08 15:00 | 14.3 | 10 | 12.8
| 2014-11-08 15:30 | 13.7 | 10 | 12.8
| 2014-11-08 16:00 | 12.5 | 10 | 12.8
| 2014-11-08 16:30 | 11.5 | 10 | 12.8
| 2014-11-08 17:00 | 10 | 10 | 12.8
| 2014-11-08 17:30 | 8.4 | 10 | 12.8
| 2014-11-08 18:00 | 7.7 | 10 | 12.8
| 2014-11-08 18:30 | 7.2 | 10 | 12.8
| 2014-11-08 19:00 | 6.9 | 10 | 12.8
| 2014-11-08 19:30 | 6.7 | 10 | 12.8
| 2014-11-08 20:00 | 6.3 | 10 | 12.8
| 2014-11-08 20:30 | 6.6 | 10 | 12.8
| 2014-11-08 21:00 | 7 | 10 | 12.8
| 2014-11-08 21:30 | 7.2 | 9.4 | 12.8
| 2014-11-08 22:00 | 6.9 | 9.4 | 12.8
| 2014-11-08 22:30 | 6.5 | 9.4 | 12.8
| 2014-11-08 23:00 | 6.2 | 9.4 | 12.8
| 2014-11-08 23:30 | 5.8 | 9.4 | 12.8
| 2014-11-09 | 5.6 | 9.4 | 12.8
| 2014-11-09 00:30 | 5.6 | 9.4 | 12.8
| 2014-11-09 01:00 | 5.6 | 9.4 | 12.8
| 2014-11-09 01:30 | 5.7 | 9.4 | 12.8
| 2014-11-09 02:00 | 5.8 | 9.4 | 12.8
| 2014-11-09 02:30 | 5.8 | 8.9 | 12.8
| 2014-11-09 03:00 | 5.8 | 8.9 | 12.8
| 2014-11-09 03:30 | 5.8 | 8.9 | 12.8
| 2014-11-09 04:00 | 5.2 | 8.9 | 12.8
| 2014-11-09 04:30 | 5.3 | 8.9 | 12.8
| 2014-11-09 05:00 | 5.2 | 8.9 | 12.8
| 2014-11-09 05:30 | 4.5 | 8.9 | 12.8
| 2014-11-09 06:00 | 3.8 | 8.9 | 12.8
| 2014-11-09 06:30 | 3.3 | 8.9 | 12.8
| 2014-11-09 07:00 | 2.6 | 8.9 | 12.8
| 2014-11-09 07:30 | 2.2 | 8.9 | 12.8
| 2014-11-09 08:00 | 2.1 | 8.3 | 12.8
| 2014-11-09 08:30 | 3.1 | 8.3 | 12.8
| 2014-11-09 09:00 | 4.3 | 8.3 | 12.8
| 2014-11-09 09:30 | 5.5 | 8.3 | 12.8
| 2014-11-09 10:00 | 6.3 | 8.3 | 12.8
| 2014-11-09 10:30 | 7.3 | 8.3 | 12.8
| 2014-11-09 11:00 | 8.4 | 8.3 | 12.8
| 2014-11-09 11:30 | 9.1 | 8.3 | 12.8
| 2014-11-09 12:00 | 9.3 | 8.3 | 12.8
| 2014-11-09 12:30 | 9.4 | 8.3 | 12.8
| 2014-11-09 13:00 | 9.4 | 8.3 | 12.8
| 2014-11-09 13:30 | 9.7 | 8.3 | 12.8
| 2014-11-09 14:00 | 10.4 | 8.3 | 12.8
| 2014-11-09 14:30 | 10.8 | 8.3 | 12.8
| 2014-11-09 15:00 | 10.8 | 8.9 | 12.8
| 2014-11-09 15:30 | 10.9 | 8.9 | 12.8
| 2014-11-09 16:00 | 10.7 | 8.9 | 12.8
| 2014-11-09 16:30 | 10.5 | 8.9 | 12.8
| 2014-11-09 17:00 | 9.3 | 8.9 | 12.8
| 2014-11-09 17:30 | 8.1 | 8.9 | 12.2
| 2014-11-09 18:00 | 7.3 | 8.9 | 12.2
| 2014-11-09 18:30 | 6.6 | 8.9 | 12.2
| 2014-11-09 19:00 | 5.8 | 8.9 | 12.2
| 2014-11-09 19:30 | 5.7 | 8.9 | 12.2
| 2014-11-09 20:00 | 5.9 | 8.9 | 12.2
| 2014-11-09 20:30 | 5.8 | 8.9 | 12.2
| 2014-11-09 21:00 | 6.2 | 8.9 | 12.2
| 2014-11-09 21:30 | 6 | 8.9 | 12.2
| 2014-11-09 22:00 | 6.1 | 8.9 | 12.2
| 2014-11-09 22:30 | 5.9 | 8.9 | 12.2
| 2014-11-09 23:00 | 6.1 | 8.9 | 12.2
| 2014-11-09 23:30 | 6.3 | 8.9 | 12.2
| 2014-11-10 | 6.6 | 8.9 | 12.2
| 2014-11-10 00:30 | 6.7 | 8.9 | 12.2
| 2014-11-10 01:00 | 6.4 | 8.9 | 12.2
| 2014-11-10 01:30 | 6.7 | 8.9 | 12.2
| 2014-11-10 02:00 | 6.4 | 8.9 | 12.2
| 2014-11-10 02:30 | 6.3 | 8.9 | 12.2
| 2014-11-10 03:00 | 6.2 | 8.9 | 12.2
| 2014-11-10 03:30 | 6.3 | 8.9 | 12.2
| 2014-11-10 04:00 | 6.3 | 8.9 | 12.2
| 2014-11-10 04:30 | 6.6 | 8.9 | 12.2
| 2014-11-10 05:00 | 6.6 | 8.9 | 12.2
| 2014-11-10 05:30 | 6.6 | 8.9 | 12.2
| 2014-11-10 06:00 | 6.4 | 8.9 | 12.2
| 2014-11-10 06:30 | 6.6 | 8.9 | 12.2
| 2014-11-10 07:00 | 6.7 | 8.9 | 12.2
| 2014-11-10 07:30 | 6.7 | 8.9 | 12.2
| 2014-11-10 08:00 | 6.9 | 8.9 | 12.2
| 2014-11-10 08:30 | 7.2 | 8.9 | 12.2
| 2014-11-10 09:00 | 7.4 | 8.9 | 12.2
| 2014-11-10 09:30 | 7.8 | 8.9 | 12.2
| 2014-11-10 10:00 | 8.2 | 8.9 | 12.2
| 2014-11-10 10:30 | 8.9 | 8.9 | 12.2
| 2014-11-10 11:00 | 9.6 | 8.9 | 12.2
| 2014-11-10 11:30 | 9.9 | 8.9 | 12.2
| 2014-11-10 12:00 | 10.1 | 8.9 | 12.2
| 2014-11-10 12:30 | 10.3 | 8.9 | 12.2
| 2014-11-10 13:00 | 10.4 | 8.9 | 12.2
| 2014-11-10 13:30 | 10.7 | 8.9 | 12.2
| 2014-11-10 14:00 | 10.6 | 8.9 | 12.2
| 2014-11-10 14:30 | 10.5 | 8.9 | 12.2
| 2014-11-10 15:00 | 10.6 | 9.4 | 12.2
| 2014-11-10 15:30 | 10.4 | 9.4 | 12.2
| 2014-11-10 16:00 | 10.3 | 9.4 | 12.2
| 2014-11-10 16:30 | 10.2 | 9.4 | 12.2
| 2014-11-10 17:00 | 10 | 9.4 | 12.2
| 2014-11-10 17:30 | 9.4 | 9.4 | 12.2
| 2014-11-10 18:00 | 8.9 | 9.4 | 12.2
| 2014-11-10 18:30 | 8.2 | 9.4 | 12.2
| 2014-11-10 19:00 | 7.8 | 9.4 | 12.2
| 2014-11-10 19:30 | 7.3 | 9.4 | 12.2
| 2014-11-10 20:00 | 6.9 | 9.4 | 12.2
| 2014-11-10 20:30 | 6.9 | 9.4 | 12.2
| 2014-11-10 21:00 | 7.1 | 9.4 | 12.2
| 2014-11-10 21:30 | 7.1 | 9.4 | 12.2
| 2014-11-10 22:00 | 6.7 | 9.4 | 12.2
| 2014-11-10 22:30 | 6.9 | 9.4 | 12.2
| 2014-11-10 23:00 | 6.7 | 9.4 | 12.2
| 2014-11-10 23:30 | 6.2 | 9.4 | 12.2
| 2014-11-11 | 6.1 | 9.4 | 12.2
| 2014-11-11 00:30 | 5.6 | 9.4 | 12.2
| 2014-11-11 01:00 | 5.4 | 8.9 | 12.2
| 2014-11-11 01:30 | 4.9 | 8.9 | 12.2
| 2014-11-11 02:00 | 4.6 | 8.9 | 12.2
| 2014-11-11 02:30 | 4.2 | 8.9 | 12.2
| 2014-11-11 03:00 | 4.1 | 8.9 | 12.2
| 2014-11-11 03:30 | 3.6 | 8.9 | 12.2
| 2014-11-11 04:00 | 3.3 | 8.9 | 12.2
| 2014-11-11 04:30 | 3.5 | 8.9 | 12.2
| 2014-11-11 05:00 | 3.4 | 8.9 | 12.2
| 2014-11-11 05:30 | 3.8 | 8.9 | 12.2
| 2014-11-11 06:00 | 4.9 | 8.3 | 12.2
| 2014-11-11 06:30 | 5.2 | 8.3 | 12.2
| 2014-11-11 07:00 | 5.2 | 8.3 | 12.2
| 2014-11-11 07:30 | 5.3 | 8.3 | 12.2
| 2014-11-11 08:00 | 5.5 | 8.3 | 12.2
| 2014-11-11 08:30 | 5.8 | 8.3 | 12.2
| 2014-11-11 09:00 | 6.1 | 8.3 | 12.2
| 2014-11-11 09:30 | 6.8 | 8.3 | 12.2
| 2014-11-11 10:00 | 7.1 | 8.3 | 12.2
| 2014-11-11 10:30 | 7.9 | 8.3 | 12.2
| 2014-11-11 11:00 | 9.1 | 8.3 | 12.2
| 2014-11-11 11:30 | 9.1 | 8.3 | 12.2
| 2014-11-11 12:00 | 9.9 | 8.3 | 12.2
| 2014-11-11 12:30 | 10 | 8.3 | 12.2
| 2014-11-11 13:00 | 10.1 | 8.3 | 12.2
| 2014-11-11 13:30 | 9.8 | 8.3 | 12.2
| 2014-11-11 14:00 | 10.1 | 8.3 | 12.2
| 2014-11-11 14:30 | 9.9 | 8.3 | 12.2
| 2014-11-11 15:00 | 9.8 | 8.3 | 12.2
| 2014-11-11 15:30 | 9.4 | 8.9 | 11.7
| 2014-11-11 16:00 | 9.4 | 8.9 | 11.7
| 2014-11-11 16:30 | 9.3 | 8.9 | 11.7
| 2014-11-11 17:00 | 9.3 | 8.9 | 11.7
| 2014-11-11 17:30 | 9.2 | 8.9 | 11.7
| 2014-11-11 18:00 | 9.1 | 8.9 | 11.7
| 2014-11-11 18:30 | 9.1 | 8.9 | 11.7
| 2014-11-11 19:00 | 9.1 | 8.9 | 11.7
| 2014-11-11 19:30 | 8.8 | 8.9 | 11.7
| 2014-11-11 20:00 | 8.3 | 8.9 | 11.7
| 2014-11-11 20:30 | 8 | 8.9 | 11.7
| 2014-11-11 21:00 | 7.7 | 8.9 | 11.7
| 2014-11-11 21:30 | 7 | 8.9 | 11.7
| 2014-11-11 22:00 | 6.4 | 8.9 | 11.7
| 2014-11-11 22:30 | 5.9 | 8.9 | 11.7
| 2014-11-11 23:00 | 5.6 | 8.9 | 11.7
| 2014-11-11 23:30 | 5.3 | 8.9 | 11.7
| 2014-11-12 | 5.6 | 8.9 | 11.7
| 2014-11-12 00:30 | 5.9 | 8.9 | 11.7
| 2014-11-12 01:00 | 5.8 | 8.9 | 11.7
| 2014-11-12 01:30 | 5.6 | 8.9 | 11.7
| 2014-11-12 02:00 | 5.3 | 8.9 | 11.7
| 2014-11-12 02:30 | 5.3 | 8.9 | 11.7
| 2014-11-12 03:00 | 5.1 | 8.9 | 11.7
| 2014-11-12 03:30 | 4.8 | 8.9 | 11.7
| 2014-11-12 04:00 | 4.7 | 8.9 | 11.7
| 2014-11-12 04:30 | 5 | 8.3 | 11.7
| 2014-11-12 05:00 | 4.4 | 8.3 | 11.7
| 2014-11-12 05:30 | 4.4 | 8.3 | 11.7
| 2014-11-12 06:00 | 5.4 | 8.3 | 11.7
| 2014-11-12 06:30 | 5.7 | 8.3 | 11.7
| 2014-11-12 07:00 | 6.1 | 8.3 | 11.7
| 2014-11-12 07:30 | 6.7 | 8.3 | 11.7
| 2014-11-12 08:00 | 7.1 | 8.3 | 11.7
| 2014-11-12 08:30 | 7.2 | 8.3 | 11.7
| 2014-11-12 09:00 | 7.2 | 8.3 | 11.7
| 2014-11-12 09:30 | 7.5 | 8.3 | 11.7
| 2014-11-12 10:00 | 7.6 | 8.3 | 11.7
| 2014-11-12 10:30 | 7.8 | 8.3 | 11.7
| 2014-11-12 11:00 | 7.9 | 8.3 | 11.7
| 2014-11-12 11:30 | 8.1 | 8.3 | 11.7
| 2014-11-12 12:00 | 8.2 | 8.3 | 11.7
| 2014-11-12 12:30 | 8.3 | 8.3 | 11.7
| 2014-11-12 13:00 | 8.3 | 8.3 | 11.7
| 2014-11-12 13:30 | 8.4 | 8.3 | 11.7
| 2014-11-12 14:00 | 8.7 | 8.9 | 11.7
| 2014-11-12 14:30 | 8.7 | 8.9 | 11.7
| 2014-11-12 15:00 | 8.8 | 8.9 | 11.7
| 2014-11-12 15:30 | 8.8 | 8.9 | 11.7
| 2014-11-12 16:00 | 8.7 | 8.9 | 11.7
| 2014-11-12 16:30 | 8.6 | 8.9 | 11.7
| 2014-11-12 17:00 | 8.5 | 8.9 | 11.7
| 2014-11-12 17:30 | 8.4 | 8.9 | 11.7
| 2014-11-12 18:00 | 8.3 | 8.9 | 11.7
| 2014-11-12 18:30 | 8.2 | 8.9 | 11.7
| 2014-11-12 19:00 | 8.1 | 8.9 | 11.7
| 2014-11-12 19:30 | 8.2 | 8.9 | 11.7
| 2014-11-12 20:00 | 8.3 | 8.9 | 11.7
| 2014-11-12 20:30 | 8.3 | 8.9 | 11.7
| 2014-11-12 21:00 | 8.3 | 8.9 | 11.7
| 2014-11-12 21:30 | 8.4 | 8.9 | 11.7
| 2014-11-12 22:00 | 8.4 | 8.9 | 11.7
| 2014-11-12 22:30 | 8.6 | 8.9 | 11.7
| 2014-11-12 23:00 | 8.6 | 8.9 | 11.7
| 2014-11-12 23:30 | 8.6 | 8.9 | 11.7
| 2014-11-13 | 8.6 | 8.9 | 11.7
| 2014-11-13 00:30 | 8.5 | 8.9 | 11.7
| 2014-11-13 01:00 | 8.7 | 8.9 | 11.7
| 2014-11-13 01:30 | 8.7 | 8.9 | 11.7
| 2014-11-13 02:00 | 8.7 | 8.9 | 11.7
| 2014-11-13 02:30 | 8.8 | 8.9 | 11.7
| 2014-11-13 03:00 | 8.8 | 8.9 | 11.7
| 2014-11-13 03:30 | 8.9 | 8.9 | 11.7
| 2014-11-13 04:00 | 8.9 | 8.9 | 11.7
| 2014-11-13 04:30 | 8.9 | 8.9 | 11.7
| 2014-11-13 05:00 | 8.8 | 8.9 | 11.7
| 2014-11-13 05:30 | 8.4 | 8.9 | 11.7
| 2014-11-13 06:00 | 8.5 | 8.9 | 11.7
| 2014-11-13 06:30 | 8.6 | 8.9 | 11.7
| 2014-11-13 07:00 | 8.5 | 8.9 | 11.7
| 2014-11-13 07:30 | 8.6 | 8.9 | 11.7
| 2014-11-13 08:00 | 8.9 | 8.9 | 11.7
| 2014-11-13 08:30 | 9.2 | 8.9 | 11.7
| 2014-11-13 09:00 | 9.4 | 8.9 | 11.7
| 2014-11-13 09:30 | 9.8 | 8.9 | 11.7
| 2014-11-13 10:00 | 10.2 | 8.9 | 11.7
| 2014-11-13 10:30 | 10.3 | 8.9 | 11.7
| 2014-11-13 11:00 | 10.3 | 8.9 | 11.7
| 2014-11-13 11:30 | 10.4 | 8.9 | 11.7
| 2014-11-13 12:00 | 10.7 | 9.4 | 11.7
| 2014-11-13 12:30 | 11.1 | 9.4 | 11.7
| 2014-11-13 13:00 | 11.1 | 9.4 | 11.7
| 2014-11-13 13:30 | 11.2 | 9.4 | 11.7
| 2014-11-13 14:00 | 11 | 9.4 | 11.7
| 2014-11-13 14:30 | 10.8 | 9.4 | 11.7
| 2014-11-13 15:00 | 11.1 | 9.4 | 11.7
| 2014-11-13 15:30 | 11.1 | 9.4 | 11.7
| 2014-11-13 16:00 | 11.1 | 9.4 | 11.7
| 2014-11-13 16:30 | 10.8 | 9.4 | 11.7
| 2014-11-13 17:00 | 10.6 | 9.4 | 11.7
| 2014-11-13 17:30 | 10.4 | 10 | 11.7
| 2014-11-13 18:00 | 10.3 | 10 | 11.7
| 2014-11-13 18:30 | 10.2 | 10 | 11.7
| 2014-11-13 19:00 | 10.1 | 10 | 11.7
| 2014-11-13 19:30 | 10.1 | 10 | 11.7
| 2014-11-13 20:00 | 10.1 | 10 | 11.7
| 2014-11-13 20:30 | 9.9 | 10 | 11.7
| 2014-11-13 21:00 | 9.8 | 10 | 11.7
| 2014-11-13 21:30 | 9.7 | 10 | 11.7
| 2014-11-13 22:00 | 9.7 | 10 | 11.7
| 2014-11-13 22:30 | 9.6 | 10 | 11.7
| 2014-11-13 23:00 | 9.5 | 10 | 11.7
| 2014-11-13 23:30 | 9.4 | 10 | 11.7
| 2014-11-14 | 9.3 | 10 | 11.7
| 2014-11-14 00:30 | 9.2 | 10 | 11.7
| 2014-11-14 01:00 | 8.3 | 10 | 11.7
| 2014-11-14 01:30 | 8.3 | 10 | 11.7
| 2014-11-14 02:00 | 8.6 | 10 | 11.7
| 2014-11-14 02:30 | 8.9 | 10 | 11.7
| 2014-11-14 03:00 | 9.2 | 10 | 11.7
| 2014-11-14 03:30 | 9.2 | 10 | 11.7
| 2014-11-14 04:00 | 9.3 | 9.4 | 11.7
| 2014-11-14 04:30 | 9.3 | 9.4 | 11.7
| 2014-11-14 05:00 | 9.3 | 9.4 | 11.7
| 2014-11-14 05:30 | 9.4 | 9.4 | 11.7
| 2014-11-14 06:00 | 9.4 | 9.4 | 11.7
| 2014-11-14 06:30 | 9.4 | 9.4 | 11.7
| 2014-11-14 07:00 | 9.5 | 9.4 | 11.7
| 2014-11-14 07:30 | 9.6 | 9.4 | 11.7
| 2014-11-14 08:00 | 9.7 | 9.4 | 11.7
| 2014-11-14 08:30 | 9.9 | 9.4 | 11.7
| 2014-11-14 09:00 | 10.2 | 9.4 | 11.7
| 2014-11-14 09:30 | 10.4 | 9.4 | 11.7
| 2014-11-14 10:00 | 10.6 | 9.4 | 11.7
| 2014-11-14 10:30 | 10.8 | 9.4 | 11.7
| 2014-11-14 11:00 | 10.9 | 9.4 | 11.7
| 2014-11-14 11:30 | 11.7 | 9.4 | 11.7
| 2014-11-14 12:00 | 13 | 9.4 | 11.7
| 2014-11-14 12:30 | 13.8 | 10 | 11.7
| 2014-11-14 13:00 | 13.7 | 10 | 11.7
| 2014-11-14 13:30 | 14.2 | 10 | 11.7
| 2014-11-14 14:00 | 13.9 | 10 | 11.7
| 2014-11-14 14:30 | 13.9 | 10 | 11.7
| 2014-11-14 15:00 | 13.1 | 10 | 11.7
| 2014-11-14 15:30 | 12.2 | 10 | 11.7
| 2014-11-14 16:00 | 11.6 | 10 | 11.7
| 2014-11-14 16:30 | 10.8 | 10 | 11.7
| 2014-11-14 17:00 | 9.8 | 10 | 11.7
| 2014-11-14 17:30 | 8.9 | 10 | 11.7
| 2014-11-14 18:00 | 8.2 | 10 | 11.7
| 2014-11-14 18:30 | 7.8 | 10 | 11.7
| 2014-11-14 19:00 | 7.5 | 10 | 11.7
| 2014-11-14 19:30 | 7.2 | 10 | 11.7
| 2014-11-14 20:00 | 6.9 | 10 | 11.7
| 2014-11-14 20:30 | 6.9 | 10 | 11.7
| 2014-11-14 21:00 | 7.3 | 10 | 11.7
| 2014-11-14 21:30 | 7.6 | 10 | 11.7
| 2014-11-14 22:00 | 7.9 | 10 | 11.7
| 2014-11-14 22:30 | 7.9 | 10 | 11.7
| 2014-11-14 23:00 | 7.8 | 10 | 11.7
| 2014-11-14 23:30 | 7.9 | 10 | 11.7
| 2014-11-15 | 7.9 | 10 | 11.7
| 2014-11-15 00:30 | 7.9 | 10 | 11.7
| 2014-11-15 01:00 | 7.9 | 9.4 | 11.7
| 2014-11-15 01:30 | 7.9 | 9.4 | 11.7
| 2014-11-15 02:00 | 7.8 | 9.4 | 11.7
| 2014-11-15 02:30 | 7.7 | 9.4 | 11.7
| 2014-11-15 03:00 | 7.4 | 9.4 | 11.7
| 2014-11-15 03:30 | 7.6 | 9.4 | 11.7
| 2014-11-15 04:00 | 7.7 | 9.4 | 11.7
| 2014-11-15 04:30 | 8.1 | 9.4 | 11.7
| 2014-11-15 05:00 | 8.4 | 9.4 | 11.7
| 2014-11-15 05:30 | 8.6 | 9.4 | 11.7
| 2014-11-15 06:00 | 8.5 | 9.4 | 11.7
| 2014-11-15 06:30 | 7.9 | 9.4 | 11.7
| 2014-11-15 07:00 | 7.4 | 9.4 | 11.7
| 2014-11-15 07:30 | 7.3 | 9.4 | 11.7
| 2014-11-15 08:00 | 7.3 | 9.4 | 11.7
| 2014-11-15 08:30 | 7.7 | 9.4 | 11.7
| 2014-11-15 09:00 | 8.2 | 9.4 | 11.7
| 2014-11-15 09:30 | 8.6 | 9.4 | 11.7
| 2014-11-15 10:00 | 8.8 | 9.4 | 11.7
| 2014-11-15 10:30 | 8.9 | 9.4 | 11.7
| 2014-11-15 11:00 | 9.7 | 9.4 | 11.7
| 2014-11-15 11:30 | 10.6 | 9.4 | 11.7
| 2014-11-15 12:00 | 11.2 | 9.4 | 11.7
| 2014-11-15 12:30 | 12.8 | 9.4 | 11.7
| 2014-11-15 13:00 | 13.4 | 9.4 | 11.7
| 2014-11-15 13:30 | 12.5 | 9.4 | 11.7
| 2014-11-15 14:00 | 12.2 | 9.4 | 11.7
| 2014-11-15 14:30 | 13 | 9.4 | 11.7
| 2014-11-15 15:00 | 12.2 | 10 | 11.7
| 2014-11-15 15:30 | 11.9 | 10 | 11.7
| 2014-11-15 16:00 | 11.7 | 10 | 11.7
| 2014-11-15 16:30 | 11.4 | 10 | 11.7
| 2014-11-15 17:00 | 11.1 | 10 | 11.7
| 2014-11-15 17:30 | 10.9 | 10 | 11.7
| 2014-11-15 18:00 | 10.7 | 10 | 11.7
| 2014-11-15 18:30 | 10.6 | 10 | 11.7
| 2014-11-15 19:00 | 10.5 | 10 | 11.7
| 2014-11-15 19:30 | 10.5 | 10 | 11.7
| 2014-11-15 20:00 | 10.3 | 10 | 11.7
| 2014-11-15 20:30 | 10.1 | 10 | 11.7
| 2014-11-15 21:00 | 9.9 | 10 | 11.7
| 2014-11-15 21:30 | 9.7 | 10 | 11.7
| 2014-11-15 22:00 | 9.8 | 10 | 11.7
| 2014-11-15 22:30 | 9.8 | 10 | 11.7
| 2014-11-15 23:00 | 9.7 | 10 | 11.7
| 2014-11-15 23:30 | 9.6 | 10 | 11.7
| 2014-11-16 | 9.6 | 10 | 11.7
| 2014-11-16 00:30 | 9.4 | 10 | 11.7
| 2014-11-16 01:00 | 9.4 | 10 | 11.7
| 2014-11-16 01:30 | 9.4 | 10 | 11.7
| 2014-11-16 02:00 | 9.3 | 10 | 11.7
| 2014-11-16 02:30 | 9.3 | 10 | 11.7
| 2014-11-16 03:00 | 9.3 | 10 | 11.7
| 2014-11-16 03:30 | 9.3 | 10 | 11.7
| 2014-11-16 04:00 | 9 | 10 | 11.7
| 2014-11-16 04:30 | 8.8 | 10 | 11.7
| 2014-11-16 05:00 | 8.7 | 10 | 11.7
| 2014-11-16 05:30 | 8.7 | 10 | 11.7
| 2014-11-16 06:00 | 8.6 | 10 | 11.7
| 2014-11-16 06:30 | 8.4 | 10 | 11.7
| 2014-11-16 07:00 | 8.2 | 10 | 11.7
| 2014-11-16 07:30 | 8.2 | 10 | 11.7
| 2014-11-16 08:00 | 8.1 | 10 | 11.7
| 2014-11-16 08:30 | 8.2 | 10 | 11.7
| 2014-11-16 09:00 | 8.3 | 10 | 11.7
| 2014-11-16 09:30 | 8.4 | 10 | 11.7
| 2014-11-16 10:00 | 8.6 | 10 | 11.7
| 2014-11-16 10:30 | 8.9 | 10 | 11.7
| 2014-11-16 11:00 | 9 | 10 | 11.7
| 2014-11-16 11:30 | 9 | 10 | 11.7
| 2014-11-16 12:00 | 9.1 | 10 | 11.7
| 2014-11-16 12:30 | 9.3 | 10 | 11.7
| 2014-11-16 13:00 | 9.4 | 10 | 11.7
| 2014-11-16 13:30 | 9.6 | 10 | 11.7
| 2014-11-16 14:00 | 10.1 | 10 | 11.7
| 2014-11-16 14:30 | 10.7 | 10 | 11.7
| 2014-11-16 15:00 | 10.8 | 10 | 11.7
| 2014-11-16 15:30 | 10.7 | 10 | 11.7
| 2014-11-16 16:00 | 10.1 | 10 | 11.7
| 2014-11-16 16:30 | 9.7 | 10 | 11.7
| 2014-11-16 17:00 | 9.4 | 10 | 11.7
| 2014-11-16 17:30 | 8.5 | 10 | 11.7
| 2014-11-16 18:00 | 8.4 | 10 | 11.7
| 2014-11-16 18:30 | 8.7 | 10 | 11.7
| 2014-11-16 19:00 | 8.8 | 10 | 11.7
| 2014-11-16 19:30 | 8.7 | 10 | 11.7
| 2014-11-16 20:00 | 8.5 | 10 | 11.7
| 2014-11-16 20:30 | 8.4 | 10 | 11.7
| 2014-11-16 21:00 | 8.5 | 10 | 11.7
| 2014-11-16 21:30 | 8.4 | 10 | 11.7
| 2014-11-16 22:00 | 8.4 | 10 | 11.7
| 2014-11-16 22:30 | 8.3 | 10 | 11.7
| 2014-11-16 23:00 | 8.4 | 10 | 11.7
| 2014-11-16 23:30 | 8.5 | 10 | 11.7
| 2014-11-17 | 8.3 | 10 | 11.7
| 2014-11-17 00:30 | 7.9 | 10 | 11.7
| 2014-11-17 01:00 | 7.9 | 10 | 11.7
| 2014-11-17 01:30 | 8 | 10 | 11.7
| 2014-11-17 02:00 | 7.7 | 10 | 11.7
| 2014-11-17 02:30 | 7.7 | 10 | 11.7
| 2014-11-17 03:00 | 7.8 | 10 | 11.7
| 2014-11-17 03:30 | 7.8 | 10 | 11.7
| 2014-11-17 04:00 | 7.7 | 10 | 11.7
| 2014-11-17 04:30 | 7.8 | 10 | 11.7
| 2014-11-17 05:00 | 7.8 | 10 | 11.7
| 2014-11-17 05:30 | 7.8 | 10 | 11.7
| 2014-11-17 06:00 | 7.6 | 9.4 | 11.7
| 2014-11-17 06:30 | 7.6 | 9.4 | 11.7
| 2014-11-17 07:00 | 7.8 | 9.4 | 11.7
| 2014-11-17 07:30 | 7.8 | 9.4 | 11.7
| 2014-11-17 08:00 | 7.7 | 9.4 | 11.7
| 2014-11-17 08:30 | 7.7 | 9.4 | 11.7
| 2014-11-17 09:00 | 8.2 | 9.4 | 11.7
| 2014-11-17 09:30 | 8.8 | 9.4 | 11.7
| 2014-11-17 10:00 | 9.4 | 9.4 | 11.7
| 2014-11-17 10:30 | 9.7 | 9.4 | 11.7
| 2014-11-17 11:00 | 10.1 | 9.4 | 11.7
| 2014-11-17 11:30 | 10.4 | 9.4 | 11.7
| 2014-11-17 12:00 | 10.9 | 9.4 | 11.7
| 2014-11-17 12:30 | 10.7 | 9.4 | 11.7
| 2014-11-17 13:00 | 10.8 | 10 | 11.7
| 2014-11-17 13:30 | 12.3 | 10 | 11.7
| 2014-11-17 14:00 | 11.8 | 10 | 11.7
| 2014-11-17 14:30 | 11.4 | 10 | 11.7
| 2014-11-17 15:00 | 11 | 10 | 11.7
| 2014-11-17 15:30 | 10.7 | 10 | 11.7
| 2014-11-17 16:00 | 9.6 | 10 | 11.7
| 2014-11-17 16:30 | 9.3 | 10 | 11.7
| 2014-11-17 17:00 | 9.2 | 10 | 11.7
| 2014-11-17 17:30 | 9.2 | 10 | 11.7
| 2014-11-17 18:00 | 9.2 | 10 | 11.7
| 2014-11-17 18:30 | 9.2 | 10 | 11.7
| 2014-11-17 19:00 | 9 | 10 | 11.7
| 2014-11-17 19:30 | 8.8 | 10 | 11.7
| 2014-11-17 20:00 | 8.4 | 10 | 11.7
| 2014-11-17 20:30 | 8.1 | 10 | 11.7
| 2014-11-17 21:00 | 7.8 | 10 | 11.7
| 2014-11-17 21:30 | 7.6 | 10 | 11.7
| 2014-11-17 22:00 | 7.5 | 10 | 11.7
| 2014-11-17 22:30 | 7.7 | 10 | 11.7
| 2014-11-17 23:00 | 7.9 | 10 | 11.7
| 2014-11-17 23:30 | 8.1 | 10 | 11.7
| 2014-11-18 | 8.2 | 10 | 11.7
| 2014-11-18 00:30 | 8.1 | 10 | 11.7
| 2014-11-18 01:00 | 8.1 | 10 | 11.7
| 2014-11-18 01:30 | 8 | 10 | 11.7
| 2014-11-18 02:00 | 8 | 10 | 11.7
| 2014-11-18 02:30 | 7.9 | 10 | 11.7
| 2014-11-18 03:00 | 7.8 | 10 | 11.7
| 2014-11-18 03:30 | 7.8 | 10 | 11.7
| 2014-11-18 04:00 | 7.8 | 10 | 11.7
| 2014-11-18 04:30 | 7.8 | 10 | 11.7
| 2014-11-18 05:00 | 7.7 | 10 | 11.7
| 2014-11-18 05:30 | 7.7 | 10 | 11.7
| 2014-11-18 06:00 | 7.6 | 10 | 11.7
| 2014-11-18 06:30 | 7.6 | 9.4 | 11.7
| 2014-11-18 07:00 | 7.7 | 9.4 | 11.7
| 2014-11-18 07:30 | 7.7 | 9.4 | 11.7
| 2014-11-18 08:00 | 7.8 | 9.4 | 11.7
| 2014-11-18 08:30 | 7.8 | 9.4 | 11.7
| 2014-11-18 09:00 | 7.8 | 9.4 | 11.7
| 2014-11-18 09:30 | 7.8 | 9.4 | 11.7
| 2014-11-18 10:00 | 7.9 | 9.4 | 11.7
| 2014-11-18 10:30 | 8.2 | 9.4 | 11.7
| 2014-11-18 11:00 | 8.4 | 9.4 | 11.7
| 2014-11-18 11:30 | 8.9 | 9.4 | 11.7
| 2014-11-18 12:00 | 9.1 | 9.4 | 11.7
| 2014-11-18 12:30 | 9 | 9.4 | 11.7
| 2014-11-18 13:00 | 9.2 | 9.4 | 11.7
| 2014-11-18 13:30 | 9.2 | 9.4 | 11.7
| 2014-11-18 14:00 | 8.9 | 9.4 | 11.7
| 2014-11-18 14:30 | 8.8 | 9.4 | 11.7
| 2014-11-18 15:00 | 8.7 | 9.4 | 11.7
| 2014-11-18 15:30 | 8.7 | 9.4 | 11.7
| 2014-11-18 16:00 | 8.7 | 9.4 | 11.7
| 2014-11-18 16:30 | 8.6 | 10 | 11.7
| 2014-11-18 17:00 | 8.5 | 10 | 11.7
| 2014-11-18 17:30 | 8.4 | 10 | 11.7
| 2014-11-18 18:00 | 8.4 | 10 | 11.7
| 2014-11-18 18:30 | 8.3 | 10 | 11.7
| 2014-11-18 19:00 | 8.2 | 10 | 11.7
| 2014-11-18 19:30 | 8.2 | 10 | 11.7
| 2014-11-18 20:00 | 8.2 | 9.4 | 11.7
| 2014-11-18 20:30 | 8.1 | 9.4 | 11.7
| 2014-11-18 21:00 | 8 | 9.4 | 11.7
| 2014-11-18 21:30 | 7.8 | 9.4 | 11.7
| 2014-11-18 22:00 | 7.7 | 9.4 | 11.7
| 2014-11-18 22:30 | 7.6 | 9.4 | 11.7
| 2014-11-18 23:00 | 7.5 | 9.4 | 11.7
| 2014-11-18 23:30 | 7.4 | 9.4 | 11.7
| 2014-11-19 | 7.3 | 9.4 | 11.7
| 2014-11-19 00:30 | 7.3 | 9.4 | 11.7
| 2014-11-19 01:00 | 7.3 | 9.4 | 11.7
| 2014-11-19 01:30 | 7.4 | 9.4 | 11.7
| 2014-11-19 02:00 | 7.4 | 9.4 | 11.7
| 2014-11-19 02:30 | 7.4 | 9.4 | 11.7
| 2014-11-19 03:00 | 7.4 | 9.4 | 11.7
| 2014-11-19 03:30 | 7.5 | 9.4 | 11.7
| 2014-11-19 04:00 | 7.4 | 9.4 | 11.7
| 2014-11-19 04:30 | 7.4 | 9.4 | 11.7
| 2014-11-19 05:00 | 7.3 | 9.4 | 11.7
| 2014-11-19 05:30 | 7.3 | 9.4 | 11.7
| 2014-11-19 06:00 | 7.3 | 9.4 | 11.7
| 2014-11-19 06:30 | 7.3 | 9.4 | 11.7
| 2014-11-19 07:00 | 7.2 | 9.4 | 11.7
| 2014-11-19 07:30 | 7.2 | 9.4 | 11.7
| 2014-11-19 08:00 | 7.2 | 9.4 | 11.7
| 2014-11-19 08:30 | 7.3 | 9.4 | 11.7
| 2014-11-19 09:00 | 7.4 | 9.4 | 11.7
| 2014-11-19 09:30 | 7.6 | 9.4 | 11.7
| 2014-11-19 10:00 | 7.7 | 9.4 | 11.7
| 2014-11-19 10:30 | 8.1 | 9.4 | 11.7
| 2014-11-19 11:00 | 8.6 | 9.4 | 11.7
| 2014-11-19 11:30 | 8.7 | 9.4 | 11.7
| 2014-11-19 12:00 | 9 | 9.4 | 11.7
| 2014-11-19 12:30 | 9.2 | 9.4 | 11.7
| 2014-11-19 13:00 | 9.3 | 9.4 | 11.7
| 2014-11-19 13:30 | 9.6 | 9.4 | 11.7
| 2014-11-19 14:00 | 9.6 | 9.4 | 11.7
| 2014-11-19 14:30 | 9.4 | 9.4 | 11.7
| 2014-11-19 15:00 | 9.4 | 9.4 | 11.7
| 2014-11-19 15:30 | 9.4 | 9.4 | 11.7
| 2014-11-19 16:00 | 9.1 | 9.4 | 11.7
| 2014-11-19 16:30 | 8.7 | 10 | 11.7
| 2014-11-19 17:00 | 8.4 | 10 | 11.7
| 2014-11-19 17:30 | 8.2 | 10 | 11.7
| 2014-11-19 18:00 | 7.5 | 10 | 11.7
| 2014-11-19 18:30 | 7 | 10 | 11.7
| 2014-11-19 19:00 | 6.8 | 10 | 11.7
| 2014-11-19 19:30 | 6.3 | 10 | 11.7
| 2014-11-19 20:00 | 6.3 | 10 | 11.7
| 2014-11-19 20:30 | 6.9 | 9.4 | 11.7
| 2014-11-19 21:00 | 6.4 | 9.4 | 11.7
| 2014-11-19 21:30 | 5.8 | 9.4 | 11.7
| 2014-11-19 22:00 | 5.3 | 9.4 | 11.7
| 2014-11-19 22:30 | 5.3 | 9.4 | 11.7
| 2014-11-19 23:00 | 5.3 | 9.4 | 11.7
| 2014-11-19 23:30 | 5.2 | 9.4 | 11.7
| 2014-11-20 | 4.6 | 9.4 | 11.7
| 2014-11-20 00:30 | 4.2 | 9.4 | 11.7
| 2014-11-20 01:00 | 3.8 | 9.4 | 11.7
| 2014-11-20 01:30 | 3.6 | 9.4 | 11.7
| 2014-11-20 02:00 | 3 | 9.4 | 11.7
| 2014-11-20 02:30 | 2.7 | 8.9 | 11.7
| 2014-11-20 03:00 | 2.5 | 8.9 | 11.7
| 2014-11-20 03:30 | 2.8 | 8.9 | 11.7
| 2014-11-20 04:00 | 3.8 | 8.9 | 11.7
| 2014-11-20 04:30 | 4.1 | 8.9 | 11.7
| 2014-11-20 05:00 | 3.7 | 8.9 | 11.7
| 2014-11-20 05:30 | 3.1 | 8.9 | 11.7
| 2014-11-20 06:00 | 2.5 | 8.9 | 11.7
| 2014-11-20 06:30 | 2.6 | 8.9 | 11.7
| 2014-11-20 07:00 | 3.2 | 8.3 | 11.7
| 2014-11-20 07:30 | 3.1 | 8.3 | 11.7
| 2014-11-20 08:00 | 3.2 | 8.3 | 11.7
| 2014-11-20 08:30 | 3.8 | 8.3 | 11.7
| 2014-11-20 09:00 | 4.9 | 8.3 | 11.7
| 2014-11-20 09:30 | 5.4 | 8.3 | 11.7
| 2014-11-20 10:00 | 6 | 8.3 | 11.7
| 2014-11-20 10:30 | 6.8 | 8.3 | 11.7
| 2014-11-20 11:00 | 7.1 | 8.3 | 11.1
| 2014-11-20 11:30 | 7 | 8.3 | 11.1
| 2014-11-20 12:00 | 8.2 | 8.3 | 11.1
| 2014-11-20 12:30 | 9 | 8.3 | 11.1
| 2014-11-20 13:00 | 9.1 | 8.3 | 11.1
| 2014-11-20 13:30 | 9.7 | 8.3 | 11.1
| 2014-11-20 14:00 | 9.2 | 8.3 | 11.1
| 2014-11-20 14:30 | 9.2 | 8.3 | 11.1
| 2014-11-20 15:00 | 9.1 | 8.3 | 11.1
| 2014-11-20 15:30 | 8.9 | 8.3 | 11.1
| 2014-11-20 16:00 | 8.7 | 8.3 | 11.1
| 2014-11-20 16:30 | 8.1 | 8.3 | 11.1
| 2014-11-20 17:00 | 7.6 | 8.3 | 11.1
| 2014-11-20 17:30 | 7.4 | 8.9 | 11.1
| 2014-11-20 18:00 | 7.2 | 8.9 | 11.1
| 2014-11-20 18:30 | 6.8 | 8.9 | 11.1
| 2014-11-20 19:00 | 6.4 | 8.9 | 11.1
| 2014-11-20 19:30 | 5.9 | 8.9 | 11.1
| 2014-11-20 20:00 | 5.3 | 8.9 | 11.1
| 2014-11-20 20:30 | 4.9 | 8.9 | 11.1
| 2014-11-20 21:00 | 4.7 | 8.9 | 11.1
| 2014-11-20 21:30 | 4.3 | 8.3 | 11.1
| 2014-11-20 22:00 | 3.9 | 8.3 | 11.1
| 2014-11-20 22:30 | 3.6 | 8.3 | 11.1
| 2014-11-20 23:00 | 3.3 | 8.3 | 11.1
| 2014-11-20 23:30 | 3 | 8.3 | 11.1
| 2014-11-21 | 2.8 | 8.3 | 11.1
| 2014-11-21 00:30 | 2.4 | 8.3 | 11.1
| 2014-11-21 01:00 | 2.7 | 8.3 | 11.1
| 2014-11-21 01:30 | 2.8 | 8.3 | 11.1
| 2014-11-21 02:00 | 2.7 | 7.8 | 11.1
| 2014-11-21 02:30 | 2.7 | 7.8 | 11.1
| 2014-11-21 03:00 | 2.6 | 7.8 | 11.1
| 2014-11-21 03:30 | 2.3 | 7.8 | 11.1
| 2014-11-21 04:00 | 2.2 | 7.8 | 11.1
| 2014-11-21 04:30 | 2.1 | 7.8 | 11.1
| 2014-11-21 05:00 | 1.7 | 7.8 | 11.1
| 2014-11-21 05:30 | 1.2 | 7.2 | 11.1
| 2014-11-21 06:00 | 1.4 | 7.2 | 11.1
| 2014-11-21 06:30 | 1.5 | 7.2 | 11.1
| 2014-11-21 07:00 | 0.9 | 7.2 | 11.1
| 2014-11-21 07:30 | 1.2 | 7.2 | 11.1
| 2014-11-21 08:00 | 1.2 | 7.2 | 11.1
| 2014-11-21 08:30 | 1.6 | 7.2 | 11.1
| 2014-11-21 09:00 | 2.3 | 6.7 | 11.1
| 2014-11-21 09:30 | 3.6 | 6.7 | 11.1
| 2014-11-21 10:00 | 4.9 | 6.7 | 11.1
| 2014-11-21 10:30 | 6.1 | 6.7 | 11.1
| 2014-11-21 11:00 | 6.9 | 6.7 | 11.1
| 2014-11-21 11:30 | 8.3 | 6.7 | 11.1
| 2014-11-21 12:00 | 9.7 | 6.7 | 11.1
| 2014-11-21 12:30 | 10.2 | 6.7 | 11.1
| 2014-11-21 13:00 | 10.3 | 6.7 | 11.1
| 2014-11-21 13:30 | 10.6 | 6.7 | 11.1
| 2014-11-21 14:00 | 10.3 | 6.7 | 11.1
| 2014-11-21 14:30 | 10 | 6.7 | 11.1
| 2014-11-21 15:00 | 9.4 | 6.7 | 11.1
| 2014-11-21 15:30 | 8.3 | 7.2 | 11.1
| 2014-11-21 16:00 | 7.6 | 7.2 | 11.1
| 2014-11-21 16:30 | 6.8 | 7.2 | 11.1
| 2014-11-21 17:00 | 6.2 | 7.2 | 11.1
| 2014-11-21 17:30 | 5.5 | 7.2 | 11.1
| 2014-11-21 18:00 | 4.7 | 7.2 | 11.1
| 2014-11-21 18:30 | 3.9 | 7.2 | 11.1
| 2014-11-21 19:00 | 3.4 | 7.2 | 11.1
| 2014-11-21 19:30 | 3 | 7.2 | 11.1
| 2014-11-21 20:00 | 2.6 | 7.2 | 11.1
| 2014-11-21 20:30 | 2.7 | 7.2 | 11.1
| 2014-11-21 21:00 | 2.5 | 7.2 | 11.1
| 2014-11-21 21:30 | 2.2 | 6.7 | 11.1
| 2014-11-21 22:00 | 2 | 6.7 | 11.1
| 2014-11-21 22:30 | 1.8 | 6.7 | 11.1
| 2014-11-21 23:00 | 1.5 | 6.7 | 11.1
| 2014-11-21 23:30 | 1.5 | 6.7 | 11.1
| 2014-11-22 | 1.3 | 6.7 | 11.1
| 2014-11-22 00:30 | 1.3 | 6.7 | 11.1
| 2014-11-22 01:00 | 1.1 | 6.7 | 11.1
| 2014-11-22 01:30 | 0.8 | 6.7 | 11.1
| 2014-11-22 02:00 | 0.7 | 6.7 | 11.1
| 2014-11-22 02:30 | 0.6 | 6.7 | 11.1
| 2014-11-22 03:00 | 0.3 | 6.7 | 11.1
| 2014-11-22 03:30 | 0.5 | 6.1 | 11.1
| 2014-11-22 04:00 | 0.8 | 6.1 | 11.1
| 2014-11-22 04:30 | 0.6 | 6.1 | 11.1
| 2014-11-22 05:00 | 0.6 | 6.1 | 11.1
| 2014-11-22 05:30 | 0.8 | 6.1 | 11.1
| 2014-11-22 06:00 | 1.2 | 6.1 | 11.1
| 2014-11-22 06:30 | 1.4 | 6.1 | 11.1
| 2014-11-22 07:00 | 2.2 | 6.1 | 11.1
| 2014-11-22 07:30 | 2.5 | 6.1 | 11.1
| 2014-11-22 08:00 | 2.7 | 6.1 | 11.1
| 2014-11-22 08:30 | 3 | 6.1 | 11.1
| 2014-11-22 09:00 | 3.4 | 6.1 | 11.1
| 2014-11-22 09:30 | 3.8 | 6.1 | 11.1
| 2014-11-22 10:00 | 4.3 | 6.1 | 11.1
| 2014-11-22 10:30 | 5 | 6.1 | 11.1
| 2014-11-22 11:00 | 5.6 | 6.1 | 11.1
| 2014-11-22 11:30 | 6.4 | 6.1 | 11.1
| 2014-11-22 12:00 | 7.8 | 6.1 | 11.1
| 2014-11-22 12:30 | 8.3 | 6.1 | 11.1
| 2014-11-22 13:00 | 8.8 | 6.1 | 11.1
| 2014-11-22 13:30 | 9.4 | 6.1 | 11.1
| 2014-11-22 14:00 | 9.6 | 6.7 | 11.1
| 2014-11-22 14:30 | 9.9 | 6.7 | 11.1
| 2014-11-22 15:00 | 10 | 6.7 | 10.6
| 2014-11-22 15:30 | 9.8 | 6.7 | 10.6
| 2014-11-22 16:00 | 9 | 6.7 | 10.6
| 2014-11-22 16:30 | 7.9 | 6.7 | 10.6
| 2014-11-22 17:00 | 6.9 | 6.7 | 10.6
| 2014-11-22 17:30 | 6.3 | 6.7 | 10.6
| 2014-11-22 18:00 | 5.9 | 6.7 | 10.6
| 2014-11-22 18:30 | 5.3 | 6.7 | 10.6
| 2014-11-22 19:00 | 4.9 | 6.7 | 10.6
| 2014-11-22 19:30 | 4.7 | 6.7 | 10.6
| 2014-11-22 20:00 | 4.2 | 6.7 | 10.6
| 2014-11-22 20:30 | 3.7 | 6.7 | 10.6
| 2014-11-22 21:00 | 3.2 | 6.7 | 10.6
| 2014-11-22 21:30 | 2.7 | 6.7 | 10.6
| 2014-11-22 22:00 | 2.4 | 6.7 | 10.6
| 2014-11-22 22:30 | 2.4 | 6.7 | 10.6
| 2014-11-22 23:00 | 2.6 | 6.7 | 10.6
| 2014-11-22 23:30 | 2.6 | 6.7 | 10.6
| 2014-11-23 | 3.1 | 6.7 | 10.6
| 2014-11-23 00:30 | 3.3 | 6.7 | 10.6
| 2014-11-23 01:00 | 3.3 | 6.7 | 10.6
| 2014-11-23 01:30 | 2.7 | 6.7 | 10.6
| 2014-11-23 02:00 | 2.3 | 6.1 | 10.6
| 2014-11-23 02:30 | 2.2 | 6.1 | 10.6
| 2014-11-23 03:00 | 1.9 | 6.1 | 10.6
| 2014-11-23 03:30 | 1.9 | 6.1 | 10.6
| 2014-11-23 04:00 | 1.8 | 6.1 | 10.6
| 2014-11-23 04:30 | 1.1 | 6.1 | 10.6
| 2014-11-23 05:00 | 1.6 | 6.1 | 10.6
| 2014-11-23 05:30 | 2.2 | 6.1 | 10.6
| 2014-11-23 06:00 | 2.4 | 6.1 | 10.6
| 2014-11-23 06:30 | 2.6 | 6.1 | 10.6
| 2014-11-23 07:00 | 2.7 | 6.1 | 10.6
| 2014-11-23 07:30 | 3.1 | 6.1 | 10.6
| 2014-11-23 08:00 | 3.4 | 6.1 | 10.6
| 2014-11-23 08:30 | 3.7 | 6.1 | 10.6
| 2014-11-23 09:00 | 3.8 | 6.1 | 10.6
| 2014-11-23 09:30 | 3.8 | 6.1 | 10.6
| 2014-11-23 10:00 | 3.8 | 6.1 | 10.6
| 2014-11-23 10:30 | 3.9 | 6.1 | 10.6
| 2014-11-23 11:00 | 4.2 | 6.1 | 10.6
| 2014-11-23 11:30 | 4.4 | 6.1 | 10.6
| 2014-11-23 12:00 | 5.1 | 6.1 | 10.6
| 2014-11-23 12:30 | 5.2 | 6.1 | 10.6
| 2014-11-23 13:00 | 5.8 | 6.1 | 10.6
| 2014-11-23 13:30 | 5.9 | 6.1 | 10.6
| 2014-11-23 14:00 | 5.9 | 6.1 | 10.6
| 2014-11-23 14:30 | 5.7 | 6.7 | 10.6
| 2014-11-23 15:00 | 5.6 | 6.7 | 10.6
| 2014-11-23 15:30 | 5.3 | 6.7 | 10.6
| 2014-11-23 16:00 | 5.3 | 6.7 | 10.6
| 2014-11-23 16:30 | 5.1 | 6.7 | 10.6
| 2014-11-23 17:00 | 5.1 | 6.7 | 10.6
| 2014-11-23 17:30 | 4.9 | 6.7 | 10.6
| 2014-11-23 18:00 | 4.9 | 6.7 | 10.6
| 2014-11-23 18:30 | 4.9 | 6.7 | 10.6
| 2014-11-23 19:00 | 4.8 | 6.7 | 10.6
| 2014-11-23 19:30 | 4.7 | 6.7 | 10.6
| 2014-11-23 20:00 | 4.6 | 6.7 | 10.6
| 2014-11-23 20:30 | 4.5 | 6.7 | 10.6
| 2014-11-23 21:00 | 4.5 | 6.7 | 10.6
| 2014-11-23 21:30 | 4.5 | 6.7 | 10.6
| 2014-11-23 22:00 | 4.3 | 6.7 | 10.6
| 2014-11-23 22:30 | 4.3 | 6.7 | 10.6
| 2014-11-23 23:00 | 4.3 | 6.7 | 10.6
| 2014-11-23 23:30 | 4.4 | 6.7 | 10.6
| 2014-11-24 | 4.4 | 6.7 | 10.6
| 2014-11-24 00:30 | 4.4 | 6.7 | 10.6
| 2014-11-24 01:00 | 4.5 | 6.7 | 10.6
| 2014-11-24 01:30 | 4.6 | 6.7 | 10.6
| 2014-11-24 02:00 | 4.6 | 6.7 | 10.6
| 2014-11-24 02:30 | 4.4 | 6.7 | 10.6
| 2014-11-24 03:00 | 4.2 | 6.7 | 10.6
| 2014-11-24 03:30 | 4.5 | 6.7 | 10.6
| 2014-11-24 04:00 | 4.4 | 6.7 | 10.6
| 2014-11-24 04:30 | 4.2 | 6.7 | 10.6
| 2014-11-24 05:00 | 3.7 | 6.7 | 10.6
| 2014-11-24 05:30 | 3.4 | 6.7 | 10.6
| 2014-11-24 06:00 | 3.2 | 6.7 | 10.6
| 2014-11-24 06:30 | 3.2 | 6.7 | 10.6
| 2014-11-24 07:00 | 3.8 | 6.7 | 10
| 2014-11-24 07:30 | 4.2 | 6.7 | 10
| 2014-11-24 08:00 | 4.7 | 6.7 | 10
| 2014-11-24 08:30 | 5.1 | 6.7 | 10
| 2014-11-24 09:00 | 5.4 | 6.7 | 10
| 2014-11-24 09:30 | 5.7 | 6.7 | 10
| 2014-11-24 10:00 | 6.1 | 6.7 | 10
| 2014-11-24 10:30 | 6.3 | 6.7 | 10
| 2014-11-24 11:00 | 6.5 | 6.7 | 10
| 2014-11-24 11:30 | 6.7 | 6.7 | 10
| 2014-11-24 12:00 | 6.9 | 6.7 | 10
| 2014-11-24 12:30 | 7.4 | 6.7 | 10
| 2014-11-24 13:00 | 7.7 | 6.7 | 10
| 2014-11-24 13:30 | 8.2 | 6.7 | 10
| 2014-11-24 14:00 | 8.5 | 6.7 | 10
| 2014-11-24 14:30 | 8.7 | 6.7 | 10
| 2014-11-24 15:00 | 8.8 | 7.2 | 10
| 2014-11-24 15:30 | 9.1 | 7.2 | 10
| 2014-11-24 16:00 | 9 | 7.2 | 10
| 2014-11-24 16:30 | 8.9 | 7.2 | 10
| 2014-11-24 17:00 | 8.7 | 7.2 | 10
| 2014-11-24 17:30 | 8.6 | 7.2 | 10
| 2014-11-24 18:00 | 8.4 | 7.2 | 10
| 2014-11-24 18:30 | 8.5 | 7.2 | 10
| 2014-11-24 19:00 | 8.5 | 7.2 | 10
| 2014-11-24 19:30 | 7.6 | 7.2 | 10
| 2014-11-24 20:00 | 6.3 | 7.2 | 10
| 2014-11-24 20:30 | 5.7 | 7.2 | 10
| 2014-11-24 21:00 | 5.1 | 7.2 | 10
| 2014-11-24 21:30 | 4.1 | 7.2 | 10
| 2014-11-24 22:00 | 3.4 | 7.2 | 10
| 2014-11-24 22:30 | 3.6 | 7.2 | 10
| 2014-11-24 23:00 | 3.2 | 7.2 | 10
| 2014-11-24 23:30 | 2.6 | 7.2 | 10
| 2014-11-25 | 2.3 | 7.2 | 10
| 2014-11-25 00:30 | 2 | 7.2 | 10
| 2014-11-25 01:00 | 1.9 | 6.7 | 10
| 2014-11-25 01:30 | 2.1 | 6.7 | 10
| 2014-11-25 02:00 | 1.9 | 6.7 | 10
| 2014-11-25 02:30 | 1.7 | 6.7 | 10
| 2014-11-25 03:00 | 1.7 | 6.7 | 10
| 2014-11-25 03:30 | 1.7 | 6.7 | 10
| 2014-11-25 04:00 | 1.6 | 6.7 | 10
| 2014-11-25 04:30 | 1.2 | 6.1 | 10
| 2014-11-25 05:00 | 0.9 | 6.1 | 10
| 2014-11-25 05:30 | 0.9 | 6.1 | 10
| 2014-11-25 06:00 | 0.7 | 6.1 | 10
| 2014-11-25 06:30 | 0.7 | 6.1 | 10
| 2014-11-25 07:00 | 0.8 | 6.1 | 10
| 2014-11-25 07:30 | 0.8 | 6.1 | 10
| 2014-11-25 08:00 | 0.8 | 6.1 | 10
| 2014-11-25 08:30 | 0.8 | 5.6 | 10
| 2014-11-25 09:00 | 1.2 | 5.6 | 10
| 2014-11-25 09:30 | 2.3 | 5.6 | 10
| 2014-11-25 10:00 | 3.3 | 5.6 | 10
| 2014-11-25 10:30 | 4.2 | 5.6 | 10
| 2014-11-25 11:00 | 4.6 | 5.6 | 10
| 2014-11-25 11:30 | 4.4 | 5.6 | 10
| 2014-11-25 12:00 | 4.6 | 5.6 | 10
| 2014-11-25 12:30 | 4.9 | 5.6 | 10
| 2014-11-25 13:00 | 5.2 | 5.6 | 10
| 2014-11-25 13:30 | 5.3 | 5.6 | 10
| 2014-11-25 14:00 | 5.4 | 5.6 | 10
| 2014-11-25 14:30 | 5.3 | 5.6 | 10
| 2014-11-25 15:00 | 5.3 | 5.6 | 10
| 2014-11-25 15:30 | 5.4 | 5.6 | 10
| 2014-11-25 16:00 | 5.3 | 5.6 | 10
| 2014-11-25 16:30 | 5.2 | 5.6 | 10
| 2014-11-25 17:00 | 5.3 | 5.6 | 10
| 2014-11-25 17:30 | 5.3 | 6.1 | 10
| 2014-11-25 18:00 | 5.3 | 6.1 | 10
| 2014-11-25 18:30 | 5.2 | 6.1 | 10
| 2014-11-25 19:00 | 5.2 | 6.1 | 10
| 2014-11-25 19:30 | 5.4 | 6.1 | 10
| 2014-11-25 20:00 | 5.6 | 6.1 | 10
| 2014-11-25 20:30 | 5.7 | 6.1 | 10
| 2014-11-25 21:00 | 5.4 | 6.1 | 10
| 2014-11-25 21:30 | 5.3 | 6.1 | 10
| 2014-11-25 22:00 | 5.2 | 6.1 | 10
| 2014-11-25 22:30 | 4.9 | 6.1 | 10
| 2014-11-25 23:00 | 4.9 | 6.1 | 10
| 2014-11-25 23:30 | 5.1 | 6.1 | 10
| 2014-11-26 | 4.8 | 6.1 | 10
| 2014-11-26 00:30 | 4.4 | 6.1 | 10
| 2014-11-26 01:00 | 3.9 | 6.1 | 10
| 2014-11-26 01:30 | 3.6 | 6.1 | 10
| 2014-11-26 02:00 | 3.7 | 6.1 | 10
| 2014-11-26 02:30 | 3.4 | 6.1 | 10
| 2014-11-26 03:00 | 3.4 | 6.1 | 10
| 2014-11-26 03:30 | 3.1 | 6.1 | 10
| 2014-11-26 04:00 | 3 | 5.6 | 10
| 2014-11-26 04:30 | 3 | 5.6 | 10
| 2014-11-26 05:00 | 3.1 | 5.6 | 10
| 2014-11-26 05:30 | 3.3 | 5.6 | 10
| 2014-11-26 06:00 | 3.4 | 5.6 | 10
| 2014-11-26 06:30 | 3.5 | 5.6 | 10
| 2014-11-26 07:00 | 3.6 | 5.6 | 10
| 2014-11-26 07:30 | 3.6 | 5.6 | 10
| 2014-11-26 08:00 | 3.6 | 5.6 | 10
| 2014-11-26 08:30 | 3.7 | 5.6 | 10
| 2014-11-26 09:00 | 3.9 | 5.6 | 10
| 2014-11-26 09:30 | 4.1 | 5.6 | 10
| 2014-11-26 10:00 | 4.3 | 5.6 | 10
| 2014-11-26 10:30 | 4.8 | 5.6 | 10
| 2014-11-26 11:00 | 5.1 | 5.6 | 10
| 2014-11-26 11:30 | 5.2 | 5.6 | 10
| 2014-11-26 12:00 | 5.5 | 5.6 | 10
| 2014-11-26 12:30 | 5.5 | 5.6 | 10
| 2014-11-26 13:00 | 5.5 | 5.6 | 10
| 2014-11-26 13:30 | 5.4 | 5.6 | 10
| 2014-11-26 14:00 | 5.5 | 5.6 | 10
| 2014-11-26 14:30 | 5.8 | 6.1 | 10
| 2014-11-26 15:00 | 5.7 | 6.1 | 10
| 2014-11-26 15:30 | 5.6 | 6.1 | 9.4
| 2014-11-26 16:00 | 5.5 | 6.1 | 9.4
| 2014-11-26 16:30 | 5.4 | 6.1 | 9.4
| 2014-11-26 17:00 | 5.3 | 6.1 | 9.4
| 2014-11-26 17:30 | 5.3 | 6.1 | 9.4
| 2014-11-26 18:00 | 5.4 | 6.1 | 9.4
| 2014-11-26 18:30 | 5.4 | 6.1 | 9.4
| 2014-11-26 19:00 | 5.4 | 6.1 | 9.4
| 2014-11-26 19:30 | 5.4 | 6.1 | 9.4
| 2014-11-26 20:00 | 5.5 | 6.1 | 9.4
| 2014-11-26 20:30 | 5.5 | 6.1 | 9.4
| 2014-11-26 21:00 | 5.6 | 6.1 | 9.4
| 2014-11-26 21:30 | 5.5 | 6.1 | 9.4
| 2014-11-26 22:00 | 5.6 | 6.1 | 9.4
| 2014-11-26 22:30 | 5.5 | 6.1 | 9.4
| 2014-11-26 23:00 | 5.5 | 6.1 | 9.4
| 2014-11-26 23:30 | 5.4 | 6.1 | 9.4
| 2014-11-27 | 5.4 | 6.1 | 9.4
| 2014-11-27 00:30 | 5.4 | 6.1 | 9.4
| 2014-11-27 01:00 | 5.4 | 6.1 | 9.4
| 2014-11-27 01:30 | 5.3 | 6.1 | 9.4
| 2014-11-27 02:00 | 5.3 | 6.1 | 9.4
| 2014-11-27 02:30 | 5.2 | 6.1 | 9.4
| 2014-11-27 03:00 | 5.2 | 6.1 | 9.4
| 2014-11-27 03:30 | 5.2 | 6.1 | 9.4
| 2014-11-27 04:00 | 5.1 | 6.1 | 9.4
| 2014-11-27 04:30 | 5.1 | 6.1 | 9.4
| 2014-11-27 05:00 | 5 | 6.1 | 9.4
| 2014-11-27 05:30 | 4.9 | 6.1 | 9.4
| 2014-11-27 06:00 | 4.8 | 6.1 | 9.4
| 2014-11-27 06:30 | 4.8 | 6.1 | 9.4
| 2014-11-27 07:00 | 4.9 | 6.1 | 9.4
| 2014-11-27 07:30 | 4.9 | 6.1 | 9.4
| 2014-11-27 08:00 | 4.9 | 6.1 | 9.4
| 2014-11-27 08:30 | 4.9 | 6.1 | 9.4
| 2014-11-27 09:00 | 5.1 | 6.1 | 9.4
| 2014-11-27 09:30 | 5.3 | 6.1 | 9.4
| 2014-11-27 10:00 | 5.8 | 6.1 | 9.4
| 2014-11-27 10:30 | 6.1 | 6.1 | 9.4
| 2014-11-27 11:00 | 6.6 | 6.1 | 9.4
| 2014-11-27 11:30 | 6.8 | 6.1 | 9.4
| 2014-11-27 12:00 | 6.9 | 6.1 | 9.4
| 2014-11-27 12:30 | 7.1 | 6.1 | 9.4
| 2014-11-27 13:00 | 7.2 | 6.7 | 9.4
| 2014-11-27 13:30 | 7.4 | 6.7 | 9.4
| 2014-11-27 14:00 | 7.3 | 6.7 | 9.4
| 2014-11-27 14:30 | 6.9 | 6.7 | 9.4
| 2014-11-27 15:00 | 6.7 | 6.7 | 9.4
| 2014-11-27 15:30 | 6.4 | 6.7 | 9.4
| 2014-11-27 16:00 | 6.1 | 6.7 | 9.4
| 2014-11-27 16:30 | 5.8 | 6.7 | 9.4
| 2014-11-27 17:00 | 5.7 | 6.7 | 9.4
| 2014-11-27 17:30 | 5.6 | 6.7 | 9.4
| 2014-11-27 18:00 | 5.6 | 6.7 | 9.4
| 2014-11-27 18:30 | 5.6 | 6.7 | 9.4
| 2014-11-27 19:00 | 5.6 | 6.7 | 9.4
| 2014-11-27 19:30 | 5.6 | 6.7 | 9.4
| 2014-11-27 20:00 | 5.7 | 6.7 | 9.4
| 2014-11-27 20:30 | 5.3 | 6.7 | 9.4
| 2014-11-27 21:00 | 4.9 | 6.7 | 9.4
| 2014-11-27 21:30 | 4.7 | 6.7 | 9.4
| 2014-11-27 22:00 | 4.3 | 6.7 | 9.4
| 2014-11-27 22:30 | 3.7 | 6.7 | 9.4
| 2014-11-27 23:00 | 3.3 | 6.7 | 9.4
| 2014-11-27 23:30 | 3.2 | 6.7 | 9.4
| 2014-11-28 | 2.9 | 6.7 | 9.4
| 2014-11-28 00:30 | 3.2 | 6.7 | 9.4
| 2014-11-28 01:00 | 3 | 6.7 | 9.4
| 2014-11-28 01:30 | 2.9 | 6.7 | 9.4
| 2014-11-28 02:00 | 2.9 | 6.7 | 9.4
| 2014-11-28 02:30 | 2.9 | 6.1 | 9.4
| 2014-11-28 03:00 | 2.8 | 6.1 | 9.4
| 2014-11-28 03:30 | 2.8 | 6.1 | 9.4
| 2014-11-28 04:00 | 2.7 | 6.1 | 9.4
| 2014-11-28 04:30 | 2.6 | 6.1 | 9.4
| 2014-11-28 05:00 | 2.6 | 6.1 | 9.4
| 2014-11-28 05:30 | 2.7 | 6.1 | 9.4
| 2014-11-28 06:00 | 2.4 | 6.1 | 9.4
| 2014-11-28 06:30 | 2.1 | 6.1 | 9.4
| 2014-11-28 07:00 | 1.7 | 5.6 | 9.4
| 2014-11-28 07:30 | 2.2 | 5.6 | 9.4
| 2014-11-28 08:00 | 3.1 | 5.6 | 9.4
| 2014-11-28 08:30 | 4.1 | 5.6 | 9.4
| 2014-11-28 09:00 | 4.6 | 5.6 | 9.4
| 2014-11-28 09:30 | 4.8 | 5.6 | 9.4
| 2014-11-28 10:00 | 4.9 | 5.6 | 9.4
| 2014-11-28 10:30 | 5.1 | 5.6 | 9.4
| 2014-11-28 11:00 | 5.3 | 5.6 | 9.4
| 2014-11-28 11:30 | 5.3 | 5.6 | 9.4
| 2014-11-28 12:00 | 5.3 | 5.6 | 9.4
| 2014-11-28 12:30 | 5.3 | 5.6 | 9.4
| 2014-11-28 13:00 | 5.2 | 5.6 | 9.4
| 2014-11-28 13:30 | 5.1 | 5.6 | 9.4
| 2014-11-28 14:00 | 5.1 | 5.6 | 9.4
| 2014-11-28 14:30 | 5.1 | 5.6 | 9.4
| 2014-11-28 15:00 | 5 | 6.1 | 9.4
| 2014-11-28 15:30 | 4.9 | 6.1 | 9.4
| 2014-11-28 16:00 | 4.8 | 6.1 | 9.4
| 2014-11-28 16:30 | 4.8 | 6.1 | 9.4
| 2014-11-28 17:00 | 4.7 | 6.1 | 9.4
| 2014-11-28 17:30 | 4.6 | 6.1 | 9.4
| 2014-11-28 18:00 | 4.6 | 6.1 | 9.4
| 2014-11-28 18:30 | 4.5 | 6.1 | 9.4
| 2014-11-28 19:00 | 4.5 | 6.1 | 9.4
| 2014-11-28 19:30 | 4.5 | 6.1 | 9.4
| 2014-11-28 20:00 | 4.4 | 6.1 | 9.4
| 2014-11-28 20:30 | 4.4 | 6.1 | 9.4
| 2014-11-28 21:00 | 4.4 | 6.1 | 9.4
| 2014-11-28 21:30 | 4.3 | 6.1 | 9.4
| 2014-11-28 22:00 | 4.3 | 6.1 | 9.4
| 2014-11-28 22:30 | 4.2 | 6.1 | 9.4
| 2014-11-28 23:00 | 4.1 | 6.1 | 9.4
| 2014-11-28 23:30 | 4.1 | 6.1 | 9.4
| 2014-11-29 | 4.1 | 6.1 | 9.4
| 2014-11-29 00:30 | 4 | 6.1 | 9.4
| 2014-11-29 01:00 | 4 | 6.1 | 9.4
| 2014-11-29 01:30 | 3.9 | 6.1 | 9.4
| 2014-11-29 02:00 | 3.9 | 6.1 | 9.4
| 2014-11-29 02:30 | 3.8 | 6.1 | 9.4
| 2014-11-29 03:00 | 3.8 | 6.1 | 9.4
| 2014-11-29 03:30 | 3.7 | 6.1 | 9.4
| 2014-11-29 04:00 | 3.6 | 6.1 | 9.4
| 2014-11-29 04:30 | 3.6 | 6.1 | 9.4
| 2014-11-29 05:00 | 3.6 | 6.1 | 9.4
| 2014-11-29 05:30 | 3.6 | 6.1 | 9.4
| 2014-11-29 06:00 | 3.5 | 6.1 | 9.4
| 2014-11-29 06:30 | 3.4 | 6.1 | 9.4
| 2014-11-29 07:00 | 3.4 | 6.1 | 9.4
| 2014-11-29 07:30 | 3.4 | 6.1 | 9.4
| 2014-11-29 08:00 | 3.4 | 6.1 | 9.4
| 2014-11-29 08:30 | 3.5 | 6.1 | 9.4
| 2014-11-29 09:00 | 3.5 | 6.1 | 9.4
| 2014-11-29 09:30 | 3.6 | 6.1 | 9.4
| 2014-11-29 10:00 | 3.7 | 6.1 | 9.4
| 2014-11-29 10:30 | 3.8 | 6.1 | 9.4
| 2014-11-29 11:00 | 3.9 | 6.1 | 9.4
| 2014-11-29 11:30 | 4.1 | 6.1 | 9.4
| 2014-11-29 12:00 | 4.2 | 6.1 | 9.4
| 2014-11-29 12:30 | 4.2 | 6.1 | 9.4
| 2014-11-29 13:00 | 4.2 | 6.1 | 9.4
| 2014-11-29 13:30 | 4.3 | 6.1 | 9.4
| 2014-11-29 14:00 | 4.3 | 6.1 | 9.4
| 2014-11-29 14:30 | 4.3 | 6.1 | 9.4
| 2014-11-29 15:00 | 4.2 | 6.1 | 9.4
| 2014-11-29 15:30 | 4.1 | 6.1 | 9.4
| 2014-11-29 16:00 | 4 | 6.1 | 9.4
| 2014-11-29 16:30 | 3.9 | 6.1 | 9.4
| 2014-11-29 17:00 | 3.8 | 6.1 | 9.4
| 2014-11-29 17:30 | 3.8 | 6.1 | 9.4
| 2014-11-29 18:00 | 3.8 | 6.1 | 9.4
| 2014-11-29 18:30 | 3.8 | 6.1 | 9.4
| 2014-11-29 19:00 | 3.8 | 6.1 | 9.4
| 2014-11-29 19:30 | 3.9 | 6.1 | 9.4
| 2014-11-29 20:00 | 3.9 | 6.1 | 9.4
| 2014-11-29 20:30 | 3.9 | 6.1 | 9.4
| 2014-11-29 21:00 | 3.9 | 6.1 | 9.4
| 2014-11-29 21:30 | 3.9 | 6.1 | 9.4
| 2014-11-29 22:00 | 3.9 | 6.1 | 9.4
| 2014-11-29 22:30 | 3.9 | 6.1 | 9.4
| 2014-11-29 23:00 | 3.9 | 6.1 | 9.4
| 2014-11-29 23:30 | 3.9 | 6.1 | 9.4
| 2014-11-30 | 3.9 | 6.1 | 9.4
| 2014-11-30 00:30 | 3.9 | 6.1 | 9.4
| 2014-11-30 01:00 | 3.9 | 6.1 | 9.4
| 2014-11-30 01:30 | 3.9 | 6.1 | 9.4
| 2014-11-30 02:00 | 3.8 | 6.1 | 9.4
| 2014-11-30 02:30 | 3.8 | 6.1 | 9.4
| 2014-11-30 03:00 | 3.8 | 6.1 | 9.4
| 2014-11-30 03:30 | 3.8 | 6.1 | 9.4
| 2014-11-30 04:00 | 3.7 | 6.1 | 9.4
| 2014-11-30 04:30 | 3.7 | 6.1 | 9.4
| 2014-11-30 05:00 | 3.7 | 5.6 | 9.4
| 2014-11-30 05:30 | 3.6 | 5.6 | 9.4
| 2014-11-30 06:00 | 3.6 | 5.6 | 9.4
| 2014-11-30 06:30 | 3.4 | 5.6 | 8.9
| 2014-11-30 07:00 | 3.4 | 5.6 | 8.9
| 2014-11-30 07:30 | 3.2 | 5.6 | 8.9
| 2014-11-30 08:00 | 3.2 | 5.6 | 8.9
| 2014-11-30 08:30 | 3.2 | 5.6 | 8.9
| 2014-11-30 09:00 | 3.3 | 5.6 | 8.9
| 2014-11-30 09:30 | 3.3 | 5.6 | 8.9
| 2014-11-30 10:00 | 3.4 | 5.6 | 8.9
| 2014-11-30 10:30 | 3.5 | 5.6 | 8.9
| 2014-11-30 11:00 | 3.6 | 5.6 | 8.9
| 2014-11-30 11:30 | 3.7 | 5.6 | 8.9
| 2014-11-30 12:00 | 3.8 | 5.6 | 8.9
| 2014-11-30 12:30 | 3.9 | 5.6 | 8.9
| 2014-11-30 13:00 | 4 | 5.6 | 8.9
| 2014-11-30 13:30 | 3.9 | 5.6 | 8.9
| 2014-11-30 14:00 | 4 | 5.6 | 8.9
| 2014-11-30 14:30 | 3.9 | 5.6 | 8.9
| 2014-11-30 15:00 | 3.9 | 5.6 | 8.9
| 2014-11-30 15:30 | 3.8 | 5.6 | 8.9
| 2014-11-30 16:00 | 3.7 | 6.1 | 8.9
| 2014-11-30 16:30 | 3.7 | 6.1 | 8.9
| 2014-11-30 17:00 | 3.7 | 6.1 | 8.9
| 2014-11-30 17:30 | 3.6 | 6.1 | 8.9
| 2014-11-30 18:00 | 3.6 | 6.1 | 8.9
| 2014-11-30 18:30 | 3.5 | 6.1 | 8.9
| 2014-11-30 19:00 | 3.5 | 6.1 | 8.9
| 2014-11-30 19:30 | 3.4 | 6.1 | 8.9
| 2014-11-30 20:00 | 3.4 | 6.1 | 8.9
| 2014-11-30 20:30 | 3.4 | 6.1 | 8.9
| 2014-11-30 21:00 | 3.3 | 6.1 | 8.9
| 2014-11-30 21:30 | 3.4 | 5.6 | 8.9
| 2014-11-30 22:00 | 3.3 | 5.6 | 8.9
| 2014-11-30 22:30 | 3.3 | 5.6 | 8.9
| 2014-11-30 23:00 | 3.3 | 5.6 | 8.9
| 2014-11-30 23:30 | 3.2 | 5.6 | 8.9
| 2014-12-01 | 3.2 | 5.6 | 8.9
| 2014-12-01 00:30 | 3.2 | 5.6 | 8.9
| 2014-12-01 01:00 | 3.2 | 5.6 | 8.9
| 2014-12-01 01:30 | 3.2 | 5.6 | 8.9
| 2014-12-01 02:00 | 3.2 | 5.6 | 8.9
| 2014-12-01 02:30 | 3.3 | 5.6 | 8.9
| 2014-12-01 03:00 | 3.3 | 5.6 | 8.9
| 2014-12-01 03:30 | 3.4 | 5.6 | 8.9
| 2014-12-01 04:00 | 3.4 | 5.6 | 8.9
| 2014-12-01 04:30 | 3.6 | 5.6 | 8.9
| 2014-12-01 05:00 | 3.7 | 5.6 | 8.9
| 2014-12-01 05:30 | 3.9 | 5.6 | 8.9
| 2014-12-01 06:00 | 4 | 5.6 | 8.9
| 2014-12-01 06:30 | 4.2 | 5.6 | 8.9
| 2014-12-01 07:00 | 4.2 | 5.6 | 8.9
| 2014-12-01 07:30 | 4.3 | 5.6 | 8.9
| 2014-12-01 08:00 | 4.4 | 5.6 | 8.9
| 2014-12-01 08:30 | 4.4 | 5.6 | 8.9
| 2014-12-01 09:00 | 4.6 | 5.6 | 8.9
| 2014-12-01 09:30 | 4.7 | 5.6 | 8.9
| 2014-12-01 10:00 | 4.8 | 5.6 | 8.9
| 2014-12-01 10:30 | 4.8 | 5.6 | 8.9
| 2014-12-01 11:00 | 5 | 5.6 | 8.9
| 2014-12-01 11:30 | 4.4 | 5.6 | 8.9
| 2014-12-01 12:00 | 4 | 5.6 | 8.9
| 2014-12-01 12:30 | 3.9 | 5.6 | 8.9
| 2014-12-01 13:00 | 3.7 | 5.6 | 8.9
| 2014-12-01 13:30 | 3.6 | 5.6 | 8.9
| 2014-12-01 14:00 | 3.6 | 5.6 | 8.9
| 2014-12-01 14:30 | 3.7 | 5.6 | 8.9
| 2014-12-01 15:00 | 3.8 | 5.6 | 8.9
| 2014-12-01 15:30 | 3.8 | 5.6 | 8.9
| 2014-12-01 16:00 | 3.7 | 5.6 | 8.9
| 2014-12-01 16:30 | 3.3 | 5.6 | 8.9
| 2014-12-01 17:00 | 3.2 | 5.6 | 8.9
| 2014-12-01 17:30 | 2.8 | 5.6 | 8.9
| 2014-12-01 18:00 | 2.5 | 5.6 | 8.9
| 2014-12-01 18:30 | 2.4 | 5.6 | 8.9
| 2014-12-01 19:00 | 2.4 | 5.6 | 8.9
| 2014-12-01 19:30 | 2.3 | 5.6 | 8.9
| 2014-12-01 20:00 | 2.2 | 5.6 | 8.9
| 2014-12-01 20:30 | 2.1 | 5.6 | 8.9
| 2014-12-01 21:00 | 2.2 | 5.6 | 8.9
| 2014-12-01 21:30 | 2.1 | 5.6 | 8.9
| 2014-12-01 22:00 | 2 | 5.6 | 8.9
| 2014-12-01 22:30 | 1.9 | 5.6 | 8.9
| 2014-12-01 23:00 | 1.8 | 5.6 | 8.9
| 2014-12-01 23:30 | 1.8 | 5.6 | 8.9
| 2014-12-02 | 1.9 | 5.6 | 8.9
| 2014-12-02 00:30 | 1.9 | 5.6 | 8.9
| 2014-12-02 01:00 | 1.9 | 5.6 | 8.9
| 2014-12-02 01:30 | 1.9 | 5.6 | 8.9
| 2014-12-02 02:00 | 1.9 | 5.6 | 8.9
| 2014-12-02 02:30 | 1.8 | 5.6 | 8.9
| 2014-12-02 03:00 | 1.3 | 5.6 | 8.9
| 2014-12-02 03:30 | 1.1 | 5.6 | 8.9
| 2014-12-02 04:00 | 1 | 5.6 | 8.9
| 2014-12-02 04:30 | 1.1 | 5.6 | 8.9
| 2014-12-02 05:00 | 1.2 | 5.6 | 8.9
| 2014-12-02 05:30 | 1.1 | 5.6 | 8.9
| 2014-12-02 06:00 | 1.1 | 5.6 | 8.9
| 2014-12-02 06:30 | 0.9 | 5 | 8.9
| 2014-12-02 07:00 | 0.9 | 5 | 8.9
| 2014-12-02 07:30 | 1 | 5 | 8.9
| 2014-12-02 08:00 | 1.1 | 5 | 8.9
| 2014-12-02 08:30 | 1.1 | 5 | 8.9
| 2014-12-02 09:00 | 0.8 | 5 | 8.9
| 2014-12-02 09:30 | 0.7 | 5 | 8.9
| 2014-12-02 10:00 | 0.7 | 5 | 8.9
| 2014-12-02 10:30 | 0.9 | 5 | 8.9
| 2014-12-02 11:00 | 1 | 5 | 8.9
| 2014-12-02 11:30 | 1.1 | 5 | 8.9
| 2014-12-02 12:00 | 1.3 | 5 | 8.9
| 2014-12-02 12:30 | 1.3 | 5 | 8.9
| 2014-12-02 13:00 | 1.6 | 5 | 8.9
| 2014-12-02 13:30 | 1.7 | 5 | 8.9
| 2014-12-02 14:00 | 1.8 | 5 | 8.9
| 2014-12-02 14:30 | 1.9 | 5 | 8.9
| 2014-12-02 15:00 | 2 | 5 | 8.9
| 2014-12-02 15:30 | 2.1 | 5 | 8.9
| 2014-12-02 16:00 | 1.9 | 5 | 8.9
| 2014-12-02 16:30 | 1.9 | 5 | 8.9
| 2014-12-02 17:00 | 2 | 5 | 8.9
| 2014-12-02 17:30 | 1.8 | 5 | 8.9
| 2014-12-02 18:00 | 1.7 | 5 | 8.9
| 2014-12-02 18:30 | 1.4 | 5 | 8.9
| 2014-12-02 19:00 | 1.3 | 5 | 8.9
| 2014-12-02 19:30 | 1.3 | 5 | 8.9
| 2014-12-02 20:00 | 1.4 | 5 | 8.9
| 2014-12-02 20:30 | 1.2 | 5 | 8.9
| 2014-12-02 21:00 | 0.8 | 5 | 8.9
| 2014-12-02 21:30 | 0.5 | 5 | 8.9
| 2014-12-02 22:00 | 0.4 | 5 | 8.9
| 2014-12-02 22:30 | 0.3 | 5 | 8.9
| 2014-12-02 23:00 | 0.2 | 5 | 8.9
| 2014-12-02 23:30 | 0.2 | 5 | 8.9
| 2014-12-03 | 0.2 | 5 | 8.9
| 2014-12-03 00:30 | 0.1 | 5 | 8.9
| 2014-12-03 01:00 | 0.1 | 5 | 8.9
| 2014-12-03 01:30 | 0.1 | 5 | 8.9
| 2014-12-03 02:00 | 0.1 | 4.4 | 8.9
| 2014-12-03 02:30 | 0.1 | 4.4 | 8.9
| 2014-12-03 03:00 | 0.1 | 4.4 | 8.9
| 2014-12-03 03:30 | 0.1 | 4.4 | 8.9
| 2014-12-03 04:00 | -0.1 | 4.4 | 8.9
| 2014-12-03 04:30 | -0.1 | 4.4 | 8.9
| 2014-12-03 05:00 | -0.2 | 4.4 | 8.9
| 2014-12-03 05:30 | -0.2 | 4.4 | 8.9
| 2014-12-03 06:00 | -0.2 | 4.4 | 8.9
| 2014-12-03 06:30 | -0.1 | 4.4 | 8.9
| 2014-12-03 07:00 | -0.1 | 4.4 | 8.9
| 2014-12-03 07:30 | -0.1 | 4.4 | 8.9
| 2014-12-03 08:00 | -0.2 | 4.4 | 8.9
| 2014-12-03 08:30 | -0.1 | 4.4 | 8.9
| 2014-12-03 09:00 | 0 | 4.4 | 8.9
| 2014-12-03 09:30 | 0.2 | 4.4 | 8.9
| 2014-12-03 10:00 | 0.3 | 4.4 | 8.9
| 2014-12-03 10:30 | 0.6 | 4.4 | 8.9
| 2014-12-03 11:00 | 0.7 | 4.4 | 8.9
| 2014-12-03 11:30 | 0.9 | 4.4 | 8.9
| 2014-12-03 12:00 | 1.2 | 4.4 | 8.9
| 2014-12-03 12:30 | 1.5 | 4.4 | 8.9
| 2014-12-03 13:00 | 1.9 | 4.4 | 8.9
| 2014-12-03 13:30 | 1.9 | 4.4 | 8.9
| 2014-12-03 14:00 | 2.3 | 4.4 | 8.9
| 2014-12-03 14:30 | 2.4 | 4.4 | 8.9
| 2014-12-03 15:00 | 2.3 | 4.4 | 8.9
| 2014-12-03 15:30 | 2.3 | 4.4 | 8.9
| 2014-12-03 16:00 | 2.2 | 4.4 | 8.9
| 2014-12-03 16:30 | 2.1 | 4.4 | 8.9
| 2014-12-03 17:00 | 1.8 | 4.4 | 8.9
| 2014-12-03 17:30 | 1.8 | 5 | 8.9
| 2014-12-03 18:00 | 1.7 | 5 | 8.9
| 2014-12-03 18:30 | 1.6 | 5 | 8.9
| 2014-12-03 19:00 | 1.6 | 5 | 8.9
| 2014-12-03 19:30 | 1.6 | 5 | 8.9
| 2014-12-03 20:00 | 1.4 | 5 | 8.9
| 2014-12-03 20:30 | 1.3 | 5 | 8.9
| 2014-12-03 21:00 | 1.3 | 5 | 8.9
| 2014-12-03 21:30 | 1.3 | 4.4 | 8.9
| 2014-12-03 22:00 | 1.3 | 4.4 | 8.9
| 2014-12-03 22:30 | 1.3 | 4.4 | 8.3
| 2014-12-03 23:00 | 1.3 | 4.4 | 8.3
| 2014-12-03 23:30 | 1.4 | 4.4 | 8.3
| 2014-12-04 | 1.4 | 4.4 | 8.3
| 2014-12-04 00:30 | 1.4 | 4.4 | 8.3
| 2014-12-04 01:00 | 1.4 | 4.4 | 8.3
| 2014-12-04 01:30 | 1.5 | 4.4 | 8.3
| 2014-12-04 02:00 | 1.6 | 4.4 | 8.3
| 2014-12-04 02:30 | 1.6 | 4.4 | 8.3
| 2014-12-04 03:00 | 1.6 | 4.4 | 8.3
| 2014-12-04 03:30 | 1.4 | 4.4 | 8.3
| 2014-12-04 04:00 | 1.3 | 4.4 | 8.3
| 2014-12-04 04:30 | 1.2 | 4.4 | 8.3
| 2014-12-04 05:00 | 1.2 | 4.4 | 8.3
| 2014-12-04 05:30 | 1.2 | 4.4 | 8.3
| 2014-12-04 06:00 | 1.2 | 4.4 | 8.3
| 2014-12-04 06:30 | 1.2 | 4.4 | 8.3
| 2014-12-04 07:00 | 1.2 | 4.4 | 8.3
| 2014-12-04 07:30 | 1.2 | 4.4 | 8.3
| 2014-12-04 08:00 | 1.3 | 4.4 | 8.3
| 2014-12-04 08:30 | 1.4 | 4.4 | 8.3
| 2014-12-04 09:00 | 1.5 | 4.4 | 8.3
| 2014-12-04 09:30 | 1.7 | 4.4 | 8.3
| 2014-12-04 10:00 | 1.9 | 4.4 | 8.3
| 2014-12-04 10:30 | 2.3 | 4.4 | 8.3
| 2014-12-04 11:00 | 2.6 | 4.4 | 8.3
| 2014-12-04 11:30 | 2.7 | 4.4 | 8.3
| 2014-12-04 12:00 | 2.9 | 4.4 | 8.3
| 2014-12-04 12:30 | 3.1 | 4.4 | 8.3
| 2014-12-04 13:00 | 3.2 | 4.4 | 8.3
| 2014-12-04 13:30 | 3.2 | 4.4 | 8.3
| 2014-12-04 14:00 | 3.3 | 4.4 | 8.3
| 2014-12-04 14:30 | 3.3 | 4.4 | 8.3
| 2014-12-04 15:00 | 3.3 | 4.4 | 8.3
| 2014-12-04 15:30 | 3.4 | 4.4 | 8.3
| 2014-12-04 16:00 | 3.5 | 4.4 | 8.3
| 2014-12-04 16:30 | 3.4 | 4.4 | 8.3
| 2014-12-04 17:00 | 3.3 | 4.4 | 8.3
| 2014-12-04 17:30 | 3.2 | 4.4 | 8.3
| 2014-12-04 18:00 | 3.1 | 4.4 | 8.3
| 2014-12-04 18:30 | 3.1 | 4.4 | 8.3
| 2014-12-04 19:00 | 3.1 | 5 | 8.3
| 2014-12-04 19:30 | 3.1 | 5 | 8.3
| 2014-12-04 20:00 | 3.1 | 5 | 8.3
| 2014-12-04 20:30 | 3.1 | 5 | 8.3
| 2014-12-04 21:00 | 3.1 | 5 | 8.3
| 2014-12-04 21:30 | 3.1 | 5 | 8.3
| 2014-12-04 22:00 | 3.1 | 5 | 8.3
| 2014-12-04 22:30 | 3.1 | 5 | 8.3
| 2014-12-04 23:00 | 3.1 | 5 | 8.3
| 2014-12-04 23:30 | 3.1 | 5 | 8.3
| 2014-12-05 | 3 | 5 | 8.3
| 2014-12-05 00:30 | 2.9 | 5 | 8.3
| 2014-12-05 01:00 | 2.8 | 5 | 8.3
| 2014-12-05 01:30 | 2.7 | 5 | 8.3
| 2014-12-05 02:00 | 2.6 | 5 | 8.3
| 2014-12-05 02:30 | 2.6 | 5 | 8.3
| 2014-12-05 03:00 | 2.6 | 5 | 8.3
| 2014-12-05 03:30 | 2.6 | 5 | 8.3
| 2014-12-05 04:00 | 2.7 | 5 | 8.3
| 2014-12-05 04:30 | 2.7 | 5 | 8.3
| 2014-12-05 05:00 | 2.7 | 5 | 8.3
| 2014-12-05 05:30 | 2.7 | 5 | 8.3
| 2014-12-05 06:00 | 2.7 | 5 | 8.3
| 2014-12-05 06:30 | 2.7 | 5 | 8.3
| 2014-12-05 07:00 | 2.6 | 5 | 8.3
| 2014-12-05 07:30 | 2.7 | 5 | 8.3
| 2014-12-05 08:00 | 2.7 | 5 | 8.3
| 2014-12-05 08:30 | 2.7 | 5 | 8.3
| 2014-12-05 09:00 | 2.7 | 5 | 8.3
| 2014-12-05 09:30 | 2.8 | 5 | 8.3
| 2014-12-05 10:00 | 3 | 5 | 8.3
| 2014-12-05 10:30 | 3.1 | 5 | 8.3
| 2014-12-05 11:00 | 3.3 | 5 | 8.3
| 2014-12-05 11:30 | 3.3 | 5 | 8.3
| 2014-12-05 12:00 | 3.5 | 5 | 8.3
| 2014-12-05 12:30 | 3.7 | 5 | 8.3
| 2014-12-05 13:00 | 3.8 | 5 | 8.3
| 2014-12-05 13:30 | 4.1 | 5 | 8.3
| 2014-12-05 14:00 | 4.4 | 5 | 8.3
| 2014-12-05 14:30 | 4.4 | 5 | 8.3
| 2014-12-05 15:00 | 4.4 | 5 | 8.3
| 2014-12-05 15:30 | 4.3 | 5 | 8.3
| 2014-12-05 16:00 | 4.3 | 5 | 8.3
| 2014-12-05 16:30 | 4 | 5 | 8.3
| 2014-12-05 17:00 | 3.8 | 5 | 8.3
| 2014-12-05 17:30 | 3.8 | 5 | 8.3
| 2014-12-05 18:00 | 3.8 | 5 | 8.3
| 2014-12-05 18:30 | 3.7 | 5 | 8.3
| 2014-12-05 19:00 | 3.6 | 5 | 8.3
| 2014-12-05 19:30 | 3.6 | 5 | 8.3
| 2014-12-05 20:00 | 3.5 | 5 | 8.3
| 2014-12-05 20:30 | 3.4 | 5 | 8.3
| 2014-12-05 21:00 | 3.4 | 5 | 8.3
| 2014-12-05 21:30 | 3.4 | 5 | 8.3
| 2014-12-05 22:00 | 3.4 | 5 | 8.3
| 2014-12-05 22:30 | 3.5 | 5 | 8.3
| 2014-12-05 23:00 | 3.4 | 5 | 8.3
| 2014-12-05 23:30 | 3.1 | 5 | 8.3
| 2014-12-06 | 2.8 | 5 | 8.3
| 2014-12-06 00:30 | 2.8 | 5 | 8.3
| 2014-12-06 01:00 | 3 | 5 | 8.3
| 2014-12-06 01:30 | 3.1 | 5 | 8.3
| 2014-12-06 02:00 | 3.2 | 5 | 8.3
| 2014-12-06 02:30 | 3.2 | 5 | 8.3
| 2014-12-06 03:00 | 3.2 | 5 | 8.3
| 2014-12-06 03:30 | 3.2 | 5 | 8.3
| 2014-12-06 04:00 | 3.2 | 5 | 8.3
| 2014-12-06 04:30 | 3.2 | 5 | 8.3
| 2014-12-06 05:00 | 3.3 | 5 | 8.3
| 2014-12-06 05:30 | 3.3 | 5 | 8.3
| 2014-12-06 06:00 | 3.3 | 5 | 8.3
| 2014-12-06 06:30 | 3.3 | 5 | 8.3
| 2014-12-06 07:00 | 3.3 | 5 | 8.3
| 2014-12-06 07:30 | 3.3 | 5 | 8.3
| 2014-12-06 08:00 | 3.3 | 5 | 8.3
| 2014-12-06 08:30 | 3.4 | 5 | 8.3
| 2014-12-06 09:00 | 3.5 | 5 | 8.3
| 2014-12-06 09:30 | 3.7 | 5 | 8.3
| 2014-12-06 10:00 | 3.9 | 5 | 8.3
| 2014-12-06 10:30 | 4.1 | 5 | 8.3
| 2014-12-06 11:00 | 4 | 5 | 8.3
| 2014-12-06 11:30 | 4.2 | 5 | 8.3
| 2014-12-06 12:00 | 4.6 | 5 | 8.3
| 2014-12-06 12:30 | 4.9 | 5 | 8.3
| 2014-12-06 13:00 | 5.2 | 5 | 8.3
| 2014-12-06 13:30 | 5.3 | 5 | 8.3
| 2014-12-06 14:00 | 5.4 | 5 | 8.3
| 2014-12-06 14:30 | 5.4 | 5 | 8.3
| 2014-12-06 15:00 | 5.4 | 5 | 8.3
| 2014-12-06 15:30 | 5.3 | 5 | 8.3
| 2014-12-06 16:00 | 5.2 | 5 | 8.3
| 2014-12-06 16:30 | 5.1 | 5.6 | 8.3
| 2014-12-06 17:00 | 4.8 | 5.6 | 8.3
| 2014-12-06 17:30 | 4.6 | 5.6 | 8.3
| 2014-12-06 18:00 | 4.6 | 5.6 | 8.3
| 2014-12-06 18:30 | 4.6 | 5.6 | 8.3
| 2014-12-06 19:00 | 4.3 | 5.6 | 8.3
| 2014-12-06 19:30 | 4.5 | 5.6 | 8.3
| 2014-12-06 20:00 | 4.6 | 5.6 | 8.3
| 2014-12-06 20:30 | 4.6 | 5.6 | 8.3
| 2014-12-06 21:00 | 4.4 | 5.6 | 8.3
| 2014-12-06 21:30 | 4.3 | 5.6 | 8.3
| 2014-12-06 22:00 | 4.4 | 5.6 | 8.3
| 2014-12-06 22:30 | 4.4 | 5.6 | 8.3
| 2014-12-06 23:00 | 4.3 | 5.6 | 8.3
| 2014-12-06 23:30 | 3.2 | 5.6 | 8.3
| 2014-12-07 | 1.8 | 5.6 | 8.3
| 2014-12-07 00:30 | 1.4 | 5 | 8.3
| 2014-12-07 01:00 | 2.1 | 5 | 8.3
| 2014-12-07 01:30 | 2.6 | 5 | 8.3
| 2014-12-07 02:00 | 2.7 | 5 | 8.3
| 2014-12-07 02:30 | 2.4 | 5 | 8.3
| 2014-12-07 03:00 | 2.3 | 5 | 8.3
| 2014-12-07 03:30 | 1.8 | 5 | 8.3
| 2014-12-07 04:00 | 2.2 | 5 | 8.3
| 2014-12-07 04:30 | 1.9 | 5 | 8.3
| 2014-12-07 05:00 | 1.9 | 5 | 8.3
| 2014-12-07 05:30 | 1.9 | 5 | 8.3
| 2014-12-07 06:00 | 1.9 | 5 | 8.3
| 2014-12-07 06:30 | 1.8 | 5 | 8.3
| 2014-12-07 07:00 | 1.7 | 5 | 8.3
| 2014-12-07 07:30 | 1.3 | 5 | 8.3
| 2014-12-07 08:00 | 1.2 | 5 | 8.3
| 2014-12-07 08:30 | 1.3 | 5 | 8.3
| 2014-12-07 09:00 | 1.8 | 5 | 8.3
| 2014-12-07 09:30 | 2.2 | 5 | 8.3
| 2014-12-07 10:00 | 2.6 | 5 | 8.3
| 2014-12-07 10:30 | 3.2 | 5 | 8.3
| 2014-12-07 11:00 | 3.8 | 5 | 8.3
| 2014-12-07 11:30 | 4.2 | 5 | 8.3
| 2014-12-07 12:00 | 4.8 | 5 | 8.3
| 2014-12-07 12:30 | 5 | 5 | 8.3
| 2014-12-07 13:00 | 5.3 | 5 | 8.3
| 2014-12-07 13:30 | 5.3 | 5 | 8.3
| 2014-12-07 14:00 | 5.3 | 5 | 8.3
| 2014-12-07 14:30 | 5.3 | 5 | 8.3
| 2014-12-07 15:00 | 5.3 | 5 | 8.3
| 2014-12-07 15:30 | 5 | 5 | 8.3
| 2014-12-07 16:00 | 4.4 | 5 | 8.3
| 2014-12-07 16:30 | 3.4 | 5 | 8.3
| 2014-12-07 17:00 | 2.9 | 5 | 8.3
| 2014-12-07 17:30 | 2.9 | 5 | 8.3
| 2014-12-07 18:00 | 3.2 | 5 | 8.3
| 2014-12-07 18:30 | 3.1 | 5 | 8.3
| 2014-12-07 19:00 | 3.8 | 5 | 8.3
| 2014-12-07 19:30 | 3.9 | 5 | 8.3
| 2014-12-07 20:00 | 3.7 | 5 | 8.3
| 2014-12-07 20:30 | 3.4 | 5 | 8.3
| 2014-12-07 21:00 | 3.4 | 5 | 8.3
| 2014-12-07 21:30 | 3.4 | 5 | 8.3
| 2014-12-07 22:00 | 3.3 | 5 | 8.3
| 2014-12-07 22:30 | 3.2 | 5 | 8.3
| 2014-12-07 23:00 | 3 | 5 | 8.3
| 2014-12-07 23:30 | 3 | 5 | 8.3
| 2014-12-08 | 3.1 | 5 | 8.3
| 2014-12-08 00:30 | 3.2 | 5 | 8.3
| 2014-12-08 01:00 | 3.3 | 5 | 8.3
| 2014-12-08 01:30 | 3.4 | 5 | 8.3
| 2014-12-08 02:00 | 3.5 | 5 | 8.3
| 2014-12-08 02:30 | 3.6 | 5 | 8.3
| 2014-12-08 03:00 | 3.7 | 5 | 8.3
| 2014-12-08 03:30 | 3.8 | 5 | 8.3
| 2014-12-08 04:00 | 3.8 | 5 | 8.3
| 2014-12-08 04:30 | 3.4 | 5 | 8.3
| 2014-12-08 05:00 | 3.3 | 5 | 8.3
| 2014-12-08 05:30 | 3.3 | 5 | 8.3
| 2014-12-08 06:00 | 2.7 | 5 | 8.3
| 2014-12-08 06:30 | 2.5 | 5 | 8.3
| 2014-12-08 07:00 | 2.6 | 5 | 8.3
| 2014-12-08 07:30 | 2.3 | 5 | 8.3
| 2014-12-08 08:00 | 2.3 | 5 | 8.3
| 2014-12-08 08:30 | 2.2 | 5 | 8.3
| 2014-12-08 09:00 | 2.6 | 5 | 8.3
| 2014-12-08 09:30 | 2.4 | 5 | 8.3
| 2014-12-08 10:00 | 2.7 | 5 | 8.3
| 2014-12-08 10:30 | 3.7 | 4.4 | 8.3
| 2014-12-08 11:00 | 4.2 | 4.4 | 8.3
| 2014-12-08 11:30 | 4.4 | 4.4 | 8.3
| 2014-12-08 12:00 | 5.6 | 4.4 | 7.8
| 2014-12-08 12:30 | 5.7 | 4.4 | 8.3
| 2014-12-08 13:00 | 6.3 | 4.4 | 7.8
| 2014-12-08 13:30 | 6.3 | 4.4 | 7.8
| 2014-12-08 14:00 | 5.8 | 4.4 | 7.8
| 2014-12-08 14:30 | 5.4 | 4.4 | 7.8
| 2014-12-08 15:00 | 6.2 | 4.4 | 7.8
| 2014-12-08 15:30 | 6.1 | 4.4 | 7.8
| 2014-12-08 16:00 | 5 | 5 | 7.8
| 2014-12-08 16:30 | 3.5 | 5 | 7.8
| 2014-12-08 17:00 | 2.5 | 5 | 7.8
| 2014-12-08 17:30 | 1.8 | 5 | 7.8
| 2014-12-08 18:00 | 1.3 | 5 | 7.8
| 2014-12-08 18:30 | 0.8 | 4.4 | 7.8
| 2014-12-08 19:00 | 0.2 | 4.4 | 7.8
| 2014-12-08 19:30 | 0.3 | 4.4 | 7.8
| 2014-12-08 20:00 | 0 | 4.4 | 7.8
| 2014-12-08 20:30 | -0.3 | 4.4 | 7.8
| 2014-12-08 21:00 | -0.4 | 4.4 | 7.8
| 2014-12-08 21:30 | -0.6 | 4.4 | 7.8
| 2014-12-08 22:00 | -0.8 | 4.4 | 7.8
| 2014-12-08 22:30 | -1.4 | 4.4 | 7.8
| 2014-12-08 23:00 | -1.4 | 4.4 | 7.8
| 2014-12-08 23:30 | -1.8 | 3.9 | 7.8
| 2014-12-09 | -1.7 | 3.9 | 7.8
| 2014-12-09 00:30 | -1.2 | 3.9 | 7.8
| 2014-12-09 01:00 | -0.9 | 3.9 | 7.8
| 2014-12-09 01:30 | -0.3 | 3.9 | 7.8
| 2014-12-09 02:00 | -0.1 | 3.9 | 7.8
| 2014-12-09 02:30 | -0.1 | 3.9 | 7.8
| 2014-12-09 03:00 | 0.1 | 3.9 | 7.8
| 2014-12-09 03:30 | 0.2 | 3.9 | 7.8
| 2014-12-09 04:00 | 0.3 | 3.9 | 7.8
| 2014-12-09 04:30 | 0.4 | 3.9 | 7.8
| 2014-12-09 05:00 | 0.6 | 3.9 | 7.8
| 2014-12-09 05:30 | 0.6 | 3.9 | 7.8
| 2014-12-09 06:00 | 0.6 | 3.9 | 7.8
| 2014-12-09 06:30 | 0.7 | 3.9 | 7.8
| 2014-12-09 07:00 | 0.9 | 3.9 | 7.8
| 2014-12-09 07:30 | 0.8 | 3.9 | 7.8
| 2014-12-09 08:00 | 1.1 | 3.9 | 7.8
| 2014-12-09 08:30 | 1.1 | 3.9 | 7.8
| 2014-12-09 09:00 | 1.1 | 3.9 | 7.8
| 2014-12-09 09:30 | 1 | 3.9 | 7.8
| 2014-12-09 10:00 | 1 | 3.9 | 7.8
| 2014-12-09 10:30 | 1.7 | 3.9 | 7.8
| 2014-12-09 11:00 | 2.2 | 3.9 | 7.8
| 2014-12-09 11:30 | 2.6 | 3.9 | 7.8
| 2014-12-09 12:00 | 2.8 | 3.9 | 7.8
| 2014-12-09 12:30 | 2.9 | 3.9 | 7.8
| 2014-12-09 13:00 | 3.2 | 3.9 | 7.8
| 2014-12-09 13:30 | 3.2 | 3.9 | 7.8
| 2014-12-09 14:00 | 3.2 | 3.9 | 7.8
| 2014-12-09 14:30 | 3.3 | 3.9 | 7.8
| 2014-12-09 15:00 | 4.3 | 3.9 | 7.8
| 2014-12-09 15:30 | 4.2 | 3.9 | 7.8
| 2014-12-09 16:00 | 3.6 | 3.9 | 7.8
| 2014-12-09 16:30 | 2.8 | 3.9 | 7.8
| 2014-12-09 17:00 | 2.6 | 3.9 | 7.8
| 2014-12-09 17:30 | 2.8 | 3.9 | 7.8
| 2014-12-09 18:00 | 2.8 | 3.9 | 7.8
| 2014-12-09 18:30 | 2.7 | 3.9 | 7.8
| 2014-12-09 19:00 | 2.7 | 3.9 | 7.8
| 2014-12-09 19:30 | 2.6 | 3.9 | 7.8
| 2014-12-09 20:00 | 2.4 | 3.9 | 7.8
| 2014-12-09 20:30 | 2.4 | 3.9 | 7.8
| 2014-12-09 21:00 | 1.2 | 3.9 | 7.8
| 2014-12-09 21:30 | 0.3 | 3.9 | 7.8
| 2014-12-09 22:00 | -0.2 | 3.9 | 7.8
| 2014-12-09 22:30 | 0.1 | 3.9 | 7.8
| 2014-12-09 23:00 | 0.6 | 3.9 | 7.8
| 2014-12-09 23:30 | 0 | 3.9 | 7.8
| 2014-12-10 | 0.1 | 3.9 | 7.8
| 2014-12-10 00:30 | 0.1 | 3.9 | 7.8
| 2014-12-10 01:00 | -0.4 | 3.9 | 7.8
| 2014-12-10 01:30 | 0.1 | 3.9 | 7.8
| 2014-12-10 02:00 | -0.2 | 3.9 | 7.8
| 2014-12-10 02:30 | -0.5 | 3.9 | 7.8
| 2014-12-10 03:00 | -0.7 | 3.9 | 7.8
| 2014-12-10 03:30 | -0.1 | 3.3 | 7.8
| 2014-12-10 04:00 | 0.2 | 3.3 | 7.8
| 2014-12-10 04:30 | 0.6 | 3.3 | 7.8
| 2014-12-10 05:00 | 0.6 | 3.3 | 7.8
| 2014-12-10 05:30 | 0.8 | 3.3 | 7.8
| 2014-12-10 06:00 | 0.9 | 3.3 | 7.8
| 2014-12-10 06:30 | 0.8 | 3.3 | 7.8
| 2014-12-10 07:00 | 0.9 | 3.3 | 7.8
| 2014-12-10 07:30 | 1.1 | 3.3 | 7.8
| 2014-12-10 08:00 | 1.3 | 3.3 | 7.8
| 2014-12-10 08:30 | 1.3 | 3.3 | 7.8
| 2014-12-10 09:00 | 1.3 | 3.3 | 7.8
| 2014-12-10 09:30 | 1.2 | 3.3 | 7.8
| 2014-12-10 10:00 | 1.1 | 3.3 | 7.8
| 2014-12-10 10:30 | 1.5 | 3.3 | 7.8
| 2014-12-10 11:00 | 1.7 | 3.3 | 7.8
| 2014-12-10 11:30 | 1.7 | 3.3 | 7.8
| 2014-12-10 12:00 | 1.7 | 3.3 | 7.8
| 2014-12-10 12:30 | 1.9 | 3.3 | 7.8
| 2014-12-10 13:00 | 2.1 | 3.3 | 7.8
| 2014-12-10 13:30 | 2.3 | 3.3 | 7.8
| 2014-12-10 14:00 | 2.4 | 3.3 | 7.8
| 2014-12-10 14:30 | 2.6 | 3.3 | 7.8
| 2014-12-10 15:00 | 2.7 | 3.3 | 7.8
| 2014-12-10 15:30 | 2.8 | 3.3 | 7.8
| 2014-12-10 16:00 | 2.9 | 3.3 | 7.8
| 2014-12-10 16:30 | 3 | 3.3 | 7.8
| 2014-12-10 17:00 | 3.1 | 3.3 | 7.8
| 2014-12-10 17:30 | 2.9 | 3.3 | 7.8
| 2014-12-10 18:00 | 2.8 | 3.3 | 7.8
| 2014-12-10 18:30 | 3.1 | 3.3 | 7.8
| 2014-12-10 19:00 | 3.3 | 3.3 | 7.8
| 2014-12-10 19:30 | 3.3 | 3.3 | 7.8
| 2014-12-10 20:00 | 3.4 | 3.3 | 7.8
| 2014-12-10 20:30 | 2.8 | 3.3 | 7.8
| 2014-12-10 21:00 | 3.3 | 3.3 | 7.8
| 2014-12-10 21:30 | 3.4 | 3.3 | 7.8
| 2014-12-10 22:00 | 3.4 | 3.3 | 7.8
| 2014-12-10 22:30 | 3.5 | 3.3 | 7.8
| 2014-12-10 23:00 | 3.6 | 3.3 | 7.8
| 2014-12-10 23:30 | 3.7 | 3.3 | 7.8
| 2014-12-11 | 3.8 | 3.3 | 7.8
| 2014-12-11 00:30 | 3.8 | 3.9 | 7.8
| 2014-12-11 01:00 | 3.8 | 3.9 | 7.8
| 2014-12-11 01:30 | 3.8 | 3.9 | 7.8
| 2014-12-11 02:00 | 3.9 | 3.9 | 7.8
| 2014-12-11 02:30 | 4 | 3.9 | 7.8
| 2014-12-11 03:00 | 4.3 | 3.9 | 7.8
| 2014-12-11 03:30 | 4.3 | 3.9 | 7.8
| 2014-12-11 04:00 | 4.2 | 3.9 | 7.8
| 2014-12-11 04:30 | 4.3 | 3.9 | 7.8
| 2014-12-11 05:00 | 4.2 | 3.9 | 7.8
| 2014-12-11 05:30 | 4.3 | 3.9 | 7.8
| 2014-12-11 06:00 | 4.4 | 3.9 | 7.8
| 2014-12-11 06:30 | 4.4 | 3.9 | 7.8
| 2014-12-11 07:00 | 4.6 | 3.9 | 7.8
| 2014-12-11 07:30 | 4.8 | 3.9 | 7.8
| 2014-12-11 08:00 | 4.9 | 3.9 | 7.8
| 2014-12-11 08:30 | 5.2 | 3.9 | 7.8
| 2014-12-11 09:00 | 5.3 | 3.9 | 7.8
| 2014-12-11 09:30 | 5.4 | 3.9 | 7.8
| 2014-12-11 10:00 | 5.4 | 3.9 | 7.8
| 2014-12-11 10:30 | 5.8 | 3.9 | 7.8
| 2014-12-11 11:00 | 5.9 | 3.9 | 7.8
| 2014-12-11 11:30 | 6.1 | 3.9 | 7.8
| 2014-12-11 12:00 | 6.3 | 3.9 | 7.8
| 2014-12-11 12:30 | 6.3 | 3.9 | 7.8
| 2014-12-11 13:00 | 6.5 | 3.9 | 7.8
| 2014-12-11 13:30 | 6.6 | 3.9 | 7.8
| 2014-12-11 14:00 | 6.6 | 3.9 | 7.8
| 2014-12-11 14:30 | 6.6 | 3.9 | 7.2
| 2014-12-11 15:00 | 6.6 | 4.4 | 7.2
| 2014-12-11 15:30 | 6.6 | 4.4 | 7.2
| 2014-12-11 16:00 | 6.7 | 4.4 | 7.2
| 2014-12-11 16:30 | 6.8 | 4.4 | 7.2
| 2014-12-11 17:00 | 6.8 | 4.4 | 7.2
| 2014-12-11 17:30 | 6.6 | 4.4 | 7.2
| 2014-12-11 18:00 | 6.4 | 4.4 | 7.2
| 2014-12-11 18:30 | 6.8 | 4.4 | 7.2
| 2014-12-11 19:00 | 5.9 | 4.4 | 7.2
| 2014-12-11 19:30 | 5.9 | 4.4 | 7.2
| 2014-12-11 20:00 | 5.6 | 4.4 | 7.2
| 2014-12-11 20:30 | 5 | 4.4 | 7.2
| 2014-12-11 21:00 | 4.4 | 4.4 | 7.2
| 2014-12-11 21:30 | 4.9 | 4.4 | 7.2
| 2014-12-11 22:00 | 5.2 | 4.4 | 7.2
| 2014-12-11 22:30 | 5.9 | 4.4 | 7.2
| 2014-12-11 23:00 | 5.8 | 4.4 | 7.2
| 2014-12-11 23:30 | 6.2 | 4.4 | 7.2
| 2014-12-12 | 6.4 | 4.4 | 7.2
| 2014-12-12 00:30 | 6.3 | 4.4 | 7.2
| 2014-12-12 01:00 | 6.3 | 4.4 | 7.2
| 2014-12-12 01:30 | 6.4 | 4.4 | 7.2
| 2014-12-12 02:00 | 6.6 | 4.4 | 7.2
| 2014-12-12 02:30 | 7.2 | 4.4 | 7.2
| 2014-12-12 03:00 | 7.3 | 4.4 | 7.2
| 2014-12-12 03:30 | 7.3 | 4.4 | 7.2
| 2014-12-12 04:00 | 7.4 | 4.4 | 7.2
| 2014-12-12 04:30 | 7.2 | 4.4 | 7.2
| 2014-12-12 05:00 | 6.7 | 4.4 | 7.2
| 2014-12-12 05:30 | 6.8 | 4.4 | 7.2
| 2014-12-12 06:00 | 7 | 4.4 | 7.2
| 2014-12-12 06:30 | 7.2 | 4.4 | 7.2
| 2014-12-12 07:00 | 7.1 | 4.4 | 7.2
| 2014-12-12 07:30 | 7 | 4.4 | 7.2
| 2014-12-12 08:00 | 7.2 | 4.4 | 7.2
| 2014-12-12 08:30 | 7.4 | 4.4 | 7.2
| 2014-12-12 09:00 | 7.3 | 5 | 7.2
| 2014-12-12 09:30 | 7.1 | 5 | 7.2
| 2014-12-12 10:00 | 7.2 | 5 | 7.2
| 2014-12-12 10:30 | 7.3 | 5 | 7.2
| 2014-12-12 11:00 | 7.9 | 5 | 7.2
| 2014-12-12 11:30 | 8.3 | 5 | 7.2
| 2014-12-12 12:00 | 8.7 | 5 | 7.2
| 2014-12-12 12:30 | 9.2 | 5 | 7.2
| 2014-12-12 13:00 | 9.4 | 5 | 7.2
| 2014-12-12 13:30 | 9.4 | 5 | 7.2
| 2014-12-12 14:00 | 9.6 | 5 | 7.2
| 2014-12-12 14:30 | 9.3 | 5 | 7.2
| 2014-12-12 15:00 | 9.3 | 5 | 7.2
| 2014-12-12 15:30 | 9.4 | 5 | 7.2
| 2014-12-12 16:00 | 9.4 | 5 | 7.2
| 2014-12-12 16:30 | 9.5 | 5 | 7.2
| 2014-12-12 17:00 | 9.4 | 5.6 | 7.2
| 2014-12-12 17:30 | 9.3 | 5.6 | 7.2
| 2014-12-12 18:00 | 9.2 | 5.6 | 7.2
| 2014-12-12 18:30 | 9.3 | 5.6 | 7.2
| 2014-12-12 19:00 | 9.3 | 5.6 | 7.2
| 2014-12-12 19:30 | 9.3 | 5.6 | 7.2
| 2014-12-12 20:00 | 10.1 | 5.6 | 7.2
| 2014-12-12 20:30 | 10.2 | 5.6 | 7.2
| 2014-12-12 21:00 | 10.4 | 5.6 | 7.2
| 2014-12-12 21:30 | 10.4 | 5.6 | 7.2
| 2014-12-12 22:00 | 10.8 | 5.6 | 7.2
| 2014-12-12 22:30 | 10.8 | 5.6 | 7.2
| 2014-12-12 23:00 | 10.8 | 5.6 | 7.2
| 2014-12-12 23:30 | 10.8 | 5.6 | 7.2
| 2014-12-13 | 10.8 | 5.6 | 7.2
| 2014-12-13 00:30 | 10.7 | 5.6 | 7.2
| 2014-12-13 01:00 | 10.7 | 5.6 | 7.2
| 2014-12-13 01:30 | 10.5 | 5.6 | 7.2
| 2014-12-13 02:00 | 8.7 | 5.6 | 7.2
| 2014-12-13 02:30 | 7.8 | 5.6 | 7.2
| 2014-12-13 03:00 | 7.2 | 5.6 | 7.2
| 2014-12-13 03:30 | 7.1 | 6.1 | 7.2
| 2014-12-13 04:00 | 6.9 | 6.1 | 7.2
| 2014-12-13 04:30 | 6.7 | 6.1 | 7.2
| 2014-12-13 05:00 | 6.5 | 6.1 | 7.2
| 2014-12-13 05:30 | 6.5 | 6.1 | 7.2
| 2014-12-13 06:00 | 6.5 | 6.1 | 7.2
| 2014-12-13 06:30 | 6.6 | 6.1 | 7.2
| 2014-12-13 07:00 | 6.6 | 6.1 | 7.2
| 2014-12-13 07:30 | 6.6 | 6.1 | 7.2
| 2014-12-13 08:00 | 6.6 | 6.1 | 7.2
| 2014-12-13 08:30 | 6.4 | 6.1 | 7.2
| 2014-12-13 09:00 | 6.5 | 6.1 | 7.2
| 2014-12-13 09:30 | 6.6 | 6.1 | 7.2
| 2014-12-13 10:00 | 6.8 | 6.1 | 7.2
| 2014-12-13 10:30 | 7.3 | 6.1 | 7.2
| 2014-12-13 11:00 | 7.3 | 6.1 | 7.2
| 2014-12-13 11:30 | 7.3 | 6.1 | 7.2
| 2014-12-13 12:00 | 7.5 | 6.1 | 7.2
| 2014-12-13 12:30 | 8.2 | 6.1 | 7.2
| 2014-12-13 13:00 | 8.6 | 6.1 | 7.2
| 2014-12-13 13:30 | 8.7 | 6.1 | 7.2
| 2014-12-13 14:00 | 8.9 | 6.1 | 7.2
| 2014-12-13 14:30 | 8.2 | 6.1 | 7.2
| 2014-12-13 15:00 | 7.2 | 6.1 | 7.2
| 2014-12-13 15:30 | 6.5 | 6.1 | 7.2
| 2014-12-13 16:00 | 5.9 | 6.1 | 7.2
| 2014-12-13 16:30 | 5.7 | 6.1 | 7.2
| 2014-12-13 17:00 | 5.6 | 6.1 | 7.2
| 2014-12-13 17:30 | 5.4 | 6.1 | 7.2
| 2014-12-13 18:00 | 5.3 | 6.1 | 7.2
| 2014-12-13 18:30 | 5.1 | 6.1 | 7.2
| 2014-12-13 19:00 | 4.9 | 6.1 | 7.2
| 2014-12-13 19:30 | 4.7 | 6.1 | 7.2
| 2014-12-13 20:00 | 4.4 | 6.1 | 7.2
| 2014-12-13 20:30 | 4.3 | 6.1 | 7.2
| 2014-12-13 21:00 | 4.2 | 6.1 | 7.2
| 2014-12-13 21:30 | 4.3 | 6.1 | 7.2
| 2014-12-13 22:00 | 4.1 | 6.1 | 7.2
| 2014-12-13 22:30 | 4 | 6.1 | 7.2
| 2014-12-13 23:00 | 4.1 | 6.1 | 7.8
| 2014-12-13 23:30 | 4.1 | 6.1 | 7.8
| 2014-12-14 | 4.2 | 6.1 | 7.8
| 2014-12-14 00:30 | 4.2 | 6.1 | 7.8
| 2014-12-14 01:00 | 4.1 | 6.1 | 7.8
| 2014-12-14 01:30 | 4.1 | 6.1 | 7.8
| 2014-12-14 02:00 | 4 | 6.1 | 7.8
| 2014-12-14 02:30 | 3.8 | 6.1 | 7.8
| 2014-12-14 03:00 | 3.7 | 6.1 | 7.8
| 2014-12-14 03:30 | 3.7 | 6.1 | 7.8
| 2014-12-14 04:00 | 3.8 | 6.1 | 7.8
| 2014-12-14 04:30 | 3.9 | 6.1 | 7.8
| 2014-12-14 05:00 | 3.8 | 6.1 | 7.8
| 2014-12-14 05:30 | 3.8 | 6.1 | 7.8
| 2014-12-14 06:00 | 3.7 | 6.1 | 7.8
| 2014-12-14 06:30 | 3.7 | 6.1 | 7.8
| 2014-12-14 07:00 | 3.6 | 6.1 | 7.8
| 2014-12-14 07:30 | 3.5 | 6.1 | 7.8
| 2014-12-14 08:00 | 3.5 | 6.1 | 7.8
| 2014-12-14 08:30 | 3.4 | 6.1 | 7.8
| 2014-12-14 09:00 | 3.4 | 6.1 | 7.8
| 2014-12-14 09:30 | 3.5 | 5.6 | 7.8
| 2014-12-14 10:00 | 3.7 | 5.6 | 7.8
| 2014-12-14 10:30 | 3.7 | 5.6 | 7.8
| 2014-12-14 11:00 | 3.8 | 5.6 | 7.8
| 2014-12-14 11:30 | 4.1 | 5.6 | 7.8
| 2014-12-14 12:00 | 4.2 | 5.6 | 7.8
| 2014-12-14 12:30 | 4.4 | 5.6 | 7.8
| 2014-12-14 13:00 | 4.7 | 5.6 | 7.8
| 2014-12-14 13:30 | 5 | 5.6 | 7.8
| 2014-12-14 14:00 | 4.9 | 5.6 | 7.8
| 2014-12-14 14:30 | 4.9 | 6.1 | 7.8
| 2014-12-14 15:00 | 5 | 6.1 | 7.8
| 2014-12-14 15:30 | 5 | 6.1 | 7.8
| 2014-12-14 16:00 | 5 | 6.1 | 7.8
| 2014-12-14 16:30 | 4.9 | 6.1 | 7.8
| 2014-12-14 17:00 | 4.8 | 6.1 | 7.8
| 2014-12-14 17:30 | 4.7 | 6.1 | 7.8
| 2014-12-14 18:00 | 4.7 | 6.1 | 7.8
| 2014-12-14 18:30 | 4.7 | 6.1 | 7.8
| 2014-12-14 19:00 | 4.7 | 6.1 | 7.8
| 2014-12-14 19:30 | 4.7 | 6.1 | 7.8
| 2014-12-14 20:00 | 4.6 | 6.1 | 7.8
| 2014-12-14 20:30 | 4.6 | 6.1 | 7.8
| 2014-12-14 21:00 | 4.5 | 6.1 | 7.8
| 2014-12-14 21:30 | 4.5 | 6.1 | 7.8
| 2014-12-14 22:00 | 4.6 | 6.1 | 7.8
| 2014-12-14 22:30 | 4.6 | 6.1 | 7.8
| 2014-12-14 23:00 | 4.7 | 6.1 | 7.8
| 2014-12-14 23:30 | 4.7 | 6.1 | 7.8
| 2014-12-15 | 4.7 | 6.1 | 7.8
| 2014-12-15 00:30 | 4.7 | 6.1 | 7.8
| 2014-12-15 01:00 | 4.7 | 6.1 | 7.8
| 2014-12-15 01:30 | 4.7 | 6.1 | 7.8
| 2014-12-15 02:00 | 4.6 | 6.1 | 7.8
| 2014-12-15 02:30 | 4.6 | 6.1 | 7.8
| 2014-12-15 03:00 | 4.6 | 6.1 | 7.8
| 2014-12-15 03:30 | 4.7 | 6.1 | 7.8
| 2014-12-15 04:00 | 4.9 | 6.1 | 7.8
| 2014-12-15 04:30 | 4.9 | 6.1 | 7.8
| 2014-12-15 05:00 | 5.1 | 6.1 | 7.8
| 2014-12-15 05:30 | 5.2 | 6.1 | 7.8
| 2014-12-15 06:00 | 4.8 | 6.1 | 7.8
| 2014-12-15 06:30 | 4.1 | 6.1 | 7.8
| 2014-12-15 07:00 | 5 | 6.1 | 7.8
| 2014-12-15 07:30 | 4.2 | 6.1 | 7.8
| 2014-12-15 08:00 | 3.8 | 5.6 | 7.8
| 2014-12-15 08:30 | 4.3 | 5.6 | 7.8
| 2014-12-15 09:00 | 4.6 | 5.6 | 7.8
| 2014-12-15 09:30 | 5 | 5.6 | 7.8
| 2014-12-15 10:00 | 6.4 | 5.6 | 7.8
| 2014-12-15 10:30 | 6.6 | 5.6 | 7.8
| 2014-12-15 11:00 | 6.5 | 5.6 | 7.8
| 2014-12-15 11:30 | 6.8 | 5.6 | 7.8
| 2014-12-15 12:00 | 7.1 | 5.6 | 7.8
| 2014-12-15 12:30 | 7.7 | 5.6 | 7.8
| 2014-12-15 13:00 | 7.5 | 5.6 | 7.8
| 2014-12-15 13:30 | 7.3 | 5.6 | 7.8
| 2014-12-15 14:00 | 7.3 | 5.6 | 7.8
| 2014-12-15 14:30 | 7.2 | 5.6 | 7.8
| 2014-12-15 15:00 | 7 | 5.6 | 7.8
| 2014-12-15 15:30 | 6.8 | 5.6 | 7.8
| 2014-12-15 16:00 | 6.7 | 6.1 | 7.8
| 2014-12-15 16:30 | 6.5 | 6.1 | 7.8
| 2014-12-15 17:00 | 6.4 | 6.1 | 7.8
| 2014-12-15 17:30 | 6.1 | 6.1 | 7.8
| 2014-12-15 18:00 | 6.1 | 6.1 | 7.8
| 2014-12-15 18:30 | 6.2 | 6.1 | 7.8
| 2014-12-15 19:00 | 6 | 6.1 | 7.8
| 2014-12-15 19:30 | 5.8 | 6.1 | 7.8
| 2014-12-15 20:00 | 5.9 | 6.1 | 7.8
| 2014-12-15 20:30 | 5.9 | 6.1 | 7.8
| 2014-12-15 21:00 | 5.9 | 6.1 | 7.8
| 2014-12-15 21:30 | 5.8 | 6.1 | 7.8
| 2014-12-15 22:00 | 5.8 | 6.1 | 7.8
| 2014-12-15 22:30 | 5.8 | 6.1 | 7.8
| 2014-12-15 23:00 | 5.9 | 6.1 | 7.8
| 2014-12-15 23:30 | 6 | 6.1 | 7.8
| 2014-12-16 | 5.9 | 6.1 | 7.8
| 2014-12-16 00:30 | 5.9 | 6.1 | 7.8
| 2014-12-16 01:00 | 5.9 | 6.1 | 7.8
| 2014-12-16 01:30 | 6 | 6.1 | 7.8
| 2014-12-16 02:00 | 6 | 6.1 | 7.8
| 2014-12-16 02:30 | 5.9 | 6.1 | 7.8
| 2014-12-16 03:00 | 5.9 | 6.1 | 7.8
| 2014-12-16 03:30 | 5.8 | 6.1 | 7.8
| 2014-12-16 04:00 | 5.7 | 6.1 | 7.8
| 2014-12-16 04:30 | 5.7 | 6.1 | 7.8
| 2014-12-16 05:00 | 5.6 | 6.1 | 7.8
| 2014-12-16 05:30 | 5.6 | 6.1 | 7.8
| 2014-12-16 06:00 | 5.6 | 6.1 | 7.8
| 2014-12-16 06:30 | 5.6 | 6.1 | 7.8
| 2014-12-16 07:00 | 5.6 | 6.1 | 7.8
| 2014-12-16 07:30 | 5.6 | 6.1 | 7.8
| 2014-12-16 08:00 | 5.6 | 6.1 | 7.8
| 2014-12-16 08:30 | 5.7 | 6.1 | 7.8
| 2014-12-16 09:00 | 5.8 | 6.1 | 7.8
| 2014-12-16 09:30 | 5.9 | 6.1 | 7.8
| 2014-12-16 10:00 | 6.2 | 6.1 | 7.8
| 2014-12-16 10:30 | 6.3 | 6.1 | 7.8
| 2014-12-16 11:00 | 6.6 | 6.1 | 7.8
| 2014-12-16 11:30 | 6.6 | 6.1 | 7.8
| 2014-12-16 12:00 | 6.9 | 6.1 | 7.8
| 2014-12-16 12:30 | 6.9 | 6.1 | 7.8
| 2014-12-16 13:00 | 7.1 | 6.1 | 7.8
| 2014-12-16 13:30 | 7.3 | 6.1 | 7.8
| 2014-12-16 14:00 | 7.3 | 6.1 | 7.8
| 2014-12-16 14:30 | 7.1 | 6.1 | 7.8
| 2014-12-16 15:00 | 7.2 | 6.1 | 7.8
| 2014-12-16 15:30 | 7.1 | 6.1 | 7.8
| 2014-12-16 16:00 | 6.5 | 6.1 | 7.8
| 2014-12-16 16:30 | 5.8 | 6.1 | 7.8
| 2014-12-16 17:00 | 5.7 | 6.1 | 7.8
| 2014-12-16 17:30 | 5.8 | 6.1 | 7.8
| 2014-12-16 18:00 | 5.8 | 6.1 | 7.8
| 2014-12-16 18:30 | 5.3 | 6.1 | 7.8
| 2014-12-16 19:00 | 4.1 | 6.1 | 7.8
| 2014-12-16 19:30 | 3.1 | 6.1 | 7.8
| 2014-12-16 20:00 | 3.1 | 6.1 | 7.8
| 2014-12-16 20:30 | 2.3 | 6.1 | 7.8
| 2014-12-16 21:00 | 1.6 | 6.1 | 7.8
| 2014-12-16 21:30 | 1.4 | 6.1 | 7.8
| 2014-12-16 22:00 | 0.8 | 6.1 | 7.8
| 2014-12-16 22:30 | 0.8 | 6.1 | 7.8
| 2014-12-16 23:00 | 0.7 | 6.1 | 7.8
| 2014-12-16 23:30 | 0.4 | 6.1 | 7.8
| 2014-12-17 | 0.2 | 5.6 | 7.8
| 2014-12-17 00:30 | 0 | 5.6 | 7.8
| 2014-12-17 01:00 | 0.2 | 5.6 | 7.8
| 2014-12-17 01:30 | 0.1 | 5.6 | 7.8
| 2014-12-17 02:00 | 0 | 5.6 | 7.8
| 2014-12-17 02:30 | -0.1 | 5.6 | 7.8
| 2014-12-17 03:00 | 0.1 | 5.6 | 7.8
| 2014-12-17 03:30 | 0.1 | 5 | 7.8
| 2014-12-17 04:00 | 0.4 | 5 | 7.8
| 2014-12-17 04:30 | 1 | 5 | 7.8
| 2014-12-17 05:00 | 1.5 | 5 | 7.8
| 2014-12-17 05:30 | 1.7 | 5 | 7.8
| 2014-12-17 06:00 | 1.9 | 5 | 7.8
| 2014-12-17 06:30 | 2.1 | 5 | 7.8
| 2014-12-17 07:00 | 2.3 | 5 | 7.8
| 2014-12-17 07:30 | 2.5 | 5 | 7.8
| 2014-12-17 08:00 | 2.8 | 4.4 | 7.8
| 2014-12-17 08:30 | 3.1 | 4.4 | 7.8
| 2014-12-17 09:00 | 3.3 | 4.4 | 7.8
| 2014-12-17 09:30 | 3.6 | 4.4 | 7.8
| 2014-12-17 10:00 | 3.8 | 4.4 | 7.8
| 2014-12-17 10:30 | 3.8 | 4.4 | 7.8
| 2014-12-17 11:00 | 3.9 | 4.4 | 7.8
| 2014-12-17 11:30 | 3.9 | 4.4 | 7.8
| 2014-12-17 12:00 | 3.9 | 4.4 | 7.8
| 2014-12-17 12:30 | 3.9 | 4.4 | 7.8
| 2014-12-17 13:00 | 4 | 4.4 | 7.8
| 2014-12-17 13:30 | 4.1 | 4.4 | 7.8
| 2014-12-17 14:00 | 4.1 | 5 | 7.8
| 2014-12-17 14:30 | 4.2 | 5 | 7.8
| 2014-12-17 15:00 | 4.2 | 5 | 7.8
| 2014-12-17 15:30 | 4.1 | 5 | 7.8
| 2014-12-17 16:00 | 4.1 | 5 | 7.8
| 2014-12-17 16:30 | 4.2 | 5 | 7.8
| 2014-12-17 17:00 | 4.4 | 5 | 7.8
| 2014-12-17 17:30 | 4.7 | 5 | 7.8
| 2014-12-17 18:00 | 4.9 | 5 | 7.8
| 2014-12-17 18:30 | 5.1 | 5 | 7.8
| 2014-12-17 19:00 | 5.3 | 5 | 7.8
| 2014-12-17 19:30 | 5.5 | 5 | 7.8
| 2014-12-17 20:00 | 5.6 | 5 | 7.8
| 2014-12-17 20:30 | 5.7 | 5 | 7.8
| 2014-12-17 21:00 | 5.8 | 5 | 7.8
| 2014-12-17 21:30 | 5.9 | 5 | 7.8
| 2014-12-17 22:00 | 5.9 | 5 | 7.8
| 2014-12-17 22:30 | 6 | 5 | 7.8
| 2014-12-17 23:00 | 6.2 | 5 | 7.8
| 2014-12-17 23:30 | 6.4 | 5 | 7.8
| 2014-12-18 | 6.4 | 5 | 7.8
| 2014-12-18 00:30 | 6.4 | 5 | 7.8
| 2014-12-18 01:00 | 6.6 | 5 | 7.8
| 2014-12-18 01:30 | 6.6 | 5 | 7.8
| 2014-12-18 02:00 | 6.7 | 5 | 7.8
| 2014-12-18 02:30 | 6.7 | 5 | 7.8
| 2014-12-18 03:00 | 6.8 | 5 | 7.8
| 2014-12-18 03:30 | 7 | 5 | 7.8
| 2014-12-18 04:00 | 7.2 | 5 | 7.8
| 2014-12-18 04:30 | 7.3 | 5.6 | 7.8
| 2014-12-18 05:00 | 7.4 | 5.6 | 7.8
| 2014-12-18 05:30 | 7.6 | 5.6 | 7.8
| 2014-12-18 06:00 | 7.8 | 5.6 | 7.8
| 2014-12-18 06:30 | 7.8 | 5.6 | 7.8
| 2014-12-18 07:00 | 7.8 | 5.6 | 7.8
| 2014-12-18 07:30 | 7.9 | 5.6 | 7.8
| 2014-12-18 08:00 | 7.9 | 5.6 | 7.8
| 2014-12-18 08:30 | 8 | 5.6 | 7.8
| 2014-12-18 09:00 | 8.2 | 5.6 | 7.8
| 2014-12-18 09:30 | 8.4 | 5.6 | 7.8
| 2014-12-18 10:00 | 8.6 | 5.6 | 7.8
| 2014-12-18 10:30 | 8.8 | 5.6 | 7.8
| 2014-12-18 11:00 | 8.9 | 5.6 | 7.8
| 2014-12-18 11:30 | 9.1 | 5.6 | 7.8
| 2014-12-18 12:00 | 9.3 | 5.6 | 7.8
| 2014-12-18 12:30 | 9.4 | 5.6 | 7.8
| 2014-12-18 13:00 | 9.6 | 6.1 | 7.8
| 2014-12-18 13:30 | 9.8 | 6.1 | 7.8
| 2014-12-18 14:00 | 9.9 | 6.1 | 7.8
| 2014-12-18 14:30 | 10.1 | 6.1 | 7.8
| 2014-12-18 15:00 | 10.2 | 6.1 | 7.8
| 2014-12-18 15:30 | 10.2 | 6.1 | 7.8
| 2014-12-18 16:00 | 10.4 | 6.1 | 7.8
| 2014-12-18 16:30 | 10.6 | 6.1 | 7.8
| 2014-12-18 17:00 | 10.7 | 6.1 | 7.8
| 2014-12-18 17:30 | 10.8 | 6.1 | 7.8
| 2014-12-18 18:00 | 11.2 | 6.1 | 7.8
| 2014-12-18 18:30 | 11.7 | 6.7 | 7.8
| 2014-12-18 19:00 | 11.9 | 6.7 | 7.8
| 2014-12-18 19:30 | 12.2 | 6.7 | 7.8
| 2014-12-18 20:00 | 12.5 | 6.7 | 7.8
| 2014-12-18 20:30 | 12.6 | 6.7 | 7.8
| 2014-12-18 21:00 | 12.5 | 6.7 | 7.8
| 2014-12-18 21:30 | 12.6 | 6.7 | 7.8
| 2014-12-18 22:00 | 12.4 | 6.7 | 7.8
| 2014-12-18 22:30 | 12.4 | 6.7 | 7.8
| 2014-12-18 23:00 | 12.1 | 6.7 | 7.8
| 2014-12-18 23:30 | 11.9 | 6.7 | 7.8
| 2014-12-19 | 11.8 | 6.7 | 7.8
| 2014-12-19 00:30 | 11.8 | 6.7 | 7.8
| 2014-12-19 01:00 | 11.6 | 6.7 | 7.8
| 2014-12-19 01:30 | 11.4 | 7.2 | 7.8
| 2014-12-19 02:00 | 11.3 | 7.2 | 7.8
| 2014-12-19 02:30 | 11.6 | 7.2 | 7.8
| 2014-12-19 03:00 | 11.6 | 7.2 | 7.8
| 2014-12-19 03:30 | 11.3 | 7.2 | 7.8
| 2014-12-19 04:00 | 11.1 | 7.2 | 7.8
| 2014-12-19 04:30 | 11.1 | 7.2 | 7.8
| 2014-12-19 05:00 | 10.9 | 7.2 | 7.8
| 2014-12-19 05:30 | 10.8 | 7.2 | 7.8
| 2014-12-19 06:00 | 11.2 | 7.2 | 7.8
| 2014-12-19 06:30 | 11.1 | 7.2 | 7.8
| 2014-12-19 07:00 | 11 | 7.2 | 7.8
| 2014-12-19 07:30 | 11.1 | 7.2 | 7.8
| 2014-12-19 08:00 | 10.9 | 7.2 | 7.8
| 2014-12-19 08:30 | 10.8 | 7.2 | 7.8
| 2014-12-19 09:00 | 10.7 | 7.2 | 7.8
| 2014-12-19 09:30 | 10.7 | 7.2 | 7.8
| 2014-12-19 10:00 | 10.7 | 7.2 | 7.8
| 2014-12-19 10:30 | 10.8 | 7.2 | 7.8
| 2014-12-19 11:00 | 10.9 | 7.2 | 7.8
| 2014-12-19 11:30 | 11.2 | 7.2 | 7.8
| 2014-12-19 12:00 | 11.1 | 7.2 | 7.8
| 2014-12-19 12:30 | 11.1 | 7.2 | 7.8
| 2014-12-19 13:00 | 11.2 | 7.2 | 7.8
| 2014-12-19 13:30 | 11.2 | 7.8 | 7.8
| 2014-12-19 14:00 | 11.3 | 7.8 | 7.8
| 2014-12-19 14:30 | 11.2 | 7.8 | 7.8
| 2014-12-19 15:00 | 10.9 | 7.8 | 7.8
| 2014-12-19 15:30 | 10.8 | 7.8 | 7.8
| 2014-12-19 16:00 | 10.7 | 7.8 | 7.8
| 2014-12-19 16:30 | 10.8 | 7.8 | 7.8
| 2014-12-19 17:00 | 10.9 | 7.8 | 7.8
| 2014-12-19 17:30 | 10.8 | 7.8 | 7.8
| 2014-12-19 18:00 | 10.6 | 7.8 | 7.8
| 2014-12-19 18:30 | 9.9 | 7.8 | 7.8
| 2014-12-19 19:00 | 9.5 | 7.8 | 7.8
| 2014-12-19 19:30 | 9 | 7.8 | 7.8
| 2014-12-19 20:00 | 8.5 | 7.8 | 7.8
| 2014-12-19 20:30 | 8.1 | 7.8 | 7.8
| 2014-12-19 21:00 | 7.9 | 7.8 | 7.8
| 2014-12-19 21:30 | 7.5 | 7.8 | 7.8
| 2014-12-19 22:00 | 6.8 | 7.8 | 7.8
| 2014-12-19 22:30 | 6.4 | 7.8 | 7.8
| 2014-12-19 23:00 | 5.9 | 7.8 | 7.8
| 2014-12-19 23:30 | 5.5 | 7.8 | 7.8
| 2014-12-20 | 5.7 | 7.8 | 7.8
| 2014-12-20 00:30 | 5.7 | 7.8 | 7.8
| 2014-12-20 01:00 | 5.7 | 7.8 | 7.8
| 2014-12-20 01:30 | 4.3 | 7.2 | 7.8
| 2014-12-20 02:00 | 3.7 | 7.2 | 7.8
| 2014-12-20 02:30 | 3.4 | 7.2 | 7.8
| 2014-12-20 03:00 | 3.6 | 7.2 | 7.8
| 2014-12-20 03:30 | 2.4 | 7.2 | 7.8
| 2014-12-20 04:00 | 2.5 | 7.2 | 7.8
| 2014-12-20 04:30 | 1.8 | 7.2 | 7.8
| 2014-12-20 05:00 | 1.6 | 6.7 | 7.8
| 2014-12-20 05:30 | 2.3 | 6.7 | 7.8
| 2014-12-20 06:00 | 2.6 | 6.7 | 7.8
| 2014-12-20 06:30 | 2.8 | 6.7 | 7.8
| 2014-12-20 07:00 | 2.9 | 6.7 | 7.8
| 2014-12-20 07:30 | 3 | 6.7 | 7.8
| 2014-12-20 08:00 | 3 | 6.7 | 7.8
| 2014-12-20 08:30 | 3.4 | 6.1 | 7.8
| 2014-12-20 09:00 | 4.1 | 6.1 | 7.8
| 2014-12-20 09:30 | 4.7 | 6.1 | 7.8
| 2014-12-20 10:00 | 5.3 | 6.1 | 7.8
| 2014-12-20 10:30 | 5.3 | 6.1 | 7.8
| 2014-12-20 11:00 | 5.6 | 6.1 | 7.8
| 2014-12-20 11:30 | 6.1 | 6.1 | 7.8
| 2014-12-20 12:00 | 6.1 | 6.1 | 7.8
| 2014-12-20 12:30 | 6 | 6.1 | 7.8
| 2014-12-20 13:00 | 6.8 | 6.1 | 7.8
| 2014-12-20 13:30 | 6.7 | 6.1 | 7.8
| 2014-12-20 14:00 | 6.8 | 6.1 | 7.8
| 2014-12-20 14:30 | 6.4 | 6.1 | 7.8
| 2014-12-20 15:00 | 5.9 | 6.1 | 7.8
| 2014-12-20 15:30 | 5.8 | 6.1 | 7.8
| 2014-12-20 16:00 | 6 | 6.1 | 7.8
| 2014-12-20 16:30 | 6.2 | 6.1 | 7.8
| 2014-12-20 17:00 | 6.7 | 6.1 | 7.8
| 2014-12-20 17:30 | 6.8 | 6.1 | 7.8
| 2014-12-20 18:00 | 6.8 | 6.1 | 7.8
| 2014-12-20 18:30 | 6.8 | 6.1 | 7.8
| 2014-12-20 19:00 | 6.6 | 6.1 | 7.8
| 2014-12-20 19:30 | 6.3 | 6.1 | 7.8
| 2014-12-20 20:00 | 5.9 | 6.1 | 7.8
| 2014-12-20 20:30 | 5.9 | 6.1 | 7.8
| 2014-12-20 21:00 | 6.1 | 6.1 | 7.8
| 2014-12-20 21:30 | 5.6 | 6.1 | 7.8
| 2014-12-20 22:00 | 5.4 | 6.1 | 7.8
| 2014-12-20 22:30 | 5.2 | 6.1 | 7.8
| 2014-12-20 23:00 | 4.7 | 6.1 | 7.8
| 2014-12-20 23:30 | 3.7 | 6.1 | 7.8
| 2014-12-21 | 4 | 6.1 | 7.8
| 2014-12-21 00:30 | 4.3 | 6.1 | 7.8
| 2014-12-21 01:00 | 3.9 | 6.1 | 7.8
| 2014-12-21 01:30 | 4 | 6.1 | 7.8
| 2014-12-21 02:00 | 2.3 | 6.1 | 7.8
| 2014-12-21 02:30 | 2.7 | 5.6 | 7.8
| 2014-12-21 03:00 | 2.6 | 5.6 | 7.8
| 2014-12-21 03:30 | 4.7 | 5.6 | 7.8
| 2014-12-21 04:00 | 4.9 | 5.6 | 7.8
| 2014-12-21 04:30 | 4.2 | 5.6 | 7.8
| 2014-12-21 05:00 | 4.1 | 5.6 | 7.8
| 2014-12-21 05:30 | 3.8 | 5.6 | 7.8
| 2014-12-21 06:00 | 3.7 | 5.6 | 7.8
| 2014-12-21 06:30 | 3.3 | 5.6 | 7.8
| 2014-12-21 07:00 | 3.3 | 5.6 | 7.8
| 2014-12-21 07:30 | 3.1 | 5.6 | 7.8
| 2014-12-21 08:00 | 3.1 | 5.6 | 7.8
| 2014-12-21 08:30 | 3 | 5.6 | 7.8
| 2014-12-21 09:00 | 3.4 | 5.6 | 7.8
| 2014-12-21 09:30 | 4.2 | 5.6 | 7.8
| 2014-12-21 10:00 | 5.1 | 5.6 | 7.8
| 2014-12-21 10:30 | 5.2 | 5.6 | 7.8
| 2014-12-21 11:00 | 5.5 | 5.6 | 7.8
| 2014-12-21 11:30 | 6.1 | 5.6 | 7.8
| 2014-12-21 12:00 | 6.1 | 5.6 | 7.8
| 2014-12-21 12:30 | 6.2 | 5.6 | 7.8
| 2014-12-21 13:00 | 6.2 | 5.6 | 7.8
| 2014-12-21 13:30 | 6.5 | 5.6 | 7.8
| 2014-12-21 14:00 | 6.6 | 5.6 | 7.8
| 2014-12-21 14:30 | 6.7 | 5.6 | 7.8
| 2014-12-21 15:00 | 6.6 | 5.6 | 7.8
| 2014-12-21 15:30 | 6.7 | 5.6 | 7.8
| 2014-12-21 16:00 | 6.5 | 5.6 | 7.8
| 2014-12-21 16:30 | 6.4 | 5.6 | 7.8
| 2014-12-21 17:00 | 6.3 | 5.6 | 7.8
| 2014-12-21 17:30 | 6.4 | 5.6 | 7.8
| 2014-12-21 18:00 | 6.5 | 5.6 | 7.8
| 2014-12-21 18:30 | 6.7 | 5.6 | 7.8
| 2014-12-21 19:00 | 6.8 | 5.6 | 7.8
| 2014-12-21 19:30 | 6.9 | 5.6 | 7.8
| 2014-12-21 20:00 | 6.8 | 5.6 | 7.8
| 2014-12-21 20:30 | 6.7 | 5.6 | 7.8
| 2014-12-21 21:00 | 6.8 | 5.6 | 7.8
| 2014-12-21 21:30 | 6.8 | 5.6 | 7.8
| 2014-12-21 22:00 | 6.9 | 5.6 | 7.8
| 2014-12-21 22:30 | 6.8 | 5.6 | 7.8
| 2014-12-21 23:00 | 6.9 | 5.6 | 7.8
| 2014-12-21 23:30 | 6.9 | 5.6 | 7.8
| 2014-12-22 | 7.1 | 5.6 | 7.8
| 2014-12-22 00:30 | 7 | 5.6 | 7.8
| 2014-12-22 01:00 | 6.9 | 5.6 | 7.8
| 2014-12-22 01:30 | 6.9 | 5.6 | 7.8
| 2014-12-22 02:00 | 6.9 | 5.6 | 7.8
| 2014-12-22 02:30 | 6.8 | 5.6 | 7.8
| 2014-12-22 03:00 | 6.9 | 5.6 | 7.8
| 2014-12-22 03:30 | 6.9 | 5.6 | 7.8
| 2014-12-22 04:00 | 6.9 | 5.6 | 7.8
| 2014-12-22 04:30 | 7.2 | 5.6 | 7.8
| 2014-12-22 05:00 | 7.1 | 5.6 | 7.8
| 2014-12-22 05:30 | 7.1 | 5.6 | 7.8
| 2014-12-22 06:00 | 7.1 | 5.6 | 7.8
| 2014-12-22 06:30 | 7.1 | 5.6 | 7.8
| 2014-12-22 07:00 | 7.1 | 5.6 | 7.8
| 2014-12-22 07:30 | 7.2 | 5.6 | 7.8
| 2014-12-22 08:00 | 7.1 | 5.6 | 7.8
| 2014-12-22 08:30 | 7.1 | 5.6 | 7.8
| 2014-12-22 09:00 | 7 | 5.6 | 7.8
| 2014-12-22 09:30 | 7 | 5.6 | 7.8
| 2014-12-22 10:00 | 7 | 5.6 | 7.8
| 2014-12-22 10:30 | 7 | 5.6 | 7.8
| 2014-12-22 11:00 | 7.2 | 5.6 | 7.8
| 2014-12-22 11:30 | 7.3 | 5.6 | 7.8
| 2014-12-22 12:00 | 7.6 | 5.6 | 7.8
| 2014-12-22 12:30 | 7.6 | 6.1 | 7.8
| 2014-12-22 13:00 | 7.7 | 6.1 | 7.8
| 2014-12-22 13:30 | 7.7 | 6.1 | 7.8
| 2014-12-22 14:00 | 7.6 | 6.1 | 7.8
| 2014-12-22 14:30 | 7.6 | 6.1 | 7.8
| 2014-12-22 15:00 | 7.6 | 6.1 | 7.8
| 2014-12-22 15:30 | 7.6 | 6.1 | 7.8
| 2014-12-22 16:00 | 7.6 | 6.1 | 7.8
| 2014-12-22 16:30 | 7.5 | 6.1 | 7.8
| 2014-12-22 17:00 | 7.4 | 6.1 | 7.8
| 2014-12-22 17:30 | 7.4 | 6.1 | 7.8
| 2014-12-22 18:00 | 7.5 | 6.1 | 7.8
| 2014-12-22 18:30 | 7.6 | 6.1 | 7.8
| 2014-12-22 19:00 | 7.7 | 6.1 | 7.8
| 2014-12-22 19:30 | 7.8 | 6.1 | 7.8
| 2014-12-22 20:00 | 7.8 | 6.1 | 7.8
| 2014-12-22 20:30 | 7.8 | 6.1 | 7.8
| 2014-12-22 21:00 | 7.8 | 6.1 | 7.8
| 2014-12-22 21:30 | 7.8 | 6.1 | 7.8
| 2014-12-22 22:00 | 7.7 | 6.1 | 7.8
| 2014-12-22 22:30 | 7.7 | 6.1 | 7.8
| 2014-12-22 23:00 | 7.6 | 6.1 | 7.8
| 2014-12-22 23:30 | 7.7 | 6.1 | 7.8
| 2014-12-23 | 7.8 | 6.1 | 7.8
| 2014-12-23 00:30 | 7.9 | 6.1 | 7.8
| 2014-12-23 01:00 | 7.9 | 6.1 | 7.8
| 2014-12-23 01:30 | 7.9 | 6.1 | 7.8
| 2014-12-23 02:00 | 7.9 | 6.1 | 7.8
| 2014-12-23 02:30 | 8 | 6.1 | 7.8
| 2014-12-23 03:00 | 8.2 | 6.1 | 7.8
| 2014-12-23 03:30 | 8.2 | 6.1 | 7.8
| 2014-12-23 04:00 | 8.2 | 6.1 | 7.8
| 2014-12-23 04:30 | 8.1 | 6.1 | 7.8
| 2014-12-23 05:00 | 8 | 6.1 | 7.8
| 2014-12-23 05:30 | 8.1 | 6.1 | 7.8
| 2014-12-23 06:00 | 7.8 | 6.1 | 7.8
| 2014-12-23 06:30 | 7.4 | 6.1 | 7.8
| 2014-12-23 07:00 | 7.5 | 6.1 | 7.8
| 2014-12-23 07:30 | 7.6 | 6.1 | 7.8
| 2014-12-23 08:00 | 7.6 | 6.1 | 7.8
| 2014-12-23 08:30 | 7.7 | 6.1 | 7.8
| 2014-12-23 09:00 | 7.7 | 6.1 | 7.8
| 2014-12-23 09:30 | 8.1 | 6.1 | 7.8
| 2014-12-23 10:00 | 8.3 | 6.1 | 7.8
| 2014-12-23 10:30 | 8.3 | 6.1 | 7.8
| 2014-12-23 11:00 | 8.4 | 6.1 | 7.8
| 2014-12-23 11:30 | 8.5 | 6.1 | 7.8
| 2014-12-23 12:00 | 8.7 | 6.1 | 7.8
| 2014-12-23 12:30 | 8.7 | 6.7 | 7.8
| 2014-12-23 13:00 | 8.8 | 6.7 | 7.8
| 2014-12-23 13:30 | 8.8 | 6.7 | 7.8
| 2014-12-23 14:00 | 8.7 | 6.7 | 7.8
| 2014-12-23 14:30 | 8.6 | 6.7 | 7.8
| 2014-12-23 15:00 | 8.5 | 6.7 | 7.8
| 2014-12-23 15:30 | 8.4 | 6.7 | 7.8
| 2014-12-23 16:00 | 8.4 | 6.7 | 7.8
| 2014-12-23 16:30 | 8.3 | 6.7 | 7.8
| 2014-12-23 17:00 | 8.3 | 6.7 | 7.8
| 2014-12-23 17:30 | 8.2 | 6.7 | 7.8
| 2014-12-23 18:00 | 8.1 | 6.7 | 7.8
| 2014-12-23 18:30 | 8.1 | 6.7 | 7.8
| 2014-12-23 19:00 | 7.8 | 6.7 | 7.8
| 2014-12-23 19:30 | 7.7 | 6.7 | 7.8
| 2014-12-23 20:00 | 7.5 | 6.7 | 7.8
| 2014-12-23 20:30 | 7.3 | 6.7 | 7.8
| 2014-12-23 21:00 | 7 | 6.7 | 7.8
| 2014-12-23 21:30 | 6.9 | 6.7 | 7.8
| 2014-12-23 22:00 | 6.9 | 6.7 | 7.8
| 2014-12-23 22:30 | 6.8 | 6.7 | 7.8
| 2014-12-23 23:00 | 6.7 | 6.7 | 7.8
| 2014-12-23 23:30 | 6.5 | 6.7 | 7.8
| 2014-12-24 | 6.5 | 6.7 | 7.8
| 2014-12-24 00:30 | 6.1 | 6.7 | 7.8
| 2014-12-24 01:00 | 5.8 | 6.7 | 7.8
| 2014-12-24 01:30 | 5.4 | 6.7 | 7.8
| 2014-12-24 02:00 | 5.2 | 6.7 | 7.8
| 2014-12-24 02:30 | 4.8 | 6.7 | 7.8
| 2014-12-24 03:00 | 4.4 | 6.7 | 7.8
| 2014-12-24 03:30 | 4.6 | 6.7 | 7.8
| 2014-12-24 04:00 | 4.8 | 6.7 | 7.8
| 2014-12-24 04:30 | 5.2 | 6.7 | 7.8
| 2014-12-24 05:00 | 5 | 6.7 | 7.8
| 2014-12-24 05:30 | 4.8 | 6.7 | 7.8
| 2014-12-24 06:00 | 4.8 | 6.7 | 7.8
| 2014-12-24 06:30 | 4.9 | 6.7 | 7.8
| 2014-12-24 07:00 | 4.7 | 6.1 | 7.8
| 2014-12-24 07:30 | 4.8 | 6.1 | 7.8
| 2014-12-24 08:00 | 4.9 | 6.1 | 7.8
| 2014-12-24 08:30 | 5.3 | 6.1 | 7.8
| 2014-12-24 09:00 | 5.6 | 6.1 | 7.8
| 2014-12-24 09:30 | 5.6 | 6.1 | 7.8
| 2014-12-24 10:00 | 5.9 | 6.1 | 7.8
| 2014-12-24 10:30 | 6.3 | 6.1 | 7.8
| 2014-12-24 11:00 | 7.1 | 6.1 | 7.8
| 2014-12-24 11:30 | 7.5 | 6.1 | 7.8
| 2014-12-24 12:00 | 7.8 | 6.1 | 7.8
| 2014-12-24 12:30 | 8.2 | 6.1 | 7.8
| 2014-12-24 13:00 | 8.2 | 6.1 | 7.8
| 2014-12-24 13:30 | 8.3 | 6.1 | 7.8
| 2014-12-24 14:00 | 8.3 | 6.1 | 7.8
| 2014-12-24 14:30 | 8.3 | 6.1 | 7.8
| 2014-12-24 15:00 | 8.4 | 6.1 | 7.8
| 2014-12-24 15:30 | 8.5 | 6.1 | 7.8
| 2014-12-24 16:00 | 8.4 | 6.1 | 7.8
| 2014-12-24 16:30 | 8.4 | 6.1 | 7.8
| 2014-12-24 17:00 | 8.5 | 6.1 | 7.8
| 2014-12-24 17:30 | 8.5 | 6.1 | 7.8
| 2014-12-24 18:00 | 8.5 | 6.1 | 7.8
| 2014-12-24 18:30 | 8.6 | 6.1 | 7.8
| 2014-12-24 19:00 | 8.5 | 6.1 | 7.8
| 2014-12-24 19:30 | 8.5 | 6.1 | 7.8
| 2014-12-24 20:00 | 8.6 | 6.1 | 7.8
| 2014-12-24 20:30 | 8.6 | 6.7 | 7.8
| 2014-12-24 21:00 | 8.6 | 6.7 | 7.8
| 2014-12-24 21:30 | 8.6 | 6.7 | 7.8
| 2014-12-24 22:00 | 8.7 | 6.7 | 7.8
| 2014-12-24 22:30 | 8.7 | 6.7 | 7.8
| 2014-12-24 23:00 | 8.5 | 6.7 | 7.8
| 2014-12-24 23:30 | 8.6 | 6.7 | 7.8
| 2014-12-25 | 7.8 | 6.7 | 7.8
| 2014-12-25 00:30 | 7.3 | 6.7 | 7.8
| 2014-12-25 01:00 | 6.9 | 6.7 | 7.8
| 2014-12-25 01:30 | 6.5 | 6.7 | 7.8
| 2014-12-25 02:00 | 6.3 | 6.7 | 7.8
| 2014-12-25 02:30 | 6.1 | 6.7 | 7.8
| 2014-12-25 03:00 | 5.8 | 6.7 | 7.8
| 2014-12-25 03:30 | 5.2 | 6.7 | 7.8
| 2014-12-25 04:00 | 5.3 | 6.7 | 7.8
| 2014-12-25 04:30 | 4.8 | 6.7 | 7.8
| 2014-12-25 05:00 | 3.5 | 6.7 | 7.8
| 2014-12-25 05:30 | 2.6 | 6.7 | 7.8
| 2014-12-25 06:00 | 2.6 | 6.7 | 7.8
| 2014-12-25 06:30 | 3 | 6.1 | 7.8
| 2014-12-25 07:00 | 2.3 | 6.1 | 7.8
| 2014-12-25 07:30 | 1.8 | 6.1 | 7.8
| 2014-12-25 08:00 | 2 | 6.1 | 7.8
| 2014-12-25 08:30 | 1.8 | 6.1 | 7.8
| 2014-12-25 09:00 | 2.1 | 6.1 | 7.8
| 2014-12-25 09:30 | 1.8 | 6.1 | 7.8
| 2014-12-25 10:00 | 3.2 | 6.1 | 7.8
| 2014-12-25 10:30 | 4.3 | 6.1 | 7.8
| 2014-12-25 11:00 | 4.8 | 5.6 | 7.8
| 2014-12-25 11:30 | 5.1 | 5.6 | 7.8
| 2014-12-25 12:00 | 5.4 | 5.6 | 7.8
| 2014-12-25 12:30 | 5.8 | 5.6 | 7.8
| 2014-12-25 13:00 | 6 | 5.6 | 7.8
| 2014-12-25 13:30 | 6.2 | 5.6 | 7.8
| 2014-12-25 14:00 | 6.1 | 5.6 | 7.8
| 2014-12-25 14:30 | 6.2 | 5.6 | 7.8
| 2014-12-25 15:00 | 6.2 | 5.6 | 7.8
| 2014-12-25 15:30 | 6.1 | 5.6 | 7.8
| 2014-12-25 16:00 | 5.9 | 5.6 | 7.8
| 2014-12-25 16:30 | 5.7 | 5.6 | 7.8
| 2014-12-25 17:00 | 5.2 | 5.6 | 7.8
| 2014-12-25 17:30 | 5.2 | 5.6 | 7.8
| 2014-12-25 18:00 | 5 | 5.6 | 7.8
| 2014-12-25 18:30 | 5.1 | 5.6 | 7.8
| 2014-12-25 19:00 | 5 | 5.6 | 7.8
| 2014-12-25 19:30 | 4.8 | 5.6 | 7.8
| 2014-12-25 20:00 | 4.6 | 5.6 | 7.8
| 2014-12-25 20:30 | 4.4 | 5.6 | 7.8
| 2014-12-25 21:00 | 4.2 | 5.6 | 7.8
| 2014-12-25 21:30 | 3.8 | 5.6 | 7.8
| 2014-12-25 22:00 | 3.7 | 5.6 | 7.8
| 2014-12-25 22:30 | 3.8 | 5.6 | 7.8
| 2014-12-25 23:00 | 3.2 | 5.6 | 7.8
| 2014-12-25 23:30 | 2.7 | 5.6 | 7.8
| 2014-12-26 | 1.7 | 5.6 | 7.8
| 2014-12-26 00:30 | 0.8 | 5.6 | 7.8
| 2014-12-26 01:00 | 0.8 | 5.6 | 7.8
| 2014-12-26 01:30 | -0.1 | 5.6 | 7.8
| 2014-12-26 02:00 | -0.3 | 5.6 | 7.8
| 2014-12-26 02:30 | -0.7 | 5.6 | 7.8
| 2014-12-26 03:00 | -1.1 | 5.6 | 7.8
| 2014-12-26 03:30 | -1 | 5 | 7.8
| 2014-12-26 04:00 | -0.3 | 5 | 7.8
| 2014-12-26 04:30 | 0.1 | 5 | 7.8
| 2014-12-26 05:00 | -0.3 | 5 | 7.8
| 2014-12-26 05:30 | -0.8 | 5 | 7.8
| 2014-12-26 06:00 | -1.3 | 5 | 7.8
| 2014-12-26 06:30 | -1.1 | 5 | 7.8
| 2014-12-26 07:00 | -1.6 | 5 | 7.8
| 2014-12-26 07:30 | -1.3 | 5 | 7.8
| 2014-12-26 08:00 | -0.7 | 4.4 | 7.8
| 2014-12-26 08:30 | -0.4 | 4.4 | 7.8
| 2014-12-26 09:00 | -0.3 | 4.4 | 7.8
| 2014-12-26 09:30 | 0.2 | 4.4 | 7.8
| 2014-12-26 10:00 | 1 | 4.4 | 7.8
| 2014-12-26 10:30 | 1.6 | 4.4 | 7.8
| 2014-12-26 11:00 | 2.1 | 4.4 | 7.8
| 2014-12-26 11:30 | 2.6 | 4.4 | 7.8
| 2014-12-26 12:00 | 2.7 | 4.4 | 7.8
| 2014-12-26 12:30 | 3.1 | 4.4 | 7.8
| 2014-12-26 13:00 | 2.9 | 4.4 | 7.8
| 2014-12-26 13:30 | 3.9 | 4.4 | 7.8
| 2014-12-26 14:00 | 3.8 | 4.4 | 7.8
| 2014-12-26 14:30 | 3.6 | 4.4 | 7.8
| 2014-12-26 15:00 | 3.4 | 4.4 | 7.8
| 2014-12-26 15:30 | 3.3 | 4.4 | 7.8
| 2014-12-26 16:00 | 3.2 | 4.4 | 7.8
| 2014-12-26 16:30 | 2.6 | 4.4 | 7.8
| 2014-12-26 17:00 | 2.2 | 4.4 | 7.8
| 2014-12-26 17:30 | 1.7 | 4.4 | 7.8
| 2014-12-26 18:00 | 1.5 | 4.4 | 7.8
| 2014-12-26 18:30 | 1.3 | 4.4 | 7.8
| 2014-12-26 19:00 | 1.1 | 4.4 | 7.8
| 2014-12-26 19:30 | 0.4 | 4.4 | 7.8
| 2014-12-26 20:00 | -0.1 | 4.4 | 7.8
| 2014-12-26 20:30 | -0.2 | 4.4 | 7.8
| 2014-12-26 21:00 | -0.8 | 4.4 | 7.8
| 2014-12-26 21:30 | -0.9 | 4.4 | 7.8
| 2014-12-26 22:00 | -0.7 | 4.4 | 7.8
| 2014-12-26 22:30 | -0.7 | 4.4 | 7.8
| 2014-12-26 23:00 | -1 | 4.4 | 7.8
| 2014-12-26 23:30 | -1.2 | 4.4 | 7.8
| 2014-12-27 | -0.8 | 4.4 | 7.8
| 2014-12-27 00:30 | -0.1 | 4.4 | 7.8
| 2014-12-27 01:00 | 0.1 | 3.9 | 7.8
| 2014-12-27 01:30 | 0.2 | 3.9 | 7.8
| 2014-12-27 02:00 | 0.6 | 3.9 | 7.8
| 2014-12-27 02:30 | 0.7 | 3.9 | 7.8
| 2014-12-27 03:00 | 0.7 | 3.9 | 7.8
| 2014-12-27 03:30 | 1 | 3.9 | 7.8
| 2014-12-27 04:00 | 1.1 | 3.9 | 7.8
| 2014-12-27 04:30 | 0.8 | 3.9 | 7.8
| 2014-12-27 05:00 | 0.7 | 3.9 | 7.8
| 2014-12-27 05:30 | 0.6 | 3.9 | 7.8
| 2014-12-27 06:00 | 0.7 | 3.9 | 7.8
| 2014-12-27 06:30 | 0.8 | 3.9 | 7.8
| 2014-12-27 07:00 | 0.6 | 3.9 | 7.8
| 2014-12-27 07:30 | 0.6 | 3.9 | 7.8
| 2014-12-27 08:00 | 0.6 | 3.9 | 7.8
| 2014-12-27 08:30 | 0.3 | 3.9 | 7.8
| 2014-12-27 09:00 | 0.2 | 3.9 | 7.8
| 2014-12-27 09:30 | 0.3 | 3.9 | 7.8
| 2014-12-27 10:00 | 0.3 | 3.9 | 7.8
| 2014-12-27 10:30 | 0.3 | 3.9 | 7.8
| 2014-12-27 11:00 | 0.4 | 3.9 | 7.8
| 2014-12-27 11:30 | 0.5 | 3.9 | 7.8
| 2014-12-27 12:00 | 0.4 | 3.9 | 7.8
| 2014-12-27 12:30 | 0.5 | 3.3 | 7.8
| 2014-12-27 13:00 | 0.5 | 3.3 | 7.8
| 2014-12-27 13:30 | 0.5 | 3.3 | 7.8
| 2014-12-27 14:00 | 0.4 | 3.3 | 7.8
| 2014-12-27 14:30 | 0.6 | 3.3 | 7.8
| 2014-12-27 15:00 | 0.7 | 3.3 | 7.8
| 2014-12-27 15:30 | 0.6 | 3.3 | 7.8
| 2014-12-27 16:00 | 0.6 | 3.3 | 7.8
| 2014-12-27 16:30 | 0.5 | 3.3 | 7.8
| 2014-12-27 17:00 | 0.4 | 3.3 | 7.8
| 2014-12-27 17:30 | 0.3 | 3.3 | 7.8
| 2014-12-27 18:00 | 0.2 | 3.3 | 7.8
| 2014-12-27 18:30 | 0 | 3.3 | 7.8
| 2014-12-27 19:00 | -0.2 | 3.3 | 7.8
| 2014-12-27 19:30 | -0.4 | 3.3 | 7.8
| 2014-12-27 20:00 | -0.7 | 3.3 | 7.8
| 2014-12-27 20:30 | -0.8 | 3.3 | 7.8
| 2014-12-27 21:00 | -0.8 | 3.3 | 7.8
| 2014-12-27 21:30 | -0.9 | 3.3 | 7.8
| 2014-12-27 22:00 | -1.1 | 3.3 | 7.8
| 2014-12-27 22:30 | -1.2 | 3.3 | 7.8
| 2014-12-27 23:00 | -1.3 | 3.3 | 7.8
| 2014-12-27 23:30 | -1.4 | 3.3 | 7.8
| 2014-12-28 | -1.4 | 3.3 | 7.8
| 2014-12-28 00:30 | -1.4 | 3.3 | 7.8
| 2014-12-28 01:00 | -1.6 | 3.3 | 7.8
| 2014-12-28 01:30 | -1.8 | 3.3 | 7.2
| 2014-12-28 02:00 | -2.1 | 3.3 | 7.2
| 2014-12-28 02:30 | -2.5 | 3.3 | 7.2
| 2014-12-28 03:00 | -2.7 | 3.3 | 7.2
| 2014-12-28 03:30 | -2.7 | 3.3 | 7.2
| 2014-12-28 04:00 | -2.9 | 3.3 | 7.2
| 2014-12-28 04:30 | -3 | 3.3 | 7.2
| 2014-12-28 05:00 | -3 | 3.3 | 7.2
| 2014-12-28 05:30 | -2.9 | 3.3 | 7.2
| 2014-12-28 06:00 | -3.2 | 3.3 | 7.2
| 2014-12-28 06:30 | -3.6 | 3.3 | 7.2
| 2014-12-28 07:00 | -3.7 | 3.3 | 7.2
| 2014-12-28 07:30 | -3.8 | 3.3 | 7.2
| 2014-12-28 08:00 | -4.1 | 3.3 | 7.2
| 2014-12-28 08:30 | -4.2 | 3.3 | 7.2
| 2014-12-28 09:00 | -4.4 | 3.3 | 7.2
| 2014-12-28 09:30 | -4.3 | 3.3 | 7.2
| 2014-12-28 10:00 | -4.4 | 3.3 | 7.2
| 2014-12-28 10:30 | -4.9 | 3.3 | 7.2
| 2014-12-28 11:00 | -5.3 | 2.8 | 7.2
| 2014-12-28 11:30 | -4.5 | 2.8 | 7.2
| 2014-12-28 12:00 | -4 | 2.8 | 7.2
| 2014-12-28 12:30 | -3.7 | 2.8 | 7.2
| 2014-12-28 13:00 | -3.3 | 2.8 | 7.2
| 2014-12-28 13:30 | -3.1 | 2.8 | 7.2
| 2014-12-28 14:00 | -2.8 | 2.8 | 7.2
| 2014-12-28 14:30 | -2.6 | 2.8 | 7.2
| 2014-12-28 15:00 | -2.6 | 2.8 | 7.2
| 2014-12-28 15:30 | -2.6 | 2.8 | 7.2
| 2014-12-28 16:00 | -3 | 2.8 | 7.2
| 2014-12-28 16:30 | -3.4 | 2.8 | 7.2
| 2014-12-28 17:00 | -3.8 | 2.8 | 7.2
| 2014-12-28 17:30 | -4.7 | 2.8 | 7.2
| 2014-12-28 18:00 | -5.3 | 2.8 | 7.2
| 2014-12-28 18:30 | -5.9 | 2.8 | 7.2
| 2014-12-28 19:00 | -5.7 | 2.8 | 7.2
| 2014-12-28 19:30 | -5.6 | 2.8 | 7.2
| 2014-12-28 20:00 | -5.9 | 2.8 | 7.2
| 2014-12-28 20:30 | -6.6 | 2.8 | 7.2
| 2014-12-28 21:00 | -7.1 | 2.8 | 7.2
| 2014-12-28 21:30 | -7.8 | 2.8 | 7.2
| 2014-12-28 22:00 | -8.3 | 2.8 | 7.2
| 2014-12-28 22:30 | -8.6 | 2.8 | 7.2
| 2014-12-28 23:00 | -8.6 | 2.8 | 7.2
| 2014-12-28 23:30 | -9 | 2.8 | 7.2
| 2014-12-29 | -9.4 | 2.8 | 7.2
| 2014-12-29 00:30 | -9.7 | 2.2 | 7.2
| 2014-12-29 01:00 | -10.1 | 2.2 | 7.2
| 2014-12-29 01:30 | -10.2 | 2.2 | 7.2
| 2014-12-29 02:00 | -10 | 2.2 | 7.2
| 2014-12-29 02:30 | -9.6 | 2.2 | 7.2
| 2014-12-29 03:00 | -9.5 | 2.2 | 7.2
| 2014-12-29 03:30 | -8.7 | 2.2 | 7.2
| 2014-12-29 04:00 | -8.3 | 2.2 | 7.2
| 2014-12-29 04:30 | -7.1 | 2.2 | 7.2
| 2014-12-29 05:00 | -6.3 | 2.2 | 7.2
| 2014-12-29 05:30 | -5.7 | 2.2 | 7.2
| 2014-12-29 06:00 | -5.5 | 2.2 | 7.2
| 2014-12-29 06:30 | -5.3 | 2.2 | 7.2
| 2014-12-29 07:00 | -5.1 | 2.2 | 7.2
| 2014-12-29 07:30 | -5.1 | 2.2 | 7.2
| 2014-12-29 08:00 | -5.2 | 2.2 | 7.2
| 2014-12-29 08:30 | -5.1 | 2.2 | 7.2
| 2014-12-29 09:00 | -4.8 | 2.2 | 7.2
| 2014-12-29 09:30 | -4.4 | 2.2 | 7.2
| 2014-12-29 10:00 | -4 | 2.2 | 7.2
| 2014-12-29 10:30 | -3.6 | 2.2 | 7.2
| 2014-12-29 11:00 | -3.2 | 2.2 | 7.2
| 2014-12-29 11:30 | -3 | 2.2 | 7.2
| 2014-12-29 12:00 | -2.6 | 2.2 | 7.2
| 2014-12-29 12:30 | -2.4 | 2.2 | 6.7
| 2014-12-29 13:00 | -2.2 | 2.2 | 6.7
| 2014-12-29 13:30 | -2.2 | 2.2 | 6.7
| 2014-12-29 14:00 | -1.7 | 2.2 | 6.7
| 2014-12-29 14:30 | -1.8 | 2.2 | 6.7
| 2014-12-29 15:00 | -1.8 | 2.2 | 6.7
| 2014-12-29 15:30 | -1.8 | 2.2 | 6.7
| 2014-12-29 16:00 | -1.8 | 2.2 | 6.7
| 2014-12-29 16:30 | -1.6 | 2.2 | 6.7
| 2014-12-29 17:00 | -1.9 | 2.2 | 6.7
| 2014-12-29 17:30 | -2.2 | 2.2 | 6.7
| 2014-12-29 18:00 | -2.3 | 2.2 | 6.7
| 2014-12-29 18:30 | -2.4 | 2.2 | 6.7
| 2014-12-29 19:00 | -3.1 | 2.2 | 6.7
| 2014-12-29 19:30 | -3.4 | 2.2 | 6.7
| 2014-12-29 20:00 | -3.3 | 2.2 | 6.7
| 2014-12-29 20:30 | -3.5 | 2.2 | 6.7
| 2014-12-29 21:00 | -3.3 | 2.2 | 6.7
| 2014-12-29 21:30 | -3.5 | 2.2 | 6.7
| 2014-12-29 22:00 | -3.9 | 2.2 | 6.7
| 2014-12-29 22:30 | -4.2 | 2.2 | 6.7
| 2014-12-29 23:00 | -4 | 2.2 | 6.7
| 2014-12-29 23:30 | -3.8 | 2.2 | 6.7
| 2014-12-30 | -3.9 | 2.2 | 6.7
| 2014-12-30 00:30 | -4.2 | 2.2 | 6.7
| 2014-12-30 01:00 | -4 | 2.2 | 6.7
| 2014-12-30 01:30 | -3.7 | 2.2 | 6.7
| 2014-12-30 02:00 | -4 | 2.2 | 6.7
| 2014-12-30 02:30 | -4.4 | 2.2 | 6.7
| 2014-12-30 03:00 | -4.2 | 2.2 | 6.7
| 2014-12-30 03:30 | -2.8 | 2.2 | 6.7
| 2014-12-30 04:00 | -2.6 | 2.2 | 6.7
| 2014-12-30 04:30 | -2.3 | 2.2 | 6.7
| 2014-12-30 05:00 | -2.2 | 2.2 | 6.7
| 2014-12-30 05:30 | -2.2 | 2.2 | 6.7
| 2014-12-30 06:00 | -2.1 | 2.2 | 6.7
| 2014-12-30 06:30 | -1.9 | 2.2 | 6.7
| 2014-12-30 07:00 | -1.8 | 2.2 | 6.7
| 2014-12-30 07:30 | -1.7 | 1.7 | 6.7
| 2014-12-30 08:00 | -1.6 | 1.7 | 6.7
| 2014-12-30 08:30 | -1.6 | 1.7 | 6.7
| 2014-12-30 09:00 | -1.5 | 1.7 | 6.7
| 2014-12-30 09:30 | -1.3 | 1.7 | 6.7
| 2014-12-30 10:00 | -1.1 | 1.7 | 6.7
| 2014-12-30 10:30 | -0.8 | 1.7 | 6.7
| 2014-12-30 11:00 | -0.5 | 1.7 | 6.7
| 2014-12-30 11:30 | -0.3 | 1.7 | 6.7
| 2014-12-30 12:00 | -0.1 | 1.7 | 6.7
| 2014-12-30 12:30 | 0 | 1.7 | 6.7
| 2014-12-30 13:00 | 0.3 | 1.7 | 6.7
| 2014-12-30 13:30 | 0.4 | 1.7 | 6.7
| 2014-12-30 14:00 | 0.4 | 1.7 | 6.7
| 2014-12-30 14:30 | 0.6 | 1.7 | 6.7
| 2014-12-30 15:00 | 0.7 | 1.7 | 6.7
| 2014-12-30 15:30 | 0.6 | 1.7 | 6.7
| 2014-12-30 16:00 | 0.4 | 1.7 | 6.7
| 2014-12-30 16:30 | 0.2 | 1.7 | 6.7
| 2014-12-30 17:00 | 0.2 | 1.7 | 6.7
| 2014-12-30 17:30 | 0.2 | 1.7 | 6.7
| 2014-12-30 18:00 | 0.2 | 1.7 | 6.7
| 2014-12-30 18:30 | 0.2 | 1.7 | 6.7
| 2014-12-30 19:00 | 0.1 | 1.7 | 6.7
| 2014-12-30 19:30 | 0.2 | 1.7 | 6.7
| 2014-12-30 20:00 | 0.1 | 1.7 | 6.7
| 2014-12-30 20:30 | -0.1 | 1.7 | 6.7
| 2014-12-30 21:00 | -0.1 | 1.7 | 6.7
| 2014-12-30 21:30 | -0.2 | 1.7 | 6.7
| 2014-12-30 22:00 | -0.2 | 1.7 | 6.7
| 2014-12-30 22:30 | 0.1 | 1.7 | 6.7
| 2014-12-30 23:00 | 0.1 | 1.7 | 6.7
| 2014-12-30 23:30 | 0 | 1.7 | 6.7
| 2014-12-31 | 0.2 | 1.7 | 6.7
| 2014-12-31 00:30 | 0.1 | 1.7 | 6.7
| 2014-12-31 01:00 | 0.2 | 1.7 | 6.7
| 2014-12-31 01:30 | 0.3 | 1.7 | 6.7
| 2014-12-31 02:00 | 0.3 | 1.7 | 6.1
| 2014-12-31 02:30 | 0.3 | 1.7 | 6.1
| 2014-12-31 03:00 | 0.4 | 1.7 | 6.1
| 2014-12-31 03:30 | 0.4 | 1.7 | 6.1
| 2014-12-31 04:00 | 0.3 | 1.7 | 6.1
| 2014-12-31 04:30 | 0.4 | 2.2 | 6.1
| 2014-12-31 05:00 | 0.4 | 2.2 | 6.1
| 2014-12-31 05:30 | 0.4 | 2.2 | 6.1
| 2014-12-31 06:00 | 0.5 | 2.2 | 6.1
| 2014-12-31 06:30 | 0.6 | 2.2 | 6.1
| 2014-12-31 07:00 | 0.6 | 2.2 | 6.1
| 2014-12-31 07:30 | 0.7 | 2.2 | 6.1
| 2014-12-31 08:00 | 0.7 | 2.2 | 6.1
| 2014-12-31 08:30 | 0.8 | 2.2 | 6.1
| 2014-12-31 09:00 | 0.8 | 2.2 | 6.1
| 2014-12-31 09:30 | 0.8 | 2.2 | 6.1
| 2014-12-31 10:00 | 0.8 | 2.2 | 6.1
| 2014-12-31 10:30 | 0.9 | 2.2 | 6.1
| 2014-12-31 11:00 | 1.1 | 2.2 | 6.1
| 2014-12-31 11:30 | 1.1 | 2.2 | 6.1
| 2014-12-31 12:00 | 1.2 | 2.2 | 6.1
| 2014-12-31 12:30 | 1.2 | 2.2 | 6.1
| 2014-12-31 13:00 | 1.3 | 2.2 | 6.1
| 2014-12-31 13:30 | 1.4 | 2.2 | 6.1
| 2014-12-31 14:00 | 1.5 | 2.2 | 6.1
| 2014-12-31 14:30 | 1.5 | 2.2 | 6.1
| 2014-12-31 15:00 | 1.5 | 2.2 | 6.1
| 2014-12-31 15:30 | 1.5 | 2.2 | 6.1
| 2014-12-31 16:00 | 1.4 | 2.2 | 6.1
| 2014-12-31 16:30 | 1.3 | 2.2 | 6.1
| 2014-12-31 17:00 | 1.2 | 2.2 | 6.1
| 2014-12-31 17:30 | 1.2 | 2.2 | 6.1
| 2014-12-31 18:00 | 1.1 | 2.2 | 6.1
| 2014-12-31 18:30 | 1.1 | 2.2 | 6.1
| 2014-12-31 19:00 | 0.9 | 2.2 | 6.1
| 2014-12-31 19:30 | 0.9 | 2.2 | 6.1
| 2014-12-31 20:00 | 0.8 | 2.2 | 6.1
| 2014-12-31 20:30 | 0.9 | 2.2 | 6.1
| 2014-12-31 21:00 | 0.9 | 2.2 | 6.1
| 2014-12-31 21:30 | 0.9 | 2.2 | 6.1
| 2014-12-31 22:00 | 0.9 | 2.2 | 6.1
| 2014-12-31 22:30 | 1 | 2.2 | 6.1
| 2014-12-31 23:00 | 1 | 2.2 | 6.1
| 2014-12-31 23:30 | 0.9 | 2.2 | 6.1